H106.1.1 Internally illuminated signs. | Wiring for electric lighting shall be entirely enclosed in the sign cabinet with a clearance of not less than 2 inches (51 mm) from the facing material. | H106.1.1 Internally illuminated signs. | Except as provided for in Section 2611, where internally illuminated signs have facings of wood or of approved plastic complying with the requirements of Section 2606.4, the area of such facing section shall be not more than 120 square feet (11.16 m2) and the wiring for electric lighting shall be entirely enclosed in the sign cabinet with a clearance of not less than 2 inches (51 mm) from the facing material. The dimensional limitation of 120 square feet (11.16 m2) shall not apply to sign facing sections made from flame-resistant-coated fabric (ordinarily known as “flexible sign face plastic”) that weighs less than 20 ounces per square yard (678 g/m2) and that, when tested in accordance with NFPA 701, meets the fire propagation performance requirements of both Test 1 and Test 2 or that, when tested in accordance with an approved test method, exhibits an average burn time of 2 seconds or less and a burning extent of 5.9 inches (150 mm) or less for 10 specimens.
H106.2 Electrical service. | Signs that require electrical service shall comply with the New York City Electrical Code. | H106.2 Electrical service. | Signs that require electrical service shall comply with NFPA 70.
H107.1 Use of combustibles. | In all signs required to be constructed of noncombustible materials pursuant to the provi­sions of Sections H109 through H116, the following materials may be used for moldings, cappings, nailing blocks, letters and latticing, or other purely ornamental features of signs, unless otherwise directed by the commissioner: wood, approved plastic or plastic veneer panels as provided for in Chapter 26 of this code, or other materials of combustible characteristics similar to wood. | H107.1 Use of combustibles. | Wood, plastics complying with the requirements of Section H107.1.1 or plastic veneer panels as provided for in Chapter 26, or other materials of combustible characteristics similar to wood, used for moldings, cappings, nailing blocks, letters and latticing, shall comply with Section H109.1 and shall not be used for other ornamental features of signs, unless approved.
H106.3 Material limitations. | All sign structures for signs requiring electric service shall be constructed of noncombustible materials, except as permitted by Section H107.
H106.4 Projecting reflectors. | Lighting reflectors may project beyond the top or face of all signs provided that every part of such reflector is at least 10 feet (3048 mm) above the ground or sidewalk level. Reflectors shall be constructed, attached, and maintained so that they shall not be, or become, a hazard to the public.
H107.1.1 Approved plastic materials. | Plastic materials which burn at a rate no faster than 2.5 inches per minute (64 mm/s) when tested in accordance with ASTM D 635 shall be deemed approved plastics and can be used as the display surface material and for the letters, decorations and facings on signs, subject to the area limitations of Sections H107.1.2 through H107.1.3.
H107.1.2 Plastic area limitations for internally illuminated signs. | Except as provided for in Sections 402.14 and 2611 of this code, approved plastic used on the display surface of internally illuminated signs shall be permitted up to 200 square feet (18.6 m2) in area on signs required to be of noncombustible construction and on signs permitted to be of combustible construction.
H108.1 Fail-safe device. | Signs that contain moving sections or ornaments shall have fail-safe provisions to prevent the section or ornament from releasing and falling or shifting its center of gravity more than 15 inches (381 mm). The fail-safe device shall be in addition to the mechanism and the mechanism’s housing that operate the movable section or ornament. The fail-safe device shall be capable of supporting the full dead weight of the section or ornament when the moving mechanism releases. | H108.1 Fail-safe device. | Signs that contain moving sections or ornaments shall have fail-safe provisions to prevent the section or ornament from releasing and falling or shifting its center of gravity more than 15 inches (381 mm). The fail-safe device shall be in addition to the mechanism and the mechanism’s housing that operate the movable section or ornament. The fail-safe device shall be capable of supporting the full dead weight of the section or ornament when the moving mechanism releases.
H107.1.3 Plastic area limitations for all other signs. | Approved plastic used on the display surface of ground signs, walls signs, roof signs, projecting signs, and marquee signs shall be limited in area as provided by Sections H107.1.3.1 through H107.1.3.4.
H107.1.3.1 Plastic area limitations on noncombustible ground signs and wall signs. | On ground signs and wall signs required to be constructed of noncombustible materials, if the display surface does not exceed 150 square feet (13.9 m2), the entire display sur­face shall be permitted to be covered by approved plastic. If the area of a display surface exceeds 150 square feet (13.9 m2), the area occupied or covered by approved plastics shall be limited to 150 square feet (13.9 m2) plus 50 percent of the difference between 150 square feet (13.9 m2) and the total area of display surface. The area of plastic on a display surface shall not in any case exceed 1,050 square feet (97.5 m2), unless approved by the com­missioner.
H109.2 Required clearance. | The bottom coping of every ground sign shall be not less than 3 feet (914 mm) above the ground or street level, which space can be filled with platform decorative trim or light wooden construction. | H109.2 Required clearance. | The bottom coping of every ground sign shall be not less than 3 feet (914 mm) above the ground or street level, which space can be filled with platform decorative trim or light wooden construction.
H107.1.3.2 Plastic area limitations on combustible ground signs and wall signs. | On ground signs and wall signs permitted to be constructed of combustible materi­als, if the display surface does not exceed 300 square feet (27.9 m2), 50 percent of the display surface shall be per­mitted to be covered by approved plastic. If the area of a display surface exceeds 300 square feet (27.9 m2), the area occupied or covered by approved plastics shall be limited to 150 square feet (13.9 m2) plus 25 percent of the difference between 150 square feet (13.9 m2) and the total area of display surface. The area of plastic on a dis­play surface shall not in any case exceed 575 square feet (53.4 m2), unless approved by the commissioner.
H109.3 Wood anchors and supports. | Where wood anchors or supports are embedded in the soil, the wood shall be pressure treated with an approved preservative. | H109.3 Wood anchors and supports. | Where wood anchors or supports are embedded in the soil, the wood shall be pressure treated with an approved preservative.
H107.1.3.3 Plastic area limitations on noncombustible roof signs, projecting signs, and marquee signs. | On roof signs, projecting signs, and marquee signs required to be constructed of noncombustible materials, if the display surface does not exceed 150 square feet (13.9 m2), the entire display sur­face shall be permitted to be covered by approved plastic. If the area of a display surface exceeds 150 square feet (13.9 m2), the area occupied or covered by approved plastics shall be limited to 150 square feet (13.9 m2) plus 25 percent of the difference between 150 square feet (13.9 m2) and the total area of display surface. The area of plastic on a display surface shall not in any case exceed 575 square feet (53.4 m2), unless approved by the com­missioner.
H107.1.3.4 Plastic area limitations on combustible roof signs. | On roof signs permitted to be constructed of combustible materials, if the display surface does not exceed 1,000 square feet (92.9 m2), 25 percent of the dis­play surface shall be permitted to be covered by approved plastic. If the area of a display surface exceeds 1,000 square feet (92.9 m2), the area occupied or covered by approved plastics shall be limited to 250 square feet (23.2 m2) plus 10 percent of the difference between 250 square feet (23.2 m2) and the total area of display surface. The area of plastic on a display surface shall not in any case exceed 350 square feet (32.5 m2), unless approved by the commissioner.
H107.2 Glass panels. | Glass panels used in display areas of signs shall be designed in accordance with Chapter 24 of this code.
H109.1 Materials. | Ground signs erected inside the fire dis­tricts shall be constructed entirely of noncombustible materials and the facings of such signs shall be of noncombustible mate­rials, except as permitted by Section H107. Outside the fire dis­tricts, the structure of ground signs exceeding 25 feet (7620 mm) in height above grade or exceeding 2500 square feet (232 m2) in display area shall be constructed of noncombustible materials, and the facing of such signs shall be noncombustible, except as permitted by Section H107.
H111.1 Materials. | Wall signs erected inside the fire districts shall be constructed entirely of noncombustible materials, and the facings of such signs shall be of noncombustible materials, except as permitted by Section H107. Outside of the fire dis­tricts, the structure of wall signs exceeding 500 square feet (46 m2) in display area shall be constructed of noncombustible materials, and the facings of such signs shall be of noncombustible materials, except as permitted in Section H107. | H111.1 Materials. | Wall signs that have an area exceeding 40 square feet (3.72 m2) shall be constructed of metal or other approved noncombustible material, except for nailing rails and as provided for in Sections H106.1.1 and H107.1.
H111.2 Exterior wall mounting details. | Wall signs attached to exterior walls of solid masonry, concrete or stone shall be safely and securely attached by means of metal anchors, bolts or expansion screws of not less than 3/8 inch (9.5 mm) diameter and shall be embedded at least 5 inches (127 mm). Wood blocks shall not be used for anchorage, except in the case of wall signs attached to buildings with walls of wood. A wall sign shall not be supported by anchorages secured to an unbraced parapet wall. | H111.2 Exterior wall mounting details. | Wall signs attached to exterior walls of solid masonry, concrete or stone shall be safely and securely attached by means of metal anchors, bolts or expansion screws of not less than 3/8 inch (9.5 mm) diameter and shall be embedded not less than 5 inches (127 mm). Wood blocks shall not be used for anchorage, except in the case of wall signs attached to buildings with walls of wood. A wall sign shall not be supported by anchorages secured to an unbraced parapet wall.
H110.1 Materials. | Roof signs erected inside the fire districts shall be constructed entirely of noncombustible materials and the facings of such signs shall be of noncombustible materials, except as permitted by Section H107. Outside of the fire dis­tricts, the structure of roof signs exceeding 65 feet (19 812 mm) in height above grade, or exceeding 1500 square feet (139 m2) in display area, shall be constructed of noncombustible materi­als and the facings of such signs shall be of noncombustible materials, except as permitted by Section H107.
H111.3 Extension. | Wall signs shall not extend above the top of the wall, nor beyond the ends of the wall to which the signs are attached unless such signs conform to the requirements for roof signs, projecting signs or ground signs. | H111.3 Extension. | Wall signs shall not extend above the top of the wall or beyond the ends of the wall to which the signs are attached unless such signs conform to the requirements for roof signs, projecting signs or ground signs.
H110.2 Required clearance. | Roof signs shall be constructed so as to provide a clear space of at least 7 feet (2134 mm) between the roof and the lowest part of the sign and at least 5 feet (1524 mm) between the vertical supports thereof.
H110.3 Location. | Roof signs shall be set back a minimum of 6 feet (1829 mm) from the face of the walls of the building on which they are erected.
H110.4 Bearing plates. | The bearing plates of roof signs shall distribute the load directly to or upon masonry walls, steel roof girders, columns or beams. The building shall be designed to avoid overstress of these members.
H112.3 Wall mounting details. | Chains, cables, guys or steel rods used to support the live or dead load of projecting signs are permitted to be fastened to solid masonry walls with expansion bolts or by machine screws in iron supports, but such supports shall not be attached to an unbraced parapet wall. Where the supports must be fastened to walls made of wood, the supporting anchor bolts must go through the wall and be plated or fas­tened on the inside in a secure manner. | H112.3 Wall mounting details. | Chains, cables, guys or steel rods used to support the live or dead load of projecting signs are permitted to be fastened to solid masonry walls with expansion bolts or by machine screws in iron supports, but such supports shall not be attached to an unbraced parapet wall. Where the supports must be fastened to walls made of wood, the supporting anchor bolts must go through the wall and be plated or fastened on the inside in a secure manner.
H110.5 Reserved.
H112.4 Height limitation. | A projecting sign shall not be erected on the wall of any building so as to project above the roof or cornice wall or above the roof level where there is no cornice wall; except that a sign erected at a right angle to the building, the horizontal width of which sign is perpendicular to such a wall and does not exceed 24 inches (610 mm), is permit­ted to be erected to a height not exceeding 5 feet (1524 mm) above the roof or cornice wall or above the roof level where there is no cornice wall. A sign attached to a corner of a building and parallel to the vertical line of such corner shall be deemed to be erected at a right angle to the building wall. | H112.4 Height limitation. | A projecting sign shall not be erected on the wall of any building so as to project above the roof or cornice wall or, on buildings without a cornice wall, above the roof level except that a sign erected at a right angle to the building, the horizontal width of which sign is perpendicular to such a wall and does not exceed 18 inches (457 mm), is permitted to be erected to a height not exceeding 2 feet (610 mm) above the roof or cornice wall or above the roof level where there is no cornice wall. A sign attached to a corner of a building and parallel to the vertical line of such corner shall be deemed to be erected at a right angle to the building wall.
H112.5 Additional loads. | Projecting sign structures which will be used to support an individual on a ladder or other servicing device, whether or not specifically designed for the servic­ing device, shall be capable of supporting the anticipated additional load, but not less than a 100-pound (445 N) concen­trated horizontal load and a 300-pound (1334 N) concentrated vertical load applied at the point of assumed or most eccentric loading. The building component to which the projecting sign is attached shall also be designed to support the additional loads. | H112.5 Additional loads. | Projecting sign structures that will be used to support an individual on a ladder or other servicing device, whether or not specifically designed for the servicing device, shall be capable of supporting the anticipated additional load, but not less than a 100-pound (445 N) concentrated horizontal load and a 300-pound (1334 N) concentrated vertical load applied at the point of assumed or most eccentric loading. The building component to which the projecting sign is attached shall be designed to support the additional loads.
H112.1 Materials. | Projecting signs shall be constructed entirely of noncombustible materials, and the facings of such signs shall be of noncombustible materials, except as permitted by Section H107.
H112.2 Attachment. | Projecting signs shall be securely attached to a building or structure by metal supports such as bolts, anchors, chains, guys or steel rods. Supports shall be secured to a bolt or expansion screw that will develop the strength of the supporting chains, guys or steel rods, with a minimum ⅝-inch (15.9 mm) bolt or lag screw, by an expansion shield. Turn buckles shall be placed in chains, guys or steel rods supporting projecting signs. Staples or nails shall not be used to secure any projecting sign to any building or structure. The dead load of projecting signs not parallel to the building or structure and the load due to wind pressure shall be supported with chains, guys or steel rods having net cross-sectional dimension of not less than ⅜-inch (9.5 mm) diameter. Such supports shall be erected or maintained at an angle of at least 45 degrees (0.78 rad) from the horizontal to resist the dead load and at angle of 45 degrees (0.78 rad) or more with the face of the sign to resist the specified wind pressure. If such projecting sign exceeds 30 square feet (2.8 m2) in one facial area, there shall be provided at least two such supports on each side not more than 8 feet (2438 mm) apart to resist the wind pressure.
H112.6 Thickness. | Projecting signs shall be limited in thickness as provided for in Table H112.6.
H112.7 Location restrictions. | Projecting signs shall not be erected on buildings located on those streets and avenues listed in Section 3202.2.1.8.
H113.1 Materials. | Marquee signs shall be constructed entirely of noncombustible materials, and the facings of such signs shall be of noncombustible materials, except as provided for in Section H107. | H113.1 Materials. | Marquee signs shall be constructed entirely of metal or other approved noncombustible material except as provided for in Sections H106.1.1 and H107.1.
H113.2 Attachment. | Marquee signs shall be attached to approved marquees that are constructed in accordance with Section 3106 of this code and shall be anchored in confor­mance with the requirements for projecting signs under Section H112. | H113.2 Attachment. | Marquee signs shall be attached to approved marquees that are constructed in accordance with Section 3106.
H113.3 Extension. | No part of a marquee sign shall project above or below the marquee fascia, or beyond the perimeter of the marquee.
H113.4 Location restrictions. | Marquee signs erected on mar­quees projecting beyond the street line shall be limited to those occupancy groups and locations provided by Section 3202.2.1.4.5 of this code.
H114.1 General. | The provisions of this section shall apply to flexible fabric signs and flexible fabric sign structures, includ­ing the fabric display area, the restraining framework, and all stiffening and fastening devices. | H114.1 General. | Portable signs shall conform to requirements for ground, roof, projecting, flat and temporary signs where such signs are used in a similar capacity. The requirements of this section shall not be construed to require portable signs to have connections to surfaces, tie-downs or foundations where provisions are made by temporary means or configuration of the structure to provide stability for the expected duration of the installation.
H114.2 Materials. | Fabric used in flexible fabric signs shall be flame resistant in accordance with NFPA 701 or listed under UL 214.
H114.2.1 Longevity. | The same fabric shall not be used for longer than a 12-month period. The same fabric may be relocated and re-erected within that 12-month period, but in no case shall re-inking of fabrics be permitted.
H114.2.2 Affidavit. | Prior to installation of a flexible fabric sign, an affidavit shall be submitted to the Department in which the sign graphic producer shall attest that the sign was made from noncombustible fabric, flame-resistant fabric tested in accordance with NFPA 701 by a nationally recognized testing entity, or fabric bearing a UL classification mark obtained from the manufacturer of the fabric.
H114.2.3 Identification. | The additional requirements set forth in Sections H114.2.3.1 through H114.2.3.2 shall apply:
H114.2.3.1 UL classification decal. | All signs shall bear a decal bearing the UL classification mark or name of the testing entity and its listing number, on a corner of the face of the fabric. This decal shall be of color(s) contrasting with those of the background of the display, and shall be readable from street or roadway level with the aid of binoculars.
H114.2.3.2 Date of sign erection. | All signs shall bear a decal identifying the date of erection of the flexible sign structure on a corner of the face of the sign fabric. This decal shall be of color(s) contrasting with those of the background of the display, and shall be readable from street or roadway level with the aid of binoculars. If the same fabric is relocated, the existing decal shall remain, and a new decal stating the re-erection date shall be affixed.
H114.2.4 Limitations. | When erected on walls, flexible fab­ric signs exceeding 500 square feet (46.5 m2) in area shall be of the open weave type, unless backed by means of a wall sign or projecting sign structure supported as provided by Sections H111 and H112.
H114.3 Attachment to exterior walls. | A flexible fabric sign attached to an exterior wall shall be attached in accordance with this section. The sign fabric shall not be placed in front of doors, windows, glass blocks, louvers, grilles, fire escapes, exterior stairs, balconies, marquees, wall recesses or projections unless backed by a wall sign or a pro­jecting sign structure as provided by Sections H111 and H112.
H114.3.1 Load spreader bars. | Load spreader bars com­prised of noncombustible materials must be inserted around the entire perimeter of the fabric display area into pockets that are either woven, or heat-welded and stitched seamed. The load spreader bars shall be provided with rounded edges to prevent tearing of the fabric.
H114.3.2 Spring snaps. | As an alternate to load spreader bars, the side hems of the fabric may be equipped with grommets to receive spring snaps. The applicant shall determine the appropriate spacing of grommets. The sides of fab­ric display areas equipped with grommets may be secured with spring snaps to vertical steel wire rope in lieu of restraining angles. The vertical steel wire rope shall be anchored to the wall or other mounting surface by means of eyebolts spaced at intervals to be determined by the appli­cant. The ends of the vertical steel wire rope shall be restrained by means of turnbuckles or “J” hooks secured to metal angles.
H114.3.3 Fasteners. | Fasteners shall consist of “J” hooks secured with lock nuts or double nuts to continuous metal restraining angles around the perimeter of the display area. The “J” hooks shall extend through holes in the load spreader bars. The ends of the “J” hooks shall be secured with either safety clips or nuts in order to prevent accidental dislodging of the load spreader bars. In lieu of “J” hooks and restraining angles, the load spreader bars in the pockets along the top edge of the fabric display area may be bolted to steel flat bars.
H114.3.3.1 Metal restraining angles and bars. | For all flexible sign structures, the metal angles and/or steel flat bars shall be secured to the wall or other mounting sur­face. Angles and/or bars shall not be secured to any para­pet or wall unless the applicant has determined that the parapet or wall is capable of resisting the loads imposed on it by the flexible sign structure. Unsatisfactory para­pets or walls shall be braced or otherwise reinforced as determined by the applicant, prior to the erection of the flexible sign structure. A wall sign, projecting sign, roof sign or ground sign structure must be capable of resisting the loads imposed on it by the flexible sign structure.
H114.3.4 Tensioning. | Initial tension may be applied mechanically to the fabric display area, but it shall be held in final position by adjusting or tightening the turnbuckles, or the nuts holding the “J” hooks to the restraining angles. Mechanical tensioning devices may not remain attached to the flexible sign, except as permitted by Section H114.4.
H114.4 Attachment to sign structures. | Fabric stretched around any edge of a sign structure shall be protected from any sharp edge that may cut or tear the fabric. The perimeter of the fabric located on the front or rear of a sign structure shall be secured as required by Section H114.3, except that the “J” hooks may be secured directly to the sign structure.
H114.4.1 Tensioning devices. | Opposing ends of a fabric sign stretched around the edges of a sign structure may be secured to each other by means of mechanical tensioning devices behind the sign structure, provided that the open ends for the “S” hooks shall be closed with safety clips. Spring snaps may be used in lieu of “S” hooks. The mechan­ical tensioning devices shall be fastened to safety wires, placed through the holes in the load spreader bars or grom­mets, to prevent the devices from falling in the event of loss of tension.
H114.4.2 Limitations. | The length of the fabric or safety wire perpendicular to any edge of the sign structure shall be dimensioned such that in the event of failure of any part of the flexible sign structure, no load spreader bars, mechani­cal tensioning devices, clamps, or wires will strike any nearby doors, windows, vents, chimneys, grilles, skylights, light fixtures, decorations or other wall appurtenances, or mechanical equipment, nor shall any load spreader bar fall within 10 feet (3048 mm) of grade.
H115.1 General. | Portable signs shall conform to requirements for ground, roof, projecting, flat and temporary signs where such signs are used in a similar capacity. The requirements of this section shall not be construed to require portable signs to have connections to surfaces, tie-downs or foundations where provisions are made by temporary means or configuration of the structure to provide stability for the expected duration of the installation. | H115.1 General. | Tables H115.1(1) and H115.1(2) provide requirements for the size, thicknesses and types of glass panels and projection signs, respectively.
H116.1 Materials. | Temporary signs less than 500 square feet (46.5 m2) in display area may be constructed of combustible materials. Temporary sign structures, with display area greater than 100 square feet (9.3 m2), shall be constructed of rigid materials with rigid frames.
H116.2 Attachment. | Temporary signs shall be securely attached to the sign structure.
H116.3 Duration. | Temporary signs shall be removed no later than 30 days after erection or as soon as such sign is torn or damaged.
H116.4 Limitations. | Temporary signs constructed of com­bustible materials shall not extend more than 12 inches (305 mm) over, or into, a street.
H117.1 General. | This section lists the standards that are referenced in various sections of this appendix. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title and the section or sections of this document that reference the standard.
H117.2 Subsequent additions, modifications or deletions. | Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to these standards in accordance with Section 28-103.19 of the Administrative Code.
H117.3 Applicability. | The application of the referenced standards shall be as specified in Section 102.4.
H117.4 Standards.
|  | H102.1 General. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein. Refer to Chapter 2 of this code for general definitions.
|  | H107.1.1 Plastic materials. | Notwithstanding any other provisions of this code, plastics that burn at a rate not faster than 2.5 inches per minute (64 mm/s) when tested in accordance with ASTM D635 shall be approved for use as the display surface material and for the letters, decorations and facings on signs and outdoor display structures.
|  | H107.1.2 Electric sign faces. | Individual plastic facings of electric signs shall not exceed 200 square feet (18.6 m2) in area.
|  | H107.1.3 Area limitation. | If the area of a display surface exceeds 200 square feet (18.6 m2), the area occupied or covered by plastics complying with the requirements of Section H107.1.1 shall be limited to 200 square feet (18.6 m2) plus 50 percent of the difference between 200 square feet (18.6 m2) and the area of display surface. The area of plastic on a display surface shall not in any case exceed 1,100 square feet (102 m2).
|  | H107.1.4 Plastic appurtenances. | Letters and decorations mounted on a plastic facing or display surface can be made of plastics complying with the requirements of Section H107.1.1.
|  | H109.1 Height restrictions. | The structural frame of ground signs shall not be erected of combustible materials to a height of more than 35 feet (10 668 mm) above the ground. Ground signs constructed entirely of noncombustible material shall not be erected to a height of greater than 100 feet (30 480 mm) above the ground. Greater heights are permitted where approved and located so as not to create a hazard or danger to the public.
|  | H110.1 General. | Roof signs shall be constructed entirely of metal or other approved noncombustible material except as provided for in Sections H106.1.1 and H107.1. Provisions shall be made for electric grounding of metallic parts. Where combustible materials are permitted in letters or other ornamental features, wiring and tubing shall be kept free and insulated therefrom. Roof signs shall be so constructed as to leave a clear space of not less than 6 feet (1829 mm) between the roof level and the lowest part of the sign and shall have not less than 5 feet (1524 mm) clearance between the vertical supports thereof. Roof sign structures shall not project beyond an exterior wall.
|  | H110.2 Bearing plates. | The bearing plates of roof signs shall distribute the load directly to or on masonry walls, steel roof girders, columns or beams. The building shall be designed to avoid overstress of these members.
|  | H110.3 Height of solid signs. | A roof sign having a solid surface shall not exceed, at any point, a height of 24 feet (7315 mm) measured from the roof surface.
|  | H110.4 Height of open signs. | Open roof signs in which the uniform open area is not less than 40 percent of total gross area shall not exceed a height of 75 feet (22 860 mm) on buildings of Type 1 or Type 2 construction. On buildings of other construction types, the height shall not exceed 40 feet (12 192 mm). Such signs shall be thoroughly secured to the building on which they are installed, erected or constructed by iron, metal anchors, bolts, supports, chains, stranded cables, steel rods or braces and they shall be maintained in good condition.
|  | H110.5 Height of closed signs. | A closed roof sign shall not be erected to a height greater than 50 feet (15 240 mm) above the roof of buildings of Type 1 or 2 construction or more than 35 feet (10 668 mm) above the roof of buildings of Type 3, 4 or 5 construction.
|  | H112.1 General. | Projecting signs shall be constructed entirely of metal or other noncombustible material and securely attached to a building or structure by metal supports such as bolts, anchors, supports, chains, guys or steel rods. Staples or nails shall not be used to secure any projecting sign to any building or structure. The dead load of projecting signs not parallel to the building or structure and the load due to wind pressure shall be supported with chains, guys or steel rods having net cross-sectional dimension of not less than 3/8 inch (9.5 mm) diameter. Such supports shall be erected or maintained at an angle of not less than 45 percent (0.78 rad) with the horizontal to resist the dead load and at angle of 45 percent (0.78 rad) or more with the face of the sign to resist the specified wind pressure. If such projecting sign exceeds 30 square feet (2.8 m2) in one facial area, there shall be provided not fewer than two such supports on each side not more than 8 feet (2438 mm) apart to resist the wind pressure.
|  | H112.2 Attachment of supports. | Supports shall be secured to a bolt or expansion screw that will develop the strength of the supporting chains, guys or steel rods, with a minimum 5/8-inch (15.9 mm) bolt or lag screw, by an expansion shield. Turnbuckles shall be placed in chains, guys or steel rods supporting projecting signs.
|  | H113.3 Dimensions. | Marquee signs, whether on the front or side, shall not project beyond the perimeter of the marquee.
|  | H113.4 Height limitation. | Marquee signs shall not extend more than 6 feet (1829 mm) above, or 1 foot (305 mm) below such marquee. Signs shall not have a vertical dimension greater than 8 feet (2438 mm).
|  | H116.1 General. | ​ See Table H115.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard. ​

## BC-I
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | I101.1 General. | Patio covers shall be permitted to be detached from or attached to dwelling units. Patio covers shall be used only for recreational, outdoor living purposes and not as carports, garages, storage rooms or habitable rooms.
|  | I102.1 General. | The following term shall, for the purposes of this appendix, have the meaning shown herein. Refer to Chapter 2 of this code for general definitions.
|  | I103.1 Enclosure walls. | Enclosure walls shall be permitted to be of any configuration, provided that the open or glazed area of the longer wall and one additional wall is equal to not less than 65 percent of the area below not less than 6 feet 8 inches (2032 mm) of each wall, measured from the floor. Openings shall be permitted to be enclosed with insect screening, translucent or transparent plastic conforming to the provisions of Sections 2606 through 2610, glass conforming to the provisions of Chapter 24 or any combination of the foregoing.
|  | I103.2 Light, ventilation and emergency egress. | Exterior openings of the dwelling unit required for light and ventilation shall be permitted to open into a patio structure. However, the patio structure shall be unenclosed if such openings are serving as emergency egress or rescue openings from sleeping rooms. Where such exterior openings serve as an exit from the dwelling unit, the patio structure, unless unenclosed, shall be provided with exits conforming to the provisions of Chapter 10.
|  | I104.1 Height. | Patio covers shall be limited to one-story structures not more than 12 feet (3657 mm) in height.
|  | I105.1 Design loads. | Patio covers shall be designed and constructed to sustain, within the stress limits of this code, all dead loads plus a minimum vertical live load of 10 pounds per square foot (0.48 kN/m2) except that snow loads shall be used where such snow loads exceed this minimum. Such patio covers shall be designed to resist the minimum wind and seismic loads set forth in this code.
|  | I105.2 Footings. | In areas with a frost depth of zero, a patio cover shall be permitted to be supported on a concrete slab on grade without footings, provided that the slab conforms to the provisions of Chapter 19 of this code and is not less than 31/2 inches (89 mm) thick, and the columns do not support loads in excess of 750 pounds (3.36 kN) per column.
IDENTIFICATION
In all signs permitted to be constructed of combustible materials pursuant to the provisions of Sections H107 through H116, wood and other materials of combustible characteristics similar to wood shall be permitted, pursuant to the provisions of Sections H109 through H116, on the display surface without limit, except that approved plastic shall be limited in area by the provisions of Section H107. | 1.3.

## BC-J
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | J101.1 Scope. | The provisions of this chapter apply to grading, excavation and earthwork construction, including fills and embankments. Where conflicts occur between the technical requirements of this chapter and the geotechnical report, the geotechnical report shall govern.
|  | J101.2 Flood hazard areas. | Unless the applicant has submitted an engineering analysis, prepared in accordance with standard engineering practice by a registered design professional, that demonstrates the proposed work will not result in any increase in the level of the base flood, grading, excavation and earthwork construction, including fills and embankments, shall not be permitted in floodways that are in flood hazard areas established in Section 1612.3 or in flood hazard areas where design flood elevations are specified but floodways have not been designated.
|  | J102.1 Definitions. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein. Refer to Chapter 2 of this code for general definitions.
|  | J103.1 Permits required. | Except as exempted in Section J103.2, grading shall not be performed without first having obtained a permit therefor from the building official. A grading permit does not include the construction of retaining walls or other structures.
|  | J103.2 Exemptions. | A grading permit shall not be required for the following:
|  | J104.1 Submittal requirements. | In addition to the provisions of Section 105.3, the applicant shall state the estimated quantities of excavation and fill.
|  | J104.2 Site plan requirements. | In addition to the provisions of Section 107, a grading plan shall show the existing grade and finished grade in contour intervals of sufficient clarity to indicate the nature and extent of the work and show in detail that it complies with the requirements of this code. The plans shall show the existing grade on adjoining properties in sufficient detail to identify how grade changes will conform to the requirements of this code.
|  | J104.3 Geotechnical report. | A geotechnical report prepared by a registered design professional shall be provided. The report shall contain not less than the following:
|  | J104.4 Liquefaction study. | For sites with mapped maximum considered earthquake spectral response accelerations at short periods (Ss) greater than 0.5g as determined by Section 1613, a study of the liquefaction potential of the site shall be provided and the recommendations incorporated in the plans.
|  | J105.1 General. | Inspections shall be governed by Section 110 of this code.
|  | J105.2 Special inspections. | The special inspection requirements of Section 1705.6 shall apply to work performed under a grading permit where required by the building official.
|  | J106.1 Maximum slope. | The slope of cut surfaces shall be not steeper than is safe for the intended use, and shall be not more than one unit vertical in two units horizontal (50-percent slope) unless the owner or the owner’s authorized agent furnishes a geotechnical report justifying a steeper slope.
|  | J107.1 General. | Unless otherwise recommended in the geotechnical report, fills shall comply with the provisions of this section.
|  | J107.2 Surface preparation. | The ground surface shall be prepared to receive fill by removing vegetation, topsoil and other unsuitable materials, and scarifying the ground to provide a bond with the fill material.
|  | J107.3 Benching. | Where existing grade is at a slope steeper than one unit vertical in five units horizontal (20-percent slope) and the depth of the fill exceeds 5 feet (1524 mm) benching shall be provided in accordance with Figure J107.3. A key shall be provided that is not less than 10 feet (3048 mm) in width and 2 feet (610 mm) in depth.
|  | J107.4 Fill material. | Fill material shall not include organic, frozen or other deleterious materials. Rock or similar irreducible material greater than 12 inches (305 mm) in any dimension shall not be included in fills.
|  | J107.5 Compaction. | All fill material shall be compacted to 90 percent of maximum density as determined by ASTM D1557, Modified Proctor, in lifts not exceeding 12 inches (305 mm) in depth.
|  | J107.6 Maximum slope. | The slope of fill surfaces shall be not steeper than is safe for the intended use. Fill slopes steeper than one unit vertical in two units horizontal (50-percent slope) shall be justified by a geotechnical report or engineering data.
|  | J108.1 General. | Cut and fill slopes shall be set back from the property lines in accordance with this section. Setback dimensions shall be measured perpendicular to the property line and shall be as shown in Figure J108.1, unless substantiating data is submitted justifying reduced setbacks.
|  | J108.2 Top of slope. | The setback at the top of a cut slope shall be not less than that shown in Figure J108.1, or than is required to accommodate any required interceptor drains, whichever is greater.
|  | J108.3 Slope protection. | Where required to protect adjacent properties at the toe of a slope from adverse effects of the grading, additional protection, approved by the building official, shall be included. Examples of such protection include but are not be limited to:
|  | J109.1 General. | Unless otherwise recommended by a registered design professional, drainage facilities and terracing shall be provided in accordance with the requirements of this section.
|  | J109.2 Terraces. | Terraces not less than 6 feet (1829 mm) in width shall be established at not more than 30-foot (9144 mm) vertical intervals on all cut or fill slopes to control surface drainage and debris. Suitable access shall be provided to allow for cleaning and maintenance.
|  | J109.3 Interceptor drains. | Interceptor drains shall be installed along the top of cut slopes receiving drainage from a tributary width greater than 40 feet (12 192 mm), measured horizontally. They shall have a minimum depth of 1 foot (305 mm) and a minimum width of 3 feet (915 mm). The slope shall be approved by the building official, but shall be not less than one unit vertical in 50 units horizontal (2-percent slope). The drain shall be paved with concrete not less than 3 inches (76 mm) in thickness, or by other materials suitable to the application. Discharge from the drain shall be accomplished in a manner to prevent erosion and shall be approved by the building official.
|  | J109.4 Drainage across property lines. | Drainage across property lines shall not exceed that which existed prior to grading. Excess or concentrated drainage shall be contained on site or directed to an approved drainage facility. Erosion of the ground in the area of discharge shall be prevented by installation of nonerosive down drains or other devices.
|  | J110.1 General. | The faces of cut and fill slopes shall be prepared and maintained to control erosion. This control shall be permitted to consist of effective planting.
|  | J110.2 Other devices. | Where necessary, check dams, cribbing, riprap or other devices or methods shall be employed to control erosion and provide safety.
|  | J111.1 General. | ​ See Table J111.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard. ​

## BC-K
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
|  | K101.1 Purpose. | A purpose of this code is to establish minimum requirements to safeguard public health, safety and general welfare by regulating and controlling the design, construction, installation, quality of materials, location, operation and maintenance or use of electrical systems and equipment.
|  | K101.2 Scope. | This code applies to the design, construction, installation, alteration, repairs, relocation, replacement, addition to, use or maintenance of electrical systems and equipment.
|  | K102.1 General. | The provisions of this code apply to all matters affecting or relating to structures and premises, as set forth in Section K101.
|  | K102.2 Existing installations. | Except as otherwise provided for in this chapter, a provision in this code shall not require the removal, alteration or abandonment of, or prevent the continued utilization and maintenance of, existing electrical systems and equipment lawfully in existence at the time of the adoption of this code.
|  | K102.3 Maintenance. | Electrical systems, equipment, materials and appurtenances, both existing and new, and parts thereof shall be maintained in proper operating condition in accordance with the original design and in a safe, hazard-free condition. Devices or safeguards that are required by this code shall be maintained in compliance with the code edition under which installed. The owner or the owner’s authorized agent shall be responsible for the maintenance of the electrical systems and equipment. To determine compliance with this provision, the building official shall have the authority to require that the electrical systems and equipment be reinspected.
|  | K102.4 Additions, alterations and repairs. | Additions, alterations, renovations and repairs to electrical systems and equipment shall conform to that required for new electrical systems and equipment without requiring that the existing electrical systems or equipment comply with all of the requirements of this code. Additions, alterations and repairs shall not cause existing electrical systems or equipment to become unsafe, hazardous or overloaded.
|  | K102.5 Subjects not regulated by this code. | Where no applicable standards or requirements are set forth in this code, or are contained within other laws, codes, regulations, ordinances or bylaws adopted by the jurisdiction, compliance with applicable standards of nationally recognized standards as are approved shall be deemed as prima facie evidence of compliance with the intent of this code. Nothing herein shall derogate from the authority of the building official to determine compliance with codes or standards for those activities or installations within the building official’s jurisdiction or responsibility.
|  | K103.1 Types of permits. | An owner, authorized agent or contractor who desires to construct, enlarge, alter, repair, move, demolish or change the occupancy of a building or structure, or to erect, install, enlarge, alter, repair, remove, convert or replace electrical systems or equipment, the installation of which is regulated by this code, or to cause such work to be done, shall first make application to the building official and obtain the required permit for the work.
|  | K103.2 Work exempt from permit. | The following work shall be exempt from the requirement for a permit:
|  | K104.1 Information on construction documents. | Construction documents shall be drawn to scale upon suitable material. Electronic media documents are permitted to be submitted where approved by the building official. Construction documents shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that such work will conform to the provisions of this code and relevant laws, ordinances, rules and regulations, as determined by the building official.
|  | K104.2 Penetrations. | Construction documents shall indicate where penetrations will be made for electrical systems and shall indicate the materials and methods for maintaining required structural safety, fire-resistance rating and fireblocking.
|  | K104.3 Load calculations. | Where an addition or alteration is made to an existing electrical system, an electrical load calculation shall be prepared to determine if the existing electrical service has the capacity to serve the added load.
|  | K105.1 General. | The design, documentation, inspection, testing and approval of an alternative engineered design electrical system shall comply with this section.
|  | K105.2 Design criteria. | An alternative engineered design shall conform to the intent of the provisions of this code and shall provide an equivalent level of quality, strength, effectiveness, fire resistance, durability and safety. Materials, equipment or components shall be designed and installed in accordance with the manufacturer’s instructions.
|  | K105.3 Submittal. | The registered design professional shall indicate on the permit application that the electrical system is an alternative engineered design. The permit and permanent permit records shall indicate that an alternative engineered design was part of the approved installation.
|  | K105.4 Technical data. | The registered design professional shall submit sufficient technical data to substantiate the proposed alternative engineered design and to prove that the performance meets the intent of this code.
|  | K105.5 Construction documents. | The registered design professional shall submit to the building official two complete sets of signed and sealed construction documents for the alternative engineered design. The construction documents shall include floor plans and a diagram of the work.
|  | K105.6 Design approval. | Where the building official determines that the alternative engineered design conforms to the intent of this code, the electrical system shall be approved. If the alternative engineered design is not approved, the building official shall notify the registered design professional in writing, stating the reasons therefor.
|  | K105.7 Inspection and testing. | The alternative engineered design shall be tested and inspected in accordance with the requirements of this code.
|  | K106.1 General. | The building official, upon notification, shall make the inspections set forth in this section.
|  | K106.2 Underground. | Underground inspection shall be made after trenches or ditches are excavated and bedded, piping and conductors installed, and before backfill is put in place. Where excavated soil contains rocks, broken concrete, frozen chunks and other rubble that would damage or break the raceway, cable or conductors, or where corrosive action will occur, protection shall be provided in the form of granular or selected material, approved running boards, sleeves or other means.
|  | K106.3 Rough-in. | Rough-in inspection shall be made after the roof, framing, fireblocking and bracing are in place and all wiring and other components to be concealed are complete, and prior to the installation of wall or ceiling membranes.
|  | K106.4 Contractors’ responsibilities. | It shall be the responsibility of every contractor who enters into contracts for the installation or repair of electrical systems for which a permit is required to comply with adopted state and local rules and regulations concerning licensing.
|  | K107.1 Prefabricated construction. | Prefabricated construction is subject to Sections K107.2 through K107.5.
|  | K107.2 Evaluation and follow-up inspection services. | Prior to the approval of a prefabricated construction assembly having concealed electrical work and the issuance of an electrical permit, the building official shall require the submittal of an evaluation report on each prefabricated construction assembly, indicating the complete details of the electrical system, including a description of the system and its components, the basis upon which the system is being evaluated, test results and similar information, and other data as necessary for the building official to determine conformance to this code.
|  | K107.3 Evaluation service. | The building official shall designate the evaluation service of an approved agency as the evaluation agency and review such agency’s evaluation report for adequacy and conformance to this code.
|  | K107.4 Follow-up inspection. | Except where ready access is provided to electrical systems, service equipment and accessories for complete inspection at the site without disassembly or dismantling, the building official shall conduct the in-plant inspections as frequently as necessary to ensure conformance to the approved evaluation report or shall designate an independent, approved inspection agency to conduct such inspections. The inspection agency shall furnish the building official with the follow-up inspection manual and a report of inspections upon request, and the electrical system shall have an identifying label permanently affixed to the system indicating that factory inspections have been performed.
|  | K107.5 Test and inspection records. | Required test and inspection records shall be available to the building official at all times during the fabrication of the electrical system and the erection of the building; or such records as the building official designates shall be filed.
|  | K108.1 Testing. | Electrical work shall be tested as required in this code. Tests shall be performed by the permit holder and observed by the building official.
|  | K108.1.1 Apparatus, material and labor for tests. | Apparatus, material and labor required for testing an electrical system or part thereof shall be furnished by the permit holder.
|  | K108.1.2 Reinspection and testing. | Where any work or installation does not pass an initial test or inspection, the necessary corrections shall be made so as to achieve compliance with this code. The work or installation shall then be resubmitted to the building official for inspection and testing.
|  | K109.1 Connection after order to disconnect. | A person shall not make utility service or energy source connections to systems regulated by this code, which have been disconnected or ordered to be disconnected by the building official, or the use of which has been ordered to be discontinued by the building official until the building official authorizes the reconnection and use of such systems.
|  | K110.1 Authority to condemn electrical systems. | Wherever the building official determines that any electrical system, or portion thereof, regulated by this code has become hazardous to life, health or property, the building official shall order in writing that such electrical systems either be removed or restored to a safe condition. A time limit for compliance with such order shall be specified in the written notice. A person shall not use or maintain a defective electrical system or equipment after receiving such notice.
|  | K111.1 Adoption. | Electrical systems and equipment shall be designed, constructed and installed in accordance with the International Residential Code or NFPA 70 as applicable, except as otherwise provided in this code.
|  | K111.2 Abatement of electrical hazards. | All identified electrical hazards shall be abated. All identified hazardous electrical conditions in permanent wiring shall be brought to the attention of the building official responsible for enforcement of this code. Electrical wiring, devices, appliances and other equipment that is modified or damaged and constitutes an electrical shock or fire hazard shall not be used.
|  | K111.3 Appliance and fixture listing. | Electrical appliances and fixtures shall be tested and listed in published reports of inspected electrical equipment by an approved agency and installed in accordance with all instructions included as part of such listing.
|  | K111.4 Nonmetallic-sheathed cable. | The use of Type NM, NMC and NMS (nonmetallic sheathed) cable wiring methods shall not be limited based on height, number of stories or construction type of the building or structure.
|  | K111.5 Cutting, notching and boring. | The cutting, notching and boring of wood and steel framing members, structural members and engineered wood products shall be in accordance with this code.
|  | K111.6 Smoke alarm circuits. | Single- and multiple-station smoke alarms required by this code and installed within dwelling units shall not be connected as the only load on a branch circuit. Such alarms shall be supplied by branch circuits having lighting loads consisting of lighting outlets in habitable spaces.
|  | K111.7 Equipment and door labeling. | Doors into electrical control panel rooms shall be marked with a plainly visible and legible sign stating “ELECTRICAL ROOM” or similar approved wording. The disconnecting means for each service, feeder or branch circuit originating on a switchboard or panelboard shall be legibly and durably marked to indicate its purpose unless such purpose is clearly evident.
K101.1 General. | As referenced by Chapter 30 of the New York City Building Code, the provisions of ASME A17.1-2013 shall be modified in accordance with this chapter. The section numbers correlate to those in the referenced ASME standard. Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to this standard in accor­dance with Section 28-103.19 of the Administrative Code.
K201.1 General. | As referenced in Section 3001.2 of this code, the provisions of ASME B20.1-2015 shall be modified in accordance with this appendix. The section numbers correlate to those in the referenced ASME standard. Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to this standard in accordance with Section 28-103.19 of the Administrative Code.
K301.1 Retroactive requirements for existing elevators and escalators. | As referenced in Section 3001.2 of this code, the provisions of ASME A17.3-2015 shall be modified in accordance with this appendix and are applicable to all existing elevators and escalators. The section numbers correlate to those in the referenced ASME standard. Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to this standard in accordance with Section 28-103.19 of the Administrative Code.

## BC-L
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
|  | L101.1 General. | Every structure located where the 1-second spectral response acceleration, S1, determined in accordance with Section 1613.2, is greater than 0.40 and either exceeds six stories in height with an aggregate floor area of 60,000 square feet (5574 m2) or more, or exceeds 10 stories in height regardless of floor area, shall be equipped with not fewer than three approved recording accelerographs. The accelerographs shall be interconnected for common start and common timing.
|  | L101.2 Location. | As a minimum, instruments shall be located at the lowest level, mid-height, and near the top of the structure. Each instrument shall be located so that access is maintained at all times and is unobstructed by room contents. A sign stating “MAINTAIN CLEAR ACCESS TO THIS INSTRUMENT” in 1-inch (25 mm) block letters shall be posted in a conspicuous location.
|  | L101.3 Maintenance. | Maintenance and service of the instrumentation shall be provided by the owner of the structure. Data produced by the instrument shall be made available to the building official on request.

## BC-M
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
M101.1 General. | The provisions of this appendix contain sup­plementary requirements for the design and construction of one- and two-family dwellings not more than three stories in height. | M101.1 General. | The purpose of this appendix is to provide tsunami vertical evacuation planning criteria for those coastal communities that have a tsunami hazard as shown in a Tsunami Design Zone Map.
|  | M101.2 Definitions. | The following term shall, for the purposes of this appendix, have the meaning shown herein. Refer to Chapter 2 of this code for general definitions.
|  | M101.3 Establishment of tsunami design zone. | Where applicable, the Tsunami Design Zone Map shall meet or exceed the inundation limit given by the ASCE 7 Tsunami Design Geodatabase.
|  | M101.4 Planning of tsunami vertical evacuation refuge structures within the tsunami design zone. | Tsunami Vertical Evacuation Refuge Structures located within a tsunami hazard design zone shall be planned, sited, and developed in general accordance with the planning criteria of the FEMA P646 guidelines.
|  | M102.1 General. | ​ See Table M102.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard. ​
M102.1 Definitions. | The following terms are defined in Chapter 2:
M103.1 General. | A fire wall shall be provided between build­ings in accordance with Chapter 7. However, attached one- and two-family dwellings of construction Type IIIA, IIIB, VA and VB, where permitted and where each building is not more than three stories in height and not more than 2,100 square feet (195 m2) on a story, may be separated by party walls constructed in accor­dance with the following and as illustrated in Figures M103(1) and M103(2):

## BC-N
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
|  | N101.1 Purpose. | The purpose of this appendix is to provide a format and direction regarding the implementation of a replicable building program.
|  | N101.2 Objectives. | Such programs allow a jurisdiction to recover from a natural disaster faster and allow for consistent application of the codes for replicable building projects. It will result in faster turnaround for the end user, and a quicker turnaround through the plan review process.
|  | N102.1 Definitions. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein.
|  | N103.1 Prototypical construction documents. | A replicable design shall establish prototypical construction documents for application at multiple locations. The construction documents shall include details appropriate to each wind region, seismic design category, and climate zone for locations in which the replicable design is intended for application. Application of replicable design shall not vary with regard to the following, except for allowable variations in accordance with Section N106.
|  | N104.1 General. | A summary description of the replicable design and related construction documents shall be submitted to an approved agency. Where approval is requested for elements of the replicable design that is not within the scope of the International Building Code, the construction documents shall specifically designate the codes for which review is sought. Construction documents shall be signed, sealed and dated by a registered design professional.
|  | N104.1.1 Architectural plans and specifications. | Where approval of the architectural requirements of the replicable design is sought, the submittal documents shall include architectural plans and specifications as follows:
|  | N104.1.2 Structural plans, specifications and engineering details. | Where approval of the structural requirements of the replicable design is sought, the submittal documents shall include details for each wind region, seismic design category and climate zone for which approval is sought; and shall include the following:
|  | N104.1.3 Energy conservation details. | Where approval of the energy conservation requirements of the replicable design is sought, the submittal documents shall include details for each climate zone for which approval is sought; and shall include the following:
|  | N105.1 General. | Proposed replicable designs shall be reviewed by an approved agency. The review shall be applicable only to the replicable design features submitted in accordance with Section N104. The review shall determine compliance with this code and additional codes specified in Section N104.1.
|  | N105.2 Documentation. | The results of the review shall be documented indicating compliance with the code requirements.
|  | N105.3 Deficiencies. | Where the review of the submitted construction documents identifies elements where the design is deficient and will not comply with the applicable code requirements, the approved agency shall notify the proponent of the replicable design, in writing, of the specific areas of noncompliance and request correction.
|  | N105.4 Approval. | Where the review of the submitted construction documents determines that the design is in compliance with the codes designated in Section N104.1, and where deficiencies identified in Section N105.3 have been corrected the approved agency shall issue a summary report of Approved Replicable Design. The summary report shall include any limitations on the approved replicable design including, but not limited to climate zones, wind regions and seismic design categories.
|  | N106.1 General. | Where site-specific application of a replicable design that has been approved under the provisions of Section N105 is sought, the construction documents submitted to the building official shall comply with this section.
|  | N106.2 Submittal documents. | A summary description of the replicable design and related construction document shall be submitted. Construction documents shall be signed, sealed and dated by the registered design professional. A statement, signed, sealed and dated by the registered design professional, that the replicable design submitted for local review is the same as the replicable design reviewed by the approved agency, shall be submitted.
|  | N106.2.1 Architectural plans and specifications. | Architectural plans and specifications shall include the following:
|  | N107.1 General. | Proposed site-specific application of replicable design shall be submitted to the building official in accordance with the provisions of Chapter 1 and Appendix N.
|  | N107.2 Site-specific review and approval of replicable design. | The building official shall verify that the replicable design submitted for site-specific application is the same as the approved replicable design reviewed by the approved agency. In addition, the building official shall review the following for code compliance.
N101.1 Scope. | The provisions of this appendix shall control the performance standards of assistive listening systems (ALS).
N102.1 Induction loop system specifications.
N102.2 Capital projects. | City funded projects shall provide induction-loop systems pursuant to Section 224.3 of the New York City Charter.
N103.1 Infra-red system specifications.
N104.1 FM system specifications.

## BC-O
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | O101.1 Introduction. | The following administrative provisions are excerpted from the ICC Performance Code for Buildings and Facilities and can be used in conjunction with the Alternate Methods provisions in Chapter 1, or for a review of submittals requiring a rational analysis or performance-based design. These provisions provide an established framework for the building official in terms of the design expertise needed, the necessary submittals, a review framework and related items.
|  | O101.2 Qualifications. | Registered design professionals shall possess the knowledge, skills and abilities necessary to demonstrate compliance with this code.
|  | O101.3 Construction document preparation. | Construction documents required by this code shall be prepared in adequate detail and submitted for review and approval in accordance with Section 107.
|  | O101.3.1 Review. | Construction documents submitted in accordance with this code shall be reviewed for code compliance with the appropriate code provisions in accordance with Section 107.
|  | O101.4 Construction. | Construction shall comply with the approved construction documents submitted in accordance with this code, and shall be verified and approved to demonstrate compliance with this code.
|  | O101.4.1 Facility operating policies and procedures. | Policies, operations, training and procedures shall comply with approved documents submitted in accordance with this code, and shall be verified and approved to demonstrate compliance with this code.
|  | O101.4.2 Maintenance. | Maintenance of the performance-based design shall be ensured throughout the life of the building or portion thereof.
|  | O101.4.3 Changes. | The owner or the owner’s authorized agent shall be responsible to ensure that any change to the facility, process, or system does not increase the hazard level beyond that originally designed without approval and that changes shall be documented in accordance with the code.
|  | O101.5 Documentation. | The registered design professional shall prepare appropriate documentation for the project, clearly detailing the approach and rationale for the design submittal, the construction and the future use of the building, facility or process.
|  | O101.5.1 Reports and manuals. | The design report shall document the steps taken in the design analysis, clearly identifying the criteria, parameters, inputs, assumptions, sensitivities and limitations involved in the analysis. The design report shall clearly identify bounding conditions, assumptions and sensitivities that clarify the expected uses and limitations of the performance analysis. This report shall verify that the design approach is in compliance with the applicable codes and acceptable methods and shall be submitted for concurrence by the building official prior to the construction documents being completed. The report shall document the design features to be incorporated based on the analysis.
|  | O101.5.2 Design submittal. | Applicable construction documents shall be submitted to the building official for review. The documents shall be submitted in accordance with the jurisdiction’s procedures and in sufficient detail to obtain appropriate permits.
|  | O101.6 Review. | Construction documents submitted in accordance with this code shall be reviewed for code compliance with the appropriate code provisions.
|  | O101.6.1 Peer review. | The owner or the owner’s authorized agent shall be responsible for retaining and furnishing the services of a registered design professional or recognized expert, who will perform as a peer reviewer, where required and approved by the building official.
|  | O101.6.2 Costs. | The costs of special services, including contract review, where required by the building official, shall be borne by the owner or the owner’s authorized agent.
|  | O101.7 Permits. | Prior to the start of construction, appropriate permits shall be obtained in accordance with the jurisdiction’s procedures and applicable codes.
|  | O101.8 Verification of compliance. | Upon completion of the project, documentation shall be prepared that verifies performance and prescriptive code provisions have been met. Where required by the building official, the registered design professional shall file a report that verifies bounding conditions are met.
|  | O101.9 Extent of documentation. | Approved construction documents, the operations and maintenance manual, inspection and testing records, and certificates of occupancy with conditions shall be included in the project documentation of the building official’s records.
|  | O101.10 Analysis of change. | The registered design professional shall evaluate the existing building, facilities, premises, processes, and contents, and the applicable documentation of the proposed change as it affects portions of the building, facility, premises, processes and contents that were previously designed for compliance under a performance-based code. Prior to any change that was not documented in a previously approved design, the registered design professional shall examine the applicable design documents, bounding conditions, operation and maintenance manuals, and deed restrictions.