## BC1
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
101.1 Title. | This code shall be known and may be cited as the “New York City Building Code,” “NYCBC” or “BC.” All section numbers in this code shall be deemed to be preceded by the designation “BC.” | 101.1 Title. | These regulations shall be known as the Building Code of , hereinafter referred to as “this code.”
101.2 Scope. | The provisions of this code shall apply to the construction, alteration, movement, addition, replacement, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every building or structure or any appurtenances connected or attached to such buildings or structures. | 101.2 Scope. | The provisions of this code shall apply to the construction, alteration, relocation, enlargement, replacement, repair, equipment, use and occupancy, location, maintenance, removal and demolition of every building or structure or any appurtenances connected or attached to such buildings or structures. Exception: Detached one- and two-family dwellings and townhouses not more than three stories above grade plane in height with a separate means of egress, and their accessory structures not more than three stories above grade plane in height, shall comply with this code or the International Residential Code.
|  | 101.2.1 Appendices. | Provisions in the appendices shall not apply unless specifically adopted.
101.4 Referenced codes. | The other codes listed in Sections 101.4.1 through 101.4.6 and referenced elsewhere in this code shall be considered part of the requirements of this code to the prescribed extent of each such reference. | 101.4 Referenced codes. | The other codes specified in Sections 101.4.1 through 101.4.7 and referenced elsewhere in this code shall be considered to be part of the requirements of this code to the prescribed extent of each such reference.
101.3 Intent. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 101.3 Purpose. | The purpose of this code is to establish the minimum requirements to provide a reasonable level of safety, health and general welfare through structural strength, means of egress, stability, sanitation, light and ventilation, energy conservation, and for providing a reasonable level of life safety and property protection from the hazards of fire, explosion or dangerous conditions, and to provide a reasonable level of safety to fire fighters and emergency responders during emergency operations.
101.4.1 Electrical. | The provisions of the New York City Electrical Code shall apply to the installation of electrical systems, including alterations, repairs, replacement, equipment, appliances, fixtures, fittings and appurtenances thereto. | 101.4.1 Gas. | The provisions of the International Fuel Gas Code shall apply to the installation of gas piping from the point of delivery, gas appliances and related accessories as covered in this code. These requirements apply to gas piping systems extending from the point of delivery to the inlet connections of appliances and the installation and operation of residential and commercial gas appliances and related accessories.
101.4.2 Gas. | The provisions of the New York City Fuel Gas Code shall apply to the installation of gas piping, gas appliances and related accessories as covered in this code. These requirements apply to gas piping systems extending to the inlet connections of appliances and the installation and operation of residential and commercial gas appliances and related accessories. | 101.4.2 Mechanical. | The provisions of the International Mechanical Code shall apply to the installation, alterations, repairs and replacement of mechanical systems, including equipment, appliances, fixtures, fittings and appurtenances, including ventilating, heating, cooling, air-conditioning and refrigeration systems, incinerators and other energy-related systems.
101.4.3 Mechanical. | The provisions of the New York City Mechanical Code shall apply to the installation, alterations, repairs and replacement of mechanical systems, including equipment, appliances, fixtures, fittings and/or appurtenances, including ventilating, heating, cooling, air-condi­tioning and refrigeration systems, incinerators and other energy-related systems. | 101.4.3 Plumbing. | The provisions of the International Plumbing Code shall apply to the installation, alteration, repair and replacement of plumbing systems, including equipment, appliances, fixtures, fittings and appurtenances, and where connected to a water or sewage system and all aspects of a medical gas system. The provisions of the International Private Sewage Disposal Code shall apply to private sewage disposal systems.
101.4.5 Fire prevention. | The provisions of the New York City Fire Code shall apply to: | 101.4.5 Fire prevention. | The provisions of the International Fire Code shall apply to matters affecting or relating to structures, processes and premises from the hazard of fire and explosion arising from the storage, handling or use of structures, materials or devices; from conditions hazardous to life, property or public welfare in the occupancy of structures or premises; and from the construction, extension, repair, alteration or removal of fire suppression, automatic sprinkler systems and alarm systems or fire hazards in the structure or on the premises from occupancy or operation.
101.4.4 Plumbing. | The provisions of the New York City Plumbing Code shall apply to the alteration, repair and replacement of plumbing systems, including equipment, appliances, fixtures, fittings and appurtenances, and where connected to a water or sewage system and all aspects of a medical gas system. | 101.4.4 Property maintenance. | The provisions of the International Property Maintenance Code shall apply to existing structures and premises; equipment and facilities; light, ventilation, space heating, sanitation, life and fire safety hazards; responsibilities of owners, operators and occupants; and occupancy of existing premises and structures.
101.4.6 Energy. | The provisions of the New York City Energy Conservation Code shall apply to all matters governing the design, construction and alteration of buildings for energy efficiency. | 101.4.6 Energy. | The provisions of the International Energy Conservation Code shall apply to all matters governing the design and construction of buildings for energy efficiency.
102.1 General. | Where there is a conflict between a general requirement and a specific requirement, the specific requirement shall govern. Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern. | 102.1 General. | Where there is a conflict between a general requirement and a specific requirement, the specific requirement shall be applicable. Where, in any specific case, different sections of this code specify different materials, methods of construction or other requirements, the most restrictive shall govern.
|  | 101.4.7 Existing buildings. | The provisions of the International Existing Building Code shall apply to matters governing the repair, alteration, change of occupancy, addition to and relocation of existing buildings.
102.3 Application of references. | References to chapter or section numbers, or to provisions not specifically identified by number, shall be construed to refer to such chapter, section or provision of this code. | 102.3 Application of references. | References to chapter or section numbers, or to provisions not specifically identified by number, shall be construed to refer to such chapter, section or provision of this code.
102.2 Reserved. |  | 102.2 Other laws. | The provisions of this code shall not be deemed to nullify any provisions of local, state or federal law.
102.4 Referenced standards. | The standards referenced in this code and in the rules of the department shall be considered part of the requirements of this code to the prescribed extent of each such reference. Where differences occur between provisions of this code and referenced standards, the provisions of this code shall apply. Refer to Article 103 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to referenced standards. | 102.4 Referenced codes and standards. | The codes and standards referenced in this code shall be considered to be part of the requirements of this code to the prescribed extent of each such reference and as further regulated in Sections 102.4.1 and 102.4.2.
102.5 Partial invalidity. | In the event that any part or provision of this code is held to be illegal or void, this shall not have the effect of making void or illegal any of the other parts or provisions. | 102.5 Partial invalidity. | In the event that any part or provision of this code is held to be illegal or void, this shall not have the effect of making void or illegal any of the other parts or provisions.
102.4.1 Editions of referenced standards. | References to standards in this code shall be to the editions of those standards provided for in Chapter 35 of this code, or as otherwise provided by rule. | 102.4.1 Conflicts. | Where conflicts occur between provisions of this code and referenced codes and standards, the provisions of this code shall apply.
102.6 Existing structures. | The legal occupancy of any structure lawfully in existence at the time of the adoption or a subsequent amendment of this code shall be permitted to continue without change, except as is otherwise specifically provided in this code or as is deemed necessary by the commissioner for the general safety and welfare of the occupants and the public. Refer to Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to existing structures. | 102.6 Existing structures. | The legal occupancy of any structure existing on the date of adoption of this code shall be permitted to continue without change, except as otherwise specifically provided in this code, the International Existing Building Code, the International Property Maintenance Code or the International Fire Code.
|  | 102.4.2 Provisions in referenced codes and standards. | Where the extent of the reference to a referenced code or standard includes subject matter that is within the scope of this code or the International Codes specified in Section 101.4, the provisions of this code or the International Codes specified in Section 101.4, as applicable, shall take precedence over the provisions in the referenced code or standard.
104.1 General. | The commissioner shall have the authority to render interpretations of this code, adopt rules, and establish policies and procedures in order to clarify and implement its provisions. Such interpretations, policies, procedures, and rules shall be in compliance with the intent and purpose of this code. See the New York City Charter and Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to the authority of the Commissioner of Buildings. | 104.1 General. | The building official is hereby authorized and directed to enforce the provisions of this code. The building official shall have the authority to render interpretations of this code and to adopt policies and procedures in order to clarify the application of its provisions. Such interpretations, policies and procedures shall be in compliance with the intent and purpose of this code. Such policies and procedures shall not have the effect of waiving requirements specifically provided for in this code.
|  | 102.6.1 Buildings not previously occupied. | A building or portion of a building that has not been previously occupied or used for its intended purpose in accordance with the laws in existence at the time of its completion shall comply with the provisions of this code or the International Residential Code, as applicable, for new construction or with any current permit for such occupancy.
|  | 102.6.2 Buildings previously occupied. | The legal occupancy of any building existing on the date of adoption of this code shall be permitted to continue without change, except as otherwise specifically provided in this code, the International Fire Code or International Property Maintenance Code, or as is deemed necessary by the building official for the general safety and welfare of the occupants and the public.
103.1 General. | Refer to the New York City Charter and Chapter 1 of Title 28 of the Administrative Code. | 103.1 Creation of enforcement agency. | The is hereby created and the official in charge thereof shall be known as the building official. The function of the agency shall be the implementation, administration and enforcement of the provisions of this code.
|  | 103.2 Appointment. | The building official shall be appointed by the chief appointing authority of the jurisdiction.
|  | 103.3 Deputies. | In accordance with the prescribed procedures of this jurisdiction and with the concurrence of the appointing authority, the building official shall have the authority to appoint a deputy building official, other related technical officers, inspectors and other employees. Such employees shall have powers as delegated by the building official.
|  | 104.2 Applications and permits. | The building official shall receive applications, review construction documents and issue permits for the erection, and alteration, demolition and moving of buildings and structures, inspect the premises for which such permits have been issued and enforce compliance with the provisions of this code.
|  | 104.2.1 Determination of substantially improved or substantially damaged existing buildings and structures in flood hazard areas. | For applications for reconstruction, rehabilitation, repair, alteration, addition or other improvement of existing buildings or structures located in flood hazard areas, the building official shall determine if the proposed work constitutes substantial improvement or repair of substantial damage. Where the building official determines that the proposed work constitutes substantial improvement or repair of substantial damage, and where required by this code, the building official shall require the building to meet the requirements of Section 1612 or Section R322 of the International Residential Code, as applicable.
|  | 104.3 Notices and orders. | The building official shall issue necessary notices or orders to ensure compliance with this code.
|  | 104.4 Inspections. | The building official shall make the required inspections, or the building official shall have the authority to accept reports of inspection by approved agencies or individuals. Reports of such inspections shall be in writing and be certified by a responsible officer of such approved agency or by the responsible individual. The building official is authorized to engage such expert opinion as deemed necessary to report on unusual technical issues that arise, subject to the approval of the appointing authority.
|  | 104.5 Identification. | The building official shall carry proper identification when inspecting structures or premises in the performance of duties under this code.
|  | 104.6 Right of entry. | Where it is necessary to make an inspection to enforce the provisions of this code, or where the building official has reasonable cause to believe that there exists in a structure or on a premises a condition that is contrary to or in violation of this code that makes the structure or premises unsafe, dangerous or hazardous, the building official is authorized to enter the structure or premises at reasonable times to inspect or to perform the duties imposed by this code, provided that if such structure or premises be occupied that credentials be presented to the occupant and entry requested. If such structure or premises is unoccupied, the building official shall first make a reasonable effort to locate the owner or other person having charge or control of the structure or premises and request entry. If entry is refused, the building official shall have recourse to the remedies provided by law to secure entry.
|  | 104.7 Department records. | The building official shall keep official records of applications received, permits and certificates issued, fees collected, reports of inspections, and notices and orders issued. Such records shall be retained in the official records for the period required for retention of public records.
|  | 104.8 Liability. | The building official, member of the board of appeals or employee charged with the enforcement of this code, while acting for the jurisdiction in good faith and without malice in the discharge of the duties required by this code or other pertinent law or ordinance, shall not thereby be civilly or criminally rendered liable personally and is hereby relieved from personal liability for any damage accruing to persons or property as a result of any act or by reason of an act or omission in the discharge of official duties.
|  | 104.8.1 Legal defense. | Any suit or criminal complaint instituted against an officer or employee because of an act performed by that officer or employee in the lawful discharge of duties and under the provisions of this code shall be defended by legal representatives of the jurisdiction until the final termination of the proceedings. The building official or any subordinate shall not be liable for cost in any action, suit or proceeding that is instituted in pursuance of the provisions of this code.
|  | 104.9 Approved materials and equipment. | Materials, equipment and devices approved by the building official shall be constructed and installed in accordance with such approval.
|  | 104.9.1 Used materials and equipment. | Materials that are reused shall comply with the requirements of this code for new materials. Used equipment and devices shall not be reused unless approved by the building official.
|  | 104.10 Modifications. | Where there are practical difficulties involved in carrying out the provisions of this code, the building official shall have the authority to grant modifications for individual cases, upon application of the owner or the owner’s authorized agent, provided that the building official shall first find that special individual reason makes the strict letter of this code impractical, the modification is in compliance with the intent and purpose of this code and that such modification does not lessen health, accessibility, life and fire safety or structural requirements. The details of action granting modifications shall be recorded and entered in the files of the department of building safety.
|  | 104.10.1 Flood hazard areas. | The building official shall not grant modifications to any provision required in flood hazard areas as established by Section 1612.3 unless a determination has been made that:
|  | 104.11 Alternative materials, design and methods of construction and equipment. | The provisions of this code are not intended to prevent the installation of any material or to prohibit any design or method of construction not specifically prescribed by this code, provided that any such alternative has been approved. An alternative material, design or method of construction shall be approved where the building official finds that the proposed alternative meets all of the following:
|  | 104.11.1 Research reports. | Supporting data, where necessary to assist in the approval of materials or assemblies not specifically provided for in this code, shall consist of valid research reports from approved sources.
|  | 104.11.2 Tests. | Whenever there is insufficient evidence of compliance with the provisions of this code, or evidence that a material or method does not conform to the requirements of this code, or in order to substantiate claims for alternative materials or methods, the building official shall have the authority to require tests as evidence of compliance to be made without expense to the jurisdiction. Test methods shall be as specified in this code or by other recognized test standards. In the absence of recognized and accepted test methods, the building official shall approve the testing procedures. Tests shall be performed by an approved agency. Reports of such tests shall be retained by the building official for the period required for retention of public records.
105.1 Approvals. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 105.1 Required. | Any owner or owner’s authorized agent who intends to construct, enlarge, alter, repair, move, demolish or change the occupancy of a building or structure, or to erect, install, enlarge, alter, repair, remove, convert or replace any electrical, gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be performed, shall first make application to the building official and obtain the required permit.
|  | 105.1.1 Annual permit. | Instead of an individual permit for each alteration to an already approved electrical, gas, mechanical or plumbing installation, the building official is authorized to issue an annual permit upon application therefor to any person, firm or corporation regularly employing one or more qualified tradespersons in the building, structure or on the premises owned or operated by the applicant for the permit.
107.1 General. | Construction documents shall comply with Chapter 1 of Title 28 of the Administrative Code, this section and other applicable provisions of this code and its referenced standards. | 107.1 General. | Submittal documents consisting of construction documents, statement of special inspections, geotechnical report and other data shall be submitted in two or more sets, or in a digital format where allowed by the building official, with each permit application. The construction documents shall be prepared by a registered design professional where required by the statutes of the jurisdiction in which the project is to be constructed. Where special conditions exist, the building official is authorized to require additional construction documents to be prepared by a registered design professional. Exception: The building official is authorized to waive the submission of construction documents and other data not required to be prepared by a registered design professional if it is found that the nature of the work applied for is such that review of construction documents is not necessary to obtain compliance with this code.
|  | 105.1.2 Annual permit records. | The person to whom an annual permit is issued shall keep a detailed record of alterations made under such annual permit. The building official shall have access to such records at all times or such records shall be filed with the building official as designated.
|  | 105.2 Work exempt from permit. | Exemptions from permit requirements of this code shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code or any other laws or ordinances of this jurisdiction. Permits shall not be required for the following:
|  | 105.2.1 Emergency repairs. | Where equipment replacements and repairs must be performed in an emergency situation, the permit application shall be submitted within the next working business day to the building official.
|  | 105.2.2 Public service agencies. | A permit shall not be required for the installation, alteration or repair of generation, transmission, distribution or metering or other related equipment that is under the ownership and control of public service agencies by established right.
|  | 105.3 Application for permit. | To obtain a permit, the applicant shall first file an application therefor in writing on a form furnished by the department of building safety for that purpose. Such application shall:
|  | 105.3.1 Action on application. | The building official shall examine or cause to be examined applications for permits and amendments thereto within a reasonable time after filing. If the application or the construction documents do not conform to the requirements of pertinent laws, the building official shall reject such application in writing, stating the reasons therefor. If the building official is satisfied that the proposed work conforms to the requirements of this code and laws and ordinances applicable thereto, the building official shall issue a permit therefor as soon as practicable.
|  | 105.3.2 Time limitation of application. | An application for a permit for any proposed work shall be deemed to have been abandoned 180 days after the date of filing, unless such application has been pursued in good faith or a permit has been issued; except that the building official is authorized to grant one or more extensions of time for additional periods not exceeding 90 days each. The extension shall be requested in writing and justifiable cause demonstrated.
|  | 105.4 Validity of permit. | The issuance or granting of a permit shall not be construed to be a permit for, or an approval of, any violation of any of the provisions of this code or of any other ordinance of the jurisdiction. Permits presuming to give authority to violate or cancel the provisions of this code or other ordinances of the jurisdiction shall not be valid. The issuance of a permit based on construction documents and other data shall not prevent the building official from requiring the correction of errors in the construction documents and other data. The building official is authorized to prevent occupancy or use of a structure where in violation of this code or of any other ordinances of this jurisdiction.
|  | 105.5 Expiration. | Every permit issued shall become invalid unless the work on the site authorized by such permit is commenced within 180 days after its issuance, or if the work authorized on the site by such permit is suspended or abandoned for a period of 180 days after the time the work is commenced. The building official is authorized to grant, in writing, one or more extensions of time, for periods not more than 180 days each. The extension shall be requested in writing and justifiable cause demonstrated.
|  | 105.6 Suspension or revocation. | The building official is authorized to suspend or revoke a permit issued under the provisions of this code wherever the permit is issued in error or on the basis of incorrect, inaccurate or incomplete information, or in violation of any ordinance or regulation or any of the provisions of this code.
|  | 105.7 Placement of permit. | The building permit or copy shall be kept on the site of the work until the completion of the project.
106.1 General. | Permits shall comply with this section, with Article 105 of Chapter 1 of Title 28 of the Administrative Code, and with requirements found elsewhere in this code. | 106.1 Live loads posted. | In commercial or industrial buildings, for each floor or portion thereof designed for live loads exceeding 50 psf (2.40 kN/m2), such design live loads shall be conspicuously posted by the owner or the owner’s authorized agent in that part of each story in which they apply, using durable signs. It shall be unlawful to remove or deface such notices.
106.2 Required. | Any owner or authorized agent who intends to construct, add to, alter, repair, move, demolish, or change the occupancy of a building or structure, or to erect, install, add to, alter, repair, remove, convert or replace any gas, mechanical or plumbing system, the installation of which is regulated by this code, or to cause any such work to be done, shall first make application for construction document approval in accordance with Chapter 1 of Title 28 of the Administrative Code and this chapter and obtain the required permit. | 106.2 Issuance of certificate of occupancy. | A certificate of occupancy required by Section 111 shall not be issued until the floor load signs, required by Section 106.1, have been installed.
106.3 Work exempt from permit. | Exemptions from permit requirements of this code as authorized in Chapter 1 of Title 28 of the Administrative Code and the rules of the department shall not be deemed to grant authorization for any work to be done in any manner in violation of the provisions of this code or any other laws or rules. | 106.3 Restrictions on loading. | It shall be unlawful to place, or cause or permit to be placed, on any floor or roof of a building, structure or portion thereof, a load greater than is permitted by this code.
107.2 Required construction documents. | In addition to the requirements of Article 104 of Title 28 of the Administrative Code, the applicant shall submit any and all of the documents specified in Sections 107.3 through 107.16 as appropriate to the nature and extent of the work proposed. | 107.2 Construction documents. | Construction documents shall be in accordance with Sections 107.2.1 through 107.2.8.
107.2.1 Composite plans. | Composite plans showing architectural, structural, and mechanical parts and related energy use systems of a building may be submitted provided that a clear understanding of each part and system is not impaired. | 107.2.1 Information on construction documents. | Construction documents shall be dimensioned and drawn on suitable material. Electronic media documents are permitted to be submitted where approved by the building official. Construction documents shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that it will conform to the provisions of this code and relevant laws, ordinances, rules and regulations, as determined by the building official.
107.2.2 Multiple building developments. | The same set of plans may be used for several buildings of the same construction, if such buildings are located on adjoining lots under the same ownership, and if applications for construction document approval for the lots are filed simultaneously. | 107.2.2 Fire protection system shop drawings. | Shop drawings for the fire protection systems shall be submitted to indicate conformance to this code and the construction documents and shall be approved prior to the start of system installation. Shop drawings shall contain all information as required by the referenced installation standards in Chapter 9.
|  | 107.2.3 Means of egress. | The construction documents shall show in sufficient detail the location, construction, size and character of all portions of the means of egress including the path of the exit discharge to the public way in compliance with the provisions of this code. In other than occupancies in Groups R-2, R-3, and I-1, the construction documents shall designate the number of occupants to be accommodated on every floor, and in all rooms and spaces.
|  | 107.2.4 Exterior wall envelope. | Construction documents for all buildings shall describe the exterior wall envelope in sufficient detail to determine compliance with this code. The construction documents shall provide details of the exterior wall envelope as required, including flashing, intersections with dissimilar materials, corners, end details, control joints, intersections at roof, eaves or parapets, means of drainage, water-resistive barrier and details around openings.
|  | 107.2.5 Exterior balconies and elevated walking surfaces. | Where balconies or other elevated walking surfaces have weather-exposed surfaces, and the structural framing is protected by an impervious moisture barrier, the construction documents shall include details for all elements of the impervious moisture barrier system. The construction documents shall include manufacturer’s installation instructions.
|  | 107.2.6 Site plan. | The construction documents submitted with the application for permit shall be accompanied by a site plan showing to scale the size and location of new construction and existing structures on the site, distances from lot lines, the established street grades and the proposed finished grades and, as applicable, flood hazard areas, floodways, and design flood elevations; and it shall be drawn in accordance with an accurate boundary line survey. In the case of demolition, the site plan shall show construction to be demolished and the location and size of existing structures and construction that are to remain on the site or plot. The building official is authorized to waive or modify the requirement for a site plan where the application for permit is for alteration or repair or where otherwise warranted.
|  | 107.2.6.1 Design flood elevations. | Where design flood elevations are not specified, they shall be established in accordance with Section 1612.3.1.
|  | 107.2.7 Structural information. | The construction documents shall provide the information specified in Section 1603.
|  | 107.2.8 Relocatable buildings. | Construction documents for relocatable buildings shall comply with Section 3112.
107.3 Lot diagram. | The lot diagram shall show compliance with the New York City Zoning Resolution, indicating the size, height, and location of the proposed construction including parking and curb cuts; all existing structures on the zoning lot and their distances from lot and street lines; the established grade and existing curb elevations; and the proposed final grade elevations of the site shown by contours or spot grades at reasonable intervals. The lot diagram shall be drawn in accordance with an accurate boundary survey to the city datum, made by a land surveyor, which shall be attached to and form part of the application. A complete zoning analysis shall accompany the lot diagram with citation to the relevant sections of the New York City Zoning Resolution. | 107.3 Examination of documents. | The building official shall examine or cause to be examined the accompanying submittal documents and shall ascertain by such examinations whether the construction indicated and described is in accordance with the requirements of this code and other pertinent laws or ordinances.
|  | 107.3.1 Approval of construction documents. | When the building official issues a permit, the construction documents shall be approved, in writing or by stamp, as “Reviewed for Code Compliance.” One set of construction documents so reviewed shall be retained by the building official. The other set shall be returned to the applicant, shall be kept at the site of work and shall be open to inspection by the building official or a duly authorized representative.
|  | 107.3.2 Previous approvals. | This code shall not require changes in the construction documents, construction or designated occupancy of a structure for which a lawful permit has been heretofore issued or otherwise lawfully authorized, and the construction of which has been pursued in good faith within 180 days after the effective date of this code and has not been abandoned.
|  | 107.3.3 Phased approval. | The building official is authorized to issue a permit for the construction of foundations or any other part of a building or structure before the construction documents for the whole building or structure have been submitted, provided that adequate information and detailed statements have been filed complying with pertinent requirements of this code. The holder of such permit for the foundation or other parts of a building or structure shall proceed at the holder’s own risk with the building operation and without assurance that a permit for the entire structure will be granted.
|  | 107.3.4 Design professional in responsible charge. | Where it is required that documents be prepared by a registered design professional, the building official shall be authorized to require the owner or the owner’s authorized agent to engage and designate on the building permit application a registered design professional who shall act as the registered design professional in responsible charge. If the circumstances require, the owner or the owner’s authorized agent shall designate a substitute registered design professional in responsible charge who shall perform the duties required of the original registered design professional in responsible charge. The building official shall be notified in writing by the owner or the owner’s authorized agent if the registered design professional in responsible charge is changed or is unable to continue to perform the duties.
|  | 107.3.4.1 Deferred submittals. | Deferral of any submittal items shall have the prior approval of the building official. The registered design professional in responsible charge shall list the deferred submittals on the construction documents for review by the building official.
107.4 Building classification statement. | The statement shall identify: 1. The occupancy group or groups that apply to parts of the building in accordance with Section 302;. | 107.4 Amended construction documents. | Work shall be installed in accordance with the approved construction documents, and any changes made during construction that are not in compliance with the approved construction documents shall be resubmitted for approval as an amended set of construction documents.
107.5 Means of egress plans. | Floor and roof plans shall show compliance with the requirements of Chapter 10, with sufficient notations indicating egress features and complete egress analysis as required by this code. | 107.5 Retention of construction documents. | One set of approved construction documents shall be retained by the building official for a period of not less than 180 days from date of completion of the permitted work, or as required by state or local laws.
108.1 General. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 108.1 General. | The building official is authorized to issue a permit for temporary structures and temporary uses. Such permits shall be limited as to time of service, but shall not be permitted for more than 180 days. The building official is authorized to grant extensions for demonstrated cause.
|  | 108.2 Conformance. | Temporary structures and uses shall comply with the requirements in Section 3103.
|  | 108.3 Temporary power. | The building official is authorized to give permission to temporarily supply and use power in part of an electric installation before such installation has been fully completed and the final certificate of completion has been issued. The part covered by the temporary certificate shall comply with the requirements specified for temporary lighting, heat or power in NFPA 70.
|  | 108.4 Termination of approval. | The building official is authorized to terminate such permit for a temporary structure or use and to order the temporary structure or use to be discontinued.
109.1 Payment of fees. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 109.1 Payment of fees. | A permit shall not be valid until the fees prescribed by law have been paid, nor shall an amendment to a permit be released until the additional fee, if any, has been paid.
|  | 109.2 Schedule of permit fees. | Where a permit is required, a fee for each permit shall be paid as required, in accordance with the schedule as established by the applicable governing authority.
|  | 109.3 Permit valuations. | The applicant for a permit shall provide an estimated permit value at time of application. Permit valuations shall reflect the total value of work, including materials and labor, for which the permit is being issued, such as electrical, gas, mechanical, plumbing equipment and permanent systems. If, in the opinion of the building official, the valuation is underestimated on the application, the permit shall be denied, unless the applicant can show detailed estimates to meet the approval of the building official. Final building permit valuation shall be set by the building official.
|  | 109.4 Work commencing before permit issuance. | Any person who commences any work before obtaining the necessary permits shall be subject to a fee established by the building official that shall be in addition to the required permit fees.
|  | 109.5 Related fees. | The payment of the fee for the construction, alteration, removal or demolition for work done in connection to or concurrently with the work authorized by a building permit shall not relieve the applicant or holder of the permit from the payment of other fees that are prescribed by law.
|  | 109.6 Refunds. | The building official is authorized to establish a refund policy.
110.1 General. | Except as otherwise specified, inspections required by this code or by the department during the progress of work may be performed on behalf of the owner by approved agencies or, if applicable, by special inspectors. However, in the interest of public safety, the commissioner may direct that any of such inspections be performed by the department. All inspections shall be performed at the sole cost and expense of the owner. Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to inspections. | 110.1 General. | Construction or work for which a permit is required shall be subject to inspection by the building official and such construction or work shall remain visible and able to be accessed for inspection purposes until approved. Approval as a result of an inspection shall not be construed to be an approval of a violation of the provisions of this code or of other ordinances of the jurisdiction. Inspections presuming to give authority to violate or cancel the provisions of this code or of other ordinances of the jurisdiction shall not be valid. It shall be the duty of the owner or the owner’s authorized agent to cause the work to remain visible and able to be accessed for inspection purposes. Neither the building official nor the jurisdiction shall be liable for expense entailed in the removal or replacement of any material required to allow inspection.
110.2 Preliminary inspection. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 110.2 Preliminary inspection. | Before issuing a permit, the building official is authorized to examine or cause to be examined buildings, structures and sites for which an application has been filed.
|  | 110.3 Required inspections. | The building official, upon notification, shall make the inspections set forth in Sections 110.3.1 through 110.3.12.
110.3.1 Footing and foundation inspection. | Footing and foundation inspections shall be made after excavations for footings are complete and any required reinforcing steel is in place. For concrete foundations, any required forms shall be in place prior to inspection. Materials for the foundation shall be on the job, except where concrete is ready mixed in accordance with ASTM C 94, the concrete need not be on the job. | 110.3.1 Footing and foundation inspection. | Footing and foundation inspections shall be made after excavations for footings are complete and any required reinforcing steel is in place. For concrete foundations, any required forms shall be in place prior to inspection. Materials for the foundation shall be on the job, except where concrete is ready mixed in accordance with ASTM C94, the concrete need not be on the job.
110.3.2 Lowest floor elevation. | In flood hazard areas, upon placement of the lowest floor, including the basement (for flood zone purposes), and prior to further vertical construction, the elevation inspection report required in Item 1 of Section G107.3 of Appendix G shall be submitted to the department. | 110.3.2 Concrete slab and under-floor inspection. | Concrete slab and under-floor inspections shall be made after in-slab or under-floor reinforcing steel and building service equipment, conduit, piping accessories and other ancillary equipment items are in place, but before any concrete is placed or floor sheathing installed, including the subfloor.
110.3.3 Structural wood frame inspection. | Inspections shall be performed for wood structural framing to determine compliance with the approved construction documents. Exception: Prefabricated wood structural elements and assemblies subject to Section 1705.5.1 through 1705.5.3 shall not be subject to progress inspection. | 110.3.3 Lowest floor elevation. | In flood hazard areas, upon placement of the lowest floor, including the basement, and prior to further vertical construction, the elevation certification required in Section 1612.4 or the International Residential Code, as applicable, shall be submitted to the building official.
110.3.4 Fire-resistance-rated construction inspection. | Fire-resistance-rated construction shall be inspected to determine compliance with the approved construction documents, including inspection of the following work: 1. Fire-resistance-rated partitions, floors, ceilings, shafts; and 2. Fire shutters. Exception: Where the scope of work affecting an existing fire-rated wall assembly is limited to through-penetration firestopping and, in the course of work, the cutting away or removal of any part of the existing fire-resistance-rated construction becomes necessary in the general area surrounding the penetration, not to exceed 4 square feet (0.37 m2) in any given area, the progress inspection for fire-resistance-rated construction shall not be required provided that the special inspection agency for the through-penetration firestopping special inspection verifies that the removed portion of fire-resistance-rated construction (i) is less than 4 square feet (0.37 m2), and (ii) has been restored to its original condition. | 110.3.4 Frame inspection. | Framing inspections shall be made after the roof deck or sheathing, all framing, fire-blocking and bracing are in place and pipes, chimneys and vents to be concealed are complete and the rough electrical, plumbing, heating wires, pipes and ducts are approved.
110.3.5 Energy code compliance inspections. | Inspections shall be made to determine compliance with approved construction documents. | 110.3.5 Types IV-A, IV-B and IV-C connection protection inspection. | In buildings of Types IV-A, IV-B and IV-C construction, where connection fire-resistance ratings are provided by wood cover calculated to meet the requirements of Section 2304.10.1, inspection of the wood cover shall be made after the cover is installed, but before any other coverings or finishes are installed.
110.3.6 Other inspections. | In addition to the inspections specified above, the commissioner is authorized to make or require other inspections of any construction work to ascertain compliance with the provisions of this code and other laws that are enforced by the department. | 110.3.6 Lath, gypsum board and gypsum panel product inspection. | Lath, gypsum board and gypsum panel product inspections shall be made after lathing, gypsum board and gypsum panel products, interior and exterior, are in place, but before any plastering is applied or gypsum board and gypsum panel product joints and fasteners are taped and finished. Exception: Gypsum board and gypsum panel products that are not part of a fire-resistance-rated assembly or a shear assembly.
110.3.7 Tenant protection plan compliance inspections. | For buildings undergoing work for which a tenant protection plan is required by Article 120 of Title 28 of the Administrative Code, inspections shall be made by the department to determine compliance with the tenant protection plan. | 110.3.7 Weather-exposed balcony and walking surface waterproofing. | Where balconies or other elevated walking surfaces have weather-exposed surfaces, and the structural framing is protected by an impervious moisture barrier, all elements of the impervious moisture barrier system shall not be concealed until inspected and approved. Exception: Where special inspections are provided in accordance with Section 1705.1.1, Item 3.
|  | 110.3.8 Fire- and smoke-resistant penetrations. | Protection of joints and penetrations in fire-resistance-rated assemblies, smoke barriers and smoke partitions shall not be concealed from view until inspected and approved.
|  | 110.3.9 Energy efficiency inspections. | Inspections shall be made to determine compliance with Chapter 13 and shall include, but not be limited to, inspections for: envelope insulation R- and U-values, fenestration U-value, duct system R-value, and HVAC and water-heating equipment efficiency.
|  | 110.3.10 Other inspections. | In addition to the inspections specified in Sections 110.3.1 through 110.3.9, the building official is authorized to make or require other inspections of any construction work to ascertain compliance with the provisions of this code and other laws that are enforced by the department of building safety.
|  | 110.3.11 Special inspections. | For special inspections, see Chapter 17.
|  | 110.3.12 Final inspection. | The final inspection shall be made after all work required by the building permit is completed.
|  | 110.3.12.1 Flood hazard documentation. | If located in a flood hazard area, documentation of the elevation of the lowest floor as required in Section 1612.4 shall be submitted to the building official prior to the final inspection.
|  | 110.4 Inspection agencies. | The building official is authorized to accept reports of approved inspection agencies, provided that such agencies satisfy the requirements as to qualifications and reliability.
|  | 110.5 Inspection requests. | It shall be the duty of the holder of the building permit or their duly authorized agent to notify the building official when work is ready for inspection. It shall be the duty of the permit holder to provide access to and means for inspections of such work that are required by this code.
|  | 110.6 Approval required. | Work shall not be done beyond the point indicated in each successive inspection without first obtaining the approval of the building official. The building official, upon notification, shall make the requested inspections and shall either indicate the portion of the construction that is satisfactory as completed, or notify the permit holder or the permit holder’s agent wherein the same fails to comply with this code. Any portions that do not comply shall be corrected and such portion shall not be covered or concealed until authorized by the building official.
111.1 General. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 111.1 Change of occupancy. | A building or structure shall not be used or occupied in whole or in part, and a change of occupancy of a building or structure or portion thereof shall not be made, until the building official has issued a certificate of occupancy therefor as provided herein. Issuance of a certificate of occupancy shall not be construed as an approval of a violation of the provisions of this code or of other ordinances of the jurisdiction. Certificates presuming to give authority to violate or cancel the provisions of this code or other ordinances of the jurisdiction shall not be valid. Exception: Certificates of occupancy are not required for work exempt from permits in accordance with Section 105.2.
|  | 111.2 Certificate issued. | After the building official inspects the building or structure and does not find violations of the provisions of this code or other laws that are enforced by the department, the building official shall issue a certificate of occupancy that contains the following:
|  | 111.3 Temporary occupancy. | The building official is authorized to issue a temporary certificate of occupancy before the completion of the entire work covered by the permit, provided that such portion or portions shall be occupied safely. The building official shall set a time period during which the temporary certificate of occupancy is valid.
|  | 111.4 Revocation. | The building official is authorized to suspend or revoke a certificate of occupancy or completion issued under the provisions of this code, in writing, wherever the certificate is issued in error, or on the basis of incorrect information supplied, or where it is determined that the building or structure or portion thereof is in violation of the provisions of this code or other ordinance of the jurisdiction.
112.1 General. | Refer to Chapter 1 of Title 28 of the Administrative Code. | 112.1 Connection of service utilities. | A person shall not make connections from a utility, a source of energy, fuel, or power, or a water system or sewer system to any building or system that is regulated by this code for which a permit is required, until approved by the building official.
|  | 112.2 Temporary connection. | The building official shall have the authority to authorize the temporary connection of the building or system to the utility, the source of energy, fuel, or power, or the water system or sewer system for the purpose of testing systems or for use under a temporary approval.
|  | 112.3 Authority to disconnect service utilities. | The building official shall have the authority to authorize disconnection of utility service to the building, structure or system regulated by this code and the referenced codes and standards in case of emergency where necessary to eliminate an immediate hazard to life or property or where such utility connection has been made without the approval required by Section 112.1 or 112.2. The building official shall notify the serving utility, and wherever possible the owner or the owner’s authorized agent and occupant of the building, structure or service system of the decision to disconnect prior to taking such action. If not notified prior to disconnecting, the owner or the owner’s authorized agent or occupant of the building, structure or service system shall be notified in writing, as soon as practical thereafter.
|  | 113.1 General. | In order to hear and decide appeals of orders, decisions or determinations made by the building official relative to the application and interpretation of this code, there shall be and is hereby created a board of appeals. The board of appeals shall be appointed by the applicable governing authority and shall hold office at its pleasure. The board shall adopt rules of procedure for conducting its business and shall render all decisions and findings in writing to the appellant with a duplicate copy to the building official.
|  | 113.2 Limitations on authority. | An application for appeal shall be based on a claim that the true intent of this code or the rules legally adopted thereunder have been incorrectly interpreted, the provisions of this code do not fully apply or an equivalent or better form of construction is proposed. The board shall not have authority to waive requirements of this code or interpret the administration of this code.
|  | 113.3 Qualifications. | The board of appeals shall consist of members who are qualified by experience and training to pass on matters pertaining to building construction and are not employees of the jurisdiction.
|  | 113.4 Administration. | The building official shall take immediate action in accordance with the decision of the board.
114.1 General. | Refer to Chapter 2 of Title 28 of the Administrative Code. | 114.1 Unlawful acts. | It shall be unlawful for any person, firm or corporation to erect, construct, alter, extend, repair, move, remove, demolish or occupy any building, structure or equipment regulated by this code, or cause same to be done, in conflict with or in violation of any of the provisions of this code.
|  | 114.2 Notice of violation. | The building official is authorized to serve a notice of violation or order on the person responsible for the erection, construction, alteration, extension, repair, moving, removal, demolition or occupancy of a building or structure in violation of the provisions of this code, or in violation of a permit or certificate issued under the provisions of this code. Such order shall direct the discontinuance of the illegal action or condition and the abatement of the violation.
|  | 114.3 Prosecution of violation. | If the notice of violation is not complied with promptly, the building official is authorized to request the legal counsel of the jurisdiction to institute the appropriate proceeding at law or in equity to restrain, correct or abate such violation, or to require the removal or termination of the unlawful occupancy of the building or structure in violation of the provisions of this code or of the order or direction made pursuant thereto.
|  | 114.4 Violation penalties. | Any person who violates a provision of this code or fails to comply with any of the requirements thereof or who erects, constructs, alters or repairs a building or structure in violation of the approved construction documents or directive of the building official, or of a permit or certificate issued under the provisions of this code, shall be subject to penalties as prescribed by law.
115.1 General. | Refer to Chapter 2 of Title 28 of the Administrative Code. | 115.1 Authority. | Where the building official finds any work regulated by this code being performed in a manner contrary to the provisions of this code or in a dangerous or unsafe manner, the building official is authorized to issue a stop work order.
|  | 115.2 Issuance. | The stop work order shall be in writing and shall be given to the owner of the property, the owner’s authorized agent or the person performing the work. Upon issuance of a stop work order, the cited work shall immediately cease. The stop work order shall state the reason for the order and the conditions under which the cited work is authorized to resume.
|  | 115.3 Emergencies. | Where an emergency exists, the building official shall not be required to give a written notice prior to stopping the work.
|  | 115.4 Failure to comply. | Any person who shall continue any work after having been served with a stop work order, except such work as that person is directed to perform to remove a violation or unsafe condition, shall be subject to fines established by the authority having jurisdiction.
116.1 General. | Refer to Chapters 2 and 3 of Title 28 of the Administrative Code. | 116.1 Unsafe conditions. | Structures or existing equipment that are or hereafter become unsafe, insanitary or deficient because of inadequate means of egress facilities, inadequate light and ventilation, or that constitute a fire hazard, or are otherwise dangerous to human life or the public welfare, or that involve illegal or improper occupancy or inadequate maintenance, shall be deemed an unsafe condition. Unsafe structures shall be taken down and removed or made safe, as the building official deems necessary and as provided for in this section. A vacant structure that is not secured against unauthorized entry shall be deemed unsafe.
|  | 116.2 Record. | The building official shall cause a report to be filed on an unsafe condition. The report shall state the occupancy of the structure and the nature of the unsafe condition.
|  | 116.3 Notice. | If an unsafe condition is found, the building official shall serve on the owner of the structure, or the owner’s authorized agent, a written notice that describes the condition deemed unsafe and specifies the required repairs or improvements to be made to abate the unsafe condition, or that requires the unsafe structure to be demolished within a stipulated time. Such notice shall require the person thus notified to declare immediately to the building official acceptance or rejection of the terms of the order.
|  | 116.4 Method of service. | Such notice shall be deemed properly served where a copy thereof is served in accordance with one of the following methods:
|  | 116.5 Restoration or abatement. | Where the structure or equipment determined to be unsafe by the building official is restored to a safe condition, the owner, the owner’s authorized agent, operator or occupant of a structure, premises or equipment deemed unsafe by the building official shall abate or cause to be abated or corrected such unsafe conditions either by repair, rehabilitation, demolition or other approved corrective action. To the extent that repairs, alterations or additions are made or a change of occupancy occurs during the restoration of the structure, such repairs, alterations, additions and change of occupancy shall comply with the requirements of the International Existing Building Code.
106.4 Validity of permit. | The issuance or granting of a permit shall not be construed to be a permit for, or an approval of, any violation of any of the provisions of this code or of any other law. Permits presuming to give authority to violate or cancel the provisions of this code or other law shall not be valid. The issuance of a permit based on construction documents and other data shall not prevent the commissioner from requiring the correction of errors in the construction documents and other data. The commissioner is also authorized to prevent occupancy or use of a structure where in violation of this code or of any other law.
106.5 Foundation and earthwork permits. | In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code and Chapter 33 of this code, applications for foundation and earthwork permits shall include:
1. Notice to adjoining owners. | Proof of notice to adjoining owners as required by Section 3304.3.2.
106.5.1 Notice to the department of commencement of foundation and earthwork. | The foundation and earthwork permit shall be issued on the condition that the applicant will provide written notice to the department at least 24 but no more than 48 hours prior to the commencement of the foundation or earthwork as required by Section 3304.3.1.
106.6 Full demolition permits. | In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code and Chapter 33 of this code, applications for full demolition permits shall include:
1. Utility certifications. | Certifications by the respective utility companies or governmental agencies having jurisdiction that all gas, electric, water, steam and other service lines to the building have been disconnected as required by Section 3303.2.5.
106.6.1 Notice to department of commencement of demolition work. | The full demolition permit shall be issued on the condition that the applicant will provide written notice to the department at least 48 hours prior to the commencement of demolition work.
106.7 Sign permits. | In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code, permits for the erection, alteration or installation of signs shall be subject to the special provisions set forth in Sections 106.7.1 through 106.7.5.
106.7.1 Identification number. | Every sign permit shall have an identification number.
106.7.2 Changing copy or structural change of sign or sign structure. | The changing of copy on a sign not permitted for changeable copy or any structural change of the sign or sign structure shall require a new permit pursuant to this code.
106.7.3 Permit does not constitute authorization for illegal sign. | The issuance of a permit for the erection, alteration or installation of a sign or sign structure issued pursuant to this code shall not be deemed to constitute permission or authorization to maintain a sign that would otherwise be illegal without a maintenance permit for an outdoor sign if required pursuant to this code and department rule or that is otherwise illegal pursuant to any other provision of law nor shall any permit issued hereunder constitute a defense in an action or proceeding with respect to such an unlawful sign.
106.7.4 Name and business address of licensed sign hanger. | The application shall contain the name and business address of the licensed sign hanger who is to perform or supervise the proposed work.
106.7.5 Outdoor advertising company. | If the sign or sign location is under the control of an outdoor advertising company, as defined in Chapter 5 of Title 28 of the Administrative Code, the application shall be accompanied by the name and, where provided by rule, the registration number of such outdoor advertising company.
106.8 Temporary construction installation permits. | In addition to the requirements of Chapter 1 of Title 28 of the Administrative Code, permits for the erection, installation and use of temporary construction installations shall be subject to the special provisions set forth in Sections 106.8.1 through 106.8.3.
106.8.1 Application. | The need for each specific item of temporary construction installation shall be stated on the application.
106.8.2 Term of permit. | Notwithstanding any other provision of this code, a temporary construction installation permit shall expire 1 year from the date of issuance, or when the permit holder’s insurance or street obstruction bond expires, whichever is earlier. Such permit shall be renewable. Such permit must be in effect at all times during which the temporary construction installation is at the work site.
106.8.3 Special provisions for renewal of permit for a sidewalk shed. | An application for the renewal of a temporary construction installation permit for a sidewalk shed used in connection with the alteration of a building shall be accompanied by a report, acceptable to the department, prepared by a registered design professional who has examined that part of the premises on which the work requiring the use of a sidewalk shed is being performed. Such report shall document the condition of the applicable part of the premises and the scope of work that has been performed thereon since the issuance of the permit and shall provide an estimate of the additional time needed to complete the work.
106.9 Mandatory sewer and catch basin work required by Section 24-526 of the Administrative Code. | In addition to the requirements of Chapter 1 of Title 28, an applicant for a permit who is required pursuant to Section 24-526 of the Administrative Code to construct or repair defects in sewers or catch basins that lie outside the property shall submit certification from the Department of Environmental Protection that the applicant or owner has provided the Department of Environmental Protection with:
1. A performance bond or other security satisfactory to the Department of Environmental Protection and approved as to form by the Law Department for the full cost, as estimated by the Department of Environmental Protection, of constructing the part of the storm water drainage system for such property which shall lay outside the property line and repairing defects in such construction, if and as required by Section 24-526 of the Administrative Code;.
106.10 Permits with respect to limited alteration applications. | For permits with respect to limited alteration applications, refer to Sections 28-101.5 and 28-104.6, Exception 1, of the Administrative Code.
107.6 Architectural plans. | Construction documents for all buildings shall provide detailed drawings of all architectural elements of the building showing compliance with the code, including but not limited to doors, windows and interior finish schedules, details necessary to substantiate all required fire-protection characteristics, details demonstrating compliance with the New York City Energy Conservation Code and details demonstrating compliance with all accessibility requirements of this code. Plans shall also provide details of the exterior wall envelope as required, including but not limited to flashing, insulation, vapor retarder, intersections with dissimilar materials, corners, end details, control joints, intersections at roof, eaves or parapets, means of drainage, water-resistive membrane and details around openings. Exception: Where a curtain wall system is to be employed containing elements that are normally detailed on shop or working drawings, approval of construction documents shall be conditioned upon deferred submittal of such shop or working drawings showing the approval of the registered design professional who prepared the architectural construction documents, or of a signed statement by such registered design professional that such drawings were prepared to his or her satisfaction. In such cases, submittal of construction documents showing compliance with the New York City Energy Conservation Code related to such curtain wall may also be deferred. Such deferred submittal of construction documents must demonstrate that the estimated annual energy use for the envelope in the energy analysis submitted as part of the initial filing is not exceeded.
107.7 Structural plans. | Structural plans shall include the data and information described in this section and in Chapter 16. Structural calculations shall be made available to the department upon request. Exceptions: 1. Where structural elements are normally detailed on shop or working drawings, approval of construction documents shall be conditioned upon deferred submittal of such shop or working drawings showing the approval of the registered design professional who prepared the structural construction documents, or of a signed statement by such registered design professional that such drawings were prepared to his or her satisfaction. 2. In cases where the detailing of structural elements has been made on the basis of fire-resistance ratings, load tables, or similar data as given in manufacturer’s catalogues, approval of construction documents shall be conditional upon submission of a manufacturer’s des¬ignation attesting to the accuracy of the data and indicating that such data were derived in conformance with the provisions of this code. Where the detailing of structural elements has been made on the basis of data published in technical documents of recognized authority issued or accredited by the agency or association promulgating the applicable referenced standard, such manufacturer’s designation will not be required.
1. Where structural elements are normally detailed on shop or working drawings, approval of construction documents shall be conditioned upon deferred submittal of such shop or working drawings showing the approval of the registered design professional who prepared the structural construction documents, or of a signed statement by such registered design professional that such drawings were prepared to his or her satisfaction.
107.7.1 Foundation plans. | Foundation plans shall show compliance with the requirements of Chapter 18 of this code regarding foundation design and shall show the plan locations, design loads, design elevations of the bottoms, and details as to sizes, reinforcements, and construction of all footings, piers, foundation walls, pile groups, and pile caps. The foundation systems shown on plans shall be of a type indicated in the geotechnical report required by Section 1803.6. The levels of footings of adjacent structures shall be indicated or, if the adjacent structures are pile supported, this shall be stated. Where applicable, the plans shall include underpinning details. In addition, there shall be a statement indicating the character and minimum class of the soil strata required for the support of the foundation; the allowable soil pressure used for the design of footings; and the character, class, and presumptive bearing capacity of the bearing stratum to which piling is required to penetrate. The types and design capacities of piling and the records of required borings or test pits shall also be shown. In addition, foundation plans shall include insulation details as required by the New York City Energy Conservation Code.
107.7.2 Floor plans. | Floor plans and sections showing all structural requirements shall be provided for all levels.
107.7.3 Detailed drawings. | Drawings shall show sizes, sections, and locations of members, and such other information as may be required to indicate clearly all structural elements and special structural engineering features.
107.7.4 Column schedules. | Column schedules shall show the design load contributed by the framing at any level and the total accumulated design load at each level.
107.7.5 Truss forces. | Where trusses are employed, a diagram or table shall indicate the loads or moments in the various members under the design loading conditions. The requirement for a diagram or table may be waived when the trusses consist of elements selected from load tables or similar data, subject to the requirements for verification described in this code.
107.7.6 Prestressing forces. | Where pre-stressed members are employed, a schedule or table shall show the total prestressing forces and the method and sequence of application.
107.8 Earthwork plans. | Where the application is sought solely for or includes earthwork, excavation or fill operations, including but not limited to site decontamination, soil remediation and grading, the applicant shall submit 1) a lot diagram showing the exact location of the lot and dimensions to the nearest corner; and 2) plans showing the exact location, extent, and depth or height of the proposed earthwork, excavation or fill operation and any existing utilities, foundations or other infrastructure potentially impacted by the earthwork, excavation or fill operation. For excavation operations, the plans shall also indicate the levels of footings of all adjacent structures or, if the adjacent structures are pile supported, this shall be stated. Where applicable, the plans shall also include underpinning details, soil information in accordance with Chapter 18, and a final grading plan representing the lot after all earthwork, excavation or fill operations have been completed.
107.9 Fire protection system plans. | Construction documents for fire protection systems shall include a plot plan to scale indicating the location of the system in relation to the rest of the building and shall comply with Sections 107.9.1 through 107.9.4. Such plans shall not be required in connection with applications for limited standpipe alterations and limited sprinkler alterations.
107.9.1 Sprinkler systems. | Sprinkler systems plans shall comply with Section 903.1.2.
107.9.2 Alternative automatic fire-extinguishing systems. | Notwithstanding any other provision of this code, design and installation documents for the installation of alternative automatic fire-extinguishing systems shall be filed with and reviewed by the Fire Department for compliance with this code, the New York City Fire Code and other applicable laws and regulations in accordance with Section 105 of the New York City Fire Code.
107.9.3 Standpipe systems. | Standpipe systems plans shall comply with Section 905.1.1.
107.9.4 Fire alarm and detection systems. | Fire alarm and detection systems plans shall comply with Section 907.1.1.
107.10 Sign installation plans. | Construction documents for sign applications shall comply with Section H105.2 of Appendix H.
107.11 Discharge of sewage and discharge and/or management of stormwater runoff. | Applications for construction document approval shall comply with Sections 107.11.1, 107.11.2 and 107.11.3.
107.11.1 Sewage. | Applications for construction document approval shall include submittal documents relating to the availability and feasibility of a public sanitary or public combined sewer and/or other approved discharge for sewage in accordance with Sections 107.11.1.1 and 107.11.1.2 for the following types of applications:
1. New buildings that include any fixtures that produce sewage;.
107.11.1.1 Connection feasible and available. | Where a public sanitary or combined sewer is certified by the Department of Environmental Protection or certified by an applicant in accordance with rules of such department to be available and connection thereto feasible, the applicant shall submit:
1. Department of Environmental Protection certification of availability and feasibility. | A sewer certification issued by the Department of Environmental Protection that a public sanitary or combined sewer is available and connection thereto is feasible. Applications for such certification shall be made to the Department of Environmental Protection on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) and shall be reviewed and approved by such department in accordance with the rules of such department. Such certification may be conditioned by such department on part or all of the sewage to be disposed of with an on-site disposal system or with the use of an alternative disposal system; or
107.11.1.2 Connection not feasible or not available. | Where a public sanitary or combined sewer is not available, or where connection thereto is not feasible, the applicant shall submit: 1. Department of Environmental Protection or applicant certification of unavailability or non-feasibility.(i) A certification issued by the Department of Environmental Protection that a public sanitary or combined sewer is not available or that connection to an available sewer is not feasible. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) or (ii) A certification submitted by the applicant to the Department of Environmental Protection that a public sanitary or combined sewer is not available or that connection thereto is not feasible, in such cases where the availability and feasibility of connection to a public sanitary or combined sewer are allowed to be certified by the applicant pursuant to the rules of such department. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); and1. Department of Environmental Protection or applicant certification of unavailability or non-feasibility. (i) Certification issued by the Department of Environmental Protection that a public storm or combined sewer is not available or that connection thereto is not feasible. Such certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); or (ii) Certification submitted by the applicant to the Department of Environmental Protection that a public storm or combined sewer is not available or that connection thereto is not feasible, in such cases where the availability and feasibility of connection to a public storm or combined sewer are allowed to be certified by the applicant pursuant to rules of such department. Certification shall be on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department); and
107.11.2 Stormwater. | Applications for construction document approval shall include submittal documents relating to the availability and feasibility of a public combined or storm sewer or other approved method for stormwater discharge in accordance with Sections 107.11.2.1 and 107.11.2.2 for the following types of applications: 1. New buildings; 2. Alterations of buildings proposing horizontal building enlargement; and/or 3. Alterations that increase impervious surfaces on the tax lot. Exceptions: 1. Applications for construction document approval for the alteration of an existing one- or two-family dwelling need not include such submittal documents, where the footprint of a proposed horizontal building enlargement and any proposed increase in impervious surfaces combined is less than or equal to 200 square feet (19 m2). Construction documents shall include the amount of proposed increase in impervious area. 1.1 This exception shall not apply if the horizontal building enlargement and increase in impervious surface related to the current application for construction document approval and any other enlargement or increase in impervious surface made on the same tax lot after July 1, 2008 together exceed 200 square feet (19 m2). 2 Applications for construction document approval for the alteration of a building need not include such submittal documents, where the increase in area of the footprint resulting from a proposed horizontal building enlargement and any proposed increase in impervious surfaces on a lot combined is less than or equal to 1,000 square feet (93 m2), and on-site disposal of stormwater conforming to the provisions of the applicable laws and rules as determined by the department is proposed for such enlargement and/or increase in impervious surface. Construction documents shall include the amount of proposed increase in impervious area. 2.1 This exception shall not apply where on-site disposal cannot be designed to conform to the provisions of the applicable laws and rules including but not limited to minimum required distances from lot lines or structures or subsoil conditions as determined by the department. 2.2 This exception shall not apply if the horizontal building enlargement and increase in impervious surface related to the current application for construction document approval and all other enlargements or increases in impervious surface made on the same tax lot after July 1, 2008 together exceed 1000 square feet (93 m2).
1. New buildings;.
1. Applications for construction document approval for the alteration of an existing one- or two-family dwelling need not include such submittal documents, where the footprint of a proposed horizontal building enlargement and any proposed increase in impervious surfaces combined is less than or equal to 200 square feet (19 m2). | Construction documents shall include the amount of proposed increase in impervious area.
1.1 This exception shall not apply if the horizontal building enlargement and increase in impervious surface related to the current application for construction document approval and any other enlargement or increase in impervious surface made on the same tax lot after July 1, 2008 together exceed 200 square feet (19 m2).
107.11.2.1 Connection feasible and available. | Where a public combined or storm sewer is certified by the Department of Environmental Protection or certified by an applicant in accordance with rules of such department to be available and connection thereto is feasible, applicants shall submit:
1 Department of Environmental Protection certification of availability and feasibility. | A sewer certification issued by the Department of Environmental Protection that a public storm or combined sewer is available and connection thereto is feasible. Applications for such certification shall be made to the Department of Environmental Protection on forms specified by such department (Department of Environmental Protection “house/site connection proposal application” or other form as specified in the rules of such department) and shall be reviewed and approved by such department in accordance with the rules of such department. Such certification may be conditioned by such department on part or all of the stormwater runoff to be disposed of through an on-site detention or retention system, or by use of alternative disposal methods including but not limited to ditches, swales or watercourses; or
107.11.2.2 Connection not feasible or not available. | Where a public combined or storm sewer is not available, or where connection thereto is not feasible, applicants shall submit:
107.11.3 Post-construction stormwater management facilities. | A post-construction stormwater management facility that is constructed as part of a covered development project shall comply with the rules of the Department of Environmental Protection and with this code.
107.12 Predemolition photographs. | In addition to the requirements of Section 3306.3, construction documents for full demolition shall comply with the following requirements for archival photographs: 1. Number required. Applications shall contain two sets of photographs of the building or buildings to be demolished or removed. Both sets shall be received by the department on behalf of the New York City Landmarks Preservation Commission and the New York City Municipal Archives Division of the Department of Records and Information Services. 2. Format. The photographs shall conform to the standards and specifications established by rules promulgated by the commissioner upon the advice of the commissioner of the Department of Records and Information Services and the chairperson of the Landmarks Preservation Commission. Exception: Applications made on behalf of the New York City Department of Housing Preservation and Development or made pursuant to Article 215 of Chapter 2 of Title 28 of the Administrative Code are exempt from the requirements of this section.
1. Number required. | Applications shall contain two sets of photographs of the building or buildings to be demolished or removed. Both sets shall be received by the department on behalf of the New York City Landmarks Preservation Commission and the New York City Municipal Archives Division of the Department of Records and Information Services.
107.13 Energy efficiency plans. | Construction documents shall include compliance documentation as required by the New York City Energy Conservation Code.
107.14 Mechanical and fuel gas plans. | Construction documents for gas piping, heating, ventilation, refrigeration and other mechanical work to be performed shall be submitted as per New York City Mechanical and Fuel Gas Codes.
107.15 Plumbing plans. | Construction documents for plumbing work to be performed shall be submitted as per the New York City Plumbing Code.
107.16 Flood zone compliance plans. | Flood zone compliance plans demonstrating compliance with Appendix G shall be submitted with applications for construction document approval for projects located within a flood hazard area, or where required by Appendix G.
107.17 Retention of construction and submittal documents. | Refer to Section 28-104.12 of the Administrative Code.
107.18 Construction documents for extension or relocation of an existing chimney or vent. | Where an owner of a new or altered taller building is required by Section 801 of the New York City Mechanical Code, Section 501 of the New York City Fuel Gas Code, or Section 2113 of this code, to extend, alter or relocate an existing chimney or vent on an affected building, the construction documents for the new or altered taller building shall comply with the requirements of Section 107.18.1 of this code.
107.18.1 Chimney and vent plan. | At the time of initial filing for construction, a chimney and vent plan shall be included as part of the construction documents. Such chimney and vent plan shall include the following information for all chimneys and vents within 100 feet (30 480 mm) of construction:
110.3 Required progress inspections. | The inspections set forth in Sections 110.3.1 through 110.3.7 shall be made during the progress of work to verify substantial compliance with the code and with approved construction documents.
110.4 Special inspections. | Special inspections required by this code or by the commissioner shall be performed by special inspection agencies.
110.5 Final inspection. | Refer to Article 116 of Chapter 1 of Title 28 of the Administrative Code.
110.6 Issuance of certificate of compliance. | Upon satisfactory inspection of service equipment and the satisfaction of all the requirements for sign-off, the department shall issue a certificate of compliance as applicable for the following service equipment:
1. Elevators;.
110.7 Approved inspection agencies. | Refer to Articles 114 and 115 of Chapter 1 of Title 28 of the Administrative Code.
110.8 Inspection requests. | Refer to Chapter 1 of Title 28 of the Administrative Code.
110.9 Satisfactory inspection report required. | Portions of work requiring inspection may be sequenced or phased to allow continuing progress of that work provided that work shall not be done beyond the point indicated in each successive required inspection for that phase. The inspector shall either indicate the portion of the construction that is satisfactory as completed, or notify the permit holder or the superintendent of construction wherein the same fails to comply with this code. Any portions that do not comply shall be corrected and such portion shall not be covered or concealed until corrected. The person performing the inspection shall complete a report of satisfactory inspection. Refer to Chapter 1 of Title 28 of the Administrative Code.

## BC2
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
201.1 Scope. | Unless otherwise expressly stated, the following words and terms shall, for the purposes of this code, have the meanings shown in this chapter. | 201.1 Scope. | Unless otherwise expressly stated, the following words and terms shall, for the purposes of this code, have the meanings shown in this chapter.
201.2 Interchangeability. | Words used in the present tense include the future; words stated in the masculine gender include the feminine and neuter; the singular number includes the plural and the plural, the singular. | 201.2 Interchangeability. | Words used in the present tense include the future; words stated in the masculine gender include the feminine and neuter; the singular number includes the plural and the plural, the singular.
201.3 Terms defined in other codes. | Where terms are not defined in this code and are defined in the New York City Fuel Gas Code, New York City Fire Code, New York City Mechanical Code, New York City Electrical Code, New York City Plumbing Code, or the New York City Energy Conservation Code, such terms shall have the meanings ascribed to them as in those codes. | 201.3 Terms defined in other codes. | Where terms are not defined in this code and are defined in the International Energy Conservation Code, International Fuel Gas Code, International Fire Code, International Mechanical Code or International Plumbing Code, such terms shall have the meanings ascribed to them as in those codes.
201.3.1 Terms defined in the general administrative provisions. | The following terms are defined in Section 28-101.5 of the Administrative Code:
201.4 Terms not defined. | Where terms are not defined through the methods authorized by this section, such terms shall have ordinarily accepted meanings such as the context implies. | 201.4 Terms not defined. | Where terms are not defined through the methods authorized by this section, such terms shall have ordinarily accepted meanings such as the context implies.
24-HOUR BASIS. | The actual time that a person is an occupant within a facility for the purpose of receiving care. It shall not include a facility that is open for 24 hours and is capable of providing care to someone visiting the facility during any segment of the 24 hours. | 24-HOUR BASIS. | The actual time that a person is an occupant within a facility for the purpose of receiving care. It shall not include a facility that is open for 24 hours and is capable of providing care to someone visiting the facility during any segment of the 24 hours.
2. The unusual and rapid accumulation or runoff of surface waters from any source.
2. Any type of injury to a member of the public;.
2. Such enclosure shall be constructed solely of flood-resistant materials and finishes;.
2. The space is primarily used for the provision of medical services to persons, including, but not limited to, consultation, evaluation, monitoring and treatment services.
2. Spaces primarily used for the provision of medical services identified in 10 NYCRR 703.
2. Structural members having direct connections to the columns, including girders, beams, trusses and spandrels;.
2. Members of the floor construction not having direct connections to the columns; and.
2.1.
2.2.
2.2.1.
2.2.2.
2.2.3.
2. Float tanks or relaxation tanks sized for use by one person at a time.
2. Any masonry or concrete wall that supports more than 200 pounds per linear foot (2919 N/m) of vertical load in addition to its own weight.

## BC3
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
301.1 Scope. | The provisions of this chapter shall control the classification of all buildings and structures, and spaces therein, as to use and occupancy. | 301.1 General. | The provisions of this chapter shall control the classification of all buildings and structures as to occupancy and use. Different classifications of occupancy and use represent varying levels of hazard and risk to building occupants and adjacent properties.
302.1 General. | Structures or portions of structures shall be classified with respect to occupancy in one or more of the groups listed below. A room or space that is intended to be occupied at different times for different purposes shall comply with all of the requirements that are applicable to each of the purposes for which the room or space will be occupied. Structures with multiple occupancies or uses shall comply with Section 508. Where a structure, or portion thereof, is proposed for a purpose that is not specifically provided for in this code, such structure, or portion thereof, shall be classified in the group that the occupancy most nearly resembles, according to the fire safety and relative hazard involved, and as approved by the commissioner. | 302.1 Occupancy classification. | Occupancy classification is the formal designation of the primary purpose of the building, structure or portion thereof. Structures shall be classified into one or more of the occupancy groups specified in this section based on the nature of the hazards and risks to building occupants generally associated with the intended purpose of the building or structure. An area, room or space that is intended to be occupied at different times for different purposes shall comply with all applicable requirements associated with such potential multipurpose. Structures containing multiple occupancy groups shall comply with Section 508. Where a structure is proposed for a purpose that is not specified in this section, such structure shall be classified in the occupancy it most nearly resembles based on the fire safety and relative hazard. Occupied roofs shall be classified in the group that the occupancy most nearly resembles, according to the fire safety and relative hazard, and shall comply with Section 503.1.4 .
303.1 Assembly Group A. | Assembly Group A occupancy includes, among others, the use of a building or structure or a portion thereof, excluding a dwelling unit, for the gathering of any number of persons for purposes such as civic, social or religious functions, recreation, food or drink consumption, awaiting transportation, or similar group activities; or when occupied by 75 persons or more for educational or instructional purposes. | 303.1 Assembly Group A. | Assembly Group A occupancy includes, among others, the use of a building or structure, or a portion thereof, for the gathering of persons for purposes such as civic, social or religious functions; recreation, food or drink consumption or awaiting transportation.
|  | 302.2 Use designation. | Occupancy groups contain subordinate uses having similar hazards and risks to building occupants. Uses include, but are not limited to, those functional designations specified within the occupancy group descriptions in Section 302.1. Certain uses require specific limitations and controls in accordance with the provisions of Chapter 4 and elsewhere in this code.
303.1.1 Definitions. | The following term is defined in Chapter 2: | 303.1.1 Small buildings and tenant spaces. | A building or tenant space used for assembly purposes with an occupant load of less than 50 persons shall be classified as a Group B occupancy.
303.1.2 Buildings and nonaccessory tenant spaces. | A building or nonaccessory tenant space used for assembly purposes with an occupant load of fewer than 75 persons shall be classified as a Group B occupancy, except that the number of plumbing fixtures for such a building or space is permitted to be calculated in accordance with the requirements for assembly occupancies. | 303.1.2 Small assembly spaces. | The following rooms and spaces shall not be classified as Assembly occupancies:
303.2 Assembly Group A-1. | Group A-1 occupancy includes assembly uses, usually with fixed seating, intended for the production and viewing of the performing arts or motion pictures including, but not limited to: | 303.2 Assembly Group A-1. | Group A-1 occupancy includes assembly uses, usually with fixed seating, intended for the production and viewing of the performing arts or motion pictures including, but not limited to:
303.1.3 Accessory assembly spaces. | A room or space used for assembly purposes with an occupant load of fewer than 75 persons and accessory to another occupancy shall be classified as a Group B occupancy or as part of that occupancy, except that the number of plumbing fixtures for such a room or space is permitted to be calculated in accordance with the requirements for assembly occupancies. | 303.1.3 Associated with Group E occupancies. | A room or space used for assembly purposes that is associated with a Group E occupancy is not considered a separate occupancy.
303.3 Assembly Group A-2. | Group A-2 occupancy includes assembly uses intended for food and/or drink consumption including, but not limited to: | 303.3 Assembly Group A-2. | Group A-2 occupancy includes assembly uses intended for food and/or drink consumption including, but not limited to:
|  | 303.1.4 Accessory to places of religious worship. | Accessory religious educational rooms and religious auditoriums with occupant loads of less than 100 per room or space are not considered separate occupancies.
303.4 Assembly Group A-3. | Group A-3 occupancy includes assembly uses intended for worship, recreation or amusement and other assembly uses not classified elsewhere in Group A including, but not limited to: | 303.4 Assembly Group A-3. | Group A-3 occupancy includes assembly uses intended for worship, recreation or amusement and other assembly uses not classified elsewhere in Group A including, but not limited to:
|  | 303.1.5 Special amusement areas. | Special amusement areas shall comply with Section 411.
303.5 Assembly Group A-4. | Group A-4 occupancy includes assembly uses intended for viewing of indoor sporting events and activities with spectator seating including, but not limited to: | 303.5 Assembly Group A-4. | Group A-4 occupancy includes assembly uses intended for viewing of indoor sporting events and activities with spectator seating including, but not limited to:
303.6 Assembly Group A-5. | Group A-5 occupancy includes assembly uses intended for participation in or viewing outdoor activities including, but not limited to: | 303.6 Assembly Group A-5. | Group A-5 occupancy includes assembly uses intended for participation in or viewing outdoor activities including, but not limited to:
304.1 Business Group B. | Business Group B occupancy includes, among others, the use of a building or structure, or a portion thereof, for office, professional, service-type transactions, or for conducting public or civic services, including the incidental storage of records and accounts and the incidental storage of limited quantities of stocks of goods for office use or purposes. Business Group B occupancies shall include, but not be limited to, the following: | 304.1 Business Group B. | Business Group B occupancy includes, among others, the use of a building or structure, or a portion thereof, for office, professional or service-type transactions, including storage of records and accounts. Business occupancies shall include, but not be limited to, the following:
305.1 Educational Group E. | Educational Group E occupancy includes, among others, the use of a building or structure, or a portion thereof, by five or more persons at any one time for educational purposes offered to children through the 12th grade and where no more than two children are under the age of 2, including but not limited to the following: Academies Day care facilities where no more than two children are under the age of 2 Libraries accessory to Group E occupancies Schools Exceptions: 1. Classrooms and instructional rooms with 75 or more persons shall be classified as Group A-3. 2. Day care services provided within a dwelling unit as described in Section 310. 3. Custodial care facilities with up to 30 children under the age of 2 are permitted to be classified as Group E when the rooms where such children are cared for are located on the level of exit discharge and each of these child care rooms has an exit door directly to the exterior. | 305.1 Educational Group E. | Educational Group E occupancy includes, among others, the use of a building or structure, or a portion thereof, by six or more persons at any one time for educational purposes through the 12th grade.
304.2 Definitions. | The following terms are defined in Chapter 2: | 304.2 Airport traffic control towers. | Airport traffic control towers shall comply with Section 412.2.
306.1 Factory Industrial Group F. | Factory Industrial Group F occupancy includes, among others, the use of a building or structure, or a portion thereof, for assembling, disassembling, fabricating, finishing, manufacturing, packaging, repair, cleaning, laundering or processing operations that are not classified as a Group H hazardous occupancy. Factory Industrial Group F occupancy also includes certain mechanical and/or electrical equipment rooms in accordance with Section 306.3. | 306.1 Factory Industrial Group F. | Factory Industrial Group F occupancy includes, among others, the use of a building or structure, or a portion thereof, for assembling, disassembling, fabricating, finishing, manufacturing, packaging, repair or processing operations that are not classified as a Group H hazardous or Group S storage occupancy.
|  | 304.3 Ambulatory care facilities. | Ambulatory care facilities shall comply with Section 422.
306.2 Moderate-hazard factory industrial, Group F-1. |  | 306.2 Moderate-hazard factory industrial, Group F-1. | Factory industrial uses that are not classified as Factory Industrial F-2 Low Hazard shall be classified as F-1 Moderate Hazard and shall include, but not be limited to, the following:
|  | 304.4 Higher education laboratories. | Higher education laboratories shall comply with Section 428.
306.3 Low-hazard factory industrial, Group F-2. | Factory industrial uses that involve the cleaning, laundering, fabrication or manufacturing of noncombustible materials that during finishing, packing or processing do not involve a significant fire hazard shall be classified as F-2 occupancies and shall include, but not be limited to, the following: | 306.3 Low-hazard factory industrial, Group F-2. | Factory industrial uses that involve the fabrication or manufacturing of noncombustible materials that during finishing, packing or processing do not involve a significant fire hazard shall be classified as F-2 occupancies and shall include, but not be limited to, the following:
|  | 305.1.1 Accessory to places of religious worship. | Religious educational rooms and religious auditoriums, which are accessory to places of religious worship in accordance with Section 303.1.4 and have occupant loads of less than 100 per room or space, shall be classified as Group A-3 occupancies.
307.1 High-hazard Group H. | High-hazard Group H occupancy includes, among others, the use of a building or structure, or a portion thereof, that involves the manufacturing, processing, generation or storage of materials that constitute a physical or health hazard in quantities in excess of those allowed in control areas complying with Section 414, based on the maximum allowable quantity limits for control areas set forth in Tables 307.1(1) and 307.1(2). Hazardous occupancies are classified in Groups H-1, H-2, H-3, H-4 and H-5 and shall be in accordance with this section, the requirements of Section 415 and the New York City Fire Code. | 307.1 High-hazard Group H. | High-hazard Group H occupancy includes, among others, the use of a building or structure, or a portion thereof, that involves the manufacturing, processing, generation or storage of materials that constitute a physical or health hazard in quantities in excess of those allowed in control areas complying with Section 414, based on the maximum allowable quantity limits for control areas set forth in Tables 307.1(1) and 307.1(2). Hazardous occupancies are classified in Groups H-1, H-2, H-3, H-4 and H-5 and shall be in accordance with this section, the requirements of Section 415 and the International Fire Code. Hazardous materials stored, or used on top of roofs or canopies, shall be classified as outdoor storage or use and shall comply with the International Fire Code. |  | See BC03 Tables&Figures
305.2 Reserved. |  | 305.2 Group E, day care facilities. | This group includes buildings and structures or portions thereof occupied by more than five children older than 21/2 years of age who receive educational, supervision or personal care services for fewer than 24 hours per day.
307.1.1 Uses other than Group H. | An occupancy that stores, uses or handles hazardous materials as described in one or more of the following items shall not be classified as Group H, but shall be classified as the occupancy that it most nearly resembles. | 307.1.1 Uses other than Group H. | An occupancy that stores, uses or handles hazardous materials as described in one or more of the following items shall not be classified as Group H, but shall be classified as the occupancy that it most nearly resembles.
|  | 305.2.1 Within places of religious worship. | Rooms and spaces within places of religious worship providing such day care during religious functions shall be classified as part of the primary occupancy.
|  | 305.2.2 Five or fewer children. | A facility having five or fewer children receiving such day care shall be classified as part of the primary occupancy.
|  | 305.2.3 Five or fewer children in a dwelling unit. | A facility such as the above within a dwelling unit and having five or fewer children receiving such day care shall be classified as a Group R-3 occupancy or shall comply with the International Residential Code.
307.3 High-hazard Group H-1. | Buildings and structures containing materials that pose a detonation hazard shall be classified as Group H-1. Such materials shall include, but not be limited to, the following: | 307.3 High-hazard Group H-1. | Buildings and structures containing materials that pose a detonation hazard shall be classified as Group H-1. Such materials shall include, but not be limited to, the following:
|  | 305.3 Storm shelters in Group E occupancies. | Storm shelters shall be provided for Group E occupancies where required by Section 423.5.
307.3.1 Occupancies containing explosives not classified as H-1. | The following occupancies containing explosive materials shall be classified as follows: | 307.3.1 Occupancies containing explosives not classified as H-1. | The following occupancies containing explosive materials shall be classified as follows:
307.4 High-hazard Group H-2. | Buildings and structures containing materials that pose a deflagration hazard or a hazard from accelerated burning shall be classified as Group H-2. Such materials shall include, but not be limited to, the following: | 307.4 High-hazard Group H-2. | Buildings and structures containing materials that pose a deflagration hazard or a hazard from accelerated burning shall be classified as Group H-2. Such materials shall include, but not be limited to, the following:
307.5 High-hazard Group H-3. | Buildings and structures containing materials that readily support combustion or that pose a physical hazard shall be classified as Group H-3. Such materials shall include, but not be limited to, the following: | 307.5 High-hazard Group H-3. | Buildings and structures containing materials that readily support combustion or that pose a physical hazard shall be classified as Group H-3. Such materials shall include, but not be limited to, the following:
|  | 306.2.1 Aircraft manufacturing facilities. | Aircraft manufacturing facilities shall comply with Section 412.6.
307.6 High-hazard Group H-4. | Buildings and structures containing materials that are health hazards shall be classified as Group H-4. Such materials shall include, but not be limited to, the following: | 307.6 High-hazard Group H-4. | Buildings and structures containing materials that are health hazards shall be classified as Group H-4. Such materials shall include, but not be limited to, the following:
307.7 High-hazard Group H-5. | Semiconductor fabrication facilities and comparable research and development areas in which hazardous production materials (HPM) are used and the aggregate quantity of materials is in excess of those listed in Tables 307.1(1) and 307.1(2) shall be classified as Group H-5. Such facilities and areas shall be designed and constructed in accordance with Section 415.11. | 307.7 High-hazard Group H-5. | Semiconductor fabrication facilities and comparable research and development areas in which hazardous production materials (HPM) are used and the aggregate quantity of materials is in excess of those specified in Table 307.1(1) and Table 307.1(2) shall be classified as Group H-5. Such facilities and areas shall be designed and constructed in accordance with Section 415.11. |  | See BC03 Tables&Figures
307.8 Multiple hazards. | Buildings and structures containing a material or materials representing hazards that are classified in one or more of Groups H-1, H-2, H-3 and H-4 shall conform to the code requirements for each of the occupancies so classified. | 307.8 Multiple hazards. | Buildings and structures containing a material or materials representing hazards that are classified in one or more of Groups H-1, H-2, H-3 and H-4 shall conform to the code requirements for each of the occupancies so classified.
308.1 Institutional Group I. | Institutional Group I occupancy includes, among others, the use of a building or structure, or a portion thereof, in which care or supervision is provided to persons who are or are not capable of self-preservation without physical assistance or in which persons are detained for penal or correctional purposes or in which the liberty of the occupants is restricted. Institutional occupancies shall be classified as Group I-1, I-2, I-3 or I-4. | 308.1 Institutional Group I. | Institutional Group I occupancy includes, among others, the use of a building or structure, or a portion thereof, in which care or supervision is provided to persons who are or are incapable of self-preservation without physical assistance or in which persons are detained for penal or correctional purposes or in which the liberty of the occupants is restricted. Institutional occupancies shall be classified as Group I-1, I-2, I-3 or I-4.
307.2 Definitions. | The following terms are defined in Chapter 2: | 307.2 Hazardous materials. | Hazardous materials in any quantity shall conform to the requirements of this code, including Section 414 , and the International Fire Code.
308.2 Definitions. | This section contains provisions for definitions of terms defined elsewhere in this code as well as the terms with definitions specific to this section. | 308.2 Institutional Group I-1. | Institutional Group I-1 occupancy shall include buildings, structures or portions thereof for more than 16 persons, excluding staff, who reside on a 24-hour basis in a supervised environment and receive custodial care. Buildings of Group I-1 shall be classified as one of the occupancy conditions specified in Section 308.2.1 or 308.2.2 and shall comply with Section 420. This group shall include, but not be limited to, the following:
308.2.1 Terms defined elsewhere in this code. | The following terms are defined in Chapter 2: | 308.2.1 Condition 1. | This occupancy condition shall include buildings in which all persons receiving custodial care who, without any assistance, are capable of responding to an emergency situation to complete building evacuation.
308.2.2 Definitions specific to this section. | The following words and terms shall, for the purposes of this section, have the meanings shown herein: | 308.2.2 Condition 2. | This occupancy condition shall include buildings in which there are any persons receiving custodial care who require limited verbal or physical assistance while responding to an emergency situation to complete building evacuation.
|  | 308.2.3 Six to 16 persons receiving custodial care. | A facility housing not fewer than six and not more than 16 persons receiving custodial care shall be classified as Group R-4.
|  | 308.2.4 Five or fewer persons receiving custodial care. | A facility with five or fewer persons receiving custodial care shall be classified as Group R-3 or shall comply with the International Residential Code provided an automatic sprinkler system is installed in accordance with Section 903.3.1.3 or Section P2904 of the International Residential Code.
308.3 Institutional Group I-1. | Institutional Group I-1 occupancy shall include buildings, structures or parts thereof housing persons, on a 24-hour basis, who because of age, mental disability or other reasons, live in a supervised residential environment that provides personal care services. The occupants are capable of self-preservation and capable of responding to an emergency situation without physical assistance from staff. Such occupancy shall be subject to the New York State Multiple Dwelling Law. This group shall include, but not be limited to, the following: | 308.3 Institutional Group I-2. | Institutional Group I-2 occupancy shall include buildings and structures used for medical care on a 24-hour basis for more than five persons who are incapable of self-preservation. This group shall include, but not be limited to, the following:
308.3.1 Adult homes and enriched housing. | Adult homes and enriched housing facilities operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health offering care on a 24-hour basis to persons capable of self-preservation, in the same building, shall be classified as Group I-1. Exception: Such a facility offering supervised care on a 24-hour basis for no more than 16 occupants capable of self-preservation, in the same building, may be classified in Group R in accordance with Section 310. | 308.3.1 Occupancy conditions. | Buildings of Group I-2 shall be classified as one of the occupancy conditions specified in Section 308.3.1.1 or 308.3.1.2 and shall comply with Section 407.
|  | 308.3.1.1 Condition 1. | This occupancy condition shall include facilities that provide nursing and medical care but do not provide emergency care, surgery, obstetrics or in-patient stabilization units for psychiatric or detoxification, including but not limited to nursing homes and foster care facilities.
|  | 308.3.1.2 Condition 2. | This occupancy condition shall include facilities that provide nursing and medical care and could provide emergency care, surgery, obstetrics or in-patient stabilization units for psychiatric or detoxification, including but not limited to hospitals.
308.3.2 Community residences or intermediate-care facilities. | Community residences or intermediate-care facilities, operated pursuant to and meeting the additional construction requirements of the New York State Mental Hygiene Law and applicable regulations of the New York State Office of Mental Health and Office for People with Developmental Disabilities shall be classified as Group I-1. Exceptions: Such facilities limited to 14 residents capable of self-preservation and three staff members per dwelling unit shall be classified as: 1. Group R-1, where such facility does not occupy more than two dwelling units in a residential build¬ing classified as R-1 of Type I or II construction, or one dwelling unit in any other type of construction, and occupied on a transient basis; or 2. Group R-2 where such facility does not occupy more than two dwelling units in a residential building classified R-2 of Type I or II construction, or one dwelling unit in any other type of construction, and occupied on a long-term basis; or 3. Group R-3 where the number of dwelling units in the building does not exceed two. | 308.3.2 Five or fewer persons receiving medical care. | A facility with five or fewer persons receiving medical care shall be classified as Group R-3 or shall comply with the International Residential Code provided an automatic sprinkler system is installed in accordance with Section 903.3.1.3 or Section P2904 of the International Residential Code.
308.4 Institutional Group I-2. | Institutional Group I-2 shall include buildings and structures used for medical, surgical, psychiatric, nursing or personal care on a 24-hour basis or overnight of more than two children under the age of 2, or more than three persons who are not capable of self-preservation and not capable of responding to an emergency situation without physical assistance from staff. This group shall include, but not be limited to, the following: Adult homes, where occupants are not capable of self-preservation (see Section 308.4.1) Child care facilities Community residences or intermediate-care facilities, where occupants are not capable of self-preservation, operated pursuant to and meeting the additional construction requirements of the New York State Mental Hygiene Law and applicable regulations of the New York State Office of Mental Health and Office for People with Developmental Disabilities Detoxification facilities Exception: Such a facility offering care on a 24-hour basis for three or fewer persons who are not capable of self-preservation may occupy not more than one dwelling unit in a Group R occupancy. Enriched Housing, where occupants are not capable of self-preservation (see Section 308.4.1) Hospitals Nursing homes Psychiatric centers where patients are not under restraint | 308.4 Institutional Group I-3. | Institutional Group I-3 occupancy shall include buildings and structures that are inhabited by more than five persons who are under restraint or security. A Group I-3 facility is occupied by persons who are generally incapable of self-preservation due to security measures not under the occupants’ control. This group shall include, but not be limited to, the following:
308.4.1 Adult homes and enriched housing. | Adult homes and enriched housing facilities operated pursuant to and meeting the additional construction requirements of Section 460 of the New York State Social Services Law and regulations of the New York State Department of Health offering care on a 24-hour basis to persons not capable of self-preservation, in the same building, shall be classified as Group I-2. | 308.4.1 Condition 1. | This occupancy condition shall include buildings in which free movement is allowed from sleeping areas, and other spaces where access or occupancy is permitted, to the exterior via means of egress without restraint. A Condition 1 facility is permitted to be constructed as Group R.
|  | 308.4.2 Condition 2. | This occupancy condition shall include buildings in which free movement is allowed from sleeping areas and any other occupied smoke compartment to one or more other smoke compartments. Egress to the exterior is impeded by locked exits.
|  | 308.4.3 Condition 3. | This occupancy condition shall include buildings in which free movement is allowed within individual smoke compartments, such as within a residential unit composed of individual sleeping units and group activity spaces, where egress is impeded by remote-controlled release of means of egress from such a smoke compartment to another smoke compartment.
|  | 308.4.4 Condition 4. | This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Remote-controlled release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.
|  | 308.4.5 Condition 5. | This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Staff-controlled manual release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.
308.5 Institutional Group I-3. | Institutional Group I-3 occupancy shall include buildings and structures that are inhabited by more than five persons who are under restraint or security. A Group I-3 facility is occupied by persons who are generally incapable of self-preservation due to security measures not under the occupants’ control. This group shall include, but not be limited to, the following: | 308.5 Institutional Group I-4, day care facilities. | Institutional Group I-4 occupancy shall include buildings and structures occupied by more than five persons of any age who receive custodial care for fewer than 24 hours per day by persons other than parents or guardians; relatives by blood, marriage or adoption; and in a place other than the home of the person cared for. This group shall include, but not be limited to, the following:
308.5.1 Condition 1. | This occupancy condition shall include buildings in which free movement is allowed from sleeping areas, and other spaces where access or occupancy is permitted, to the exterior via means of egress without restraint. A Condition 1 facility is permitted to be constructed as Group R. | 308.5.1 Classification as Group E. | A child day care facility that provides care for more than five but not more than 100 children 21/2 years or less of age, where the rooms in which the children are cared for are located on a level of exit discharge serving such rooms and each of these child care rooms has an exit door directly to the exterior, shall be classified as Group E.
308.5.2 Condition 2. | This occupancy condition shall include buildings in which free movement is allowed from sleeping areas and any other occupied smoke compartment to one or more other smoke compartments. Egress to the exterior is impeded by locked exits. | 308.5.2 Within a place of religious worship. | Rooms and spaces within places of religious worship providing such care during religious functions shall be classified as part of the primary occupancy.
308.5.3 Condition 3. | This occupancy condition shall include buildings in which free movement is allowed within individual smoke compartments, such as within a residential unit comprised of individual sleeping units and group activity spaces, where egress is impeded by remote controlled release of means of egress from such a smoke compartment to another smoke compartment. | 308.5.3 Five or fewer persons receiving care. | A facility having five or fewer persons receiving custodial care shall be classified as part of the primary occupancy.
308.5.4 Condition 4. | This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Remote-controlled release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments. | 308.5.4 Five or fewer persons receiving care in a dwelling unit. | A facility such as the above within a dwelling unit and having five or fewer persons receiving custodial care shall be classified as a Group R-3 occupancy or shall comply with the International Residential Code.
309.1 Mercantile Group M. | Mercantile Group M occupancy includes, among others, the use of a building or structure or a portion thereof for the display and sale of merchandise, and involves stocks of goods, wares or merchandise incidental to such purposes and accessible to the public. Mercantile occupancies shall include, but not be limited to, the following: | 309.1 Mercantile Group M. | Mercantile Group M occupancy includes, among others, the use of a building or structure or a portion thereof for the display and sale of merchandise, and involves stocks of goods, wares or merchandise incidental to such purposes and where the public has access. Mercantile occupancies shall include, but not be limited to, the following:
309.2 Quantity of hazardous materials. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored or displayed in a single control area of a Group M occupancy shall not exceed the quantities in Table 414.2.5(1). | 309.2 Quantity of hazardous materials. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials stored or displayed in a single control area of a Group M occupancy shall not exceed the quantities in Table 414.2.5(1). |  | See BC04 Tables&Figures
|  | 309.3 Motor fuel-dispensing facilities. | Motor fuel-dispensing facilities shall comply with Section 406.7.
310.1 Residential Group R. | Residential Group R includes, among others, the use of a building or structure, or a portion thereof, for dwelling or sleeping purposes when not classified as an Institutional Group I. Buildings containing three or more dwelling units shall be subject to the New York State Multiple Dwelling Law. Residential occupancies shall be classified as Group R-1, R-2, or R-3. | 310.1 Residential Group R. | Residential Group R includes, among others, the use of a building or structure, or a portion thereof, for sleeping purposes when not classified as an Institutional Group I or when not regulated by the International Residential Code. Group R occupancies not constructed in accordance with the International Residential Code as permitted by Sections 310.4.1 and 310.4.2 shall comply with Section 420.
310.2 Definitions. | The following terms are defined in Chapter 2: | 310.2 Residential Group R-1. | Residential Group R-1 occupancies containing sleeping units where the occupants are primarily transient in nature, including:
310.3 Residential Group R-1. | Residential Group R-1 occupancies shall include: | 310.3 Residential Group R-2. | Residential Group R-2 occupancies containing sleeping units or more than two dwelling units where the occupants are primarily permanent in nature, including:
310.4 Residential Group R-2. | Residential Group R-2 occupancies shall include buildings or portions thereof containing sleeping units or more than two dwelling units that are occupied for permanent resident purposes as defined in subparagraph (a) of paragraph 8 of subdivision a of Section 27-2004 of the New York City Housing Maintenance Code. Such occupancy shall be subject to the New York State Multiple Dwelling Law. This group shall include, but not be limited to, the following: | 310.4 Residential Group R-3. | Residential Group R-3 occupancies where the occupants are primarily permanent in nature and not classified as Group R-1, R-2, R-4 or I, including:
|  | 310.4.1 Care facilities within a dwelling. | Care facilities for five or fewer persons receiving care that are within a single-family dwelling are permitted to comply with the International Residential Code provided an automatic sprinkler system is installed in accordance with Section 903.3.1.3 or Section P2904 of the International Residential Code.
|  | 310.4.2 Lodging houses. | Owner-occupied lodging houses with five or fewer guest rooms and 10 or fewer total occupants shall be permitted to be constructed in accordance with the International Residential Code, provided that an automatic sprinkler system is installed in accordance with Section 903.3.1.3 or Section P2904 of the International Residential Code.
310.5 Residential Group R-3. | Residential Group R-3 occupancies shall include buildings or portions thereof containing no more than 2 dwelling units, occupied, as a rule, for shelter and sleeping accommodation on a long-term basis for a month or more at a time, and are not classified in Group R-1, R-2 or I. This group shall include, but not be limited to, the following: | 310.5 Residential Group R-4. | Residential Group R-4 occupancy shall include buildings, structures or portions thereof for more than five but not more than 16 persons, excluding staff, who reside on a 24-hour basis in a supervised residential environment and receive custodial care. Buildings of Group R-4 shall be classified as one of the occupancy conditions specified in Section 310.5.1 or 310.5.2. This group shall include, but not be limited to, the following:
|  | 310.5.1 Condition 1. | This occupancy condition shall include buildings in which all persons receiving custodial care, without any assistance, are capable of responding to an emergency situation to complete building evacuation.
|  | 310.5.2 Condition 2. | This occupancy condition shall include buildings in which there are any persons receiving custodial care who require limited verbal or physical assistance while responding to an emergency situation to complete building evacuation.
311.1 Storage Group S. | Storage Group S occupancy includes, among others, the use of a building or structure, or a portion thereof, for storage, such as for warehouses, storage rooms, freight depots and distribution centers, when not classified as a hazardous occupancy. | 311.1 Storage Group S. | Storage Group S occupancy includes, among others, the use of a building or structure, or a portion thereof, for storage that is not classified as a hazardous occupancy.
311.1.1 Accessory storage spaces. | A room or space used for storage purposes that is less than 100 square feet (9.3 m2) in area and accessory to another occupancy shall be classified as part of that occupancy. The aggregate area of such rooms or spaces shall not exceed the allowable area limits of Section 508.2.3. | 311.1.1 Accessory storage spaces. | A room or space used for storage purposes that is accessory to another occupancy shall be classified as part of that occupancy.
|  | 311.1.2 Combustible storage. | High-piled stock or rack storage, or attic, under-floor and concealed spaces used for storage of combustible materials, shall be in accordance with Section 413.
311.2 Moderate-hazard storage, Group S-1. | Storage Group S-1 occupancies are buildings occupied for storing any flammable or combustible materials that are likely to permit the development and production of fire with moderate rapidity including, but not limited to, storage of the following: | 311.2 Moderate-hazard storage, Group S-1. | Storage Group S-1 occupancies are buildings occupied for storage uses that are not classified as Group S-2, including, but not limited to, storage of the following:
|  | 311.2.1 Aircraft hangers. | Aircraft hangars used for storage or repair shall comply with Section 412.3.
|  | 311.2.2 Motor vehicle repair garages Motor vehicle repair garages shall comply with Section 406. | 8
311.3 Low-hazard storage, Group S-2. | Storage Group S-2 occupancies include, among others, buildings used for the storage of noncombustible materials such as products on wood pallets or in paper cartons with or without single thickness divisions; or in paper wrappings. Such products are permitted to have a negligible amount of plastic trim, such as knobs, handles or film wrapping. Group S-2 storage uses shall include, but not be limited to, storage of the following: | 311.3 Low-hazard storage, Group S-2. | Storage Group S-2 occupancies include, among others, buildings used for the storage of noncombustible materials such as products on wood pallets or in paper cartons with or without single thickness divisions; or in paper wrappings. Such products are permitted to have a negligible amount of plastic trim, such as knobs, handles or film wrapping. Group S-2 storage uses shall include, but not be limited to, storage of the following:
|  | 311.3.1 Public parking garages. | Public parking garages shall comply with Section 406.4 and the additional requirements of Section 406.5 for open parking garages or Section 406.6 for enclosed parking garages.
312.1 General. | Buildings and structures of an accessory character and miscellaneous structures not classified in any specific occupancy shall be constructed, equipped and maintained to conform to the requirements of this code commensurate with the fire and life hazard incidental to their occupancy. Group U shall include, but not be limited to, the following: | 312.1 General. | Buildings and structures of an accessory character and miscellaneous structures not classified in any specific occupancy shall be constructed, equipped and maintained to conform to the requirements of this code commensurate with the fire and life hazard incidental to their occupancy. Group U shall include, but not be limited to, the following:
|  | 312.1.1 Greenhouses. | Greenhouses not classified as another occupancy shall be classified as Use Group U.
|  | 312.2 Private garages and carports. | Private garages and carports shall comply with Section 406.3.
|  | 312.3 Residential aircraft hangars. | Aircraft hangars accessory to a one- or two-family residence shall comply with Section 412.4.
303.7 Certificate of Operation. | A Certificate of Operation shall be required, as per Section 28-117.1, for the following assembly occupancies:
306.4 Location restrictions. | Locations of spaces classified in Factory Group F may be restricted within a building containing a Group R occupancy pursuant to Section 510.8.
307.1.2 Hazardous materials. | Hazardous materials in any quantity shall conform to the requirements of this code, including Section 414 of this code, and the New York City Fire Code.
308.5.5 Condition 5. | This occupancy condition shall include buildings in which free movement is restricted from an occupied space. Staff-controlled manual release is provided to permit movement from sleeping units, activity spaces and other occupied areas within the smoke compartment to other smoke compartments.
308.6 Institutional Group I-4. | Institutional Group I-4 occupancy shall include custodial care facili­ties providing care to more than two children under the age of 2, or to more than four persons over the age of 2 who are not capa­ble of responding to an emergency situation without physical assistance from the staff. Such occupancy shall include, but not be limited to, adult custodial care facilities and day nurseries. Exceptions: 1. Custodial care facility as described in Section 303. 2. Custodial care facility as described in Section 304. 3. Custodial care facility as described in Exception 3 of Section 305.1. 4. Such facility providing care within a dwelling unit as described in Section 310. 5. Such facility providing care to children under the age of 2 in religious houses of worship during religious functions.

## BC4
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
401.1 Detailed use and occupancy requirements. | In addition to the occupancy and construction requirements in this code, the provisions of this chapter apply to the special uses and occupancies described herein. | 401.1 Detailed occupancy and use requirements. | In addition to the occupancy and construction requirements in this code, the provisions of this chapter apply to the occupancies and use described herein.
402.1 Applicability. | The provisions of this section shall apply to buildings or structures defined herein as covered or open mall buildings not exceeding three floor levels at any point nor more than three stories above grade plane. Except as specifically required by this section, covered and open mall buildings shall meet applicable provisions of this code. Exceptions: 1. Foyers and lobbies of Groups B, R-1 and R-2 are not required to comply with this section. 2. Buildings need not comply with the provisions of this section where they fully comply with other applicable provisions of this code. | 402.1 Applicability. | The provisions of this section shall apply to buildings or structures defined herein as covered or open mall buildings not exceeding three floor levels at any point nor more than three stories above grade plane. Except as specifically required by this section, covered and open mall buildings shall meet applicable provisions of this code.
402.1.1 Occupancy classification. | A mall in compliance with the provisions of this section shall be classified as occupancy Group M. | 402.1.1 Open mall building perimeter line. | For the purpose of this code, a perimeter line shall be established. The perimeter line shall encircle all buildings and structures that comprise the open mall building and shall encompass any open-air interior walkways, open-air courtyards or similar open-air spaces. The perimeter line shall define the extent of the open mall building. Anchor buildings and parking structures shall be outside of the perimeter line and are not considered as part of the open mall building.
402.1.2 Open space. | A covered mall building and attached anchor buildings and parking garages shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm). An open mall building and anchor buildings and parking garages adjoining the perimeter line shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm). Exception: The permanent open space of 60 feet (18 288 mm) shall be permitted to be reduced to not less than 40 feet (12 192 mm), provided the following requirements are met: 1. The reduced open space shall not be allowed for more than 75 percent of the perimeter of the covered mall building and anchor buildings or of the perimeter line of the open mall building and anchor buildings; 2. The exterior wall facing the reduced open space shall have a fire-resistance rating of not less than three hours; 3. Openings in the exterior wall facing the reduced open space shall have opening protectives with a fire protection rating of not less than three hours; and 4. Group E, H, I or R occupancies are not located within the covered or open mall building or anchor buildings.
402.1.3 Open mall building perimeter line. | For the purpose of this code, a perimeter line shall be established. The perimeter line shall encircle all buildings and structures that comprise the open mall building and shall encompass any open-air interior walkways, open-air courtyards or similar open-air spaces. The perimeter line shall define the extent of the open mall building. Anchor buildings and parking structures shall be outside of the perimeter line and are not considered as part of the open mall building.
402.2 Definitions. | This section contains terms defined elsewhere in this code, and terms with definitions that are specific to this section. | 402.2 Open space. | A covered mall building and attached anchor buildings and parking garages shall be surrounded on all sides by a permanent open space or not less than 60 feet (18 288 mm). An open mall building and anchor buildings and parking garages adjoining the perimeter line shall be surrounded on all sides by a permanent open space of not less than 60 feet (18 288 mm).
402.4 Construction. | The construction of covered and open mall buildings, anchor buildings and parking garages associated with a mall building shall comply with Sections 402.4.1 through 402.4.3. | 402.4 Construction. | The construction of covered and open mall buildings, anchor buildings and parking garages associated with a mall building shall comply with Sections 402.4.1 through 402.4.3.
402.2.1 Terms defined elsewhere in this code. | The following terms are defined in Chapter 2:
402.4.1 Area and types of construction. | The building area and type of construction of covered mall or open mall buildings, anchor buildings and parking garages shall comply with this section. | 402.4.1 Area and types of construction. | The building area and type of construction of covered mall or open mall buildings, anchor buildings and parking garages shall comply with this section.
402.2.2 Definitions specific to this section. | The following terms shall, for the purposes of this section, have the meanings shown herein:
402.4.1.1 Covered and open mall buildings. | Covered and open mall buildings shall be of Type I, II or IV construction. The height of covered mall buildings of Type IIB construction shall be limited to one story. The areas of covered mall buildings or open mall buildings shall not be limited provided that the covered mall building or open mall building and attached anchor buildings and parking garages are surrounded on all sides by a perma­nent open space in accordance with Section 402.1.2. | 402.4.1.1 Covered and open mall buildings. | The building area of any covered mall or open mall building shall not be limited provided that the covered mall or open mall building does not exceed three floor levels at any point nor three stories above grade plane, and is of Type I, II, III or IV construction.
402.3 Fire protection plan. | A fire protection plan shall be provided to the Fire Department pursuant to Article 109 of Title 28. | 402.3 Lease plan. | Each owner of a covered mall building or of an open mall building shall provide both the building and fire departments with a lease plan showing the location of each occupancy and its exits after the certificate of occupancy has been issued. Modifications or changes in occupancy or use from that shown on the lease plan shall not be made without prior approval of the building official.
402.4.1.2 Anchor buildings. | Anchor buildings shall be of Type I, II or IV construction. The height of anchor buildings, of Type IIB construction, shall be limited to one story. The allowable height and area of anchor buildings greater than three stories in height shall comply with Section 503, as modified by Sections 504 and 506. | 402.4.1.2 Anchor buildings. | The building area and building height of any anchor building shall be based on the type of construction as required by Section 503 as modified by Sections 504 and 506.
402.4.1.3 Parking garage. | The building area and building height of any parking garage, open or enclosed, shall be based on the type of construction as required by Sections 406.5 and 406.6, respectively. | 402.4.1.3 Parking garage. | The building area and building height of any parking garage shall be based on the type of construction as required by Sections 406.5 and 406.6, respectively.
402.4.2 Fire-resistance-rated separation. | Fire-resistance-rated separation is not required between tenant spaces and the mall. Fire-resistance-rated separation is not required between a food court and adjacent tenant spaces or the mall. | 402.4.2 Fire-resistance-rated separation. | Fire-resistance-rated separation is not required between tenant spaces and the mall. Fire-resistance-rated separation is not required between a food court and adjacent tenant spaces or the mall.
402.4.2.1 Tenant separations. | Each tenant space shall be separated from other tenant spaces by a fire partition complying with Section 708. A tenant separation wall is not required between any tenant space and the mall. | 402.4.2.1 Tenant separations. | Each tenant space shall be separated from other tenant spaces by a fire partition complying with Section 708. A tenant separation wall is not required between any tenant space and the mall.
402.4.2.2 Anchor building separation. | An anchor building shall be separated from the covered or open mall building by fire walls complying with Section 706. Exceptions: 1. Anchor buildings of not more than three sto¬ries above grade that have an occupancy classification of the same uses permitted as tenants of the covered mall building shall be separated by 2-hour fire-resistance-rated fire barriers complying with Section 707. Openings between such buildings and the mall need not be protected. 2. The exterior walls of anchor buildings separated from an open mall building by an open mall shall comply with Table 602. | 402.4.2.2 Anchor building separation. | An anchor building shall be separated from the covered or open mall building by fire walls complying with Section 706. |  | See BC06 Tables&Figures
402.4.2.3 Parking garages. | An attached garage for the storage of passenger vehicles having a capacity of not more than nine persons and open parking garages shall be considered as a separate building where it is separated from the covered or open mall building or anchor building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. | 402.4.2.3 Parking garages. | An attached garage for the storage of passenger vehicles having a capacity of not more than nine persons and open parking garages shall be considered as a separate building where it is separated from the covered or open mall building or anchor building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
402.4.3 Open mall construction. | Floor assemblies in, and roof assemblies over, the open mall of an open mall building shall be open to the atmosphere for not less than 20 feet (9096 mm), measured perpendicular from the face of the tenant spaces on the lowest level, from edge of balcony to edge of balcony on upper floors and from edge of roof line to edge of roof line. The openings within, or the unroofed area of, an open mall shall extend from the lowest/grade level of the open mall through the entire roof assembly. Balconies on upper levels of the mall shall not project into the required width of the opening. | 402.4.3 Open mall construction. | Floor assemblies in, and roof assemblies over, the open mall of an open mall building shall be open to the atmosphere for not less than 20 feet (9096 mm), measured perpendicular from the face of the tenant spaces on the lowest level, from edge of balcony to edge of balcony on upper floors and from edge of roof line to edge of roof line. The openings within, or the unroofed area of, an open mall shall extend from the lowest/grade level of the open mall through the entire roof assembly. Balconies on upper levels of the mall shall not project into the required width of the opening.
402.4.3.1 Pedestrian walkways. | Pedestrian walkways connecting balconies in an open mall shall be located not less than 20 feet (9096 mm) from any other pedestrian walkway. | 402.4.3.1 Pedestrian walkways. | Pedestrian walkways connecting balconies in an open mall shall be located not less than 20 feet (9096 mm) from any other pedestrian walkway.
402.5 Automatic sprinkler system. | Covered and open mall buildings and buildings connected shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, which shall comply with all of the following: 1. The automatic sprinkler system shall be complete and operative throughout occupied space in the mall building prior to occupancy of any of the tenant spaces. Unoccupied tenant spaces shall be similarly protected unless provided with approved alternative protection. 2. Sprinkler protection for the mall of a covered mall building shall be controlled independently from that provided for tenant spaces or anchor buildings. 3. Sprinkler protection for the tenant spaces of an open mall building shall be controlled independently from that provided for anchor buildings. 4. Sprinkler protection shall be provided beneath exterior circulation balconies located adjacent to an open mall. 5. Where tenant spaces are supplied by the same system, they shall be independently controlled. Exception: An automatic sprinkler system shall not be required in spaces or areas of open parking garages separated from the covered or open mall building in accordance with Section 402.4.2.3 and constructed in accordance with Section 406.5. | 402.5 Automatic sprinkler system. | Covered and open mall buildings and buildings connected shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, which shall comply with all of the following:
402.6 Interior finishes and features. | Interior finishes within the mall and installations within the mall shall comply with Sections 402.6.1 through 402.6.4. | 402.6 Interior finishes and features. | Interior finishes within the mall and installations within the mall shall comply with Sections 402.6.1 through 402.6.4.
402.6.2 Kiosks. | Kiosks and similar structures (temporary or permanent) located within the mall of a covered mall building or within the perimeter line of an open mall building shall meet the following requirements: | 402.6.2 Kiosks. | Kiosks and similar structures (temporary or permanent) located within the mall of a covered mall building or within the perimeter line of an open mall building shall meet the following requirements:
402.6.1 Interior finish. | Interior wall and ceiling finishes within the mall of a covered mall building and within the exits of covered or open mall buildings shall have a minimum flame spread index and smoke-developed index of Class B in accordance with Chapter 8. Interior floor finishes shall meet the requirements of Section 804. | 402.6.1 Interior finish Interior wall and ceiling finishes within the mall of a covered mall building and within the exits of covered or open mall buildings shall have a minimum flame spread index and smoke-developed index of Class B in accordance with Chapter 8. | Interior floor finishes shall meet the requirements of Section 804.
402.6.4 Plastic signs. | Plastic signs affixed to the storefront of any tenant space facing a mall or open mall shall be limited as specified in Sections 402.6.4.1 through 402.6.4.5. | 402.6.4 Plastic signs. | Plastic signs affixed to the storefront of any tenant space facing a mall or open mall shall be limited as specified in Sections 402.6.4.1 through 402.6.4.5.
402.6.4.1 Area. | Plastic signs shall be not more than 20 percent of the wall area facing the mall. | 402.6.4.1 Area. | Plastic signs shall be not more than 20 percent of the wall area facing the mall.
402.6.3 Children’s play structures. | Children’s play structures located within the mall of a covered mall building or within the perimeter line of an open mall building shall comply with Section 424. The horizontal separation between children’s play structures, kiosks and similar structures within the mall shall be not less than 20 feet (6096 mm). | 402.6.3 Play structures. | Play structures located within a mall building or within the perimeter line of an open mall building shall comply with Section 424. The horizontal separation between play structures, kiosks and similar structures within the mall shall be not less than 20 feet (6096 mm).
402.6.4.2 Height and width. | Plastic signs shall be not greater than 36 inches (914 mm) in height, except that where the sign is vertical, the height shall be not greater than 96 inches (2438 mm) and the width shall be not greater than 36 inches (914 mm). | 402.6.4.2 Height and width. | Plastic signs shall be not greater than 36 inches (914 mm) in height, except that where the sign is vertical, the height shall be not greater than 96 inches (2438 mm) and the width shall be not greater than 36 inches (914 mm).
402.6.4.3 Location. | Plastic signs shall be located not less than 18 inches (457 mm) from adjacent tenants. | 402.6.4.3 Location. | Plastic signs shall be located not less than 18 inches (457 mm) from adjacent tenants.
402.6.4.4 Plastics other than foam plastics. | Plastics other than foam plastics used in signs shall be lighttransmitting plastics complying with Section 2606.4 or shall have a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D 1929, and a flame spread index not greater than 75 and smoke-developed index not greater than 450 when tested in the manner intended for use in accordance with ASTM E 84 or UL 723 or meet the acceptance criteria of Section 803.1.2.1 when tested in accordance with NFPA 286. | 402.6.4.4 Plastics other than foam plastics. | Plastics other than foam plastics used in signs shall be light-transmitting plastics complying with Section 2606.4 or shall have a self-ignition temperature of 650°F (343°C) or greater when tested in accordance with ASTM D1929, and a flame spread index not greater than 75 and smoke-developed index not greater than 450 when tested in the manner intended for use in accordance with ASTM E84 or UL 723 or meet the acceptance criteria of Section 803.1.1.1 when tested in accordance with NFPA 286.
402.6.4.4.1 Encasement. | Edges and backs of plastic signs in the mall shall be fully encased in metal. | 402.6.4.4.1 Encasement. | Edges and backs of plastic signs in the mall shall be fully encased in metal.
402.6.4.5 Foam plastics. | Foam plastics used in signs shall have flame-retardant characteristics such that the sign has a maximum heat-release rate of 150 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source, and the foam plastics shall have the physical characteristics specified in this section. Foam plastics used in signs installed in accordance with Section 402.6.4 shall not be required to comply with the flame spread and smoke-developed indices specified in Section 2603.3. | 402.6.4.5 Foam plastics. | Foam plastics used in signs shall have flame-retardant characteristics such that the sign has a maximum heat-release rate of 150 kilowatts when tested in accordance with UL 1975 or when tested in accordance with NFPA 289 using the 20 kW ignition source, and the foam plastics shall have the physical characteristics specified in this section. Foam plastics used in signs installed in accordance with Section 402.6.4 shall not be required to comply with the flame spread and smoke-developed indices specified in Section 2603.3.
402.6.4.5.1 Density. | The density of foam plastics used in signs shall be not less than 20 pounds per cubic foot (pcf) (320 kg/m3). | 402.6.4.5.1 Density. | The density of foam plastics used in signs shall be not less than 20 pounds per cubic foot (pcf) (320 kg/ m3).
402.6.4.5.2 Thickness. | The thickness of foam plastic signs shall be not greater than 1/2 inch (12.7 mm). | 402.6.4.5.2 Thickness. | The thickness of foam plastic signs shall not be greater than 1/2 inch (12.7 mm).
402.7 Emergency systems. | Covered and open mall buildings, anchor buildings and associated parking garages shall be provided with emergency systems complying with Sections 402.7.1 through 402.7.5. | 402.7 Emergency systems. | Covered and open mall buildings, anchor buildings and associated parking garages shall be provided with emergency systems complying with Sections 402.7.1 through 402.7.5.
402.7.1 Standpipe system. | Covered and open mall buildings shall be equipped throughout with a standpipe system as required by Section 905.3.3. | 402.7.1 Standpipe system. | Covered and open mall buildings shall be equipped throughout with a standpipe system as required by Section 905.3.3.
402.7.2 Smoke control. | Where a covered mall building contains an atrium, a smoke control system shall be provided in accordance with Section 404.5. | 402.7.2 Smoke control. | Atriums connecting three or more stories in a covered mall building shall be provided with a smoke control system in accordance with Section 909.
402.7.3 Emergency power. | Covered mall buildings greater than 50,000 square feet (4645 m2) in area and open mall buildings greater than 50,000 square feet (4645 m2) within the established perimeter line shall be provided with emergency power that is capable of operating the emergency voice/alarm communication system in accordance with Section 2702. | 402.7.3 Emergency power. | Covered mall buildings greater than 50,000 square feet (4645 m2) in area and open mall buildings greater than 50,000 square feet (4645 m2) within the established perimeter line shall be provided with emergency power that is capable of operating the emergency voice/alarm communication system in accordance with Section 2702.
402.7.4 Emergency voice/alarm communication system. | Where the total floor area is greater than 50,000 square feet (4645 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided. | 402.7.4 Emergency voice/alarm communication system. | Where the total floor area is greater than 50,000 square feet (4645 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided.
402.8 Means of egress. | Covered mall buildings, open mall buildings and each tenant space within a mall building shall be provided with means of egress as required by this section and this code. Where there is a conflict between the requirements of this code and the requirements of Sections 402.8.1 through 402.8.8, the requirements of Sections 402.8.1 through 402.8.8 shall apply. | 402.8 Means of egress. | Covered mall buildings, open mall buildings and each tenant space within a mall building shall be provided with means of egress as required by this section and this code. Where there is a conflict between the requirements of this code and the requirements of Sections 402.8.1 through 402.8.8, the requirements of Sections 402.8.1 through 402.8.8 shall apply.
402.8.1 Mall width. | For the purpose of providing required egress, malls are permitted to be considered as corridors but need not comply with the requirements of Section 1005.1 of this code where the width of the mall is as specified in this section. | 402.8.1 Mall width. | For the purpose of providing required egress, malls are permitted to be considered as corridors but need not comply with the requirements of Section 1005.1 of this code where the width of the mall is as specified in this section.
402.7.5 Fire Department access to equipment. | Rooms or areas containing controls for air-conditioning systems, automatic fire-extinguishing systems, automatic sprinkler systems or other detection, suppression or control elements shall be identified for use by the Fire Department. | 402.7.5 Fire department access to equipment. | Rooms or areas containing controls for air-conditioning systems or fire protection systems shall be identified for use by the fire department.
402.8.1.1 Minimum width. | The aggregate clear egress width of the mall in either a covered or open mall building shall be not less than 20 feet (6096 mm). The mall width shall be sufficient to accommodate the occupant load served. No portion of the minimum required aggregate egress width shall be less than 10 feet (3048 mm) measured to a height of 8 feet (2438 mm) between any projection of a tenant space bordering the mall and the nearest kiosk, vending machine, bench, display opening, food court or other obstruction to means of egress travel. | 402.8.1.1 Minimum width. | The aggregate clear egress width of the mall in either a covered or open mall building shall be not less than 20 feet (6096 mm). The mall width shall be sufficient to accommodate the occupant load served. Any portion of the minimum required aggregate egress width shall be not less than 10 feet (3048 mm) measured to a height of 8 feet (2438 mm) between any projection of a tenant space bordering the mall and the nearest kiosk, vending machine, bench, display opening, food court or other obstruction to means of egress travel.
402.8.2 Occupant load. | The calculated occupant load used to determine the required number of means of egress shall be in accordance with this section. | 402.8.2 Determination of occupant load. | The occupant load permitted in any individual tenant space in a covered or open mall building shall be determined as required by this code. Means of egress requirements for individual tenant spaces shall be based on the occupant load thus determined.
402.8.2.1 Occupant load of tenant spaces. | The occu­pant load permitted in any individual tenant space in a covered mall building shall be determined in accordance with Chapter 10. Means of egress requirements for indi­vidual tenant spaces shall be based on the occupant load thus determined. | 402.8.2.1 Occupant formula. | In determining required means of egress of the mall, the number of occupants for whom means of egress are to be provided shall be based on gross leasable area of the covered or open mall building (excluding anchor buildings) and the occupant load factor as determined by Equation 4-1.
402.8.2.2 Occupant load of mall. | In determining required means of egress of the mall, the total occupant load in the mall shall include the occupant load attributed to the mall as determined by Section 402.8.2.3, plus the occupant load of the food court as determined by Section 402.8.2.5, if any. | 402.8.2.2 OLF range. | The occupant load factor (OLF) is not required to be less than 30 and shall not exceed 50.
402.8.3 Number of means of egress. | The required number of means of egress shall be determined in accordance with this section. | 402.8.3 Number of means of egress. | Wherever the distance of travel to the mall from any location within a tenant space used by persons other than employees is greater than 75 feet (22 860 mm) or the tenant space has an occupant load of 50 or more, not fewer than two means of egress shall be provided.
402.8.2.3 Occupant load formula. | To determine the occupant load attributed to the mall, the gross leasable area (square feet), excluding any food court and anchor buildings, shall be divided by the occupant load fac­tor (OLF) value determined by Equation 4-1. Exception: Tenant spaces attached to a covered mall building but with a means of egress system that is totally independent of the covered mall building shall not be considered as gross leasable area for determining the required means of egress for the covered mall building. | 402.8.2.3 Anchor buildings. | The occupant load of anchor buildings opening into the mall shall not be included in computing the total number of occupants for the mall.
402.8.4 Arrangements of means of egress. | Means of egress shall be arranged in accordance with this section. | 402.8.4 Arrangements of means of egress. | Assembly occupancies with an occupant load of 500 or more located within a covered mall building shall be so located such that their entrance will be immediately adjacent to a principal entrance to the mall and shall have not less than one-half of their required means of egress opening directly to the exterior of the covered mall building. Assembly occupancies located within the perimeter line of an open mall building shall be permitted to have their main exit open to the open mall.
402.8.2.4 OLF range. | The occupant load factor (OLF) is not required to be less than 30 and shall not exceed 50. | 402.8.2.4 Food courts. | The occupant load of a food court shall be determined in accordance with Section 1004. For the purposes of determining the means of egress requirements for the mall, the food court occupant load shall be added to the occupant load of the covered or open mall building as calculated in Section 402.8.2.1.
402.8.4.1 Anchor building means of egress. | Required means of egress for anchor buildings shall be provided independently from the mall means of egress system. The occupant load of anchor buildings opening into the mall shall not be included in determining means of egress requirements for the mall. The path of egress travel of malls shall not exit through anchor buildings. Malls terminating at an anchor building where no other means of egress has been provided shall be considered as a dead-end mall. | 402.8.4.1 Anchor building means of egress. | Required means of egress for anchor buildings shall be provided independently from the mall means of egress system. The occupant load of anchor buildings opening into the mall shall not be included in determining means of egress requirements for the mall. The path of egress travel of malls shall not exit through anchor buildings. Malls terminating at an anchor building where other means of egress has not been provided shall be considered as a dead-end mall.
402.8.2.5 Food courts. | The occupant load of a food court shall be determined in accordance with Section 1004 and shall be added to the occupant load of the mall.
402.8.5 Distance to exits. | Within each individual tenant space in a covered or open mall building, the distance of travel from any point to an exit or entrance to the mall shall be not greater than 200 feet (60 960 mm). | 402.8.5 Distance to exits. | Within each individual tenant space in a covered or open mall building, the distance of travel from any point to an exit or entrance to the mall shall be not greater than 200 feet (60 960 mm).
402.8.2.6 Anchor buildings. | The occupant load of anchor buildings opening into the mall shall not be included in computing the total number of occupants for the covered mall building.
402.8.6 Access to exits. | Where more than one exit is required, they shall be so arranged that it is possible to travel in either direction from any point in a mall of a covered mall building to separate exits or from any point in an open mall of an open mall building to two separate locations on the perimeter line, provided neither location is an exterior wall of an anchor building or parking garage. The width of an exit passageway or corridor from a mall shall be not less than 66 inches (1676 mm). Exception: Access to exits is permitted by way of a dead-end mall that does not exceed a length equal to twice the width of the mall measured at the narrowest location within the dead-end portion of the mall. | 402.8.6 Access to exits. | Where more than one exit is required, they shall be so arranged that it is possible to travel in either direction from any point in a mall of a covered mall building to separate exits or from any point in an open mall of an open mall building to two separate locations on the perimeter line, provided that neither location is an exterior wall of an anchor building or parking garage. The width of an exit passageway or corridor from a mall shall be not less than 66 inches (1676 mm).
402.8.3.1 Number of means of egress within tenant spaces. | Wherever the distance of travel to the mall from any location within a tenant space used by persons other than employees exceeds 75 feet (22 860 mm) or the tenant space exceeds an occupant load of 74, no fewer than two means of egress shall be provided.
402.8.7 Service areas fronting on exit passageways. | Mechanical rooms, electrical rooms, building service areas and service elevators are permitted to open directly into exit passageways provided that the exit passageway is separated from such rooms by fire barriers providing the same fire-resistance rating as required for the exit passageway. Door swings from these rooms shall not project into the minimum width of such exit passageways. | 402.8.7 Service areas fronting on exit passageways. | Mechanical rooms, electrical rooms, building service areas and service elevators are permitted to open directly into exit passageways, provided that the exit passageway is separated from such rooms with not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire protection rating of openings in the fire barriers shall be not less than 1 hour.
402.8.3.2 Number of means of egress from the mall. | The number of means of egress from the mall shall be determined in accordance with Chapter 10 and shall be based upon an occupant load calculated in accordance with Section 402.8.2.
402.8.8 Security grilles and doors. | Horizontal sliding or vertical security grilles or doors that are a part of a required means of egress shall conform to the following: | 402.8.8 Security grilles and doors. | Horizontal sliding or vertical security grilles or doors that are a part of a required means of egress shall conform to the following:
403.1 Applicability. | High-rise buildings shall comply with Sections 403.2 through 403.8. Exception: The provisions of Sections 403.2 through 403.8 shall not apply to the following buildings and structures: 1. Air traffic control towers in accordance with Section 412.3. 2. Buildings occupied entirely by Group R-3 classification. 3. Open parking garages in accordance with Section 406.5. 4. The portion of a building containing a Group A-5 occupancy in accordance with Section 303.6. 5. Special industrial occupancies in accordance with Section 503.1.1. 6. Buildings with: 6.1. A Group H-1 occupancy; 6.2. A Group H-2 occupancy in accordance with Section 415.8, 415.9.2, 415.9.3 or 426.1; or 6.3. A Group H-3 occupancy in accordance with Section 415.8. | 403.1 Applicability. | High-rise buildings shall comply with Sections 403.2 through 403.6.
403.2 Construction. | The construction of high-rise buildings shall comply with the provisions of Sections 403.2.1 through 403.2.4. | 403.2 Construction. | The construction of high-rise buildings shall comply with the provisions of Sections 403.2.1 through 403.2.3.
402.8.4.2 Tenant spaces requiring more than one means of egress. | Where more than one means of egress is required from an individual tenant space as determined by Chapter 10, not more than 50 percent of the occupant load shall discharge into the mall.
402.8.4.3 Large assembly occupancy. | Assembly occu­pancies with an occupant load of 500 or more shall be so located in the covered mall building such that their entrance will be immediately adjacent to a principal entrance to the mall and shall have not less than one-half of their required means of egress opening directly to the exterior of the covered mall building.
402.8.6.1 Exit passageway enclosures. | Where exit pas­sageway enclosures provide a secondary means of egress from a tenant space, doors to the exit passageway enclo­sures shall be minimum 1-hour fire doors with panic hardware. Such doors shall be self-closing and be so maintained or shall be automatic closing by smoke detection. | 402.8.6.1 Exit passageways. | Where exit passageways provide a secondary means of egress from a tenant space, the exit passageways shall be constructed in accordance with Section 1024.
403.2.1 Types of construction. | The following modifications to the minimum fire-resistance rating of the building elements in Table 601 shall be as follows: | 403.2.1 Reduction in fire-resistance rating. | The fire-resistance rating reductions specified in Sections 403.2.1.1 and 403.2.1.2 shall be allowed in buildings that have sprinkler control valves equipped with supervisory initiating devices and water-flow initiating devices for each floor. |  | See BC06 Tables&Figures
403.3 Automatic sprinkler system. | Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a secondary water supply where required by Section 403.3.3. | 403.3 Automatic sprinkler system. | Buildings and structures shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and a secondary water supply where required by Section 403.3.3.
403.2.2 Seismic considerations. | For seismic considerations, see Chapter 16. | 403.2.2 Structural integrity of interior exit stairways and elevator hoistway enclosures. | For high-rise buildings of Risk Category III or IV in accordance with Section 1604.5, and for all buildings that are more than 420 feet (128 m) in building height, enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Sections 403.2.2.1 through 403.2.2.4.
403.3.1 Number of sprinkler risers and system design. | Each sprinkler system zone in buildings that are more than 300 feet (91 440 mm) in building height shall be supplied by no fewer than two risers. Each riser shall supply sprinklers on alternate floors. If more than two risers are provided for a zone, sprinklers on adjacent floors shall not be supplied from the same riser. | 403.3.1 Number of sprinkler risers and system design. | Each sprinkler system zone in buildings that are more than 420 feet (128 m) in building height shall be supplied by not fewer than two risers. Each riser shall supply sprinklers on alternate floors. If more than two risers are provided for a zone, sprinklers on adjacent floors shall not be supplied from the same riser.
403.2.3 Structural integrity of interior exit stairways and elevator hoistway enclosures. | For all high-rise buildings, exit enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Sections 403.2.3.1 through 403.2.3.4. Exception: Where fire-resistance rating is not required by this code for the enclosure or portions thereof. | 403.2.3 Sprayed fire-resistant materials (SFRM). | The bond strength of the SFRM installed throughout the building shall be in accordance with Table 403.2.3.
403.3.1.1 Riser location. | Sprinkler risers shall be placed in interior exit stairways and ramps that are remotely located in accordance with Section 1007.1. | 403.3.1.1 Riser location. | Sprinkler risers shall be placed in interior exit stairways and ramps that are remotely located in accordance with Section 1007.1.
403.2.3.1 Wall assembly. | The wall assemblies making up the enclosures for interior exit stairways and elevator hoistway enclosures shall meet or exceed Soft Body Impact Classification Level 2 as measured by the test method described in ASTM C 1629/C 1629M.
403.3.2 Water supply to required fire pumps. | Required fire pumps shall be provided with water supplies in accordance with Section 905.2 and NFPA 14 as modified by Appendix Q of this code. | 403.3.2 Water supply to required fire pumps. | In all buildings that are more than 420 feet (128 m) in building height and buildings of Type IVA and IVB construction that are more than 120 feet (36 576 mm) in building height, required fire pumps shall be supplied by connections to not fewer than two water mains located in different streets. Separate supply piping shall be provided between each connection to the water main and the pumps. Each connection and the supply piping between the connection and the pumps shall be sized to supply the flow and pressure required for the pumps to operate.
403.2.3.2 Wall assembly materials. | The face of the wall assemblies making up the enclosures for interior exit stairways and elevator hoistway enclosures that are not exposed to the interior of the enclosures for interior exit stairways or elevator hoistway enclosure shall be constructed in accordance with one of the following methods:
403.2.3.3 Concrete and masonry walls. | Concrete or masonry walls shall be deemed to satisfy the requirements of Sections 403.2.3.1 and 403.2.3.2.
403.3.4 Fire pump room. | Fire pumps shall be located in rooms protected in accordance with Section 913.2.1. | 403.3.4 Fire pump room. | Fire pumps shall be located in rooms protected in accordance with Section 913.2.1.
403.2.3.4 Other wall assemblies. | Any other wall assembly that provides impact resistance equivalent to that required by Sections 403.2.3.1 and 403.2.3.2 for Hard Body Impact Classification Level 3, as measured by the test method described in ASTM C 1629/C 1629M, shall be permitted.
403.4 Emergency systems. | The detection, alarm and emergency systems of high-rise buildings shall comply with Sections 403.4.1 through 403.4.8. | 403.4 Emergency systems. | The detection, alarm and emergency systems of high-rise buildings shall comply with Sections 403.4.1 through 403.4.8.
403.2.4 Sprayed fire-resistant materials (SFRM). | The bond strength of the SFRM installed throughout the building shall be in accordance with Table 403.2.4. |  |  |  | See BC04 Tables&Figures
403.4.1 Smoke detection. | Smoke detection shall be provided in accordance with Section 907.2.13.1. | 403.4.1 Smoke detection. | Smoke detection shall be provided in accordance with Section 907.2.13.1.
403.4.2 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.13. | 403.4.2 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.13.
403.4.3 Standpipe system. | A high-rise building shall be equipped with a standpipe system as required by Section 905.3. | 403.4.3 Standpipe system. | A high-rise building shall be equipped with a standpipe system as required by Section 905.3.
403.4.4 Emergency voice/alarm communication system. | An emergency voice/alarm communication system shall be provided in accordance with Section 907.5.2.2. | 403.4.4 Emergency voice/alarm communication system. | An emergency voice/alarm communication system shall be provided in accordance with Section 907.5.2.2.
403.3.3 Secondary on-site water supply. | A secondary on-site water supply equal to the hydraulically calculated sprinkler demand, including the hose stream requirement, shall be provided for high-rise buildings in Seismic Design Category C or D as determined by this code, and in any high-rise building with occupied floors located more than 500 feet (152 m) above the lowest level of fire department vehicle access. The secondary on-site water supply shall have a duration of not less than 30 minutes as determined by the occupancy hazard classification in accordance with NFPA 13 as modified by Appendix Q of this code. | 403.3.3 Secondary water supply. | An automatic secondary on-site water supply having a capacity not less than the hydraulically calculated sprinkler demand, including the hose stream requirement, shall be provided for high-rise buildings assigned to Seismic Design Category C, D, E or F as determined by Section 1613. An additional fire pump shall not be required for the secondary water supply unless needed to provide the minimum design intake pressure at the suction side of the fire pump supplying the automatic sprinkler system. The secondary water supply shall have a duration of not less than 30 minutes as determined by the occupancy hazard classification in accordance with NFPA 13.
403.4.6 Fire command. | A fire command center complying with Section 911 shall be provided in a location approved by the Fire Department. | 403.4.6 Fire command. | A fire command center complying with Section 911 shall be provided in a location approved by the fire code official.
403.4.8 Standby and emergency power. | A standby power system complying with Section 2702 and Section 3003 shall be provided for the standby power loads specified in Section 403.4.8.3. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 403.4.8.4. | 403.4.8 Standby and emergency power. | A standby power system complying with Section 2702 and Section 3003 shall be provided for the standby power loads specified in Section 403.4.8.3. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 403.4.8.4.
403.4.8.1 Equipment room. | If the standby or emergency power system includes a generator set inside a building, the system shall be located in a separate room in accordance with Section 2702.1.2.2. | 403.4.8.1 Equipment room. | If the standby or emergency power system includes a generator set inside a building, the system shall be located in a separate room enclosed with 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. System supervision with manual start and transfer features shall be provided at the fire command center.
403.4.8.2 Fuel line piping protection. | Fuel lines supplying a generator set inside a building shall comply with Section 1305.9 of the New York City Mechanical Code. | 403.4.8.2 Fuel line piping protection. | Fuel lines supplying a generator set inside a building shall be separated from areas of the building other than the room the generator is located in by one of the following methods:
403.4.5 Emergency responder radio coverage. | Emergency responder radio coverage shall be provided in accordance with the New York City Fire Code and Section 907.2.13.2 of this code. | 403.4.5 Emergency communication coverage. | In-building, two-way emergency responder communication coverage shall be provided in accordance with Section 510 of the International Fire Code.
403.5 Means of egress and evacuation. | The means of egress in high-rise buildings shall comply with Sections 403.5.1 through 403.5.6. | 403.5 Means of egress and evacuation. | The means of egress in high-rise buildings shall comply with Sections 403.5.1 through 403.5.5.
403.5.1 Remoteness of interior exit stairways. | Required interior exit stairways shall be separated by a distance not less than 30 feet (9144 mm) or not less than ¼ of the length of the maximum overall diagonal dimension of the building or area to be served, whichever is less. The distance shall be measured in a straight line between the nearest points of the enclosure surrounding the interior exit stairways. In buildings with three or more interior exit stairways, no fewer than two of the interior exit stairways shall comply with this section. Stairs sharing any common wall, floors, ceilings, scissor stair assemblies, or other enclosures shall be counted as one interior exit stairway. Exception: Group R-2 occupancies. | 403.5.1 Remoteness of interior exit stairways. | Required interior exit stairways shall be separated by a distance not less than 30 feet (9144 mm) or not less than one-fourth of the length of the maximum overall diagonal dimension of the building or area to be served, whichever is less. The distance shall be measured in a straight line between the nearest points of the enclosure surrounding the interior exit stairways. In buildings with three or more interior exit stairways, not fewer than two of the interior exit stairways shall comply with this section. Interlocking or scissor stairways shall be counted as one interior exit stairway.
403.4.7 Post-fire smoke purge. | A post-fire smoke purge system shall be installed in accordance with Section 917. | 403.4.7 Smoke removal. | To facilitate smoke removal in post-fire salvage and overhaul operations, buildings and structures shall be equipped with natural or mechanical ventilation for removal of products of combustion in accordance with one of the following:
403.5.3 Stairway door operation. | Doors opening into interior stair enclosures shall not be locked from either side. However, a door locked from the stair side may be permitted provided that such door is equipped with an automatic fail safe system for opening in the event of the activation of any automatic fire detection system, or when any elevator recall is activated, or when any signal is received from the fire command center. Such door shall be deemed as openable from the stair side. Stair reentry signs shall be posted throughout the stairway indicating that reentry is provided only during fire emergencies. Such signs shall be in accordance with Section 1031.4.2. Exception: In schools classified as Group E occupancies that require “lockdown drills” as per Section 807 of the New York State Education Law, stairway egress doors from occupied spaces are permitted to be locked from the side opposite the egress side for the duration of the lockdown drill, provided they are openable from the occupied side for egress and are unlocked upon directions from the school administrative personnel following the completion of the lockdown drill. | 403.5.3 Stairway door operation. | Stairway doors other than the exit discharge doors shall be permitted to be locked from the stairway side. Stairway doors that are locked from the stairway side shall be capable of being unlocked simultaneously without unlatching upon a signal from the fire command center.
403.5.3.1 Stairway communication system. | A telephone or other two-way communications system connected to an approved constantly attended station shall be provided at not less than every fifth floor in each stairway where the doors to the stairway are locked in accordance with Section 403.5.3. | 403.5.3.1 Stairway communication system. | A telephone or other two-way communications system connected to an approved constantly attended station shall be provided at not less than every fifth floor in each stairway where the doors to the stairway are locked.
403.5.4 Smokeproof enclosures. | Every required interior exit stairway serving floors more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access shall comply with Sections 909.20 and 1023.11. Exception: Smokeproof enclosures are not required in occupancy Group R-2 unless provided pursuant to Exception 2 of Section 917.1. | 403.5.4 Smokeproof enclosures. | Every required interior exit stairway serving floors more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access shall be a smokeproof enclosure in accordance with Sections 909.20 and 1023.12.
403.4.8.3 Standby power systems. | A standby power system complying with Section 2702 shall be provided for standby power loads specified in Sections 403.4.8.3.1 and 403.4.8.3.2. Fuel sources for generators shall be in accordance with Section 2702.1.1. | 403.4.8.3 Standby power loads. | The following are classified as standby power loads:
403.5.5 Luminous egress path markings. | Luminous egress path markings shall be provided in accordance with Section 1025 and Appendix S. Exception: Egress paths serving Group R-2. | 403.5.5 Luminous egress path markings. | Luminous egress path markings shall be provided in accordance with Section 1025.
403.4.8.3.1 Standby power loads in occupancies other than Group R-2. | In buildings of any occupancy group other than Group R-2, the following are classified as standby power loads:
403.6 Elevators. | Elevator installation and operation in high-rise buildings shall comply with Chapter 30 and Sections 403.6.1 and 403.6.2. | 403.6 Elevators. | Elevator installation and operation in high-rise buildings shall comply with Chapter 30 and Sections 403.6.1 and 403.6.2.
403.4.8.3.2 Standby power loads in Group R-2 occupancies. | Group R-2 occupancies in buildings greater than 125 feet (38 100 mm) in height shall be required to provide a standby power system to support the following loads:
403.6.1 Fire service access elevator. | In buildings with an occupied floor more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, a minimum of one fire service access elevator shall be provided in accordance with Section 3007. | 403.6.1 Fire service access elevator. | In buildings with an occupied floor more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, not fewer than two fire service access elevators, or all elevators, whichever is less, shall be provided in accordance with Section 3007. Each fire service access elevator shall have a capacity of not less than 3,500 pounds (1588 kg) and shall comply with Section 3002.4.
4. Stair pressurization systems when provided.
403.6.2 Occupant evacuation elevators. | Where installed in accordance with Section 3008, passenger elevators for general public use shall be permitted to be used for occupant self-evacuation. | 403.6.2 Occupant evacuation elevators. | Where installed in accordance with Section 3008, passenger elevators for general public use shall be permitted to be used for occupant self-evacuation.
403.4.8.4 Emergency power systems. | An emergency power system complying with Section 2702 shall be provided for emergency power loads specified in Sections 403.4.8.4.1 and 403.4.8.4.3. Fuel sources for generators shall be in accordance with Section 2702.1.1.
404.1 General. | In other than Group H occupancies, and where permitted by Section 712.1.7, the provisions of Sections 404.1 through 404.10 shall apply to buildings or structures containing vertical openings defined as “atriums.” | 404.1 General. | The provisions of Sections 404.1 through 404.11 shall apply to buildings containing atriums. Atriums are not permitted in buildings or structures classified as Group H.
403.4.8.4.1 Emergency power loads in occupancies other than Group R-2. | In buildings of any occupancy group other than Group R-2, the following are classified as emergency power loads:
404.2 Use. | The floor of the atrium shall not be used for other than low fire hazard uses and only approved materials and decorations in accordance with the New York City Fire Code shall be used in the atrium space. Exception: The atrium floor area is permitted to be used for any approved use where the individual space is provided with an automatic sprinkler system in accordance with Section 903.3.1.1. | 404.2 Use. | The floor of the atrium shall not be used for other than low fire hazard uses and only approved materials and decorations in accordance with the International Fire Code shall be used in the atrium space.
403.4.8.4.2 Emergency power loads in Group R-2 occupancies. | Group R-2 occupancies in buildings greater than 125 feet (38 100 mm) in height shall be required to provide an emergency power system to support the following loads:
404.3 Automatic sprinkler protection. | An approved automatic sprinkler system shall be installed throughout the entire building. Exceptions: 1. That area of a building adjacent to or above the atrium need not be sprinklered provided that portion of the building is separated from the atrium portion by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. 2. Where the ceiling of the atrium is more than 55 feet (16 764 mm) above the floor, sprinkler protection at the ceiling of the atrium is not required. | 404.3 Automatic sprinkler protection. | An approved automatic sprinkler system shall be installed throughout the entire building.
403.4.8.4.3 Emergency power loads in Group R-2 occupancies 125 feet or less in height. | Group R-2 occupancies in buildings 125 feet (38 100 mm) or less in height shall be required to provide an emergency power system to support the following loads:
404.4 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.14. | 404.4 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.14.
404.5 Smoke control. | A smoke control system shall be installed in accordance with Section 909. Exception: In other than Groups I-1 and I-2, and covered mall buildings containing an atrium pursuant to Section 402.7.2, smoke control is not required for atriums that connect only two stories. | 404.5 Smoke control. | A smoke control system shall be installed in accordance with Section 909.
404.6 Enclosure of atriums. | Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section 711, or both. Exceptions: 1. A fire barrier is not required where a glass or glass-block wall forming a smoke partition is provided. The glass or glass-block wall shall comply with all of the following: 1.1. Automatic sprinklers are provided along both sides of the separation wall and doors, or on the room side only if there is not a walkway on the atrium side. The sprinklers shall be located between 4 inches and 12 inches (102 mm and 305 mm) away from the glass and at intervals along the glass not greater than 6 feet (1829 mm). The sprinkler system shall be designed so that the entire surface of the glass is wet upon activation of the sprinkler system without obstruction; 1.2. The glass wall shall be installed in a gasketed frame in a manner that the framing system deflects without breaking (loading) the glass before the sprinkler system operates; and 1.3. Where glass doors are provided in the glass wall, they shall be either self-closing or automatic-closing. 2. The adjacent spaces of any three floors of the atrium shall not be required to be separated from the atrium where such spaces are accounted for in the design of the smoke control system. | 404.6 Enclosure of atriums. | Atrium spaces shall be separated from adjacent spaces by a 1-hour fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section 711, or both.
403.5.2 Additional exit stairway. | For buildings other than Group R-2 that are more than 420 feet (128 m) in building height, one additional exit stairway meeting the requirements of Sections 1011 and 1023 shall be provided in addition to the minimum number of exits required by Section 1006.3. The total width of any combination of remaining exit stairways with one exit stairway removed shall not be less than the total width required by Section 1005.1. Stairs sharing any common wall, floors, ceilings, scissor stair assemblies, or other enclosures shall not be considered the additional exit stairway required by this section. Exceptions: An additional exit stairway shall not be required to be installed in any of the following instances: 1. In buildings where all passenger elevators for general public use and all other elevators used for occupant self-evacuation comply with Sections 3008.1 through 3008.11; 2. In buildings where all of the following conditions are met: 2.1. The commissioner has approved a timed egress analysis establishing the egress time it would take for a full building evacuation, utilizing the stairs required by Section 1006 and the additional stair that would have been required pursuant to Section 403.5.2; 2.2. The commissioner has approved a timed egress analysis establishing the egress time it would take for a full building evacuation, utilizing the combination of the stairs required by Section 1006 and elevators used for occupant self-evacuation as follows: 2.2.1. Such analysis need only utilize a number of designated elevators designed for occupant self-evacuation necessary to demonstrate an evacuation time that is less than the time established in Exception 2.1; and 2.2.2. Every bank of passenger elevators for general public use shall be served by at least one such designated elevator; 2.3. All elevators in the building that either are passenger elevators for general public use or are used for occupant self-evacuation shall comply with Sections 3008.1 through 3008.11. However, the standby power generating equipment required by Section 3008.9 need only be sized to satisfy the loads required to simultaneously operate those elevators identified in the timed egress analysis described in Exception 2.2. The minimum number of exits required by Section 1006 are all at least 25 percent wider than the exit width required by Chapter 10. The increase in the stair width shall not be utilized in the timed egress analyses required by Exceptions 2.1 and 2.2. | 403.5.2 Additional interior exit stairway. | For buildings other than Group R-2 and their ancillary spaces that are more than 420 feet (128 m) in building height, one additional interior exit stairway meeting the requirements of Sections 1011 and 1023 shall be provided in addition to the minimum number of exits required by Section 1006.3. The total capacity of any combination of remaining interior exit stairways with one interior exit stairway removed shall be not less than the total capacity required by Section 1005.1. Scissor stairways shall not be considered the additional interior exit stairway required by this section.
404.7 Standby power. | Equipment required to provide smoke control shall be provided with standby power in accordance with Section 909.11. | 404.7 Standby power. | Equipment required to provide smoke control shall be provided with standby power in accordance with Section 909.11.
404.8 Interior finish. | The interior finish of walls and ceilings of the atrium shall be not less than Class B with no reduction in class for sprinkler protection. | 404.8 Interior finish. | The interior finish of walls and ceilings of the atrium shall be not less than Class B. Sprinkler protection shall not result in a reduction in class.
404.9 Exit access travel distance. | Exit access travel distance for areas open to an atrium shall comply with the requirements of this section. | 404.9 Exit access travel distance. | Exit access travel distance for areas open to an atrium shall comply with the requirements of Section 1017.
403.5.6 Emergency escape and rescue. | Emergency escape and rescue openings specified in Section 1030 are not required.
405.1 General. | The provisions of Sections 405.2 through 405.9 apply to building spaces having a floor level used for human occupancy more than 30 feet (9144 mm) below the finished floor of the lowest level of exit discharge. Exceptions: The provisions of Section 405 are not applicable to the following buildings or portions of buildings: 1. One- and two-family dwellings, sprinklered in accordance with Section 903.3.1.3. 2. Parking garages provided with automatic sprinkler systems in compliance with Section 405.3. 3. Fixed guideway transit systems. 4. Grandstands, bleachers, stadiums, arenas and similar facilities. 5. Where the lowest story is the only story that would qualify the building as an underground building and has an area not greater than 1,500 square feet (139 m2) and has an occupant load less than 10. 6. Pumping stations and other similar mechanical spaces intended only for limited periodic use by service or maintenance personnel. | 405.1 General. | The provisions of Sections 405.2 through 405.9 apply to building spaces having a floor level used for human occupancy more than 30 feet (9144 mm) below the finished floor of the lowest level of exit discharge.
405.2 Construction requirements. | The underground portion of the building shall be of Type I construction. | 405.2 Construction requirements. | The underground portion of the building shall be of Type I construction.
405.3 Automatic sprinkler system. | The highest level of exit discharge serving the underground portions of the building and all levels below shall be equipped with an automatic sprinkler system installed in accordance with Section 903.3.1.1. Water-flow switches and control valves shall be supervised in accordance with Section 903.4. | 405.3 Automatic sprinkler system. | The highest level of exit discharge serving the underground portions of the building and all levels below shall be equipped with an automatic sprinkler system installed in accordance with Section 903.3.1.1. Water-flow switches and control valves shall be supervised in accordance with Section 903.4.
405.4 Compartmentation. | Compartmentation shall be in accordance with Sections 405.4.1 through 405.4.3. | 405.4 Compartmentation. | Compartmentation shall be in accordance with Sections 405.4.1 through 405.4.3.
403.6.3 Elevator lobbies. | Elevator lobbies shall be provided in accordance with Sections 3006.1.1 and 3006.1.2.
405.4.1 Number of compartments. | A building having a floor level more than 60 feet (18 288 mm) below the finished floor of the lowest level of exit discharge shall be divided into no fewer than two compartments of approximately equal size. Such compartmentation shall extend through the highest level of exit discharge serving the underground portions of the building and all levels below. Exception: The lowest story need not be compartmented where the area is not greater than 1,500 square feet (139 m2) and has an occupant load of less than 10. | 405.4.1 Number of compartments. | A building having a floor level more than 60 feet (18 288 mm) below the finished floor of the lowest level of exit discharge shall be divided into not fewer than two compartments of approximately equal size. Such compartmentation shall extend through the highest level of exit discharge serving the underground portions of the building and all levels below.
403.7 Outdoor air intakes. | For high-rise buildings, outdoor air intakes serving spaces above the second story and serving spaces greater than 10,000 square feet (929 m2) of floor area shall be located in accordance with Section 401.5 of the New York City Mechanical Code. Exception: Group R-2 occupancy.
403.8 Open web steel joists. | The use of open web steel joists shall be prohibited in high-rise buildings until the commissioner promulgates rules establishing minimum acceptable fireproofing methods.
405.4.3 Elevators. | Where elevators are provided, each compartment shall have direct access to an elevator. Where an elevator serves more than one compartment, an elevator lobby shall be provided and shall be separated from each compartment by a 2-hour fire barrier. Doors shall be gasketed, have a drop sill, and be automatic-closing by smoke detection in accordance with Section 716.5.9.3. | 405.4.3 Elevators. | Where elevators are provided, each compartment shall have direct access to an elevator. Where an elevator serves more than one compartment, an enclosed elevator lobby shall be provided and shall be separated from each compartment by a smoke barrier in accordance with Section 709. Doorways in the smoke barrier shall be protected by fire door assemblies that comply with Section 716, shall comply with the smoke and draft control assembly requirements of Section 716.2.2.1 with the UL 1784 test conducted without an artificial bottom seal, and shall be automatic-closing by smoke detection in accordance with Section 716.2.6.6.
405.5 Smoke control system. | A smoke control system shall be provided in accordance with Sections 405.5.1 and 405.5.2. | 405.5 Smoke control system. | A smoke control system shall be provided in accordance with Sections 405.5.1 and 405.5.2.
404.1.1 Definitions. | The following term is defined in Chapter 2:
405.5.1 Control system. | A smoke control system is required to control the migration of products of combustion in accordance with Section 909 and the provisions of this section. Smoke control shall restrict movement of smoke to the general area of fire origin and maintain means of egress in a usable condition. | 405.5.1 Control system. | A smoke control system is required to control the migration of products of combustion in accordance with Section 909 and the provisions of this section. Smoke control shall restrict movement of smoke to the general area of fire origin and maintain means of egress in a usable condition.
405.5.2 Compartment smoke control system. | Where compartmentation is required, each compartment shall have an independent smoke control system. The system shall be automatically activated and capable of manual operation in accordance with Sections 907.2.18 and 907.2.19. | 405.5.2 Compartment smoke control system. | Where compartmentation is required, each compartment shall have an independent smoke control system. The system shall be automatically activated and capable of manual operation in accordance with Sections 907.2.18 and 907.2.19.
405.6 Fire alarm systems. | A fire alarm system shall be provided where required by Sections 907.2.18 and 907.2.19. | 405.6 Fire alarm systems. | A fire alarm system shall be provided where required by Sections 907.2.18 and 907.2.19.
405.7 Means of egress. | Means of egress shall be in accordance with Sections 405.7.1 and 405.7.2. | 405.7 Means of egress. | Means of egress shall be in accordance with Sections 405.7.1 and 405.7.2.
405.7.1 Number of exits. | Each floor level shall be provided with no fewer than two exits. Where compartmentation is required by Section 405.4, each compartment shall have no fewer than one exit and shall also have no fewer than one exit access doorway into the adjoining compartment. | 405.7.1 Number of exits. | Each floor level shall be provided with not fewer than two exits. Where compartmentation is required by Section 405.4, each compartment shall have not fewer than one exit and not fewer than one exit access doorway into the adjoining compartment.
405.7.2 Smokeproof enclosure. | Every required stairway serving floor levels more than 30 feet (9144 mm) below its level of exit discharge shall comply with the requirements for a smokeproof enclosure as provided in Section 1023.11. | 405.7.2 Smokeproof enclosure. | Every required stairway serving floor levels more than 30 feet (9144 mm) below the finished floor of its level of exit discharge shall comply with the requirements for a smokeproof enclosure as provided in Section 1023.12.
405.8 Standby and emergency power. | A standby power system complying with Section 2702 shall be provided for the standby power loads specified in Section 405.8.1. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 405.8.2. | 405.8 Standby and emergency power. | A standby power system complying with Section 2702 shall be provided for the standby power loads specified in Section 405.8.1. An emergency power system complying with Section 2702 shall be provided for the emergency power loads specified in Section 405.8.2.
405.8.1 Standby power loads. | The following loads are classified as standby power loads: | 405.8.1 Standby power loads. | The following are classified as standby power loads:
405.8.2 Emergency power loads. | The following loads are classified as emergency power loads: | 405.8.2 Emergency power loads. | The following are classified as emergency power loads:
404.9.1 Egress not through the atrium. | Where required access to the exits is not through the atrium, exit access travel distance shall comply with Section 1017.
405.9 Standpipe system. | The underground building shall be equipped throughout with a standpipe system in accordance with Section 905. | 405.9 Standpipe system. | The underground building shall be equipped throughout with a standpipe system in accordance with Section 905.
404.9.2 Exit access travel distance at the level of exit discharge. | Where the path of egress travel is through an atrium space, exit access travel distance at the level of exit discharge shall be determined in accordance with Section 1017.
406.1 General. | Motor-vehicle-related occupancies shall comply with Sections 406.1 through 406.8. | 406.1 General. | All motor-vehicle-related occupancies shall comply with Section 406.2. Private garages and carports shall also comply with Section 406.3. Open public parking garages shall also comply with Sections 406.4 and 406.5. Enclosed public parking garages shall also comply with Sections 406.4 and 406.6. Motor fuel-dispensing facilities shall also comply with Section 406.7. Repair garages shall also comply with Section 406.8.
404.9.3 Exit access travel distance at other than the level of exit discharge. | Where the path of egress travel is not at the level of exit discharge from the atrium, that portion of the total permitted exit access travel distance that occurs within the atrium shall be not greater than 200 feet (60 960 mm).
404.10 Interior exit stairways. | A maximum of 50 percent of interior exit stairways are permitted to egress through an atrium on the level of exit discharge in accordance with Section 1028. | 404.10 Exit stairways in an atrium. | Where an atrium contains an interior exit stairway all the following shall be met:
405.4.2 Compartment separation. | The separation between the two compartments shall be of minimum 2-hour fire barrier wall construction that shall extend from floor slab to floor deck above. Penetrations between the two compartments shall be limited to plumbing and electrical piping and conduit that are firestopped in accordance with Section 714. Doorways shall be protected by fire door assemblies that are automatic-closing by smoke detection in accordance with Section 716.5.9.3 and are installed in accordance with NFPA 105 and Section 716.5.3 of this code. Where provided, each compartment shall have an air supply and an exhaust system independent of the other compartments.
406.3 Private garages and carports. | Private garages and carports shall comply with Sections 406.3.1 through 406.3.5. | 406.3 Private garages and carports. | Private garages and carports shall comply with Sections 406.2 and 406.3, or they shall comply with Sections 406.2 and 406.4.
406.3.1 Classification. | Private garages and carports shall be classified as Group U occupancy. | 406.3.1 Classification. | Private garages and carports shall be classified as Group U occupancies. Each private garage shall be not greater than 1,000 square feet (93 m2) in area. Multiple private garages are permitted in a building where each private garage is separated from the other private garages by 1-hour fire barriers in accordance with Section 707, or 1-hour horizontal assemblies in accordance with Section 711, or both.
406.2 Definitions. | The following terms are defined in Chapter 2: | 406.2 Design. | Private garages and carports, open and enclosed public parking garages, motor fuel-dispensing facilities and repair garages shall comply with Sections 406.2.1 through 406.2.9.
406.4 Public parking garages. | Parking garages, other than private parking garages, shall be classified as public parking garages and shall comply with the provisions of Sections 406.4.2 through 406.4.10 and shall be classified as either an open parking garage or an enclosed parking garage. Open parking garages shall also comply with Section 406.5. Enclosed parking garages shall also comply with Section 406.6. See Section 510 for special provisions for parking garages. | 406.4 Public parking garages. | Parking garages, other than private garages, shall be classified as public parking garages and shall comply with the provisions of Sections 406.2 and 406.4 and shall be classified as either an open parking garage or an enclosed parking garage. Open parking garages shall also comply with Section 406.5. Enclosed parking garages shall also comply with Section 406.6. See Section 510 for special provisions for parking garages.
406.3.2 Clear height. | In private garages and carports, the clear height in vehicle and pedestrian traffic areas shall be not less than 7 feet (2134 mm). Vehicle and pedestrian areas accommodating van-accessible parking shall comply with Section 1106.5. | 406.3.2 Separation. | For other than private garages adjacent to dwelling units, the separation of private garages from other occupancies shall comply with Section 508. Separation of private garages from dwelling units shall comply with Sections 406.3.2.1 and 406.3.2.2.
406.3.3 Floor construction. | Private garage and carport floors shall be of concrete or equivalent noncombustible material that will not absorb flammable liquids. The area of floor used for parking of vehicles shall be sloped to facilitate the movement of liquids to a drain. The sills of all door openings connecting a dwelling unit to a private garage shall be raised at least 4 inches (102 mm) above the floor level of the garage. Exception: Asphalt surfaces shall be permitted at ground level in carports. | 406.3.3 Carports. | Carports shall be open on not fewer than two sides. Carports open on fewer than two sides shall be considered to be a garage and shall comply with the requirements for private garages.
406.5 Open parking garages. | Open parking garages shall comply with Sections 406.5.1 through 406.5.11. | 406.5 Open parking garages. | Open parking garages shall comply with Sections 406.2, 406.4 and 406.5.
406.3.3.1 Ramps. | Ramps shall have a gradient not exceeding one in seven, with nonslip surfaces, and shall be located entirely within the property line. However, upon application to the commissioner, steeper gradients may be accepted, but in no event greater than one in three.
406.5.1 Construction. | Open parking garages shall be of Type I, II or IV construction. Open parking garages shall meet the design requirements of Chapter 16. For vehicle barriers, see Section 406.4.3. | 406.5.1 Construction. | Open parking garages shall be of Type I, II or IV construction. Open parking garages shall meet the design requirements of Chapter 16. For vehicle barriers, see Section 406.4.2.
406.3.4 Separation. | Separations shall comply with the following:
406.5.2 Openings. | For natural ventilation purposes, the exterior side of the structure shall have uniformly distributed openings on two or more sides. The area of such openings in exterior walls on a tier shall be not less than 20 percent of the total perimeter wall area of each tier. The aggregate length of the openings considered to be providing natural ventilation shall be not less than 40 percent of the perimeter of the tier. Interior walls shall be not less than 20 percent open with uniformly distributed openings. Exception: Openings are not required to be distributed over 40 percent of the building perimeter where the required openings are uniformly distributed over two opposing sides of the building. | 406.5.2 Openings. | For natural ventilation purposes, the exterior side of the structure shall have uniformly distributed openings on two or more sides. The area of such openings in exterior walls on a tier shall be not less than 20 percent of the total perimeter wall area of each tier. The aggregate length of the openings considered to be providing natural ventilation shall be not less than 40 percent of the perimeter of the tier. Interior walls shall be not less than 20 percent open with uniformly distributed openings.
406.5.2.1 Openings below grade. | Where openings below grade provide required natural ventilation, the outside horizontal clear space shall be 1 ½ times the depth of the opening. The width of the horizontal clear space shall be maintained from grade down to the bottom of the lowest required opening. | 406.5.2.1 Openings below grade. | Where openings below grade provide required natural ventilation, the outside horizontal clear space shall be one and one-half times the depth of the opening. The width of the horizontal clear space shall be maintained from grade down to the bottom of the lowest required opening.
406.3.5 Automatic garage door openers. | Automatic garage door openers, where provided, shall be listed in accordance with UL 325.
406.5.4 Area and height. | Area and height of open parking garages shall be limited as set forth in Chapter 5 for Group S-2 occupancies. | 406.5.4 Area and height. | Area and height of open parking garages shall be limited as set forth in Chapter 5 for Group S-2 occupancies and as further provided for in Section 508.1.
406.4.1 Clear height. | The clear height of each floor level in vehicle and pedestrian traffic areas shall be not less than 7 feet (2134 mm). Vehicle and pedestrian areas accommodating van-accessible parking shall comply with Section 1106.5.
406.5.4.1 Single use. | Where the open parking garage is used exclusively for the parking or storage of private motor vehicles, with no other uses in the building, the area and height shall be permitted to comply with Table 406.5.4. Exception: The grade-level tier is permitted to contain an office, waiting and toilet rooms having a total combined area of not more than 1,000 square feet (93 m2). Such area need not be separated from the open parking garage. | 406.5.4.1 Single use. | Where the open parking garage is used exclusively for the parking or storage of private motor vehicles, and the building is without other uses, the area and height shall be permitted to comply with Table 406.5.4, along with increases allowed by Section 406.5.5. |  | See BC04 Tables&Figures
406.4.2 Guards. | Guards shall be provided in accordance with Section 1015. Guards serving as vehicle barrier systems shall comply with Sections 406.4.3 and 1015.
406.5.5 Area and height increases. | The allowable area and height of open parking garages shall be increased in accordance with the provisions of this section. Garages with sides open on three-fourths of the building’s perimeter are permitted to be increased by 25 percent in area and one tier in height. Garages with sides open around the entire building’s perimeter are permitted to be increased by 50 percent in area and one tier in height. For a side to be considered open under the above provisions, the total area of openings along the side shall not be less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm). | 406.5.5 Area and height increases. | The allowable area and height of open parking garages shall be increased in accordance with the provisions of this section. Garages with sides open on three-fourths of the building’s perimeter are permitted to be increased by 25 percent in area and one tier in height. Garages with sides open around the entire building’s perimeter are permitted to be increased by 50 percent in area and one tier in height. For a side to be considered open under these provisions, the total area of openings along the side shall be not less than 50 percent of the interior area of the side at each tier and such openings shall be equally distributed along the length of the tier. For purposes of calculating the interior area of the side, the height shall not exceed 7 feet (2134 mm).
406.4.3 Vehicle barrier systems. | Vehicle barriers not less than 2 feet 9 inches (835 mm) in height shall be placed where the vertical distance from the floor of a drive lane or parking space to the ground or surface directly below is greater than 1 foot (305 mm). Vehicle barriers shall comply with the loading requirements of Section 1607.9. Exception: Vehicle barriers are not required in vehicle storage compartments in a mechanical access parking garage.
406.5.6 Fire separation distance. | Exterior walls and openings in exterior walls shall comply with Tables 601 and 602. The distance from an adjacent property line shall be determined in accordance with Table 602 and Section 705. | 406.5.6 Fire separation distance. | Exterior walls and openings in exterior walls shall comply with Table 601 and Table 705.5. The distance to an adjacent lot line shall be determined in accordance with Section 705 and Table 705.5. |  | See BC06 Tables&Figures
406.4.4 Ramps. | Ramps shall have a gradient not exceeding one in seven, with nonslip surfaces. A level landing having a minimum dimension of 20 feet (6096 mm) shall be provided at the discharge point of all ramps at the street level, within the property line. Ramps used for the movement of motor vehicles need not be enclosed when serving tiers above grade. Vehicle ramps may serve as part of a means of egress in accordance with Section 1006.4.
406.5.7 Means of egress. | Open parking garages shall meet the means of egress requirements of Chapter 10. However, where no persons other than parking attendants are permitted, required exit stairways shall not be less than 36 inches (914 mm) wide. | 406.5.7 Means of egress. | Where persons other than parking attendants are permitted, open parking garages shall meet the means of egress requirements of Chapter 10. Where persons other than parking attendants are not permitted, there shall be not fewer than two exit stairways. Each exit stairway shall be not less than 36 inches (914 mm) in width. Lifts shall be permitted to be installed for use of employees only, provided that they are completely enclosed by noncombustible materials.
406.4.5 Floor surface. | Parking surfaces shall be of concrete or similar noncombustible and nonabsorbent materials. The area of floor used for parking of vehicles shall be sloped to facilitate the movement of liquids to a drain. Exceptions: 1. Asphalt parking surfaces shall be permitted at ground level. 2. Floors of Group S-2 parking garages shall not be required to have a sloped surface.
406.4.6 Separation. | Parking garages shall be separated from other occupancies in accordance with Section 508.1.
406.5.9 Enclosure of vertical openings. | Enclosure shall not be required for vertical openings. | 406.5.9 Enclosure of vertical openings. | Enclosure shall not be required for vertical openings except as specified in Section 406.5.7.
406.4.7 Special hazards. | Connection of a parking garage with any room in which there is a fuel-fired appliance shall be by means of a vestibule providing a two-doorway separation. Such vestibule and doorway shall be minimum 1-hour rated construction. Exception: A single door shall be allowed provided the sources of ignition in the appliance are not less than 18 inches (457 mm) above the floor.
406.5.10 Ventilation. | Openings specified in Section 406.5.2 shall satisfy natural ventilation requirements. Additional mechanical ventilation shall not be required. | 406.5.10 Ventilation. | Ventilation, other than the percentage of openings specified in Section 406.5.2, shall not be required.
406.4.8 Attached to rooms. | Openings from a parking garage directly into a room used for sleeping purposes shall not be permitted.
406.5.11 Prohibitions. | The following uses and alterations are not permitted: | 406.5.11 Prohibitions. | The following uses and alterations are not permitted:
406.4.9 Fire-fighter aisles. | In any parking garage or lot, one or more aisles, at least 24 inches (610 mm) in width, shall be provided to permit access by fire-fighting personnel to all parts of the garage or lot. There shall not be more than three rows of parked motor vehicles between aisles.
406.6 Enclosed parking garages. | Parking garages and portions thereof that do not meet the definition of “Open parking garages” shall be classified as an enclosed parking garage and shall meet the requirements of this section. | 406.6 Enclosed parking garages. | Enclosed parking garages shall comply with Sections 406.2, 406.4 and 406.6.
406.4.10 Electric vehicle charging stations. | Parking garages shall be capable of supporting electrical vehicle charging stations in accordance with this section. Electrical raceway to the electrical supply panel serving the garage shall be capable of providing a minimum of 3.1 kW of electrical capacity to at least 20 percent of the parking spaces of the garage. The electrical room supplying the garage must have the physical space for an electrical supply panel sufficient to provide 3.1kW of electrical capacity to at least 20 percent of the parking spaces of the garage. Such raceway and all components and work appurtenant thereto shall be in accordance with the New York City Electrical Code. Exceptions: 1. The provisions of this section shall not apply to parking garages for buildings of Occupancy Group M (Mercantile). 2. The commissioner may waive compliance with this section if the commissioner determines that the parking garage is a temporary facility that will be in service no longer than three years. 3. The provisions of this section shall not apply to parking garages for buildings in which not less than 50 percent of the residential units are for households earning up to 60 percent of the area median income as determined by the United States Department of Housing and Urban Development.
406.6.1 Heights and areas. | Enclosed parking garages shall be limited to the allowable heights and areas specified in Chapter 5. Permitted roof parking shall not be considered as a separate story. | 406.6.1 Heights and areas. | Enclosed vehicle parking garages and portions thereof that do not meet the definition of open parking garages shall be limited to the allowable heights and areas specified in Sections 504 and 506 as modified by Section 507. Roof parking is permitted.
406.6.2 Ventilation. | A mechanical ventilation system shall be provided in accordance with the New York City Mechanical Code. | 406.6.2 Ventilation. | A mechanical ventilation system and exhaust system shall be provided in accordance with Chapters 4 and 5 of the International Mechanical Code.
406.6.3 Automatic sprinkler system. | Automatic sprinkler systems and standpipes shall be installed in accordance with the provisions of Section 903. An automatic dry sprinkler system may be installed in unheated garages. | 406.6.3 Automatic sprinkler system. | An enclosed parking garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.10.
406.5.3 Uses. | Mixed uses shall be allowed in the same building as an open parking garage subject to the provisions of Sections 402.4.2.3, 406.5.11, 508.1, 510.3, 510.4 and 510.7.
406.7 Motor fuel-dispensing facilities. | Motor fuel-dispensing facilities shall be designed and constructed in accordance with the New York City Fire Code and Sections 406.7.1 through 406.7.3 of this code. | 406.7 Motor fuel-dispensing facilities. | Motor fuel-dispensing facilities shall comply with the International Fire Code and Sections 406.2 and 406.7.
406.7.1 Vehicle fueling pad. | The vehicle shall be fueled on noncoated concrete or other approved paving material having a resistance not exceeding 1 megohm as determined by the methodology in CEN 1081. | 406.7.1 Vehicle fueling pad. | The vehicle shall be fueled on noncoated concrete or other approved paving material having a resistance not exceeding 1 megohm as determined by the methodology in CEN EN 1081.
406.5.8 Standpipes. | Standpipes shall be installed where required by the provisions of Section 905.
406.7.2 Canopies. | Canopies under which fuels are dispensed shall have a clear, unobstructed height of not less than 14 feet (4267 mm) to the lowest projecting element in the vehicle drive-through area. Canopies and their supports over pumps shall be of noncombustible materials. However, panels constructed of light-transmitting plastic materials shall be permitted to be installed in canopies erected over motor vehicle fuel-dispensing station fuel dispensers, provided the panels are located not less than 10 feet (3048 mm) from any building on the same property and face yards or streets not less than 40 feet (12 192 mm) in width on the other sides. The aggregate areas of plastics shall be not greater than 1,000 square feet (93 m2). The maximum area of any individual panel shall be not greater than 100 square feet (9.3 m2). | 406.7.2 Canopies. | Canopies under which fuels are dispensed shall have a clear, unobstructed height of not less than 13 feet 6 inches (4115 mm) to the lowest projecting element in the vehicle drive-through area. Canopies and their supports over pumps shall be of noncombustible materials, fire-retardant-treated wood complying with Chapter 23, heavy timber complying with Section 2304.11 or construction providing 1-hour fire resistance. Combustible materials used in or on a canopy shall comply with one of the following:
406.7.2.1 Canopies used to support gaseous hydrogen systems. | Where flammable compressed gases are permitted by the New York City Fire Code to be located on the roof of a canopy that is used to shelter dispensing operations, such canopy shall be in accordance with the following: | 406.7.2.1 Canopies used to support gaseous hydrogen systems. | Canopies that are used to shelter dispensing operations where flammable compressed gases are located on the roof of the canopy shall be in accordance with the following:
406.8 Repair garages. | Repair garages shall be constructed in accordance with the New York City Fire Code and Sections 406.8.1 through 406.8.6 of this code. This occupancy shall not include motor fuel-dispensing facilities, as regulated in Section 406.7. | 406.8 Repair garages. | Repair garages shall be constructed in accordance with the International Fire Code and Sections 406.2 and 406.8. This occupancy shall not include motor fuel-dispensing facilities, as regulated in Section 406.7.
406.6.4 Means of egress. | Enclosed parking garages shall meet the means of egress requirements of Chapter 10.
407.1 General. | Occupancies in Group I-2 shall comply with the provisions of Sections 407.1 through 407.10 and other applicable provisions of this code. | 407.1 General. | Occupancies in Group I-2 shall comply with the provisions of Sections 407.1 through 407.11 and other applicable provisions of this code.
407.2 Corridors continuity and separation. | Corridors in occupancies in Group I-2 shall be continuous to the exits and shall be separated from other areas in accordance with Section 407.3 except spaces conforming to Sections 407.2.1 through 407.2.6. | 407.2 Corridors continuity and separation. | Corridors in occupancies in Group I-2 shall be continuous to the exits and shall be separated from other areas in accordance with Section 407.3 except spaces conforming to Sections 407.2.1 through 407.2.6.
407.2.1 Waiting and similar areas. | Waiting areas and similar spaces constructed as required for corridors shall be permitted to be open to a corridor, only where all of the following criteria are met: | 407.2.1 Waiting and similar areas. | Waiting areas, public-use areas or group meeting spaces constructed as required for corridors shall be permitted to be open to a corridor, only where all of the following criteria are met:
407.2.2 Care providers’ stations. | Spaces for care providers’, supervisory staff, doctors’ and nurses’ charting, communications and related clerical areas shall be permitted to be open to the corridor, where such spaces are constructed as required for corridors. | 407.2.2 Care providers’ stations. | Spaces for care providers’, supervisory staff, doctors’ and nurses’ charting, communications and related clerical areas shall be permitted to be open to the corridor, where such spaces are constructed as required for corridors.
407.2.3 Psychiatric treatment areas. | Areas wherein psychiatric care recipients who are not capable of self-preservation are housed, or group meeting or multipurpose therapeutic spaces other than incidental uses in accordance with Section 509, under continuous supervision by facility staff, shall be permitted to be open to the corridor, where the following criteria are met: | 407.2.3 Psychiatric treatment areas. | Areas wherein psychiatric care recipients who are incapable of self-preservation are housed, or group meeting or multipurpose therapeutic spaces other than incidental uses in accordance with Section 509, under continuous supervision by facility staff, shall be permitted to be open to the corridor, where the following criteria are met:
406.7.3 Storage tanks. | Motor fuel storage tanks shall be installed below ground, except as authorized by the rules of the Fire Department. The installation and venting of storage tanks shall be in accordance with the rules of the Fire Department and the requirements of the New York City Fire Code. Storage tanks installed below ground shall comply with the following:
407.2.4 Gift shops. | Gift shops and associated storage that are less than 500 square feet (46 m2) in area shall be permitted to be open to the corridor where such spaces are constructed as required for corridors. | 407.2.4 Gift shops. | Gift shops and associated storage that are less than 500 square feet (455 m2) in area shall be permitted to be open to the corridor where such spaces are constructed as required for corridors.
407.2.5 Nursing home housing units. | In Group I-2 occupancies, in areas where nursing home residents are housed, shared living spaces, group meeting or multipurpose therapeutic spaces shall be permitted to be open to the corridor, where all of the following criteria are met: | 407.2.5 Nursing home housing units. | In Group I-2, Condition 1 occupancies, in areas where nursing home residents are housed, shared living spaces, group meeting or multipurpose therapeutic spaces shall be permitted to be open to the corridor, where all of the following criteria are met:
406.8.1 Mixed uses. | Mixed uses shall be allowed in the same building as a repair garage subject to the provisions of Section 508.1.
407.2.6 Nursing home cooking facilities. | In Group I-2 occupancies, rooms or spaces that contain a cooking facility with domestic cooking appliances shall be permitted to be open to the corridor where all of the following criteria are met: | 407.2.6 Nursing home cooking facilities. | In Group I-2, Condition 1 occupancies, rooms or spaces that contain a cooking facility with domestic cooking appliances shall be permitted to be open to the corridor where all of the following criteria are met:
406.8.2 Ventilation. | Repair garages shall be mechanically ventilated in accordance with the New York City Mechanical Code. The ventilation system shall be controlled at the entrance to the garage.
406.8.3 Floor surface. | Repair garage floors shall be of concrete or similar noncombustible and nonabsorbent materials. Exception: Slip-resistant, nonabsorbent, interior floor finishes having a critical radiant flux not more than 0.45 W/cm2, as determined by NFPA 253, shall be permitted.
407.3 Corridor wall construction. | Corridor walls shall be constructed as smoke partitions in accordance with Section 710. | 407.3 Corridor wall construction. | Corridor walls shall be constructed as smoke partitions in accordance with Section 710.
406.8.4 Heating equipment. | Heating equipment shall be installed in accordance with the New York City Mechanical Code.
407.3.1 Corridor doors. | Corridor doors, other than those in a wall required to be rated by Section 509.4 or for the enclosure of a vertical opening or an exit, shall not have a required fire protection rating and shall not be required to be equipped with self-closing or automatic-closing devices, but shall provide an effective barrier to limit the transfer of smoke and shall be equipped with positive latching. Roller latches are not permitted. Other doors shall conform to Section 716.5. | 407.3.1 Corridor doors. | Corridor doors, other than those in a wall required to be rated by Section 509.4 or for the enclosure of a vertical opening or an exit, shall not have a required fire protection rating and shall not be required to be equipped with self-closing or automatic-closing devices, but shall provide an effective barrier to limit the transfer of smoke and shall be equipped with positive latching. Roller latches are not permitted. Other doors shall conform to Section 716.
406.8.5 Gas detection system. | Repair garages used for the repair of vehicles fueled by CNG, LNG, or hydrogen, shall be provided with an approved flammable gas-detection system.
406.8.5.1 System design. | The flammable gas-detection system shall be listed or approved and shall be calibrated to the types of fuels or gases used by vehicles to be repaired. The gas detection system shall be designed to activate when the level of flammable gas exceeds 25 percent of the lower flammable limit (LFL). Gas detection shall be provided in lubrication or chassis service pits of repair garages used for repairing nonodorized LNG-fueled vehicles.
407.4 Means of egress. | Group I-2 occupancies shall be provided with means of egress complying with Chapter 10 and Sections 407.4.1 through 407.4.4. The fire and emergency preparedness plans provided in accordance with Section 1001.4 of this code shall identify the building components necessary to support a defend-in-place emergency response in accordance with the New York City Fire Code. | 407.4 Means of egress. | Group I-2 occupancies shall be provided with means of egress complying with Chapter 10 and Sections 407.4.1 through 407.4.4. The fire safety and evacuation plans provided in accordance with Section 1002.2 shall identify the building components necessary to support a defend-in-place emergency response in accordance with Sections 403 and 404 of the International Fire Code.
406.8.5.1.1 Gas detection system components. | Gas detection system control units shall be listed and labeled in accordance with UL 864 or UL 2017. Gas detectors shall be listed and labeled in accordance with UL 2075 for use with the gases and vapors being detected.
407.4.1 Direct access to a corridor. | Habitable rooms in Group I-2 occupancies shall have an exit access door leading directly to a corridor. Exceptions: 1. Rooms with exit doors opening directly to the outside at ground level. 2. Rooms arranged as care suites complying with Section 407.4.4. | 407.4.1 Direct access to a corridor. | Habitable rooms in Group I-2 occupancies shall have an exit access door leading directly to a corridor. |  | See BC04 Tables&Figures
406.8.5.2 Operation. | Activation of the gas detection system shall result in all of the following:
407.4.1.1 Locking devices. | Locking devices that restrict access to a care recipient’s room from the corridor and that are operable only by staff from the corridor side shall not restrict the means of egress from the care recipient’s room. Exceptions: 1. This section shall not apply to rooms in psychiatric treatment and similar care areas. 2. Locking arrangements in accordance with Section 1010.1.9.6. | 407.4.1.1 Locking devices. | Locking devices that restrict access to a care recipient’s room from the corridor and that are operable only by staff from the corridor side shall not restrict the means of egress from the care recipient’s room.
406.8.5.3 Failure of the gas detection system. | Failure of the gas detection system shall result in the deactivation of the heating system, activation of the mechanical ventilation system where the system is interlocked with the gas detection system and cause a trouble signal to sound in an approved location.
407.4.2 Distance of travel. | The distance of travel between any point in a Group I-2 occupancy sleeping room, not located in a care suite, and an exit access door in that room shall be not greater than 50 feet (15 240 mm). | 407.4.2 Distance of travel. | The distance of travel between any point in a Group I-2 occupancy sleeping room, not located in a care suite, and an exit access door in that room shall be not greater than 50 feet (15 240 mm).
406.8.6 Automatic sprinkler system. | A repair garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.4.2.
407.4.3 Projections in nursing home corridors. | In nursing homes of Group I-2 occupancies, where the corridor width is a minimum of 96 inches (2440 mm), projections shall be permitted for furniture where all of the following criteria are met: | 407.4.3 Projections in nursing home corridors. | In Group I-2, Condition 1 occupancies, where the corridor width is not less than 96 inches (2440 mm), projections shall be permitted for furniture where all of the following criteria are met:
406.9 Open parking lots. | The provisions of this section shall govern the construction of open parking lots and to all such existing premises hereafter enlarged or changed in location.
407.4.4 Group I-2 care suites. | Care suites in Group I-2 shall comply with Sections 407.4.4.1 through 407.4.4.4 and either Section 407.4.4.5 or 407.4.4.6. | 407.4.4 Group I-2 care suites. | Care suites in Group I-2 shall comply with Sections 407.4.4.1 through 407.4.4.4 and either Section 407.4.4.5 or 407.4.4.6.
406.9.1 Definitions. | The following term is defined in Chapter 2:
407.4.4.1 Exit access through care suites. | Exit access from all other portions of a building not classified as a care suite shall not pass through a care suite. In a care suite required to have more than one exit, one exit access is permitted to pass through an adjacent care suite provided all of the other requirements of Sections 407.4 and 1016.2 are satisfied. | 407.4.4.1 Exit access through care suites. | Exit access from all other portions of a building not classified as a care suite shall not pass through a care suite.
406.9.2 Permit required. | Any premise intended to be occupied for the storage or sale of motor vehicles on an open parking lot shall require an application to be filed with the department in order to obtain a Certificate of Occupancy. Such Certificate of Occupancy shall indicate the maximum number of vehicles to be accommodated and the type of vehicle, whether private passenger or commercial, to be stored. An application for or including an open parking lot shall be accompanied by a plan exhibiting the following:
407.4.4.2 Separation. | Care suites shall be separated from other portions of the building, including other care suites, by a smoke partition complying with Section 710. | 407.4.4.2 Separation. | Care suites shall be separated from other portions of the building, including other care suites, by a smoke partition complying with Section 710.
4. Structures, retaining walls, and open spaces on adjoining premises;.
407.4.4.3 Access to corridor. | Movement from habitable rooms shall not require passage through more than three doors and 100 feet (30 480 mm) distance of travel within the suite. Exception: The distance of travel shall be permitted to be increased to 125 feet (38 100 mm) where an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72 as modified by Appendix Q of this code‡. | 407.4.4.3 Access to corridor. | Every care suite shall have a door leading directly to an exit access corridor or horizontal exit. Movement from habitable rooms within a care suite shall not require more than 100 feet (30 480 mm) of travel within the care suite to a door leading to the exit access corridor or horizontal exit. Where a care suite is required to have more than one exit access door by Section 407.4.4.5.2 or 407.4.4.6.2, the additional door shall lead directly to an exit access corridor, exit or an adjacent suite.
406.9.3 Locations prohibited. | All vehicular activities associated with the operation of open parking lots shall be entirely within the property lines of the premises. Vehicles shall not be permitted to encroach upon the sidewalks. No motor vehicle may be stored or parked in any location where it would obstruct a required window or required exit of any adjacent building.
407.4.4.4 Doors within care suites. | Doors in care suites serving habitable rooms shall be permitted to comply with one of the following: 1. Manually operated horizontal sliding doors permitted in accordance with Exception 9 to Section 1010.1.2.1. 2. Power-operated doors permitted in accordance with Exception 7 to Section 1010.1.2.1. 3. Means of egress doors complying with Section 1010. | 407.4.4.4 Doors within care suites. | Doors in care suites serving habitable rooms shall be permitted to comply with one of the following:
406.9.4 Surfacing. | All driveways, parking stalls, and open spaces used for the parking or storage of motor vehicles shall be surfaced with concrete asphalt, or equivalent durable, dustless material.
407.4.4.5 Care suites containing sleeping room areas. | Sleeping rooms shall be permitted to be grouped into care suites where one of the following criteria is met: | 407.4.4.5 Care suites containing sleeping room areas. | Sleeping rooms shall be permitted to be grouped into care suites where one of the following criteria is met:
406.9.4.1 Drainage. | Open parking lots shall be graded and maintained such that no drainage will flow onto abutting sidewalks and adjoining properties.
407.4.4.5.1 Area. | Care suites containing sleeping rooms shall be not greater than 7,500 square feet (696 m2) in area. Exception: Care suites containing sleeping rooms shall be permitted to be not greater than 10,000 square feet (929 m2) in area where an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72 as modified by Appendix Q of this code. | 407.4.4.5.1 Area. | Care suites containing sleeping rooms shall be not greater than 7,500 square feet (696 m2) in area. Exception: Care suites containing sleeping rooms shall be permitted to be not greater than 10,000 square feet (929 m2) in area where an automatic smoke detection system is provided throughout the care suite and installed in accordance with NFPA 72.
406.9.4.2 Nonporous surfaces. | Where the surface paving of an open parking lot is nonporous, such lot shall be drained as required by the New York City Plumbing Code.
407.4.4.5.2 Exit access. | Any sleeping room, or any care suite that contains sleeping rooms, of more than 1,000 square feet (93 m2) shall have no fewer than two exit access doors from the care suite located in accordance with Section 1007. | 407.4.4.5.2 Exit access. | Any sleeping room, or any care suite that contains sleeping rooms, of more than 1,000 square feet (93 m2) shall have not fewer than two exit access doors from the care suite located in accordance with Section 1007.
406.9.4.3 Resurfacing. | Resurfacing of existing open parking lots shall comply with this section.
407.4.4.6 Care suites not containing sleeping rooms. | Areas not containing sleeping rooms, but only treatment areas and the associated rooms, spaces or circulation space, shall be permitted to be grouped into care suites and shall conform to the limitations in Sections 407.4.4.6.1 and 407.4.4.6.2. Exception: Care suites not containing sleeping rooms shall be permitted to be not greater than 15,000 square feet (1394 m2) in area where an automatic smoke detection system is provided throughout the care suite in accordance with Section 907. | 407.4.4.6 Care suites not containing sleeping rooms. | Areas not containing sleeping rooms, but only treatment areas and the associated rooms, spaces or circulation space, shall be permitted to be grouped into care suites and shall conform to the limitations in Sections 407.4.4.6.1 and 407.4.4.6.2.
406.9.5 Curbs and bumpers. | Open parking lots shall be completely separated from adjoining premises and public sidewalks by curbs or bumpers of concrete, masonry, steel, heavy timber, or other similar and equally substantial materials, and shall be securely anchored so as to stop motor vehicles. Curbs and bumpers shall be at least 8 inches (203 mm) high and 8 inches (203 mm) wide.
407.4.4.6.1 Area. | Care suites of rooms, other than sleeping rooms, shall have an area not greater than 12,500 square feet (1161 m2). | 407.4.4.6.1 Area. | Care suites of rooms, other than sleeping rooms, shall have an area not greater than 12,500 square feet (1161 m2). Exception: Care suites not containing sleeping rooms shall be permitted to be not greater than 15,000 square feet (1394 m2) in area where an automatic smoke detection system is provided throughout the care suite in accordance with Section 907.
406.9.5.1 Openings. | Openings in required perimeter curbs and bumpers shall be permitted only for drainage, for motor vehicle entrances and exits, and for pedestrian entrances and exits. The width of an opening for motor vehicle access shall not exceed the length of the curb cut, not including the lengths of the splays. When an opening for pedestrian access is adjacent to a motor vehicle access opening, the two openings shall be separated by a permanent and substantial post. In no case shall any pedestrian entrance or exit exceed 5 feet (1524 mm) in width.
407.4.4.6.2 Exit access. | Care suites, other than sleeping rooms, with an area of more than 2,500 square feet (232 m2) shall have no fewer than two exit access doors from the care suite located in accordance with Section 1007.1. | 407.4.4.6.2 Exit access. | Care suites, other than sleeping rooms, with an area of more than 2,500 square feet (232 m2) shall have not fewer than two exit access doors from the care suite located in accordance with Section 1007.
406.9.6 Accessory uses and occupancies. | Parking lot offices, attendant shelters, storage facilities, and similar structures used in conjunction with open parking lots may be provided as an accessory use and shall comply with the applicable code provisions. Such accessory structures may be constructed of combustible materials subject to the limitations of Section D105.1 of Appendix D.
407.5 Smoke barriers. | Smoke barriers shall be provided to subdivide every story used by persons receiving care, treatment or sleeping and to divide other stories with an occupant load of 50 or more persons, into no fewer than two smoke compartments. Such stories shall be divided into smoke compartments with an area of not more than 22,500 square feet (2090 m2) in nursing homes in Group I-2, and not more than 40,000 square feet (3716 m2) in detoxification facilities, hospitals and psychiatric centers in Group I-2, and the distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm). The smoke barrier shall be in accordance with Section 709. | 407.5 Smoke barriers. | Smoke barriers shall be provided to subdivide every story used by persons receiving care, treatment or sleeping into not fewer than two smoke compartments. Smoke barriers shall be provided to subdivide other stories with an occupant load of 50 or more persons, into not fewer than two smoke compartments. The smoke barrier shall be in accordance with Section 709.
406.9.6.1 Motor fuel-dispensing facilities. | Motor fuel-dispensing facilities, accessory to open parking lots, shall comply with the requirements of the New York City Fire Code and Section 406.8 of this code. Motor fuel pumps shall be located at least 30 feet (9144 mm) from any parking space or interior lot line.
406.9.7 Special provisions applicable to large open parking lots. | Open parking lots storing 10 or more motor vehicles shall also be subject to the special provisions of this section.
406.9.7.1 Curbs and bumpers. | Bumpers shall be situated not less than 1 foot (305 mm) from the perimeter edge of the open parking lot where vehicles are parked parallel to such perimeter edge, and not less than 4 feet (1219 mm) from the perimeter edge where vehicles are parked perpendicular to such perimeter edge. Openings shall be limited as provided for in Section 406.9.5.1. Exception: A steel guardrail or other substantial barrier designed in accordance with the provisions of Section 1607.9, that will prevent any part of a vehicle from extending across a property line, may be accepted in lieu of bumpers.
406.9.7.2 Screen enclosures. | Open parking lots shall provide a perimeter screen enclosure as per this section unless otherwise required by the New York City Zoning Resolution. Such screen enclosure may be constructed as a masonry wall, woven wire fence, iron picket fence, or uniformly painted fence of fire-resistant material at least 4 feet (1219 mm) high, but not more than 8 feet (2438 mm) above finished grade, subject to the limitations of Section 3111. Such enclosures shall completely separate the lot from adjoining premises and public sidewalks. Openings shall be limited as provided for in Section 406.9.5.1. Exception: Screening shall not be required for any portion of the lot adjacent to an existing wall located at the lot line.
406.9.7.3 Illumination. | Open parking lots operating between 6 p.m. and 6 a.m. shall be adequately illuminated to a minimum of 1 footcandle (10.8 lux) measured at grade level, distributed over the entire area. Illumination provided with reflectors or floodlights shall be arranged such that the illumination is directed downward and away from adjacent premises.
406.9.7.4 Fire-fighter aisles. | In any open parking lot, one or more aisles, at least 24 inches (610 mm) in width, shall be provided to permit access by fire-fighting personnel to all parts of the garage or lot. There shall not be more than three rows of parked motor vehicles between aisles.
406.9.8 Electric vehicle charging stations. | Open parking lots shall be capable of supporting electric vehicle charging stations in accordance with this section. A minimum of 20 percent of the parking spaces in an open parking lot shall be equipped with electrical raceway capable of providing a minimum supply of 11.5 kVA to an electrical vehicle supply equipment (EVSE) from an electrical supply panel. The raceway shall be no smaller than 1 inch (25 mm). The electrical supply panel serving such parking spaces must have at least 3.1 kW of available capacity for each stall connected to it with raceway. Such raceway and all components and work appurtenant thereto shall be in accordance with the New York City Electrical Code. Exceptions: 1. The provisions of this section shall not apply to open parking lots for buildings of Occupancy Group M (Mercantile). 2. The commissioner may waive compliance with this section if the commissioner determines that the open parking lot is a temporary facility that will be in service no longer than 3 years. 3. The provisions of this section shall not apply to open parking lots for buildings in which not less than fifty percent of the residential units are for households earning up to sixty percent of the area median income as determined by the United States Department of Housing and Urban Development.
406.10 Curb cuts and driveways. | Except where specifically provided for in the New York City Zoning Resolution, all curb cuts and driveways shall be constructed in accordance with Sections 406.10.1 and 406.10.2. All sidewalks and driveways or portions thereof that are structurally supported shall be designed for loads prescribed in Chapter 16.
406.10.1 Curb cuts. | For the purpose of this section, a curb cut shall include all splays when determining the total length of cut curb. All curb cuts shall comply with the following requirements: 1. The aggregate length of curb cuts shall not exceed 60 percent of any street frontage 100 feet (30 480 mm) or less in length. No single curb cut shall exceed 30 feet (9144 mm) in length, and there shall not be more than two curb cuts on any street frontage 100 feet (30 480 mm) or less in length. The minimum distance between two curb cuts shall be 5 feet (1524 mm). 2. For each 50 feet (15 240 mm) of street frontage length over 100 feet (30 480 mm), an additional curb cut no greater than 30 feet (9144 mm) in length may be permitted. 3. No curb cut shall commence within 8 feet (2438 mm) of a side lot line. Exceptions: 1. For open parking lots on corner lots and on lots with street frontage length of 50 feet (15 240 mm) or less, the curb cut may commence no less than 30 inches (762 mm) from the side lot line. 2. In open or enclosed parking garages where a level landing having a minimum dimension of 20 feet (6096 mm) is provided at the discharge point of all ramps at the street level within the property line, the curb cut may commence no less than 30 inches (762 mm) from a side lot line. 4. No curb cut, including splays, shall be less than 10 feet (3048 mm) in length.
406.10.2 Driveways. | Driveways serving passenger vehicles shall be a minimum of 8 feet (2438 mm) in width and shall not exceed the length of the curb cut, not including the lengths of the splays. For all other motor vehicles, the minimum width of driveways shall be 10 feet (3048 mm). Portions of the driveway located between the curb line and the lot line shall be paved in accordance with the requirements of the Department of Transportation for the construction of sidewalks.
406.11 Battery-powered industrial trucks, equipment and mobility devices. | Buildings or portions thereof that contain or store battery-powered industrial trucks, equipment and mobility devices shall be designed and constructed in accordance with Section 309.3 of the New York City Fire Code.
408.1 General. | Occupancies in Group I-3 shall comply with the provisions of Sections 408.1 through 408.11 and other applicable provisions of this code (see Section 308.5). | 408.1 General. | Occupancies in Group I-3 shall comply with the provisions of Sections 408.1 through 408.11 and other applicable provisions of this code (see Section 308.5).
408.2 Other occupancies. | Buildings or portions of buildings in Group I-3 occupancies where security operations necessitate the locking of required means of egress shall be permitted to be classified as a different occupancy. Occupancies classified as other than Group I-3 shall meet the applicable requirements of this code for that occupancy where provisions are made for the release of occupants at all times. Means of egress from detention and correctional occupancies that traverse other use areas shall, as a minimum, conform to requirements for detention and correctional occupancies. Exception: It is permissible to exit through a horizontal exit into other contiguous occupancies that do not conform to detention and correctional occupancy egress provisions but that do comply with requirements set forth in the appropriate occupancy, as long as the occupancy is not a Group H use. | 408.2 Other occupancies. | Buildings or portions of buildings in Group I-3 occupancies where security operations necessitate the locking of required means of egress shall be permitted to be classified as a different occupancy. Occupancies classified as other than Group I-3 shall meet the applicable requirements of this code for that occupancy where provisions are made for the release of occupants at all times. Means of egress from detention and correctional occupancies that traverse other use areas shall, as a minimum, con-form to requirements for detention and correctional occupancies. Exception: It is permissible to exit through a horizontal exit into other contiguous occupancies that do not conform to detention and correctional occupancy egress provisions but that do comply with requirements set forth in the appro-priate occupancy, as long as the occupancy is not a Group H use.
408.3 Means of egress. | Except as modified or as provided for in this section, the means of egress provisions of Chapter 10 shall apply. | 408.3 Means of egress. | Except as modified or as provided for in this section, the means of egress provisions of Chapter 10 shall apply.
408.3.1 Door width. | Doors to resident sleeping units shall have a clear width of not less than 28 inches (711 mm). | 408.3.1 Door width. | Doors to resident sleeping units shall have a clear width of not less than 28 inches (711 mm).
408.3.2 Sliding doors. | Where doors in a means of egress are of the horizontal-sliding type, the force to slide the door to its fully open position shall be not greater than 50 pounds (220 N) with a perpendicular force against the door of 50 pounds (220 N). | 408.3.2 Sliding doors. | Where doors in a means of egress are of the horizontal-sliding type, the force to slide the door to its fully open position shall be not greater than 50 pounds (220 N) with a perpendicular force against the door of 50 pounds (220 N).
408.3.3 Guard tower doors. | A hatch or trap door not less than 16 square feet (1.49 m2) in area through the floor and having dimensions of not less than 2 feet (610 mm) in any direction shall be permitted to be used as a portion of the means of egress from guard towers. | 408.3.3 Guard tower doors. | A hatch or trap door not less than 16 square feet (610 m2) in area through the floor and having dimensions of not less than 2 feet (610 mm) in any direction shall be permitted to be used as a portion of the means of egress from guard towers.
408.3.4 Spiral stairways. | Spiral stairways that conform to the requirements of Section 1011.10 are permitted for access to and between staff locations. | 408.3.4 Spiral stairways. | Spiral stairways that conform to the requirements of Section 1011.10 are permitted for access to and between staff locations.
408.3.6 Exit discharge. | Exits are permitted to discharge into a fenced or walled courtyard. Enclosed yards or courts shall be of a size to accommodate all occupants, be located not less than 50 feet (15 240 mm) from the building and have an area of not less than 15 square feet (1.4 m2) per person. | 408.3.6 Exit discharge. | Exits are permitted to discharge into a fenced or walled courtyard. Enclosed yards or courts shall be of a size to accommodate all occupants, be located not less than 50 feet (15 240 mm) from the building and have an area of not less than 15 square feet (1.4 m2) per person.
408.3.7 Sallyports. | A sallyport shall be permitted in a means of egress where there are provisions for continuous and unobstructed passage through the sallyport during an emergency egress condition. | 408.3.7 Sallyports. | A sallyport shall be permitted in a means of egress where there are provisions for continuous and unobstructed passage through the sallyport during an emergency egress condition.
408.3.8 Interior exit stairway and ramp construction. | One interior exit stairway or ramp in each building shall be permitted to have glazing installed in doors and interior walls at each landing level providing access to the interior exit stairway or ramp, provided that the following conditions are met: | 408.3.8 Interior exit stairway and ramp construction. | One interior exit stairway or ramp in each building shall be permitted to have glazing installed in doors and interior walls at each landing level providing access to the interior exit stairway or ramp, provided that the following conditions are met:
408.4 Locks. | Egress doors are permitted to be locked in accordance with the applicable use condition. Doors from a refuge area to the outside are permitted to be locked with a key in lieu of locking methods described in Section 408.4.1. The keys to unlock the exterior doors shall be available at all times and the locks shall be operable from both sides of the door. | 408.4 Locks. | Egress doors are permitted to be locked in accordance with the applicable use condition. Doors from a refuge area to the outside are permitted to be locked with a key in lieu of locking methods described in Section 408.4.1. The keys to unlock the exterior doors shall be available at all times and the locks shall be operable from both sides of the door.
408.4.1 Remote release. | Remote release of locks on doors in a means of egress shall be provided with reliable means of operation, remote from the resident living areas, to release locks on all required doors. In Occupancy Condition 3 or 4, the arrangement, accessibility and security of the release mechanisms required for egress shall be such that with the minimum available staff at any time, the lock mechanisms are capable of being released within 2 minutes. Exception: Provisions for remote locking and unlocking of occupied rooms in Occupancy Condition 4 are not required provided that not more than 10 locks are necessary to be unlocked in order to move occupants from one smoke compartment to a refuge area within 3 minutes. The opening of necessary locks shall be accomplished with not more than two separate keys. | 408.4.1 Remote release. | Remote release of locks on doors in a means of egress shall be provided with reliable means of operation, remote from the resident living areas, to release locks on all required doors. In Occupancy Condition 3 or 4, the arrangement, accessibility and security of the release mechanisms required for egress shall be such that with the minimum available staff at any time, the lock mechanisms are capable of being released within 2 minutes. Exception: Provisions for remote locking and unlocking of occupied rooms in Occupancy Condition 4 are not re-quired provided that not more than 10 locks are necessary to be unlocked in order to move occupants from one smoke compartment to a refuge area within 3 minutes. The opening of necessary locks shall be accomplished with not more than two separate keys.
408.4.2 Power-operated doors and locks. | Power-operated sliding doors or power-operated locks for swinging doors shall be operable by a manual release mechanism at the door. Emergency power shall be provided for the doors and locks in accordance with Section 2702. Exceptions: 1. Emergency power is not required in facilities with 10 or fewer locks complying with the exception to Section 408.4.1. 2. Emergency power is not required where remote mechanical operating releases are provided. | 408.4.2 Power-operated doors and locks. | Power-operated sliding doors or power-operated locks for swinging doors shall be operable by a manual release mechanism at the door. Emergency power shall be provided for the doors and locks in accordance with Section 2702. Exceptions: 1. Emergency power is not required in facilities with 10 or fewer locks complying with the exception to Sec-tion 408.4.1. 2. Emergency power is not required where remote mechanical operating releases are provided.
408.4.3 Redundant operation. | Remote release, mechanically operated sliding doors or remote release, mechanically operated locks shall be provided with a mechanically operated release mechanism at each door, or shall be provided with a redundant remote release control. | 408.4.3 Redundant operation. | Remote release, mechanically operated sliding doors or remote release, mechanically operated locks shall be provided with a mechanically operated release mechanism at each door, or shall be provided with a redundant remote release control.
408.4.4 Relock capability. | Doors remotely unlocked under emergency conditions shall not automatically relock when closed unless specific action is taken at the remote location to enable doors to relock. | 408.4.4 Relock capability. | Doors remotely unlocked under emergency conditions shall not automatically relock when closed unless specific action is taken at the remote location to enable doors to relock.
408.5 Protection of vertical openings. | Any vertical opening shall be protected by a shaft enclosure in accordance with Section 713, or shall be in accordance with Sections 408.5.1 and 408.5.2. | 408.5 Protection of vertical openings. | Any vertical opening shall be protected by a shaft enclosure in accordance with Section 713, or shall be in accordance with Section 408.5.1.
408.5.1 Floor openings. | Openings in floors within a housing unit are permitted without a shaft enclosure, provided all of the following conditions are met: | 408.5.1 Floor openings. | Openings in floors within a housing unit are permitted without a shaft enclosure, provided that all of the following conditions are met:
408.5.2 Shaft openings in communicating floor levels. | Where a floor opening is permitted between communicating floor levels of a housing unit in accordance with Section 408.5.1, plumbing chases serving vertically stacked individual cells contained within the housing unit shall be permitted without a shaft enclosure. | 408.5.2 Shaft openings in communicating floor levels. | Where a floor opening is permitted between communicating floor levels of a housing unit in accordance with Section 408.5.1, plumbing chases serving vertically staked individual cells contained with the housing unit shall be permitted without a shaft enclosure.
408.6 Smoke barrier. | Occupancies in Group I-3 shall have smoke barriers complying with Sections 408.8 and 709 to divide every story occupied by residents for sleeping, or any other story having an occupant load of 50 or more persons, into no fewer than two smoke compartments. Exception: Spaces having a direct exit to one of the following, provided that the locking arrangement of the doors involved complies with the requirements for doors at the smoke barrier for the use condition involved: 1. A public way. 2. A building separated from the resident housing area by a 2-hour fire-resistance-rated assembly or 50 feet (15 240 mm) of open space. 3. A secured yard or court having a holding space 50 feet (15 240 mm) from the housing area that provides 6 square feet (0.56 m2) or more of refuge area per occupant, including residents, staff and visitors. | 408.6 Smoke barrier. | Occupancies in Group I-3 shall have smoke barriers complying with Sections 408.6 and 709 to divide every story occupied by residents for sleeping, or any other story having an occupant load of 50 or more persons, into not fewer than two smoke compartments. Exception: Spaces having a direct exit to one of the following, provided that the locking arrangement of the doors in-volved complies with the requirements for doors at the smoke barrier for the use condition involved: 1. A public way. 2. A building separated from the resident housing area by a 2-hour fire-resistance-rated assembly or 50 feet (15 240 mm) of open space. 3. A secured yard or court having a holding space 50 feet (15 240 mm) from the housing area that provides 6 square feet (0.56 m2) or more of refuge area per occupant, including residents, staff and visitors.
408.6.1 Smoke compartments. | The number of residents in any smoke compartment shall be not more than 200. The distance of travel to a door in a smoke barrier from any room door required as exit access shall be not greater than 150 feet (45 720 mm). The distance of travel to a door in a smoke barrier from any point in a room shall be not greater than 200 feet (60 960 mm). | 408.6.1 Smoke compartments. | The number of residents in any smoke compartment shall be not more than 200. The distance of travel to a door in a smoke barrier from any room door required as exit access shall be not greater than 150 feet (45 720 mm). The distance of travel to a door in a smoke barrier from any point in a room shall be not greater than 200 feet (60 960 mm).
408.6.2 Refuge area. | Not less than 6 net square feet (0.56 m2) per occupant shall be provided on each side of each smoke barrier for the total number of occupants in adjoining smoke compartments. This space shall be readily available wherever the occupants are moved across the smoke barrier in a fire emergency. | 408.6.2 Refuge area. | Not less than 6 net square feet (0.56 m2) per occupant shall be provided on each side of each smoke barrier for the total number of occupants in adjoining smoke compartments. This space shall be readily available wherever the occupants are moved across the smoke barrier in a fire emergency.
408.6.3 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originates. | 408.6.3 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originates.
408.7 Security glazing. | In occupancies in Group I-3, windows and doors in 1-hour fire barriers constructed in accordance with Section 707, fire partitions constructed in accordance with Section 708 and smoke barriers constructed in accordance with Section 709 shall be permitted to have security glazing installed provided that the following conditions are met. Such glazing shall be subject to the requirements in Chapter 24. | 408.7 Security glazing. | In occupancies in Group I-3, windows and doors in 1-hour fire barriers constructed in accordance with Section 707, fire partitions constructed in accordance with Section 708 and smoke barriers constructed in accordance with Section 709 shall be permitted to have security glazing installed provided that the following conditions are met.
408.8 Subdivision of resident housing areas. | Sleeping areas and any contiguous day room, group activity space or other common spaces where residents are housed shall be separated from other spaces in accordance with Sections 408.8.1 through 408.8.4. | 408.8 Subdivision of resident housing areas. | Sleeping areas and any contiguous day room, group activity space or other common spaces where residents are housed shall be separated from other spaces in accordance with Sections 408.8.1 through 408.8.4.
408.8.1 Occupancy Conditions 3 and 4. | Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the distance of travel from the sleeping area through the common space to the corridor exceeds 50 feet (15 240 mm). | 408.8.1 Occupancy Conditions 3 and 4. | Each sleeping area in Occupancy Conditions 3 and 4 shall be separated from the adjacent common spaces by a smoke-tight partition where the distance of travel from the sleeping area through the common space to the corridor exceeds 50 feet (15 240 mm).
407.5.1 Refuge area. | Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:
408.8.2 Occupancy Condition 5. | Each sleeping area in Occupancy Condition 5 shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the corridor by a smoke-tight partition. | 408.8.2 Occupancy Condition 5. | Each sleeping area in Occupancy Condition 5 shall be separated from adjacent sleeping areas, corridors and common spaces by a smoke-tight partition. Additionally, common spaces shall be separated from the corridor by a smoke-tight partition.
407.5.2 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated.
408.8.3 Openings in room face. | The aggregate area of openings in a solid sleeping room face in Occupancy Conditions 2, 3, 4 and 5 shall not exceed 120 square inches (0.077 m2). The aggregate area shall include all openings including door undercuts, food passes and grilles. Openings shall be not more than 36 inches (914 mm) above the floor. In Occupancy Condition 5, the openings shall be closeable from the room side. | 408.8.3 Openings in room face. | The aggregate area of openings in a solid sleeping room face in Occupancy Conditions 2, 3, 4 and 5 shall not exceed 120 square inches (0.77 m2). The aggregate area shall include all openings including door undercuts, food passes and grilles. Openings shall be not more than 36 inches (914 mm) above the floor. In Occupancy Condition 5, the openings shall be closeable from the room side.
407.5.3 Horizontal assemblies. | Horizontal assemblies supporting smoke barriers required by this section shall be designed to resist the movement of smoke. Elevator lobbies shall be in accordance with Section 3006.1.
408.8.4 Smoke-tight doors. | Doors in openings in partitions required to be smoke tight by Section 408.8 shall be substantial doors, of construction that will resist the passage of smoke. Latches and door closures are not required on cell doors. | 408.8.4 Smoke-tight doors. | Doors in openings in partitions required to be smoke tight by Section 408.8 shall be substantial doors, of construction that will resist the passage of smoke. Latches and door closures are not required on cell doors.
407.6 Automatic sprinkler system. | Smoke compartments containing sleeping rooms shall be equipped throughout with an automatic fire sprinkler system in accordance with Sections 903.3.1.1 and 903.3.2.
408.9 Windowless buildings. | For the purposes of this section, a windowless building or portion of a building is one with nonopenable windows, windows not readily breakable or without windows. Windowless buildings shall be provided with an engineered smoke control system to provide a tenable environment for exiting from the smoke compartment in the area of fire origin in accordance with Section 909 for each windowless smoke compartment. | 408.9 Windowless buildings. | For the purposes of this section, a windowless building or portion of a building is one with nonopenable windows, windows not readily breakable or without windows. Windowless buildings shall be provided with an engineered smoke control system to provide a tenable environment for exiting from the smoke compartment in the area of fire origin in accordance with Section 909 for each windowless smoke compartment.
407.7 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.6. | 407.7 Automatic sprinkler system. | Smoke compartments containing sleeping rooms shall be equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 and 903.3.2.
408.10 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.6.3. | 408.10 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.6.3.
407.8 Automatic fire detection. | Corridors in nursing homes (both intermediate-care and skilled nursing facilities) and spaces permitted to be open to the corridors by Section 407.2 shall be equipped with an automatic fire detection system installed in accordance with Section 907. Detoxification facilities, hospitals and psychiatric centers shall be equipped with smoke detection as required in Section 407.2. Exceptions: 1. Corridor smoke detection is not required where sleeping rooms are provided with smoke detectors that comply with UL 268. Such detectors shall provide a visual display on the corridor side of each sleeping room and an audible and visual alarm at the care provider’s station attending each unit. 2. Corridor smoke detection is not required where sleeping room doors are equipped with automatic door-closing devices with integral smoke detectors on the unit sides installed in accordance with their listing, provided that the integral detectors perform the required alerting function. | 407.8 Fire alarm system. | A fire alarm system shall be provided in accordance with Section 907.2.6.
408.11 Automatic sprinkler system. | Group I-3 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6. | 408.11 Automatic sprinkler system. | Group I-3 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6.
407.9 Secured yards. | Grounds are permitted to be fenced and gates therein are permitted to be equipped with locks, provided that safe dispersal areas having 30 net square feet (2.8 m2) for bed and stretcher care recipients and 6 net square feet (0.56 m2) for ambulatory care recipients and other occupants are located between the building and the fence. Such provided safe dispersal areas shall be located not less than 50 feet (15 240 mm) from the building they serve. | 407.9 Automatic fire detection. | Corridors in Group I-2, Condition 1 occupancies and spaces permitted to be open to the corridors by Section 407.2 shall be equipped with an automatic fire detection system. Group I-2, Condition 2 occupancies shall be equipped with smoke detection as required in Section 407.2. Exceptions: 1. Corridor smoke detection is not required where sleeping rooms are provided with smoke detectors that comply with UL 268. Such detectors shall provide a visual display on the corridor side of each sleeping room and an audible and visual alarm at the care provider’s station attending each unit. 2. Corridor smoke detection is not required where sleeping room doors are equipped with automatic door-closing devices with integral smoke detectors on the unit sides installed in accordance with their listing, provided that the integral detectors perform the required alerting function.
409.1 General. | The provisions of Sections 409.1 through 409.5 of this code shall apply to rooms in which ribbon-type cellulose acetate or other safety film is utilized in conjunction with electric arc, xenon or other light-source projection equipment that develops hazardous gases, dust or radiation. The projection, use or storage of film having a nitrocellulose base (commonly known as nitrate film) shall not be permitted except under conditions specified in special permits when issued by the Fire Department. Safety film meeting the specification and test standards of NFPA 40 may be projected, used or stored. | 409.1 General. | The provisions of Sections 409.1 through 409.5 shall apply to rooms in which ribbon-type cellulose acetate or other safety film is utilized in conjunction with electric arc, xenon or other light-source projection equipment that develops hazardous gases, dust or radiation. Where cellulose nitrate film is utilized or stored, such rooms shall comply with NFPA 40.
407.10 Electrical systems. | In Group I-2 occupancies, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of NFPA 99 and Chapter 27 of this code. | 407.10 Secured yards. | Grounds are permitted to be fenced and gates therein are permitted to be equipped with locks, provided that safe dispersal areas having 30 net square feet (2.8 m2) for bed and stretcher care recipients and 6 net square feet (0.56 m2) for ambulatory care recipients and other occupants are located between the building and the fence. Such provided safe dispersal areas shall be located not less than 50 feet (15 240 mm) from the building they serve.
409.1.1 Projection room required. | Every motion picture machine projecting film as mentioned within the scope of this section shall be enclosed in a projection room. Appurtenant electrical equipment, such as rheostats, transformers and generators, shall be within the projection room or in an adjacent room of equivalent construction. | 409.1.1 Projection room required. | Every motion picture machine projecting film as mentioned within the scope of this section shall be enclosed in a projection room. Appurtenant electrical equipment, such as rheostats, transformers and generators, shall be within the projection room or in an adjacent room of equivalent construction.
409.2 Construction of projection rooms. | Every projection room shall be of permanent construction consistent with the construction requirements for the type of building in which the projection room is located. Openings are not required to be protected. | 409.2 Construction of projection rooms. | Every projection room shall be of permanent construction consistent with the construction requirements for the type of building in which the projection room is located. Openings are not required to be protected.
408.1.1 Definitions specific to this section. | The following terms shall, for the purposes of this section, have the meanings shown herein:
409.3 Projection room and equipment ventilation. | Ventilation shall be provided in accordance with the New York City Mechanical Code. | 409.3 Projection room and equipment ventilation. | Ventilation shall be provided in accordance with the International Mechanical Code.
409.3.1 Supply air. | Each projection room shall be provided with adequate air supply inlets so arranged as to provide well-distributed air throughout the room. Air inlet ducts shall provide an amount of air equivalent to the amount of air being exhausted by projection equipment. Air is permitted to be taken from the outside; from adjacent spaces within the building, provided the volume and infiltration rate is sufficient; or from the building air-conditioning system, provided it is so arranged as to provide sufficient air when other systems are not in operation. | 409.3.1 Supply air. | Each projection room shall be provided with adequate air supply inlets so arranged as to provide well-distributed air throughout the room. Air inlet ducts shall provide an amount of air equivalent to the amount of air being exhausted by projection equipment. Air is permitted to be taken from the outside; from adjacent spaces within the building, provided that the volume and infiltration rate are sufficient; or from the building air-conditioning system, provided that it is so arranged as to provide sufficient air when other systems are not in operation.
409.3.2 Exhaust air. | Projection rooms are permitted to be exhausted through the lamp exhaust system. The lamp exhaust system shall be positively interconnected with the lamp so that the lamp will not operate unless there is the required airflow. Exhaust air ducts shall terminate at the exterior of the building in such a location that the exhaust air cannot be readily recirculated into any air supply system. The projection room ventilation system is permitted to also serve appurtenant rooms, such as the generator and rewind rooms. | 409.3.2 Exhaust air. | Projection rooms are permitted to be exhausted through the lamp exhaust system. The lamp exhaust system shall be positively interconnected with the lamp so that the lamp will not operate unless there is the required airflow. Exhaust air ducts shall terminate at the exterior of the building in such a location that the exhaust air cannot be readily recirculated into any air supply system. The projection room ventilation system is permitted to also serve appurtenant rooms, such as the generator and rewind rooms.
409.3.3 Projection machines. | Each projection machine shall be provided with an exhaust duct that will draw air from each lamp and exhaust it directly to the outside of the building. The lamp exhaust is permitted to serve to exhaust air from the projection room to provide room air circulation. Such ducts shall be of rigid materials, except for a flexible connector approved for the purpose. The projection lamp or projection room exhaust system, or both, is permitted to be combined but shall not be interconnected with any other exhaust or return system, or both, within the building. | 409.3.3 Projection machines. | Each projection machine shall be provided with an exhaust duct that will draw air from each lamp and exhaust it directly to the outside of the building. The lamp exhaust is permitted to serve to exhaust air from the projection room to provide room air circulation. Such ducts shall be of rigid materials, except for a flexible connector approved for the purpose. The projection lamp or projection room exhaust system, or both, is permitted to be combined but shall not be interconnected with any other exhaust or return system, or both, within the building.
409.4 Lighting control. | Provisions shall be made for control of the auditorium lighting and the means of egress lighting systems of theaters from inside the projection room and from not less than one other convenient point in the building. | 409.4 Lighting control. | Provisions shall be made for control of the auditorium lighting and the means of egress lighting systems of theaters from inside the projection room and from not less than one other convenient point in the building.
409.5 Miscellaneous equipment. | Each projection room shall be provided with rewind and film storage facilities. | 409.5 Miscellaneous equipment. | Each projection room shall be provided with rewind and film storage facilities.
410.1 Applicability. | The provisions of Sections 410.1 through 410.11 shall apply to all parts of buildings and structures that contain stages or platforms and similar appurtenances as herein defined. | 410.1 Applicability. | The provisions of Sections 410.1 through 410.7 shall apply to all parts of buildings and structures that contain stages or platforms and similar appurtenances as herein defined.
408.3.5 Ship ladders. | Ship ladders shall be permitted for egress from control rooms or elevated facility observation rooms in accordance with Section 1011.15. | 408.3.5 Ship’s ladders. | Ship’s ladders shall be permitted for egress from control rooms or elevated facility observation rooms in accordance with Section 1011.15.
411.1 General. | Special amusement buildings having an occupant load of 75 or more shall comply with the requirements for the appropriate Group A occupancy and Sections 411.1 through 411.8. Special amusement buildings having an occupant load of less than 75 shall comply with the requirements for a Group B occupancy and Sections 411.1 through 411.8. Exception: Special amusement buildings or portions thereof that are without walls or a roof and constructed to prevent the accumulation of smoke. All decorative material shall be noncombustible or composed of flame-retardant fabric. | 411.1 General. | Special amusement areas having an occupant load of 50 or more shall comply with the requirements for the appropriate Group A occupancy and Sections 411.1 through 411.7. Special amusement areas having an occupant load of less than 50 shall comply with the requirements for a Group B occupancy and Sections 411.1 through 411.7. Exception: Special amusement areas that are without walls or a roof and constructed to prevent the accumulation of smoke need not comply with this section.
410.2 Definitions. | This section contains terms defined elsewhere in the code, and terms with definitions that are specific to this section.
412.1 General. | Aircraft-related occupancies shall comply with the New York City Fire Code and Sections 412.1 through 412.8 of this code. | 412.1 General. | Aircraft-related occupancies shall comply with Sections 412.1 through 412.7 and the International Fire Code.
410.2.1 Terms defined elsewhere in the code. | The following terms are defined in Chapter 2:
410.2.2 Definitions specific to this section. | The following term shall, for the purposes of this section, have the meaning shown herein:
410.3 Stages. | Stage construction shall comply with Sections 410.3.1 through 410.3.7.
410.3.1 Stage construction. | Stage floors shall be constructed of materials as required for floors for the type of construction of the building in which such stages are located. Where areas below the stage are used for other occupancies, such stage floor shall be constructed in accordance with the requirements for separated occupancies as per Chapter 5. Exceptions: 1. Stages of Type IIB or IV construction with a nominal 2-inch (51 mm) wood deck, provided that the stage is separated from other areas in accordance with Section 410.3.4. 2. In all types of construction, the finished floor shall be constructed of wood or approved noncombustible materials. Openings through stage floors shall be equipped with tight-fitting, solid wood trap doors with approved safety locks. The room or space below the stage into which the traps or lifts open shall be completely enclosed by construction having at least the fire-resistance rating required for the stage floor, and such room or space shall not be used as a workshop or storage area. Storage shall not be deemed to include the location in this area of scenery or scenic elements used during a performance. However, no combustible material that has a flame spread rating greater than 25 or that has not been rendered flameproof in accordance with the rules of the Fire Commissioner may be stored in this location at any time.
410.3.1.1 Stage height and area. | Stage areas shall be measured to include the entire performance area and adjacent backstage and support areas not separated from the performance area by fire-resistance-rated construction. Stage height shall be measured from the lowest point on the stage floor to the highest point of the roof or floor deck above the stage.
410.3.2 Technical production areas: galleries, gridirons, catwalks and pinrails. | Beams designed only for the attachment of portable or fixed theater equipment, gridirons, galleries and catwalks shall be constructed of noncombustible materials. Floors of fly galleries and catwalks shall be constructed of noncombustible material. These areas shall not be considered to be floors, stories, mezzanines or levels in applying this code.
410.3.3 Exterior stage doors. | Where protection of openings is required, exterior exit doors shall be protected with fire door assemblies that comply with Section 716. Exterior openings that are located on the stage for means of egress or loading and unloading purposes, and that are likely to be open during occupancy of the theater, shall be constructed with vestibules to prevent air drafts into the auditorium.
410.3.4 Proscenium wall. | Where the stage height is greater than 40 feet (12 192 mm), all portions of the stage shall be completely separated from the seating area by a proscenium wall with not less than a 2-hour fire-resistance rating extending continuously from the foundation to the roof.
410.3.5 Proscenium curtain. | Where a proscenium wall is required to have a fire-resistance rating, the stage opening shall be provided with one of the following:
410.3.6 Scenery. | All scenery or scenic elements shall be of noncombustible materials, or of materials having a flame-spread rating not exceeding 25, or of materials that have been rendered flameproof in compliance with the rules of the Fire Commissioner. Scenery and scenic elements not complying with the above requirements may be used only when expressly permitted by the Fire Department.
410.3.7 Stage ventilation. | Emergency ventilation shall be provided for stages larger than 1,000 square feet (93 m2) in floor area, or with a stage height greater than 40 feet (12 192 mm). Such ventilation shall comply with Section 410.3.7.1 or 410.3.7.2.
410.3.7.1 Roof vents. | Two or more vents constructed to open automatically by approved heat-activated devices and with an aggregate clear opening area of not less than 5 percent of the area of the stage shall be located near the center and above the highest part of the stage area. Supplemental means shall be provided for manual operation of the ventilator. Curbs shall be provided as required for skylights in Section 2610.2. Vents shall be labeled.
410.3.7.2 Smoke control. | Smoke control in accordance with Section 909 shall be provided to maintain the smoke layer interface not less than 6 feet (1829 mm) above the highest level of the assembly seating or above the top of the proscenium opening where a proscenium wall is provided in compliance with Section 410.3.4.
410.4 Platform construction. | Permanent platforms shall be constructed of materials as required for the type of construction of the building in which the permanent platform is located. Permanent platforms are permitted to be constructed in accordance with the following:
410.4.1 Temporary platforms. | Platforms installed for a period of not more than 30 days are permitted to be constructed of any materials permitted by this code. The space between the floor and the platform above shall only be used for plumbing and electrical wiring to platform equipment.
410.5 Dressing and appurtenant rooms. | Dressing and appurtenant rooms shall comply with Sections 410.5.1 and 410.5.2.
410.5.1 Separation from stage. | The stage shall be separated from dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage and other parts of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours for stage heights greater than 50 feet (15 240 mm) and not less than 1 hour for stage heights of 50 feet (15 240 mm) or less.
410.5.2 Separation from each other. | Dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage shall be separated from each other by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
410.6 Means of egress. | Except as modified or as provided for in this section, the provisions of Chapter 10 shall apply.
410.6.1 Stage exits. | No fewer than one exit or exit access doorway shall be provided from each side of the stage and from each side of the space under the stage. Technical production areas shall comply with Section 410.6.3.
410.6.2 Stairway and ramp enclosure. | Exit access stairways and ramps serving a stage or platform are not required to be enclosed. Exit access stairways and ramps serving technical production areas are not required to be enclosed.
410.6.3 Technical production areas. | Technical production areas shall be provided with means of egress and means of escape in accordance with Sections 410.6.3.1 through 410.6.3.5.
410.6.3.1 Number of means of egress. | No fewer than one means of egress shall be provided from technical production areas.
410.6.3.2 Exit access travel distance. | The exit access travel distance shall be not greater than 300 feet (91 440 mm) for buildings without a sprinkler system and 400 feet (121 900 mm) for buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
410.6.3.3 Two means of egress. | Where two means of egress are required, the common path of travel shall be not greater than 100 feet (30 480 mm). Exception: A means of escape to a roof in place of a second means of egress is permitted.
410.6.3.4 Path of egress travel. | The following exit access components are permitted where serving technical production areas:
410.6.3.5 Width. | The path of egress travel within and from technical support areas shall be not less than 22 inches (559 mm) in width.
410.7 Automatic sprinkler system. | An automatic sprinkler system in accordance with Section 903.3.1.1 shall be provided in the following areas when located within a place of assembly: 1. Stages including those with stage height greater than 40 feet (12 192 mm); 2. Technical production areas over the stage including under the roof, above and below the gridiron, catwalks and galleries; 3. Dressing rooms, performer lounges, shops and storerooms accessory to stages or platforms, with live entertainment; 4. Platforms with live entertainment; 5. Cabarets; or 6. When openings are provided in the stage floor for stage lifts, trap doors or stairs, sprinklers spaced 5 feet (1524 mm) on centers shall be provided around the opening at the ceiling below the stage, and baffles at least 12 inches (305 mm) in depth shall be installed around the perimeter of the opening. Exceptions: 1. Sprinklers are not required under stages or platforms less than 4 feet (1219 mm) in clear height that are utilized exclusively for storage of tables and chairs, provided the concealed space is separated from the adjacent spaces by Type X gypsum board not less than 5/8 inch (15.9 mm) in thickness. 2. Sprinklers are not required within portable orchestra enclosures on stages.
410.8 Standpipes. | Standpipe systems shall be provided in accordance with Section 905.
410.9 Voice/alarm communication system. | Stages shall be provided with a voice/alarm communication system in accordance with Section 907.2.1.1.
410.10 Construction in seating areas. | Construction in seating areas shall be in accordance with Sections 410.10.1 and 410.10.2.
410.10.1 Scenery and scenic elements in seating areas. | Scenery or scenic elements may be placed in seating sections if such elements:
410.10.2 Platforms or runways in seating areas. | Platforms or runways for performances, to accommodate the operation of cameras, electronic equipment, or motion picture projection machines not using carbon-arc or other light source that emits a gaseous discharge may be constructed in seating sections, provided such platforms or runways comply with the requirements of Section 410.4, except Item 1, and Section 410.9.
410.11 Stage lighting. | Stage lights shall be placed such that they will not develop temperatures on the surface of any material that will cause that material to ignite, or smoke, or cause its flameproofing to deteriorate.
411.2 Definitions. | The following term is defined in Chapter 2:
411.3 Automatic fire detection. | Special amusement buildings shall be equipped with an automatic fire detection system in accordance with Section 907.
411.4 Automatic sprinkler system. | Special amusement buildings shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. Where the special amusement building is temporary, the sprinkler water supply shall be of an approved temporary means. Exception: Automatic sprinklers are not required where the total floor area of a temporary special amusement building is less than 1,000 square feet (93 m2) and the exit access travel distance from any point to an exit is less than 50 feet (15 240 mm).
411.5 Alarm. | Actuation of a single smoke detector, the automatic sprinkler system or other automatic fire detection device shall initiate a pre-signal system in accordance with NFPA 72 as modified by Appendix Q of this code at a constantly attended location from which the Fire Department shall be notified and live voice evacuation instructions shall be initiated using an emergency voice/alarm communications system in accordance with Section 907.5.2.2.
411.6 Emergency voice/alarm communications system. | An emergency voice/alarm communications system shall be provided in accordance with Sections 907.2.12 and 907.5.2.2, which is also permitted to serve as a public address system and shall be audible throughout the entire special amusement building.
411.7 Exit marking. | Exit signs shall be installed at the required exit or exit access doorways of amusement buildings in accordance with this section and Section 1013 of this code. Approved directional exit markings listed in accordance with UL 1994, shall also be provided. Where mirrors, mazes or other designs are utilized that disguise the path of egress travel such that they are not apparent, approved low-level exit signs that comply with Section 1013.5 of this code, and directional path markings shall be provided and located not more than 8 inches (203 mm) above the walking surface and on or near the path of egress travel. Such markings shall become visible in an emergency. The directional exit marking shall be activated by the automatic fire detection system and the automatic sprinkler system in accordance with Section 907.2.12.2.
411.8 Interior finish. | The interior finish shall be Class A in accordance with Section 803.1.
412.2 Definitions. | The following terms are defined in Chapter 2:
412.3 Airport traffic control towers. | The provisions of Sections 412.3.1 through 412.3.9 shall apply to airport traffic control towers occupied only for the following uses:
412.3.1 Type of construction. | Airport traffic control towers shall be constructed to comply with the height limitations of Table 412.3.1. |  |  |  | See BC04 Tables&Figures
412.3.2 Stairways. | Stairways in airport traffic control towers shall be in accordance with Section 1011. Stairways in airport traffic control towers are not required to comply with Section 1011.12. Stairways shall be smokeproof enclosures complying with one of the alternatives provided in Section 909.20. The stairway shall be separated from elevators by a minimum distance of one-half of the diagonal of the area served measured in a straight line. Exception: The stairway and elevator hoistway are permitted to be located in the same shaft enclosure without the minimum separation distance, provided they are separated from each other by a 4-hour fire barrier having no openings. Such stairway shall be pressurized to a minimum of 0.15 inch of water column (43 Pa) and a maximum of 0.35 inch of water column (101 Pa) in the shaft relative to the building with stairway doors closed.
412.3.3 Exit access. | From observation levels, airport traffic control towers shall be permitted to have a single means of exit access for a distance of travel not greater than 100 feet (30 480 mm). Exit access stairways from the observation level need not be enclosed.
412.3.4 Number of exits. | Not less than one exit stairway shall be permitted for airport traffic control towers of any height provided that the occupant load per floor is not greater than 15 and the area per floor does not exceed 1,500 square feet (140 m2).
412.3.4.1 Interior finish. | Where an airport traffic control tower is provided with only one exit stairway, interior wall and ceiling finishes shall be either Class A or Class B.
412.3.5 Automatic fire detection systems. | Airport traffic control towers shall be provided with an automatic fire detection system installed in accordance with Section 907.2.
412.3.6 Automatic sprinkler system. | Where an occupied floor is located more than 35 feet (10 668 mm) above the lowest level of fire department vehicle access, airport traffic control towers shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.
412.3.7 Elevator protection. | Wires or cables that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire detecting systems to elevators shall be protected by construction having a fire-resistance rating of not less than 1 hour, or shall be circuit integrity cable having a fire-resistance rating of not less than 1 hour.
412.3.7.1 Elevators for occupant evacuation. | Where provided in addition to an exit stairway, occupant evacuation elevators shall be in accordance with Section 3008.
412.3.8 Accessibility. | Airport traffic control towers need not be accessible as specified in the provisions of Chapter 11.
413.1 General. | Storage of combustible materials in attics, under-floor spaces, concealed spaces, and below-grade storage rooms shall comply with this section. | 413.1 General. | High-piled stock or rack storage in any occupancy group shall comply with the International Fire Code.
412.3.9 Standby power and emergency power. | A standby power system and an emergency power system that conform to Chapter 27 shall be provided in airport traffic control towers more than 65 feet (19 812 mm) in height. Standby power shall be provided to the following equipment:
413.2 Attic, under-floor and concealed spaces. | Attic, under-floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required for 1-hour fire-resistance-rated construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 13/4 inch (45 mm) in thickness. Exception: Neither fire-resistance-rated construction nor opening protectives are required in any of the following locations: 1. Areas protected by approved automatic sprinkler systems. 2. Group R-3 and U occupancies. | 413.2 Attic, under-floor and concealed spaces. | Attic, under-floor and concealed spaces used for storage of combustible materials shall be protected on the storage side as required for 1-hour fire-resistance-rated construction. Openings shall be protected by assemblies that are self-closing and are of noncombustible construction or solid wood core not less than 13/4 inches (45 mm) in thickness. Exception: Neither fire-resistance-rated construction nor opening protectives are required in any of the following lo-cations: 1. Areas protected by approved automatic sprinkler systems. 2. Group R-3 and U occupancies.
412.3.9.1 Means of egress illumination. | Emergency power shall be provided for means of egress illumination in accordance with Sections 1008.3.4 and 1008.3.5.
414.1 General. | The provisions of Sections 414.1 through 414.6 shall apply to buildings and structures occupied for the manufacturing, processing, dispensing, use or storage of hazardous materials. | 414.1 General. | The provisions of Sections 414.1 through 414.6 shall apply to buildings and structures occupied for the manufacturing, processing, dispensing, use or storage of hazardous materials.
412.4 Aircraft hangars. | Aircraft hangars shall be in accordance with Sections 412.4.1 through 412.4.6.
414.1.1 Other provisions. | Buildings and structures with an occupancy in Group H shall comply with this section and the applicable provisions of the New York City Fire Code and Section 415 of this code, including, but not limited to, location, installation and mechanical provisions. | 414.1.1 Other provisions. | Buildings and structures with an occupancy in Group H shall comply with this section and the applicable provisions of Section 415 and the International Fire Code.
412.4.1 Exterior walls. | Exterior walls located less than 30 feet (9144 mm) from lot lines or a public way shall have a fire-resistance rating not less than 2 hours.
414.1.2 Materials. | The safe design of hazardous material occupancies is material dependent. Individual material requirements are also found in the New York City Mechanical Code, the New York City Fire Code, and Sections 307 and 415 of this code. | 414.1.2 Materials. | The safe design of hazardous material occupancies is material dependent. Individual material requirements are found in Sections 307 and 415, the International Mechanical Code and the International Fire Code.
412.4.2 Basements. | Where hangars have basements, floors over basements shall be of Type IA construction and shall be made tight against seepage of water, oil or vapors. There shall be no opening or communication between basements and the hangar. Access to basements shall be from outside only.
412.4.3 Floor surface. | Floors shall be graded and drained to prevent water or fuel from remaining on the floor. Floor drains shall discharge through an oil separator to the sewer or to an outside vented sump. Exception: Aircraft hangars with individual lease spaces not exceeding 2,000 square feet (186 m2) each in which servicing, repairing or washing is not conducted and fuel is not dispensed shall have floors that are graded toward the door, but shall not require a separator.
414.1.3 Information required. | A report shall be submitted to the Fire Department identifying the maximum expected quantities of hazardous materials to be stored, used in a closed system and used in an open system, and subdivided to separately address hazardous material classification categories based on Tables 307.1(1) and 307.1(2). The methods of protection from such hazards, including but not limited to control areas, fire protection systems and Group H occupancies shall be indicated in the report and on the construction documents. The opinion and report shall be prepared by a qualified person, firm or corporation approved by the Fire Commissioner and provided without charge to the Fire Department. | 414.1.3 Information required. | A report shall be submitted to the building official identifying the maximum expected quantities of hazardous materials to be stored, used in a closed system and used in an open system, and subdivided to separately address hazardous material classification categories based on Tables 307.1(1) and 307.1(2). The methods of protection from such hazards, including but not limited to control areas, fire protection systems and Group H occupancies shall be indicated in the report and on the construction documents. The opinion and report shall be prepared by a qualified person, firm or corporation approved by the building official and provided without charge to the enforcing agency.
412.4.4 Heating equipment. | Heating equipment shall be placed in another room separated by 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Entrance shall be from the outside or by means of a vestibule providing a two-doorway separation. Exceptions: 1. Unit heaters and vented infrared radiant heating equipment suspended not less than 10 feet (3048 mm) above the upper surface of wings or engine enclosures of the highest aircraft that are permitted to be housed in the hangar need not be located in a separate room provided they are mounted not less than 8 feet (2438 mm) above the floor in shops, offices and other sections of the hangar communicating with storage or service areas. 2. Entrance to the separated room shall be permitted by a single interior door provided the sources of ignition in the appliances are not less than 18 inches (457 mm) above the floor.
414.2 Control areas. | Control areas shall comply with the New York City Fire Code and Sections 414.2.1 through 414.2.5 of this code. | 414.2 Control areas. | Control areas shall comply with Sections 414.2.1 through 414.2.5 and the International Fire Code. Exception: Higher education laboratories in accordance with Section 428 and Chapter 38 of the International Fire Code.
412.4.5 Finishing. | The process of “doping,” involving use of a volatile flammable solvent, or of painting, shall be carried on in a separate detached building equipped with automatic fire-extinguishing equipment in accordance with Section 903.
414.2.1 Construction requirements. | Control areas shall be separated from each other by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. | 414.2.1 Construction requirements. | Control areas shall be separated from each other by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
412.4.6 Fire suppression. | Aircraft hangars shall be provided with a fire suppression system designed in accordance with NFPA 409, based upon the classification for the hangar given in Table 412.4.6 of this code. Exception: Where a fixed base operator has separate repair facilities on site, Group II hangars operated by a fixed base operator used for storage of transient aircraft only shall have a fire suppression system, but the system is exempt from foam requirements. |  |  |  | See BC04 Tables&Figures
414.2.2 Percentage of maximum allowable quantities. | The percentage of maximum allowable quantities of hazardous materials per control area permitted at each floor level within a building shall be in accordance with Table 414.2.2. | 414.2.2 Percentage of maximum allowable quantities. | The percentage of maximum allowable quantities of hazardous materials per control area permitted at each floor level within a building shall be in accordance with Table 414.2.2. |  | See BC04 Tables&Figures
40000
414.2.3 Number. | The maximum number of control areas within a building shall be in accordance with Table 414.2.2. | 414.2.3 Number. | The maximum number of control areas within a building shall be in accordance with Table 414.2.2. For the purposes of determining the number of control areas within a building, each portion of a building separated by one or more fire walls complying with Section 706 shall be considered a separate building. |  | See BC04 Tables&Figures
412.4.6.1 Hazardous operations. | Any Group III aircraft hangar according to Table 412.4.6 that contains hazardous operations including, but not limited to, the following shall be provided with a Group I or II fire suppression system in accordance with NFPA 409 as applicable: |  |  |  | See BC04 Tables&Figures
412.4.6.2 Separation of maximum single fire areas. | Maximum single fire areas established in accordance with hangar classification and construction type in Table 412.4.6 shall be separated by 2-hour fire walls constructed in accordance with Section 706. In determining the maximum single fire area as set forth in Table 412.4.6, ancillary uses that are separated from aircraft servicing areas by a fire barrier of not less than 1 hour, constructed in accordance with Section 707, shall not be included in the area. |  |  |  | See BC04 Tables&Figures
414.2.5 Hazardous material in Group M display and storage areas and in Group S storage areas. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials permitted within a single control area of a Group M display and storage area, a Group S storage area or an outdoor control area is permitted to exceed the maximum allowable quantities per control area specified in Tables 307.1(1) and 307.1(2) without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with the New York City Fire Code and quantities do not exceed the maximum allowable specified in Table 414.2.5(1) of this code. | 414.2.5 Hazardous material in Group M display and storage areas and in Group S storage areas. | Hazardous materials located in Group M and Group S occupancies shall be in accordance with Sections 414.2.5.1 through 414.2.5.3. |  | See BC04 Tables&Figures
412.5 Residential aircraft hangars. | Residential aircraft hangars shall comply with Sections 412.5.1 through 412.5.5.
412.5.1 Fire separation. | A hangar shall not be attached to a dwelling unless separated by a fire barrier having a fire-resistance rating of not less than 1 hour. Such separation shall be continuous from the foundation to the underside of the roof and unpierced except for doors leading to the dwelling unit. Doors into the dwelling unit shall be equipped with self-closing devices and conform to the requirements of Section 716 with a noncombustible raised sill not less than 4 inches (102 mm) in height. Openings from a hangar directly into a room used for sleeping purposes shall not be permitted.
412.5.2 Egress. | A hangar shall provide two means of egress. One of the doors into the dwelling shall be considered as meeting only one of the two means of egress.
412.5.3 Smoke alarms. | Smoke alarms shall be provided within the hangar in accordance with Section 907.2.11.
414.3 Ventilation. | Rooms, areas or spaces in which explosive, corrosive, combustible, flammable or highly toxic dusts, mists, fumes, vapors or gases are or may be emitted due to the processing, use, handling or storage of materials shall be mechanically ventilated where required by the New York City Fire Code or the New York City Mechanical Code. | 414.3 Ventilation. | Rooms, areas or spaces in which explosive, corrosive, combustible, flammable or highly toxic dusts, mists, fumes, vapors or gases are or have the potential to be emitted due to the processing, use, handling or storage of materials shall be mechanically ventilated where required by this code, the International Fire Code or the International Mechanical Code.
412.5.4 Independent systems. | Electrical, mechanical and plumbing drain, waste and vent (DWV) systems installed within the hangar shall be independent of the systems installed within the dwelling. Building sewer lines shall be permitted to be connected outside the structures. Exception: Smoke detector wiring and feed for electrical subpanels in the hangar.
414.4 Hazardous material systems. | Systems involving hazardous materials shall be suitable for the intended application. Controls shall be designed to prevent materials from entering or leaving process or reaction systems at other than the intended time, rate or path. Automatic controls, where provided, shall be designed to be fail safe. | 414.4 Hazardous material systems. | Systems involving hazardous materials shall be suitable for the intended application. Controls shall be designed to prevent materials from entering or leaving process or reaction systems at other than the intended time, rate or path. Automatic controls, where provided, shall be designed to be fail safe.
412.5.5 Height and area limits. | Residential aircraft hangars shall be not greater than 2,000 square feet (186 m2) in area and 20 feet (6096 mm) in building height.
414.5 Inside storage, dispensing and use. | The inside storage, dispensing and use of hazardous materials shall be in accordance with the New York City Fire Code and Sections 414.5.1 through 414.5.4 of this code. | 414.5 Inside storage, dispensing and use. | The inside storage, dispensing and use of hazardous materials shall be in accordance with Sections 414.5.1 through 414.5.3 of this code and the International Fire Code.
412.6 Aircraft paint hangars. | Aircraft painting operations where flammable liquids are used in excess of the maximum allowable quantities per control area listed in Table 307.1(1) shall be conducted in an aircraft paint hangar that complies with the provisions of Sections 412.6.1 through 412.6.6. |  |  |  | See BC03 Tables&Figures
414.5.1 Explosion control. | Explosion control shall be provided in accordance with the New York City Fire Code as required by Table 414.5.1 where quantities of hazardous materials specified in that table exceed the maximum allowable quantities in Table 307.1(1) or where a structure, room or space is occupied for purposes involving explosion hazards as required by the New York City Fire Code or Section 415 of this code. | 414.5.1 Explosion control. | Explosion control shall be provided in accordance with the International Fire Code as required by Table 414.5.1 where quantities of hazardous materials specified in that table exceed the maximum allowable quantities in Table 307.1(1) or where a structure, room or space is occupied for purposes involving explosion hazards as required by Section 415 or the International Fire Code. |  | See BC04 Tables&Figures | See BC03 Tables&Figures
412.6.1 Occupancy group. | Aircraft paint hangars shall be classified as Group H-2. Aircraft paint hangars shall comply with the applicable requirements of the New York City Fire Code and this code for such occupancy.
414.5.2 Emergency or standby power. | Where required by the New York City Fire Code or this code, mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems shall be provided with emergency or standby power in accordance with Section 2702 of this code. For storage and use areas for highly toxic or toxic materials, see the New York City Fire Code. | 414.5.2 Emergency or standby power. | Where required by the International Fire Code or this code, mechanical ventilation, treatment systems, temperature control, alarm, detection or other electrically operated systems shall be provided with emergency or standby power in accordance with Section 2702. For storage and use areas for highly toxic or toxic materials, see Sections 6004.2.2.8 and 6004.3.4.2 of the International Fire Code.
412.6.2 Construction. | The aircraft paint hangar shall be of Type I or II construction.
414.5.2.1 Exempt applications. | Emergency or standby power is not required for the mechanical ventilation systems provided for any of the following: | 414.5.2.1 Exempt applications. | Emergency or standby power is not required for the mechanical ventilation systems provided for any of the following:
412.6.3 Operations. | Only those flammable liquids necessary for painting operations shall be permitted in quantities less than the maximum allowable quantities per control area in Table 307.1(1). Spray equipment cleaning operations shall be conducted in a liquid use, dispensing and mixing room. |  |  |  | See BC03 Tables&Figures
414.5.2.2 Fail-safe engineered systems. | Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed. | 414.5.2.2 Fail-safe engineered systems. | Standby power for mechanical ventilation, treatment systems and temperature control systems shall not be required where an approved fail-safe engineered system is installed.
412.6.4 Storage. | Storage of flammable liquids shall be in a liquid storage room.
414.5.3 Spill control, drainage and containment. | Rooms, buildings or areas occupied for the storage of solid and liquid hazardous materials shall be provided with a means to control spillage and to contain or drain off spillage and fire protection water discharged in the storage area where required in the New York City Fire Code. The methods of spill control shall be in accordance with the New York City Fire Code. | 414.5.3 Spill control, drainage and containment. | Rooms, buildings or areas occupied for the storage of solid and liquid hazardous materials shall be provided with a means to control spillage and to contain or drain off spillage and fire protection water discharged in the storage area where required in the International Fire Code. The methods of spill control shall be in accordance with the International Fire Code.
412.6.5 Fire suppression. | Aircraft paint hangars shall be provided with fire suppression as required by NFPA 409.
414.6 Outdoor storage, dispensing and use. | The outdoor storage, dispensing and use of hazardous materials shall be in accordance with the New York City Fire Code. | 414.6 Outdoor storage, dispensing and use. | The outdoor storage, dispensing and use of hazardous materials shall be in accordance with the International Fire Code.
412.6.6 Ventilation. | Aircraft paint hangars shall be provided with ventilation as required in the New York City Mechanical Code.
414.6.1 Weather protection. | Where weather protection is provided for sheltering outdoor hazardous material storage or use areas, such areas shall be considered outdoor storage or use when the weather protection structure complies with Sections 414.6.1.1 through 414.6.1.3. | 414.6.1 Weather protection. | Where weather protection is provided for sheltering outdoor hazardous material storage or use areas, such areas shall be considered outdoor storage or use where the weather protection structure complies with Sections 414.6.1.1 through 414.6.1.3.
412.7 Aircraft manufacturing facilities. | In buildings used for the manufacturing of aircraft, exit access travel distances indicated in Section 1017.1 shall be increased in accordance with the following:
414.6.1.1 Walls. | Walls shall not obstruct more than one side of the structure. Exception: Walls shall be permitted to obstruct portions of multiple sides of the structure, provided that the obstructed area is not greater than 25 percent of the structure’s perimeter. | 414.6.1.1 Walls. | Walls shall not obstruct more than one side of the structure. Exception: Walls shall be permitted to obstruct portions of multiple sides of the structure, provided that the ob-structed area is not greater than 25 percent of the structure’s perimeter.
412.7.1 Ancillary areas. | Rooms, areas and spaces ancillary to the primary manufacturing area shall be permitted to egress through such area having a minimum height as indicated in Table 412.7. Exit access travel distance within the ancillary room, area or space shall not exceed that indicated in Table 1017.2 based on the occupancy classification of that ancillary area. Total exit access travel distance shall not exceed that indicated in Table 412.7. |  |  |  | See BC04 Tables&Figures
414.6.1.2 Separation distance. | The distance from the structure to buildings, lot lines, public ways or means of egress to a public way shall be not less than the distance required for an outside hazardous material storage or use area without weather protection. | 414.6.1.2 Separation distance. | The distance from the structure to buildings, lot lines, public ways or means of egress to a public way shall be not less than the distance required for an outside hazardous material storage or use area without weather protection.
412.8 Heliports and helistops. | Heliports and helistops shall be permitted to be erected on buildings or other locations where they are constructed in accordance with Sections 412.8.1 through 412.8.5.
414.6.1.3 Noncombustible construction. | The overhead structure shall be of approved noncombustible construction with a maximum area of 1,500 square feet (140 m2). Exception: The maximum area is permitted to be increased as provided by Section 506. | 414.6.1.3 Noncombustible construction. | The overhead structure shall be of approved noncombustible construction with a maximum area of 1,500 square feet (140 m2). Exception: The maximum area is permitted to be increased as provided by Section 506.
412.8.1 Size. | The landing area for helicopters less than 3,500 pounds (1588 kg) shall be not less than 20 feet (6096 mm) in length and width. The landing area shall be surrounded on all sides by a clear area having a minimum average width at roof level of 15 feet (4572 mm) but with no width less than 5 feet (1524 mm).
412.8.2 Design. | Helicopter landing areas and the supports thereof on the roof of a building shall be noncombustible construction. Landing areas shall be designed to confine any flammable liquid spillage to the landing area itself and provisions shall be made to drain such spillage away from any exit or stairway serving the helicopter landing area or from a structure housing such exit or stairway. For structural design requirements, see Section 1607.6.
412.8.3 Means of egress. | The means of egress from heliports and helistops shall comply with the provisions of Chapter 10. Landing areas located on buildings or structures shall have two or more means of egress. For landing areas less than 60 feet (18 288 mm) in length or less than 2,000 square feet (186 m2) in area, the second means of egress is permitted to be a fire escape, alternating tread device or ladder leading to the floor below.
415.3 Automatic fire detection systems. | Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2. | 415.3 Automatic fire detection systems. | Group H occupancies shall be provided with an automatic fire detection system in accordance with Section 907.2.
412.8.4 Rooftop heliports and helistops. | Rooftop heliports and helistops shall comply with NFPA 418 and the New York City Fire Code.
415.4 Automatic sprinkler system. | Group H occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5. | 415.4 Automatic sprinkler system. | Group H occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.5.
412.8.5 Standpipe system. | In buildings equipped with a standpipe system, the standpipe shall extend to the roof level in accordance with Section 905.3.6.
415.5 Emergency alarms. | Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided as set forth herein. | 415.5 Emergency alarms. | Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided as set forth herein.
415.5.1 Storage. | An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials. | 415.5.1 Storage. | An approved manual emergency alarm system shall be provided in buildings, rooms or areas used for storage of hazardous materials. Emergency alarm-initiating devices shall be installed outside of each interior exit or exit access door of storage buildings, rooms or areas. Activation of an emergency alarm-initiating device shall sound a local alarm to alert occupants of an emergency situation involving hazardous materials.
415.5.2 Dispensing, use and handling. | Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors, interior exit stairways or ramps, or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, proprietary or remote station service or constantly attended on-site location and shall initiate a local audible alarm. | 415.5.2 Dispensing, use and handling. | Where hazardous materials having a hazard ranking of 3 or 4 in accordance with NFPA 704 are transported through corridors, interior exit stairways or ramps, or exit passageways, there shall be an emergency telephone system, a local manual alarm station or an approved alarm-initiating device at not more than 150-foot (45 720 mm) intervals and at each exit and exit access doorway throughout the transport route. The signal shall be relayed to an approved central, proprietary or remote station service or constantly attended on-site location and shall initiate a local audible alarm.
413.3 High-piled stock or rack storage. | High-piled stock or rack storage in any occupancy group shall comply with the New York City Fire Code, including the requirement for permit approval.
415.5.3 Supervision. | Emergency alarm systems shall be supervised by an approved central, proprietary or remote station service or shall initiate an audible and visual signal at a constantly attended on-site location. | 415.5.3 Supervision. | Emergency alarm systems required by Section 415.5.1 or 415.5.2 shall be electrically supervised and monitored by an approved central, proprietary or remote station service or shall initiate an audible and visual signal at a constantly attended on-site location.
415.5.4 Emergency alarm systems. | Emergency alarm systems shall be provided with emergency power in accordance with Section 2702. | 415.5.4 Emergency alarm systems. | Emergency alarm systems required by Section 415.5.1 or 415.5.2 shall be provided with emergency or standby power in accordance with Section 2702.2.
415.6 Fire separation distance. | Group H occupancies shall be located on property in accordance with the other provisions of this chapter. In Groups H-2 and H-3, not less than 25 percent of the perimeter wall of the occupancy shall be an exterior wall. Exceptions: 1. Liquid use, dispensing and mixing rooms having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the New York City Fire Code and NFPA 30. 2. Liquid storage rooms having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the New York City Fire Code and NFPA 30. 3. Spray paint booths that comply with the New York City Fire Code need not be located on the outer perimeter. | 415.6 Fire separation distance. | Group H occupancies shall be located on property in accordance with the other provisions of this chapter. In Groups H-2 and H-3, not less than 25 percent of the perimeter wall of the occupancy shall be an exterior wall.
414.1.2.1 Aerosols. | Level 2 and 3 aerosol products shall be stored and displayed in accordance with the New York City Fire Code. See the New York City Fire Code and Section 311.2 of this code for occupancy group requirements.
414.2.4 Fire-resistance-rating requirements. | The required fire-resistance rating for fire barriers shall be in accordance with Table 414.2.2. The floor assembly of the control area and the construction supporting the floor of the control area shall have a fire-resistance rating of not less than 2 hours. Exception: The floor assembly of the control area and the construction supporting the floor of the control area are allowed to be 1-hour fire-resistance rated in buildings of Types IIA, IIIA and VA construction, provided that both of the following conditions exist: 1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1; and 2. The building is three or fewer stories above grade plane. |  |  |  | See BC04 Tables&Figures
414.2.5.1 Below-grade storage of flammable or combustible mixtures accessory to Group M establishments. | Class I liquids shall not be stored in below-grade locations. Storage of Class II and Class III liquids, accessory to retail stores, and partly or completely below grade shall be permitted, provided that such below-grade area is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and enclosed by fire barriers having a fire-resistance rating of at least 2 hours, constructed in accordance with the construction type of the building. Openings shall be protected by self-closing assemblies having a fire-resistance rating of at least 11/2 hours. Exception: Class IIIB liquids may be stored in below-grade locations that are not provided throughout with an automatic sprinkler system when such liquids are stored in a room that is separated, vertically and horizontally, from surrounding spaces by fire barriers of not less than 2-hour fire-resistance rating and such room is provided with an automatic sprinkler system.
415.7 Special provisions for Group H-1 occupancies. | Group H-1 occupancies shall be in detached buildings used for no other purpose, shall not exceed one story in height and be without basements, crawl spaces or other under-floor spaces. Roofs shall be of lightweight construction with suitable thermal insulation to prevent sensitive material from reaching its decomposition temperature. Group H-1 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for both Group H-1 and H-4 occupancies. | 415.7 Special provisions for Group H-1 occupancies. | Group H-1 occupancies shall be in detached buildings not used for other purposes. Roofs shall be of lightweight construction with suitable thermal insulation to prevent sensitive material from reaching its decomposition temperature. Group H-1 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for both Group H-1 and H-4 occupancies. |  | See BC03 Tables&Figures
415.7.1 Floors in storage rooms. | Floors in storage areas for organic peroxides, pyrophoric materials and unstable (reactive) materials shall be of liquid-tight, noncombustible construction. | 415.7.1 Floors in storage rooms. | Floors in storage areas for organic peroxides, pyrophoric materials and unstable (reactive) materials shall be of liquid-tight, noncombustible construction.
415.8 Special provisions for Group H-2 and H-3 occupancies. | Group H-2 and H-3 occupancies containing quantities of hazardous materials in excess of those set forth in Table 415.6.2 shall be in detached buildings used for manufacturing, processing, dispensing, use or storage of hazardous materials. Materials listed for Group H-1 occupancies in Section 307.3 are permitted to be located within Group H-2 or H-3 detached buildings provided the amount of materials per control area do not exceed the maximum allowed quantity specified in Table 307.1(1). | 415.8 Special provisions for Group H-2 and H-3 occupancies. | Group H-2 and H-3 occupancies containing quantities of hazardous materials in excess of those set forth in Table 415.6.5 shall be in detached buildings used for manufacturing, processing, dispensing, use or storage of hazardous materials. Materials specified for Group H-1 occupancies in Section 307.3 are permitted to be located within Group H-2 or H-3 detached buildings provided that the amount of materials per control area do not exceed the maximum allowed quantity specified in Table 307.1(1). |  | See BC03 Tables&Figures | See BC04 Tables&Figures
415.8.1 Multiple hazards. | Group H-2 or H-3 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for Group H-2, H-3 or H-4 occupancies as applicable. | 415.8.1 Multiple hazards. | Group H-2 or H-3 occupancies containing materials that are in themselves both physical and health hazards in quantities exceeding the maximum allowable quantities per control area in Table 307.1(2) shall comply with requirements for Group H-2, H-3 or H-4 occupancies as applicable. |  | See BC03 Tables&Figures
415.8.2 Separation of incompatible materials. | Hazardous materials other than those listed in Table 415.6.2 shall be allowed in manufacturing, processing, dispensing, use or storage areas when separated from incompatible materials in accordance with the provisions of the New York City Fire Code. | 415.8.2 Separation of incompatible materials. | Hazardous materials other than those specified in Table 415.6.5 shall be allowed in manufacturing, processing, dispensing, use or storage areas when separated from incompatible materials in accordance with the provisions of the International Fire Code. |  | See BC04 Tables&Figures
415.8.3 Water reactives. | Group H-2 and H-3 occupancies containing water-reactive materials shall be resistant to water penetration. Piping for conveying liquids shall not be over or through areas containing water reactives, unless isolated by approved liquid-tight construction. Exception: Fire protection piping shall be permitted over or through areas containing water reactives without isolating it with liquid-tight construction. | 415.8.3 Water reactives. | Group H-2 and H-3 occupancies containing water-reactive materials shall be resistant to water penetration. Piping for conveying liquids shall not be over or through areas containing water reactives, unless isolated by approved liquid-tight construction. Exception: Fire protection piping shall be permitted over or through areas containing water reactives without iso-lating it with liquid-tight construction.
415.8.4 Floors in storage rooms. | Floors in storage areas for organic peroxides, oxidizers, pyrophoric materials, unstable (reactive) materials and water-reactive solids and liquids shall be of liquid-tight, noncombustible construction. | 415.8.4 Floors in storage rooms. | Floors in storage areas for organic peroxides, oxidizers, pyrophoric materials, unstable (reactive) materials and water-reactive solids and liquids shall be of liquid-tight, noncombustible construction.
415.8.5 Waterproof room. | Rooms or areas used for the storage of water-reactive solids and liquids shall be constructed in a manner that resists the penetration of water through the use of waterproof materials. Piping carrying water for other than approved automatic [fire] sprinkler systems shall not be within such rooms or areas. | 415.8.5 Waterproof room. | Rooms or areas used for the storage of water-reactive solids and liquids shall be constructed in a manner that resists the penetration of water through the use of waterproof materials. Piping carrying water for other than approved automatic sprinkler systems shall not be within such rooms or areas.
414.5.4 Storage of medical gases. | When required by the New York City Fire Code, a one-hour room shall be provided for the storage of medical gases inside of buildings, with the protected openings and ventilation provisions as required by the New York City Fire Code.
415.9 Group H-2. | Occupancies in Group H-2 shall be constructed in accordance with the New York City Fire Code and Sections 415.9.1 through 415.9.3 of this code. | 415.9 Group H-2. | Occupancies in Group H-2 shall be constructed in accordance with Sections 415.9.1 through 415.9.3 and the International Fire Code.
415.9.1 Flammable and combustible liquids. | The storage, handling, processing and transporting of flammable and combustible liquids in Group H-2 and H-3 occupancies shall be in accordance with the New York City Mechanical Code, the New York City Fire Code, and Sections 415.9.1.1 through 415.9.1.9 of this code. | 415.9.1 Flammable and combustible liquids. | The storage, handling, processing and transporting of flammable and combustible liquids in Group H-2 and H-3 occupancies shall be in accordance with Sections 415.9.1.1 through 415.9.1.9, the International Mechanical Code and the International Fire Code.
415.9.1.1 Mixed occupancies. | Where the storage tank area is located in a building of two or more occupancies and the quantity of liquid exceeds the maximum allowable quantity for one control area, the use shall be completely separated from adjacent fire areas in accordance with the requirements of Section 508.4. | 415.9.1.1 Mixed occupancies. | Where the storage tank area is located in a building of two or more occupancies and the quantity of liquid exceeds the maximum allowable quantity for one control area, the use shall be completely separated from adjacent occupancies in accordance with the requirements of Section 508.4.
415.9.1.1.1 Height exception. | Where storage tanks are located within a building no more than one story above grade plane, the height limitation of Section 504 shall not apply for Group H. | 415.9.1.1.1 Height exception. | Where storage tanks are located within a building not more than one story above grade plane, the height limitation of Section 504 shall not apply for Group H.
415.9.1.2 Tank protection. | Storage tanks shall be noncombustible and protected from physical damage. Fire barriers or horizontal assemblies or both around the storage tanks shall be permitted as the method of protection from physical damage. | 415.9.1.2 Tank protection. | Storage tanks shall be noncombustible and protected from physical damage. Fire barriers or horizontal assemblies or both around the storage tanks shall be permitted as the method of protection from physical damage.
415.1 Scope. | The provisions of Sections 415.1 through 415.11 shall apply to the storage and use of hazardous materials in excess of the maximum allowable quantities per control area listed in Section 307.1. Buildings and structures with an occupancy in Group H shall also comply with the applicable provisions of the New York City Fire Code and Section 414 of this code including, but not limited to, location and installation provisions.
415.9.1.4 Leakage containment. | A liquid-tight containment area compatible with the stored liquid shall be provided. The method of spill control, drainage control and secondary containment shall be in accordance with the New York City Fire Code. Exception: Rooms where only double-wall storage tanks conforming to Section 415.9.1.3 are used to store Class I, II and IIIA flammable and combustible liquids shall not be required to have a leakage containment area. | 415.9.1.4 Leakage containment. | A liquid-tight containment area compatible with the stored liquid shall be provided. The method of spill control, drainage control and secondary containment shall be in accordance with the International Fire Code. Exception: Rooms where only double-wall storage tanks conforming to Section 415.9.1.3 are used to store Class I, II and IIIA flammable and combustible liquids shall not be required to have a leakage containment area.
415.2 Definitions. | The following terms are defined in Chapter 2:
415.9.1.5 Leakage alarm. | An approved automatic alarm shall be provided to indicate a leak in a storage tank and room. The alarm shall sound an audible signal, 15 dBa above the ambient sound level, at every point of entry into the room in which the leaking storage tank is located. An approved sign shall be posted on every entry door to the tank storage room indicating the potential hazard of the interior room environment, or the sign shall state: WARNING, WHEN ALARM SOUNDS, THE ENVIRONMENT WITHIN THE ROOM MAY BE HAZARDOUS. The leakage alarm shall also be supervised in accordance with Chapter 9 to transmit a trouble signal. | 415.9.1.5 Leakage alarm. | An approved automatic alarm shall be provided to indicate a leak in a storage tank and room. The alarm shall sound an audible signal, 15 dBa above the ambient sound level, at every point of entry into the room in which the leaking storage tank is located. An approved sign shall be posted on every entry door to the tank storage room indicating the potential hazard of the interior room environment, or the sign shall state, WARNING, WHEN ALARM SOUNDS, THE ENVIRONMENT WITHIN THE ROOM MAY BE HAZARDOUS. The leakage alarm shall be supervised in accordance with Chapter 9 to transmit a trouble signal.
415.9.1.6 Tank vent. | Storage tank vents for Class I, II or IIIA liquids shall terminate to the outdoor air in accordance with the New York City Fire Code. | 415.9.1.6 Tank vent. | Storage tank vents for Class I, II or IIIA liquids shall terminate to the outdoor air in accordance with the International Fire Code.
415.9.1.7 Room ventilation. | Storage tank areas storing Class I, II or IIIA liquids shall be provided with mechanical ventilation. The mechanical ventilation system shall be in accordance with the New York City Mechanical Code and the New York City Fire Code. | 415.9.1.7 Room ventilation. | Storage tank areas storing Class I, II or IIIA liquids shall be provided with mechanical ventilation. The mechanical ventilation system shall be in accordance with the International Mechanical Code and the International Fire Code.
415.9.1.8 Explosion venting. | Where Class I liquids are being stored, explosion venting shall be provided in accordance with the New York City Fire Code. | 415.9.1.8 Explosion venting. | Where Class I liquids are being stored, explosion venting shall be provided in accordance with the International Fire Code.
415.9.1.9 Tank openings other than vents. | Tank openings other than vents from tanks inside buildings shall be designed to ensure that liquids or vapor concentrations are not released inside the building. | 415.9.1.9 Tank openings other than vents. | Tank openings other than vents from tanks inside buildings shall be designed to ensure that liquids or vapor concentrations are not released inside the building.
415.9.3 Dry cleaning plants. | The construction and installation of dry cleaning plants shall be in accordance with the requirements of this code, the New York City Mechanical Code, the New York City Plumbing Code and NFPA 32. Dry cleaning solvents and systems shall be classified in accordance with the New York City Fire Code. | 415.9.3 Dry cleaning plants. | The construction and installation of dry cleaning plants shall be in accordance with the requirements of this code, the International Mechanical Code, the International Plumbing Code and NFPA 32. Dry cleaning solvents and systems shall be classified in accordance with the International Fire Code.
415.10 Groups H-3 and H-4. | Groups H-3 and H-4 shall be constructed in accordance with the applicable provisions of this code and the New York City Fire Code. | 415.10 Groups H-3 and H-4. | Groups H-3 and H-4 shall be constructed in accordance with the applicable provisions of this code and the International Fire Code.
415.10.1 Flammable and combustible liquids. | The storage, handling, processing and transporting of flammable and combustible liquids in Group H-3 occupancies shall be in accordance with Section 415.9.1. | 415.10.1 Flammable and combustible liquids. | The storage, handling, processing and transporting of flammable and combustible liquids in Group H-3 occupancies shall be in accordance with Section 415.9.1.
415.6.1 Group H occupancy minimum fire separation distance. | Regardless of any other provisions, buildings containing Group H occupancies shall be set back to the minimum fire separation distance as set forth in Sections 415.6.1.1 through 415.6.1.4. Distances shall be measured from the walls enclosing the occupancy to lot lines, including those on a public way. Distances to assumed lot lines established for the purpose of determining exterior wall and opening protection are not to be used to establish the minimum fire separation distance for buildings on sites where explosives are manufactured or used when separation is provided in accordance with the quantity distance tables specified for explosive materials in the New York City Fire Code. Exceptions: 1. Fireworks manufacturing buildings separated in accordance with NFPA 1124. 2. Buildings containing the following materials when separated in accordance with Table 415.6.1 of this code: 2.1. Organic peroxides, unclassified detonable. 2.2. Unstable reactive materials Class 4. 2.3. Unstable reactive materials, Class 3 detonable. 2.4. Detonable pyrophoric materials. |  |  |  | See BC04 Tables&Figures
415.10.2 Gas rooms. | Where gas rooms are provided, such rooms shall be separated from other areas by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. | 415.10.2 Gas rooms. | Where gas rooms are provided, such rooms shall be separated from other areas by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
415.6.1.1 Group H-1. | Group H-1 occupancies shall be set back not less than 75 feet (22 860 mm) and not less than required by the New York City Fire Code.
415.10.3 Floors in storage rooms. | Floors in storage areas for corrosive liquids and highly toxic or toxic materials shall be of liquid-tight, noncombustible construction. | 415.10.3 Floors in storage rooms. | Floors in storage areas for corrosive liquids and highly toxic or toxic materials shall be of liquid-tight, noncombustible construction.
415.6.1.2 Group H-2. | Group H-2 occupancies shall be set back not less than 30 feet (9144 mm) where the area of the occupancy exceeds 1,000 square feet (93 m2), and it is not required to be located in a detached building.
415.6.1.3 Groups H-2 and H-3. | Group H-2 and H-3 occupancies shall be set back not less than 50 feet (15 240 mm) where a detached building is required (see Table 415.6.2). |  |  |  | See BC04 Tables&Figures
415.11 Group H-5. | In addition to the requirements set forth elsewhere in this code, Group H-5 shall comply with the provisions of the New York City Fire Code and Section 415.9 of this code, including, but not limited to, automatic sprinkler protection for workstations, gas cabinets, exhausted enclosures, pass-throughs in exit access corridors and exhaust ducts. | 415.11 Group H-5. | In addition to the requirements set forth elsewhere in this code, Group H-5 shall comply with the provisions of Sections 415.11.1 through 415.11.12 and the International Fire Code.
415.6.1.4 Explosive materials. | Group H-2 and H-3 occupancies containing materials with explosive characteristics shall be separated as required by the New York City Fire Code. Where separations are not specified, the distances required shall not be less than the distances required by Table 415.6.1. |  |  |  | See BC04 Tables&Figures
415.11.1 Fabrication areas. | Fabrication areas shall comply with Sections 415.11.1.1 through 415.11.1.8. | 415.11.1 Fabrication areas. | Fabrication areas shall comply with Sections 415.11.1.1 through 415.11.1.8.
40
415.11.1.1 Hazardous materials. | Hazardous materials and hazardous production materials (HPM) shall comply with Sections 415.11.1.1.1 through 415.11.1.1.2. | 415.11.1.1 Hazardous materials. | Hazardous materials and hazardous production materials (HPM) shall comply with Sections 415.11.1.1.1 and 415.11.1.1.2.
400
415.11.1.1.1 Aggregate quantities. | The aggregate quantities of hazardous materials stored and used in a single fabrication area shall not exceed the quantities set forth in Table 415.11.1.1.1. Exception: The quantity limitations for any hazard category in Table 415.11.1.1.1 shall not apply where the fabrication area contains quantities of hazardous materials not exceeding the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2). | 415.11.1.1.1 Aggregate quantities. | The aggregate quantities of hazardous materials stored and used in a single fabrication area shall not exceed the quantities set forth in Table 415.11.1.1.1. Exception: The quantity limitations for any hazard category in Table 415.11.1.1.1 shall not apply where the fabrication area contains quantities of hazardous materials not exceeding the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2). |  | See BC04 Tables&Figures
4. Storage of explosives in a quantity exceeding 1,000 pounds in one magazine is prohibited.
415.11.1.1.2 Hazardous production materials. | The maximum quantities of hazardous production materials (HPM) stored in a single fabrication area shall not exceed the maximum allowable quantities per control area established by Tables 307.1(1) and 307.1(2). | 415.11.1.1.2 Hazardous production materials. | The maximum quantities of hazardous production materials (HPM) stored in a single fabrication area shall not exceed the maximum allowable quantities per control area established by Table 307.1(1) and Table 307.1(2). |  | See BC03 Tables&Figures
415.6.2 Detached buildings for Group H-1, H-2 or H-3 occupancy. | The storage or use of hazardous materials in excess of those amounts listed in Table 415.6.2 shall be in accordance with the applicable provisions of Sections 415.7 and 415.8. |  |  |  | See BC04 Tables&Figures
415.11.1.2 Separation. | Fabrication areas, whose sizes are limited by the quantity of hazardous materials allowed by Table 415.11.1.1.1, shall be separated from each other, from corridors and from other parts of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Exceptions: 1. Doors within such fire barrier walls, including doors to corridors, shall be only self-closing fire door assemblies having a fire protection rating of not less than 3/4 hour. 2. Windows between fabrication areas and exit access corridors are permitted to be fixed glazing listed and labeled for a fire protection rating of not less than 3/4 hour in accordance with Section 716. | 415.11.1.2 Separation. | Fabrication areas, whose sizes are limited by the quantity of hazardous materials allowed by Table 415.11.1.1.1, shall be separated from each other, from corridors and from other parts of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Exceptions: 1. Doors within such fire barrier walls, including doors to corridors, shall be only self-closing fire door assemblies having a fire protection rating of not less than 3/4 hour. 2. Windows between fabrication areas and corridors are permitted to be fixed glazing listed and labeled for a fire protection rating of not less than 3/4 hour in accordance with Section 716. |  | See BC04 Tables&Figures
415.6.2.1 Wall and opening protection. | Where a detached building is required by Table 415.6.2, there are no requirements for wall and opening protection based on fire separation distance. |  |  |  | See BC04 Tables&Figures
415.11.1.3 Location of occupied levels. | Occupied levels of fabrication areas shall be located at or above the first story above grade plane. | 415.11.1.3 Location of occupied levels. | Occupied levels of fabrication areas shall be located at or above the first story above grade plane.
415.11.1.4 Floors. | Except for surfacing, floors within fabrication areas shall be of noncombustible construction. | 415.11.1.4 Floors. | Except for surfacing, floors within fabrication areas shall be of noncombustible construction.
415.11.1.5 Shafts and openings through floors. | Elevator hoistways, vent shafts and other openings through floors shall be enclosed where required by Sections 712 and 713. Mechanical, duct and piping penetrations within a fabrication area shall not extend through more than two floors. The annular space around penetrations for cables, cable trays, tubing, piping, conduit or ducts shall be sealed at the floor level to restrict the movement of air. The fabrication area, including the areas through which the ductwork and piping extend, shall be considered a single conditioned environment. | 415.11.1.5 Shafts and openings through floors. | Elevator hoistways, vent shafts and other openings through floors shall be enclosed where required by Sections 712 and 713. Mechanical, duct and piping penetrations within a fabrication area shall not extend through more than two floors. The annular space around penetrations for cables, cable trays, tubing, piping, conduit or ducts shall be sealed at the floor level to restrict the movement of air. The fabrication area, including the areas through which the ductwork and piping extend, shall be considered to be a single conditioned environment.
415.11.1.6 Ventilation. | Mechanical exhaust ventilation at the rate of not less than 1 cubic foot per minute per square foot (0.0051 m3/(s m2)) of floor area shall be provided throughout portions of the fabrication area where HPM are used or stored. The exhaust air duct system of one fabrication area shall not connect to another duct system outside that fabrication area within the building. | 415.11.1.6 Ventilation. | Mechanical exhaust ventilation at the rate of not less than 1 cubic foot per minute per square foot of floor area shall be provided throughout the portions of the fabrication area where HPM are used or stored. The exhaust air duct system of one fabrication area shall not connect to another duct system outside that fabrication area within the building.
415.11.1.7 Transporting hazardous production materials to fabrication areas. | HPM shall be transported to fabrication areas through enclosed piping or tubing systems that comply with Section 415.11.6, through service corridors complying with Section 415.11.3, or in exit access corridors as permitted in the exception to Section 415.11.2. The handling or transporting of HPM within service corridors shall comply with the New York City Fire Code. | 415.11.1.7 Transporting hazardous production materials to fabrication areas. | HPM shall be transported to fabrication areas through enclosed piping or tubing systems that comply with Section 415.11.7, through service corridors complying with Section 415.11.3, or in corridors as permitted in the exception to Section 415.11.2. The handling or transporting of HPM within service corridors shall comply with the International Fire Code.
415.11.1.8 Electrical. | Electrical equipment and devices within the fabrication area shall comply with the New York City Electrical Code. The requirements for hazardous locations need not be applied where the average air change is at least four times that set forth in Section 415.11.1.6 and where the number of air changes at any location is not less than three times that required by Section 415.11.1.6. The use of recirculated air shall be permitted. | 415.11.1.8 Electrical. | Electrical equipment and devices within the fabrication area shall comply with NFPA 70. The requirements for hazardous locations need not be applied where the average air change is not less than four times that set forth in Section 415.11.1.6 and where the number of air changes at any location is not less than three times that required by Section 415.11.1.6. The use of recirculated air shall be permitted.
415.11.1.8.1 Workstations. | Workstations shall not be energized without adequate exhaust ventilation. See Section 415.11.1.6 for workstation exhaust ventilation requirements. | 415.11.1.8.1 Workstations. | Workstations shall not be energized without adequate exhaust ventilation. See Section 415.11.1.6 for workstation exhaust ventilation requirements.
415.11.2 Corridors. | Corridors shall comply with Chapter 10 and shall be separated from fabrication areas as specified in Section 415.11.1.2. Corridors shall not contain HPM and shall not be used for transporting such materials except through closed piping systems as provided in Section 415.11.6. Exception: Where existing fabrication areas are altered or modified, HPM is allowed to be transported in existing corridors, subject to the following conditions: 1. Nonproduction HPM is allowed to be transported in corridors if utilized for maintenance, lab work and testing. 2. Corridors. Corridors adjacent to the fabrication area where the alteration work is to be done shall comply with Section 1020 for a length determined as follows: 2.1. The length of the common wall of the corridor and the fabrication area; and 2.2. For the distance along the corridor to the point of entry of HPM into the corridor serving that fabrication area. 3. Emergency alarm system. There shall be an emergency telephone system, a local manual alarm station or other approved alarm-initiating device within corridors at not more than 150-foot (45 720 mm) intervals and at each exit and doorway. The signal shall be relayed to an approved central, proprietary or remote station service or the emergency control station and shall also initiate a locale audible alarm. 4. Pass-throughs. Self-closing doors having a fire-protection rating of not less than 1 hour shall separate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors, and protected by an approved automatic fire-extinguishing system. | 415.11.2 Corridors. | Corridors shall comply with Chapter 10 and shall be separated from fabrication areas as specified in Section 415.11.1.2. Corridors shall not contain HPM and shall not be used for transporting such materials except through closed piping systems as provided in Section 415.11.7.4. Exception: Where existing fabrication areas are altered or modified, HPM is allowed to be transported in existing corridors, subject to the following conditions: 1. Nonproduction HPM is allowed to be transported in corridors if utilized for maintenance, lab work and testing. 2. Where existing fabrication areas are altered or modified, HPM is allowed to be transported in existing cor-ridors, subject to the following conditions: 2.1. Corridors. Corridors adjacent to the fabrication area where the alteration work is to be done shall comply with Section 1020 for a length determined as follows: 2.1.1. The length of the common wall of the corridor and the fabrication area; and 2.1.2. For the distance along the corridor to the point of entry of HPM into the corridor serving that fabrication area. 2.2. Emergency alarm system. There shall be an emergency telephone system, a local manual alarm sta-tion or other approved alarm-initiating device within corridors at not more than 150-foot (45 720 mm) intervals and at each exit and doorway. The signal shall be relayed to an approved central, pro-prietary or remote station service or the emergency control station and shall initiate a local audible alarm. 2.3. Pass-throughs. Self-closing doors having a fire protection rating of not less than 1 hour shall sepa-rate pass-throughs from existing corridors. Pass-throughs shall be constructed as required for the corridors and protected by an approved automatic sprinkler system.
415.11.3 Service corridors. | Service corridors within a Group H-5 occupancy shall comply with Sections 415.11.3.1 through 415.11.3.4. | 415.11.3 Service corridors. | Service corridors within a Group H-5 occupancy shall comply with Sections 415.11.3.1 through 415.11.3.4.
415.11.3.1 Use conditions. | Service corridors shall be separated from exit access corridors as required by Section 415.11.1.2. Service corridors shall not be used as a required exit access corridor. | 415.11.3.1 Use conditions. | Service corridors shall be separated from corridors as required by Section 415.11.1.2. Service corridors shall not be used as a required corridor.
415.11.3.2 Mechanical ventilation. | Service corridors shall be mechanically ventilated as required by Section 415.11.1.6 or at not less than six air changes per hour. | 415.11.3.2 Mechanical ventilation. | Service corridors shall be mechanically ventilated as required by Section 415.11.1.6 or at not less than six air changes per hour.
415.11.3.3 Means of egress. | The distance of travel from any point in a service corridor to an exit, exit access corridor or door into a fabrication area shall be not greater than 75 feet (22 860 mm). Dead ends shall be not greater than 4 feet (1219 mm) in length. There shall be not less than two exits, and not more than one-half of the required means of egress shall require travel into a fabrication area. Doors from service corridors shall swing in the direction of egress travel and shall be self-closing. | 415.11.3.3 Means of egress. | The distance of travel from any point in a service corridor to an exit, exit access corridor or door into a fabrication area shall be not greater than 75 feet (22 860 mm). Dead ends shall be not greater than 4 feet (1219 mm) in length. There shall be not less than two exits, and not more than one-half of the required means of egress shall require travel into a fabrication area. Doors from service corridors shall swing in the direction of egress travel and shall be self-closing.
415.11.3.4 Minimum width. | The clear width of a service corridor shall be not less than 5 feet (1524 mm), or 33 inches (838 mm) wider than the widest cart or truck used in the service corridor, whichever is greater. | 415.11.3.4 Minimum width. | The clear width of a service corridor shall be not less than 5 feet (1524 mm), or 33 inches (838 mm) wider than the widest cart or truck used in the service corridor, whichever is greater.
415.9.1.2.1 Tanks. | Storage tanks shall be approved tanks conforming to the requirements of the New York City Fire Code.
415.9.1.3 Suppression. | Group H shall be equipped throughout with an approved automatic sprinkler system, installed in accordance with Section 903.
415.9.2 Liquefied petroleum gas-distribution facilities. | The construction and installation of liquefied petroleum gas facilities shall be in accordance with the requirements of this code, the New York City Fire Code, the New York City Mechanical Code, the New York City Fuel Gas Code and NFPA 58.
415.10.4 Separation-highly toxic solids and liquids. | Highly toxic solids and liquids not stored in approved hazardous materials storage cabinets shall be isolated from other hazardous materials storage by not less than 1-hour fire-resistance rating.
415.11.3.5 Emergency alarm system. | Emergency alarm systems shall be provided in accordance with this section and Sections 415.5.1 and 415.5.2. The maximum allowable quantity per control area provisions shall not apply to emergency alarm systems required for HPM.
415.11.3.5.1 Service corridors. | An emergency alarm system shall be provided in service corridors, with no fewer than one alarm device in each service corridor.
415.11.3.5.2 Exit access corridors and exit enclosures. | Emergency alarms for exit access corridors and exit enclosures shall comply with Section 415.5.2.
415.11.3.5.3 Liquid storage rooms, HPM rooms and gas rooms. | Emergency alarms for liquid storage rooms, HPM rooms and gas rooms shall comply with Section 415.5.1.
415.11.3.5.4 Alarm-initiating devices. | An approved emergency telephone system, local alarm manual pull stations, or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.
415.11.3.5.5 Alarm signals. | Activation of the emergency alarm system shall sound a local alarm and transmit a signal to the emergency control station.
415.11.4 Storage of hazardous production materials. | Storage of HPM in fabrication areas shall be within approved or listed storage cabinets or gas cabinets or within a workstation. The storage of HPM in quantities greater than those listed in the New York City Fire Code shall be in liquid storage rooms, HPM rooms or gas rooms as appropriate for the materials stored. The storage of other hazardous materials shall be in accordance with other applicable provisions of this code and the New York City Fire Code.
415.11.5 HPM rooms, gas rooms, liquid storage room construction. | HPM rooms, gas rooms and liquid shall be constructed in accordance with Sections 415.11.5.1 through 415.11.5.9.
415.11.5.1 HPM rooms and gas rooms. | HPM rooms and gas rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours where the area is 300 square feet (27.9 m2) or more and not less than 1 hour where the area is less than 300 square feet (27.9 m2).
415.11.5.2 Liquid storage rooms. | Liquid storage rooms shall be constructed in accordance with the fol­lowing requirements:
416.1 General. | The provisions of this section shall apply to the construction, installation and use of buildings and structures, or parts thereof, for the application of flammable paints, varnishes and lacquers or other flammable materials or mixtures or compounds used for painting, varnishing, staining or similar purposes. Such construction and equipment shall comply with the New York City Fire Code. | 416.1 General. | The provisions of this section shall apply to the construction, installation and use of buildings and structures, or parts thereof, for the spray application of flammable finishes. Operations and equipment shall comply with the International Fire Code.
4. Rooms used for the storage of Class I flamma­ble liquids shall not be located in a basement.
416.2 Spray rooms. | Spray rooms shall be enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Floors shall be waterproofed and drained in an approved manner. | 416.2 Spray rooms. | Spray rooms shall be enclosed with not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Floors shall be waterproofed and drained in an approved manner.
415.11.5.3 Floors. | Except for surfacing, floors of HPM rooms and liquid storage rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials.
415.11.5.4 Location. | Where HPM rooms, liquid storage rooms and gas rooms are provided, they shall have no fewer than one exterior wall and such wall shall be not less than 30 feet (9144 mm) from tax-lot lines, including tax-lot lines adjacent to public ways.
415.11.5.5 Explosion control. | Explosion control shall be provided where required by Section 414.5.1.
415.11.5.6 Exits. | Where two exits are required from HPM rooms, liquid storage rooms and gas rooms, one shall be directly to the outside of the building.
416.3 Spraying spaces. | Spraying spaces shall be ventilated with an exhaust system capable of at least six air changes per hour to prevent the accumulation of flammable mist or vapors in accordance with the New York City Mechanical Code. Where such spaces are not separately enclosed, noncombustible spray curtains shall be provided to restrict the spread of flammable vapors. | 416.3 Spraying spaces. | Spraying spaces shall be ventilated with an exhaust system to prevent the accumulation of flammable mist or vapors in accordance with the International Mechanical Code. Where such spaces are not separately enclosed, noncombustible spray curtains shall be provided to restrict the spread of flammable vapors.
415.11.5.7 Doors. | Doors in a fire barrier wall, including doors to corridors, shall be self-closing fire door assemblies having a fire-protection rating of not less than 3/4 hour.
416.3.1 Surfaces. | The interior surfaces of spraying spaces shall be smooth and continuous without edges; shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning; and shall be so designed to confine residues within the spraying space. Aluminum shall not be used. | 416.3.1 Surfaces. | The interior surfaces of spraying spaces shall be smooth; shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning; and shall be so designed to confine residues within the spraying space. Aluminum shall not be used.
415.11.5.8 Ventilation. | Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less than 1 cubic foot per minute per square foot (0.044 L/s/m2) of floor area or six air changes per hour.
416.4 Spray booths. | Spray booths shall be designed, constructed and operated in accordance with the New York City Fire Code. | 416.4 Spray booths. | Spray booths shall be designed, constructed and operated in accordance with the International Fire Code.
415.11.5.9 Emergency alarm system. | An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms.
416.5 Fire protection. | An automatic sprinkler system or fire-extinguishing system shall be provided in all spray, dip and immersing spaces and storage rooms and shall be installed in accordance with Chapter 9. | 416.5 Fire protection. | An automatic sprinkler system or fire-extinguishing system shall be provided in all spray rooms and spray booths, and shall be installed in accordance with Chapter 9.
415.11.6 Piping and tubing. | Hazardous production materials piping and tubing shall comply with this section and ASME B31.3.
417.1 General. | A drying room or dry kiln installed within a building shall be constructed entirely of approved noncombustible materials or assemblies of such materials regulated by the approved rules or as required in the general and specific sections of this chapter for special occupancies, where applicable to the general requirements of Chapter 28 of this code, and in accordance with the New York City Fire Code. | 417.1 General. | A drying room or dry kiln installed within a building shall be constructed entirely of approved noncombustible materials or assemblies of such materials regulated by the approved rules or as required in the general and specific sections of this chapter for special occupancies and where applicable to the general requirements of the International Mechanical Code.
415.11.6.1 HPM having a health-hazard ranking of 3 or 4. | Systems supplying HPM liquids or gases having a health-hazard ranking of 3 or 4 shall be welded throughout, except for connections, to the systems that are within a ventilated enclosure if the material is a gas, or an approved method of drainage or containment is provided for the connections if the material is a liquid.
417.2 Piping clearance. | Overhead heating pipes shall have a clearance of not less than 2 inches (51 mm) from combustible contents in the dryer. | 417.2 Piping clearance. | Overhead heating pipes shall have a clearance of not less than 2 inches (51 mm) from combustible contents in the dryer.
415.11.6.2 Location in service corridors. | Hazardous production materials supply piping or tubing in service corridors shall be exposed to view.
417.3 Insulation. | Where the operating temperature of the dryer is 175°F (79°C) or more, metal enclosures shall be insulated from adjacent combustible materials by not less than 12 inches (305 mm) of airspace, or the metal walls shall be lined with 1/4-inch (6.4 mm) insulating mill board or other approved equivalent insulation. | 417.3 Insulation. | Where the operating temperature of the dryer is 175°F (79°C) or more, metal enclosures shall be insulated from adjacent combustible materials by not less than 12 inches (305 mm) of airspace, or the metal walls shall be lined with 1/4-inch (6.4 mm) insulating mill board or other approved equivalent insulation.
415.11.6.3 Excess flow control. | Where HPM gases or liquids are carried in pressurized piping above 15 pounds per square inch gauge (psig) (103.4 kPa), excess flow control shall be provided. Where the piping originates from within a liquid storage room, HPM room or gas room, the excess flow control shall be located within the liquid storage room, HPM room or gas room. Where the piping originates from a bulk source, the excess flow control shall be located as close to the bulk source as practical.
417.4 Fire protection. | Drying rooms designed for high-hazard materials and processes, including special occupancies as provided for in this chapter, shall be protected by an approved automatic fire-extinguishing system complying with the provisions of Chapter 9. | 417.4 Fire protection. | Drying rooms designed for high-hazard materials and processes, including special occupancies as provided for in Chapter 4, shall be protected by an approved automatic fire-extinguishing system complying with the provisions of Chapter 9.
415.11.6.4 Installations in corridors and above other occupancies. | The installation of HPM piping and tubing within the space defined by the walls of exit access corridors and the floor or roof above, or in concealed spaces above other occupancies, shall be in accordance with Sections 415.11.6.1 through 415.11.6.3 and the following conditions: 1. Automatic sprinklers shall be installed within the space unless the space is less than 6 inches (152 mm) in the least dimension. 2. Ventilation not less than six air changes per hour shall be provided. The space shall not be used to convey air from any other area. 3. Where the piping or tubing is used to transport HPM liquids, a receptor shall be installed below such piping or tubing. The receptor shall be designed to collect any discharge or leakage and drain it to an approved location. The 1-hour enclosure shall not be used as part of the receptor. 4. HPM supply piping and tubing and nonmetallic waste lines shall be separated from the corridor and from occupancies other than Group H-5 by fire barriers or by an approved method or assembly that has a fire-resistance rating of not less than 1 hour. Access openings into the enclosure shall be protected by approved fire-resistance-rated assemblies. 5. Readily accessible manual or automatic remotely activated fail-safe emergency shutoff valves shall be installed on piping and tubing other than waste lines at the following locations: 5.1. At branch connections into the fabrication area. 5.2. At entries into exit access corridors. Exception: Transverse crossings of the corridors by supply piping that is enclosed within a ferrous pipe or tube for the width of the corridor need not comply with Items 1 through 5.
418.1 Building features. | Manufacturing of organic coatings shall be done only in buildings that do not have pits or basements and shall comply with the New York City Fire Code. Such buildings shall be protected by an approved automatic sprinkler system in accordance with Chapter 9 of this code. | 418.1 Building features. | Manufacturing of organic coatings shall be done only in buildings that do not have pits or basements.
415.11.6.5 Identification. | Piping, tubing and HPM waste lines shall be identified in accordance with ANSI A13.1 to indicate the material being transported.
418.2 Location. | Organic coating manufacturing operations and operations incidental to or connected therewith shall not be located in buildings having other occupancies. | 418.2 Location. | Organic coating manufacturing operations and operations incidental to or connected therewith shall not be located in buildings having other occupancies.
415.11.7 Continuous gas detection systems. | A continuous gas detection system shall be provided for HPM gases where the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases in accordance with Sections 415.11.7.1 and 415.11.7.2.
418.3 Process mills. | Mills operating with close clearances and that process flammable and heat-sensitive materials, such as nitrocellulose, shall be classified as Group H-1 occupancy. | 418.3 Process mills. | Mills operating with close clearances and that process flammable and heat-sensitive materials, such as nitrocellulose, shall be located in a detached building or noncombustible structure.
415.11.7.1 Where required. | A continuous gas detection system shall be provided in the areas identified in Sections 415.11.7.1.1 through 415.11.7.1.4.
418.4 Tank storage. | Storage areas for flammable and combustible liquid tanks inside of structures shall be located at or above grade and shall be separated from the processing area by not less than 2-hour fire-resistance-rated fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. | 418.4 Tank storage. | Storage areas for flammable and combustible liquid tanks inside of structures shall be located at or above grade and shall be separated from the processing area by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
415.11.7.1.1 Fabrication areas. | A continuous gas detection system shall be provided in fabrication areas where gas is used in the fabrication area.
418.5 Nitrocellulose storage. | Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed with no less than 2-hour fire-resistance-rated fire barriers. | 418.5 Nitrocellulose storage. | Nitrocellulose storage shall be located on a detached pad or in a separate structure or a room enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
415.11.7.1.2 HPM rooms. | A continuous gas detection system shall be provided in HPM rooms where gas is used in the room.
418.6 Finished products. | Storage rooms for finished products that are flammable or combustible liquids shall be separated from the processing area by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both having a fire-resistance rating of at least 2 hours, and openings in the walls shall be protected with approved opening protectives. | 418.6 Finished products. | Storage rooms for finished products that are flammable or combustible liquids shall be separated from the processing area by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
415.11.7.1.3 Gas cabinets, exhausted enclosures and gas rooms. | A continuous gas detection system shall be provided in gas cabinets and exhausted enclosures. A continuous gas detection system shall be provided in gas rooms where gases are not located in gas cabinets or exhausted enclosures.
415.11.7.1.4 Corridors. | Where gases are transported in piping placed within the space defined by the walls of a corridor and the floor or roof above the corridor, a continuous gas detection system shall be provided where piping is located and in the corridor. Exception: A continuous gas detection system is not required for occasional transverse crossings of the corridors by supply piping that is enclosed in a ferrous pipe or tube for the width of the corridor.
420.1 General. | Occupancies in Groups I-1, R-1, R-2 and R-3 shall comply with the provisions of Sections 420.1 through 420.6 and other applicable provisions of this code. | 420.1 General. | Occupancies in Groups I-1, R-1, R-2, R-3 and R-4 shall comply with the provisions of Sections 420.1 through 420.11 and other applicable provisions of this code.
415.11.7.2 Gas detection system operation. | The continuous gas detection system shall be capable of monitoring the room, area or equipment in which the gas is located at or below all the following gas concentrations:
420.2 Separation walls. | Walls separating dwelling units in the same building, walls separating sleeping units in the same building and walls separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as fire barriers constructed in accordance with Section 707 and shall be at least 1-hour fire-resistance-rated. | 420.2 Separation walls. | Walls separating dwelling units in the same building, walls separating sleeping units in the same building and walls separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as fire partitions in accordance with Section 708.
415.11.7.2.1 Alarms. | The gas detection system shall initiate a local alarm and transmit a signal to the emergency control station when a short-term hazard condition is detected. The alarm shall be both visual and audible and shall provide warning both inside and outside the area where the gas is detected. The audible alarm shall be distinct from all other alarms.
420.3 Horizontal separation. | Floor assemblies separating dwelling units in the same buildings, floor assemblies separating sleeping units in the same building and floor assemblies separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as horizontal assemblies in accordance with Section 711. | 420.3 Horizontal separation. | Floor assemblies separating dwelling units in the same buildings, floor assemblies separating sleeping units in the same building and floor assemblies separating dwelling or sleeping units from other occupancies contiguous to them in the same building shall be constructed as horizontal assemblies in accordance with Section 711.
415.11.7.2.2 Shutoff of gas supply. | The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for which gas is detected when a short-term hazard condition is detected. Automatic closure of shutoff valves shall comply with the following: 1. Where the gas detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close. 2. Where the gas detection sampling point initiating the gas detection system alarm is within a room and compressed gas containers are not in gas cabinets or an exhausted enclosure, the shutoff valves on all gas lines for the specific gas detected shall automatically close. 3. Where the gas detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve supplying the manifold for the compressed gas container of the specific gas detected shall automatically close. Exception: Where the gas detection sampling point initiating the gas detection system alarm is at the use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve for the branch line located in the piping distribution manifold enclosure shall automatically close.
415.11.8 Manual fire alarm system. | An approved manual fire alarm system shall be provided throughout buildings containing Group H-5. Activation of the alarm system shall initiate a local alarm and transmit a signal to the emergency control station. The fire alarm system shall be designed and installed in accordance with Section 907.
415.11.9 Emergency control station. | An emergency control station shall be provided in accordance with Sections 415.11.9.1 through 415.11.9.3.
415.11.9.1 Location. | The emergency control station shall be located on the premises at an approved location outside the fabrication area.
415.11.9.2 Staffing. | Trained personnel shall continuously staff the emergency control station.
415.11.9.3 Signals. | The emergency control station shall monitor signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detection systems shall include the following systems, whether required by this code or the New York City Construction Codes or voluntarily installed:
415.11.10 Emergency power system. | An emergency power system shall be provided in Group H-5 occupancies in accordance with Section 2702. The emergency power system shall supply power automatically to the electrical systems specified in Section 415.11.10.1 when the normal electrical supply system is interrupted.
415.11.10.1 Required electrical systems. | Emergency power shall be provided for electrically operated equipment and connected control circuits for the following systems:
415.11.10.2 Exhaust ventilation systems. | Exhaust ventilation systems are allowed to be designed to operate at not less than one-half the normal fan speed on the emergency power system where it is demonstrated that the level of exhaust will maintain a safe atmosphere.
415.11.11 Automatic sprinkler system protection in exhaust ducts for HPM. | An approved automatic fire sprinkler system shall be provided in exhaust ducts conveying vapors, fumes, mists or dusts generated from HPM in accordance with the New York City Mechanical Code and Sections 415.11.11.1 through 415.11.11.3 of this code.
415.11.11.1 Metallic and noncombustible nonmetallic exhaust ducts. | An approved automatic sprinkler system shall be provided in metallic and noncombustible nonmetallic exhaust ducts where all of the following conditions apply:
415.11.11.2 Combustible nonmetallic exhaust ducts. | Automatic fire sprinkler system protection shall be provided in combustible nonmetallic exhaust ducts where the largest cross-sectional diameter of the duct is equal to or greater than 10 inches (254 mm). Exception: Ducts need not be provided with automatic sprinkler protection as follows: 1. Ducts listed or approved for applications without automatic sprinkler system protection. 2. Ducts not more than 12 feet (3658 mm) in length installed below ceiling level.
421.1 General. | Where required by the New York City Fire Code, hydrogen fuel gas rooms shall be designed and constructed in accordance with Sections 421.1 through 421.7 of this code. | 421.1 General. | Where required by the International Fire Code, hydrogen fuel gas rooms shall be designed and constructed in accordance with Sections 421.1 through 421.7.
415.11.11.3 Automatic sprinkler locations. | Sprinkler systems shall be installed at 12-foot (3658 mm) intervals in horizontal ducts and at changes in direction. In vertical ducts, sprinklers shall be installed at the top and at alternate floor levels.
421.2 Location. | Hydrogen fuel gas rooms shall not be located below grade. | 421.2 Location. | Hydrogen fuel gas rooms shall not be located below grade.
421.3 Design and construction. | Hydrogen fuel gas rooms not classified as Occupancy Group H shall be separated from other areas of the building in accordance with Section 509.1. Such separation shall have a fire-resistance rating of not less than 2 hours for all occupancy groups. | 421.3 Design and construction. | Hydrogen fuel gas rooms not classified as Group H shall be separated from other areas of the building in accordance with Section 509.1.
421.3.1 Pressure control. | Hydrogen fuel gas rooms shall be provided with a ventilation system designed to maintain the room at a negative pressure in relation to surrounding area. | 421.3.1 Pressure control. | Hydrogen fuel gas rooms shall be provided with a ventilation system designed to maintain the room at a negative pressure in relation to surrounding rooms and spaces.
416.2.1 Surfaces. | The interior surfaces of spray rooms shall be smooth and shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning, and shall be so designed to confine residues within the room. Aluminum shall not be used.
421.3.2 Windows. | Operable windows in interior walls shall not be permitted. Fixed windows shall be permitted where in accordance with Section 716. | 421.3.2 Windows. | Operable windows in interior walls shall not be permitted. Fixed windows shall be permitted where in accordance with Section 716.
416.2.2 Ventilation. | Mechanical ventilation and interlocks with the spraying operation shall be in accordance with the New York City Mechanical Code.
421.4 Exhaust ventilation. | Hydrogen fuel gas rooms shall be separately ventilated and provided with mechanical exhaust ventilation in accordance with the applicable provisions of NFPA 2. | 421.4 Exhaust ventilation. | Hydrogen fuel gas rooms shall be provided with mechanical exhaust ventilation in accordance with the applicable provisions of Section 502.16.1 of the International Mechanical Code.
421.5 Gas detection system. | Hydrogen fuel gas rooms shall be provided with a gas detection system that complies with Sections 421.5.1, 421.5.2, and 918. | 421.5 Gas detection system. | Hydrogen fuel gas rooms shall be provided with a gas detection system that complies with Sections 421.5.1, 421.5.2, and 916.
421.5.1 System activation. | Activation of a gas detection alarm shall initiate the following notification and action: | 421.5.1 System activation. | Activation of a gas detection alarm shall result in both of the following:
421.5.2 Failure of the gas detection system. | Failure of the gas detection system shall automatically discontinue hydrogen generation, activate the mechanical exhaust ventilation system and transmit a supervisory signal to the control panel and a central station. | 421.5.2 Failure of the gas detection system. | Failure of the gas detection system shall automatically activate the mechanical exhaust ventilation system, stop hydrogen generation, and cause a trouble signal to sound at an approved location.
421.6 Explosion control. | Explosion control shall be provided where required by Section 414.5.1. | 421.6 Explosion control. | Explosion control shall be provided where required by Section 414.5.1.
422.1 General. | Ambulatory care facilities shall comply with the provisions of Sections 422.1 through 422.5 and other applicable provisions of this code. | 422.1 General. | Occupancies classified as ambulatory care facilities shall comply with the provisions of Sections 422.1 through 422.6 and other applicable provisions of this code.
422.2 Separation. | Ambulatory care facilities, where there is the potential for four or more care recipients who will be incapable of self-preservation at any time, whether rendered incapable by staff or staff accepted responsibility for a care recipient already incapable, shall be separated from adjacent spaces, corridors or tenants with a fire partition installed in accordance with Section 708. | 422.2 Separation. | Ambulatory care facilities where the potential for four or more care recipients are to be incapable of self-preservation at any time shall be separated from adjacent spaces, corridors or tenants with a fire partition installed in accordance with Section 708.
422.3 Smoke compartments. | Where the aggregate area of one or more ambulatory care facilities is greater than 10,000 square feet (929 m2) on one story, the story shall be provided with a smoke barrier to subdivide the story into no fewer than two smoke compartments. The area of any one such smoke compartment shall be not greater than 22,500 square feet (2092 m2). The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm). The smoke barrier shall be installed in accordance with Section 709 with the exception that smoke barriers shall be continuous from outside wall to an outside wall, a floor to a floor, or from a smoke barrier to a smoke barrier or a combination thereof. | 422.3 Smoke compartments. | Where the aggregate area of one or more ambulatory care facilities is greater than 10,000 square feet (929 m2) on one story, the story shall be provided with a smoke barrier to subdivide the story into not fewer than two smoke compartments. The area of any one such smoke compartment shall be not greater than 22,500 square feet (2092 m2). The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm). The smoke barrier shall be installed in accordance with Section 709 with the exception that smoke barriers shall be continuous from outside wall to an outside wall, a floor to a floor, or from a smoke barrier to a smoke barrier or a combination thereof.
422.3.1 Means of egress. | Where ambulatory care facilities require smoke compartmentation in accordance with Section 422.3 of this code, the fire protection and emergency preparedness plans shall comply with the applicable provisions of the New York City Fire Code and shall be in accordance with Section 1001.4 of this code. | 422.3.1 Means of egress. | Where ambulatory care facilities require smoke compartmentation in accordance with Section 422.3, the fire safety evacuation plans provided in accordance with Section 1002.2 shall identify the building components necessary to support a defend-in-place emergency response in accordance with Sections 403 and 404 of the International Fire Code.
422.3.2 Refuge area. | Not less than 30 net square feet (2.8 m2) for each nonambulatory care recipient shall be provided within the aggregate area of corridors, care recipient rooms, treatment rooms, lounge or dining areas and other low-hazard areas within each smoke compartment. Each occupant of an ambulatory care facility shall be provided with access to a refuge area without passing through or utilizing adjacent tenant spaces. | 422.3.2 Refuge area. | Not less than 30 net square feet (2.8 m2) for each nonambulatory care recipient shall be provided within the aggregate area of corridors, care recipient rooms, treatment rooms, lounge or dining areas and other low-hazard areas within each smoke compartment. Each occupant of an ambulatory care facility shall be provided with access to a refuge area without passing through or utilizing adjacent tenant spaces.
422.3.3 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated. | 422.3.3 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated.
422.4 Automatic sprinkler systems. | Automatic sprinkler systems shall be provided for ambulatory care facilities in accordance with Section 903.2.2. | 422.4 Automatic sprinkler systems. | Automatic sprinkler systems shall be provided for ambulatory care facilities in accordance with Section 903.2.2.
422.5 Fire alarm systems. | A fire alarm system shall be provided for ambulatory care facilities in accordance with Section 907.2.2. | 422.5 Fire alarm systems. | A fire alarm system shall be provided for ambulatory care facilities in accordance with Section 907.2.2.
423.1 General. | In addition to other applicable requirements in this code, storm shelters shall be constructed in accordance with ICC 500. | 423.1 General. | This section applies to the construction of storm shelters constructed as separate detached buildings or constructed as rooms or spaces within buildings for the purpose of providing protection from storms that produce high winds, such as tornadoes and hurricanes, during the storm. This section specifies where storm shelters are required and provides requirements for the design and construction of storm shelters. Design of facilities for use as emergency shelters after the storm are outside the scope of ICC 500 and shall comply with Table 1604.5 as a Risk Category IV Structure.
420.4 Reserved.
420.5 Automatic sprinkler system. | Group R occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.8. Group I-1 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6. Quick response or residential automatic sprinklers shall be installed in accordance with Section 903.3.2.
420.6 Fire alarm systems and smoke alarms. | Fire alarm systems and smoke alarms shall be provided in Group I-1, R-1, and R-2 occupancies in accordance with Sections 907.2.6, 907.2.8 and 907.2.9, respectively. Single or multiple station smoke alarms shall be provided in Groups I-1, R-2, and R-3 in accordance with Section 907.2.11.
421.1.1 Scope. | Hydrogen fuel gas rooms shall be separately ventilated, fully enclosed, and shall contain all equipment and piping for the immediate on-premises use of hydrogen in indoor fuel cells or other energy production process, and incidental indoor storage of gaseous hydrogen in accordance with the New York City Fire Code. A hydrogen fuel gas room shall not be used to house production or dispensing of hydrogen motor fuel.
421.1.2 Storage. | Hydrogen fuel gas rooms shall not be used for storage of gaseous hydrogen in quantities exceeding the maximum allowable quantity per control area set forth in Table 307.1(1). Where approved by the Fire Department, such hydrogen fuel gas rooms permitted to store greater quantities shall be classified as Occupancy Group H. |  |  |  | See BC03 Tables&Figures
421.1.3 Definitions. | The following term is defined in Chapter 2:
424.2 Materials. | Children’s play structures shall be constructed of noncombustible materials or of combustible materials that comply with the following: | 424.2 Materials. | Play structures shall be constructed of noncombustible materials or of combustible materials that comply with the following:
424.3 Fire protection. | Children’s play structures shall be provided with the same level of approved fire protection system required for other structures in the same occupancy. | 424.3 Fire protection. | Play structures shall be provided with the same level of approved fire suppression and detection devices required for other structures in the same occupancy.
424.4 Separation. | Children’s play structures shall have a horizontal separation from building walls, partitions and from elements of the means of egress of not less than 5 feet (1524 mm). Children’s playground structures shall have a horizontal separation from other children’s play structures of not less than 20 feet (6090 mm). | 424.4 Separation. | Play structures shall have a horizontal separation from building walls, partitions and from elements of the means of egress of not less than 5 feet (1524 mm). Play structures shall have a horizontal separation from other play structures of not less than 20 feet (6090 mm).
424.5 Area limits. | Children’s play structures shall be not greater than 300 square feet (28 m2) in area. | 424.5 Area limits. | Play structures shall be not greater than 600 square feet (56 m2) in area, unless a special investigation, acceptable to the building official, has demonstrated adequate fire safety.
425.1 Hyperbaric facilities. | Hyperbaric facilities shall meet the requirements contained in Chapter 14 of NFPA 99. | 425.1 Hyperbaric facilities. | Hyperbaric facilities shall meet the requirements contained in Chapter 14 of NFPA 99.
426.1.1 Type of construction and height exceptions. | Buildings shall be constructed in compliance with the height, number of stories and area limitations specified in Sections 504 and 506; except that where erected of Type I or II construction, the heights and areas of grain elevators and similar structures shall be unlimited, and where of Type IV construction, the maximum building height shall be 65 feet (19 812 mm) and except further that, in isolated areas, the maximum building height of Type IV structures shall be increased to 85 feet (25 908 mm). | 426.1.1 Type of construction and height exceptions. | Buildings shall be constructed in compliance with the height, number of stories and area limitations specified in Sections 504 and 506; except that where erected of Type I or II construction, the heights and areas of grain elevators and similar structures shall be unlimited, and where of Type IV construction, the maximum building height shall be 65 feet (19 812 mm) and except further that, in isolated areas, the maximum building height of Type IV structures shall be increased to 85 feet (25 908 mm).
421.7 Emergency power. | Mechanical exhaust ventilation and gas detection systems shall be provided with an emergency power system in accordance with Section 2702.
426.1.2 Grinding rooms. | Every room or space occupied for grinding or other operations that produce combustible dusts in such a manner that the room or space is classified as a Group H-2 occupancy shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating of the enclosure shall be not less than 2 hours where the area is not more than 3,000 square feet (279 m2), and not less than 4 hours where the area is greater than 3,000 square feet (279 m2). | 426.1.2 Grinding rooms. | Every room or space occupied for grinding or other operations that produce combustible dusts in such a manner that the room or space is classified as a Group H-2 occupancy shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating of the enclosure shall be not less than 2 hours where the area is not more than 3,000 square feet (279 m2), and not less than 4 hours where the area is greater than 3,000 square feet (279 m2).
426.1.3 Conveyors. | Conveyors, chutes, piping and similar equipment passing through the enclosures of rooms or spaces shall be constructed dirt tight and vapor tight, and be of approved noncombustible materials complying with Chapter 30. | 426.1.3 Conveyors. | Conveyors, chutes, piping and similar equipment passing through the enclosures of rooms or spaces shall be constructed dirt tight and vapor tight, and be of approved noncombustible materials complying with Chapter 30.
426.1.4 Explosion control. | Explosion control shall be provided as specified in the New York City Fire Code, or spaces shall be equipped with the equivalent mechanical ventilation complying with the New York City Mechanical Code. | 426.1.4 Explosion control. | Explosion control shall be provided as specified in the International Fire Code, or spaces shall be equipped with the equivalent mechanical ventilation complying with the International Mechanical Code.
426.1.5 Grain elevators. | Grain elevators, malt houses and buildings for similar occupancies shall not be located within 30 feet (9144 mm) of interior lot lines or structures on the same lot, except where erected along a railroad right-of-way. | 426.1.5 Grain elevators. | Grain elevators, malt houses and buildings for similar occupancies shall not be located within 30 feet (9144 mm) of interior lot lines or structures on the same lot, except where erected along a railroad right-of-way.
426.1.6 Coal pockets. | Coal pockets located less than 30 feet (9144 mm) from interior lot lines or from structures on the same lot shall be constructed of not less than Type IB construction. Where more than 30 feet (9144 mm) from interior lot lines, or where erected along a railroad right-of-way, the minimum type of construction of such structures not more than 65 feet (19 812 mm) in building height shall be Type IV. | 426.1.6 Coal pockets. | Coal pockets located less than 30 feet (9144 mm) from interior lot lines or from structures on the same lot shall be constructed of not less than Type IB construction. Where more than 30 feet (9144 mm) from interior lot lines, or where erected along a railroad right-of-way, the minimum type of construction of such structures not more than 65 feet (19 812 mm) in building height shall be Type IV.
423.1.1 Scope. | This section applies to the construction of storm shelters constructed as separate detached buildings or constructed as safe rooms within buildings for the purpose of providing safe refuge from storms that produce high winds, such as tornados and hurricanes. Such structures shall be designated to be hurricane shelters, tornado shelters, or combined hurricane and tornado shelters.
423.2 Definitions specific to this section. | The following terms shall, for the purposes of this section, have the meanings shown herein:
424.1 Children’s play structures. | Children’s play structures installed inside all occupancies covered by this code that exceed 10 feet (3048 mm) in height and 150 square feet (14 m2) in area shall comply with Sections 424.2 through 424.5.
426.1 Combustible dusts, grain processing and storage. | The provisions of Sections 426.1.1 through 426.1.7 shall apply to buildings in which materials that produce combustible dusts are stored or handled. Buildings that store or handle combustible dusts shall comply with the applicable provisions of NFPA 61, NFPA 69, NFPA 85, NFPA 120, NFPA 484, NFPA 654, NFPA 655 and NFPA 664 and the New York City Fire Code.
426.1.7 Tire rebuilding. | Buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operation by a 1-hour fire barrier. Exception: Buffing operations are not required to be separated where all of the following conditions are met: 1. Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action; 2. Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/5 ) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity; and 3. The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow. | 426.1.7 Tire rebuilding. | Buffing operations shall be located in a room separated from the remainder of the building housing the tire rebuilding or tire recapping operation by a 1-hour fire barrier. Exception: Buffing operations are not required to be separated where all of the following conditions are met: 1. Buffing operations are equipped with an approved continuous automatic water-spray system directed at the point of cutting action. 2. Buffing machines are connected to particle-collecting systems providing a minimum air movement of 1,500 cubic feet per minute (cfm) (0.71 m3/s) in volume and 4,500 feet per minute (fpm) (23 m/s) in-line velocity. 3. The collecting system shall discharge the rubber particles to an approved outdoor noncombustible or fire-resistant container, which is emptied at frequent intervals to prevent overflow.
427.1 General. | The provisions of this section shall govern the design, construction and chemical quantity limitations of buildings and portions thereof occupied or designed to be occupied as a nonproduction laboratory. Nonproduction laboratories shall be classified into occupancy groups in accordance with Section 427.5. The provisions of this section shall not apply to production laboratories classified in Occupancy Group F or H. | 427.1 General. | Medical gases at health care-related facilities intended for patient or veterinary care shall comply with Sections 427.2 through 427.2.3 in addition to requirements of Chapter 53 of the International Fire Code.
427.2 Standards. | Except as otherwise provided in this section, nonproduction laboratories shall meet the design, construction and chemical quantity limitation requirements for laboratory unit fire hazard Class D, as set forth in NFPA 45 as modified by the New York City Fire Code, and the New York City Mechanical Code. The storage arrangement, handling and use of chemicals within nonproduction laboratories and accessory storage rooms, and the operation and maintenance of nonproduction laboratories shall comply with the requirements of the New York City Fire Code, and the rules of the Fire Commissioner. | 427.2 Interior supply location. | Medical gases shall be located in areas dedicated to the storage of such gases without other storage or uses. Where containers of medical gases in quantities greater than the permitted amount are located inside the buildings, they shall be located in a 1-hour exterior room, 1-hour interior room or a gas cabinet in accordance with Section 427.2.1, 427.2.2 or 427.2.3, respectively. Rooms or areas where medical gases are stored or used in quantities exceeding the maximum allowable quantity per control area as set forth in TABLE 307.1(1) and TABLE 307.1(2) shall be in accordance with Group H occupancies.
427.3 Prohibitions. | It shall be unlawful in any nonproduction laboratory to:
427.4 Definitions specific to this section. | The following terms shall, for the purposes of this section, have the meanings shown herein:
427.5 Classification. | Buildings or portions thereof occupied as a nonproduction laboratory may be classified as a Group B occupancy provided they comply with the provisions of Section 427. Nonproduction laboratories not in compliance with the provisions of Section 427.7 for laboratory chemical quantity limitations shall be classified as Group H occupancy.
427.5.1 Accessory use nonproduction laboratories. | Accessory use nonproduction laboratories occupying an area not more than 10 percent of the area of the story in which such laboratories are located and not exceeding the tabular values in Sections 504 and 506, for the allowable height or area for such use shall be classified according to the main occupancy. Such accessory nonproduction laboratories shall comply with the provisions of Section 427.
427.6 Fire protection. | Fire protection systems in nonproduction laboratories shall be provided in accordance with Section 427.6.1 through 427.6.3.
427.6.1 Sprinkler system. | Laboratory units shall be pro­vided throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The entire building shall be provided throughout with an automatic sprinkler system when the aggregate floor area of all laboratory units within any building exceeds 20,000 square feet (1858 m2).
427.6.2 Standpipe and hose system. | In all nonproduction laboratory buildings that are two or more stories above or below the grade level (level of exit discharge), standpipes shall be installed in accordance with Section 905.2.
427.6.3 Fire alarm system. | A manual fire alarm system shall be installed in accordance with Section 907.2.2, 907.2.3, or 907.2.6, as applicable.
427.7 Quantity limitations. | Quantity limitations in nonproduction laboratories shall be provided in accordance with Section 427.7.1 through 427.7.10.
427.7.1 Flammable and combustible liquids. | The density and total quantity of flammable and combustible liquids allowed within a laboratory unit, outside of storage rooms, shall comply with Table 9.1.1(A) of NFPA 45, as modified by the New York City Fire Code, for laboratory unit fire hazard Class D. Exceptions: The following exceptions apply to other than educational or instructional laboratories: 1. The density of flammable and combustible liquids allowed within a laboratory unit may be increased to those set forth in Table 9.1.1(A) of NFPA 45 as modified by the New York City Fire Code, for laboratory unit fire hazard Class B provided the total quantity of flammable and combustible liquid, including any in storage cabinets or safety cans, does not exceed 25 gallons (95 L). 2. The density of flammable and combustible liquids allowed within a laboratory unit may be increased to those set forth in Table 9.1.1(A) of NFPA 45 as modified by the New York City Fire Code, for laboratory unit fire hazard Class B provided the total quantity of flammable and combustible liquid, including any in storage cabinets or safety cans, does not exceed 30 gallons (114 L) and the walls, floors and ceilings of the laboratory unit are separated from all adjoining areas by 2-hour fire-rated construction. 3. Based on a density of 1 gallon per 100 square feet (3.785 L per 9.3 m2) of area, the quantity of flammable and combustible liquid allowed within a laboratory unit, excluding quantities in storage cabinets or safety cans, may be increased to 100 gallons (379 L), and the total quantities of flammable and combustible liquids, including quantities in storage cabinets or safety cans, may be increased to 200 gallons (757 L) provided the walls, floors and ceilings of the laboratory unit are separated from all adjoining areas by 2-hour fire-rated construction.
427.7.2 Flammable solids. | The total quantity of flammable solids allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 10 pounds (4.5 kg). Exception: The total quantity of flammable solids allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 15 pounds (6.8 kg).
427.7.3 Oxidizers and organic peroxides. | The total quantity of solid and liquid oxidizers and organic peroxides combined allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 40 pounds (18 kg), provided not more than 2 pounds (0.908 kg) of which are Class 3 oxidizers and 1 pound (0.454 kg) of which is Class I organic peroxides. Exception: The total quantity of solid and liquid oxidizers and organic peroxides combined allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire rated construction shall not exceed 50 pounds (23 kg), provided not more than 2 pounds (0.908 kg) of which is Class 3 oxidizers and 1 pound (0.454 kg) of which are Class I organic peroxides.
427.7.4 Unstable (reactive). | The total quantity of unstable (reactive) material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 6 pounds (2.7 kg), provided not more than 1 pound (0.454 kg) of which is Class 3 unstable (reactive). Exception: The total quantity of unstable (reactive) material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 12 pounds (5.4 kg), provided not more than 1 pound (0.454 kg) of which is Class 3 unstable (reactive).
427.7.5 Water reactive material. | The total quantity of water reactive material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 2.5 pounds (1.1 kg). Exception: The total quantity of water-reactive material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire-rated construction shall not exceed 5 pounds (2.3 kg).
427.7.6 Pyrophoric material. | The total quantity of solid or liquid pyrophoric material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 0.5 pounds (0.227 kg). Exception: The total quantity of pyrophoric material allowed within a laboratory unit that is provided with walls, floors and ceilings that separate the laboratory unit from all adjoining areas by 2-hour fire rated construction shall not exceed 1 pound (0.454 kg).
427.7.7 Highly toxic material. | The total quantity of solid or liquid highly toxic material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 5 pounds (2.27 kg).
427.7.8 Toxic material. | The total quantity of solid or liquid toxic material allowed within a laboratory unit, excluding any quantities in a storage room, shall not exceed 250 pounds (113.4 kg).
427.7.9 Corrosive material. | The total quantity of solid or liquid corrosive material allowed within a laboratory unit, excluding any quantity in a storage room, shall not exceed 250 gallons (946 L).
427.7.10 Hazardous gases. | The storage, handling and use of hazardous gases, including highly toxic, toxic, corrosive, and asphyxiant gases, within a laboratory unit shall be in accordance the New York City Fire Code, including quantities permitted and oxygen sensors.
427.8 Storage room classification. | Storage rooms for laboratory chemicals accessory to a laboratory unit shall be classified as Occupancy Group S-1 provided they comply with the provisions of Section 427.9. Storage rooms not in compliance with the provisions of Section 427.9 for laboratory chemical quantity limitations shall be classified as a Group H occupancy.
427.9 Storage rooms. | In addition to the quantities allowed within a laboratory unit by Section 427.7, laboratory chemicals that are accessory to a laboratory unit may be stored, whether outside of or entirely within a laboratory unit, in dedicated storage rooms complying with all of the following:
4. Storage rooms shall be equipped with a continuously operated ventilation system that provides at least 6 changes of air per hour and vents to the outdoors.
427.10 Ventilation. | Nonproduction laboratories shall be ventilated in accordance with Section 408 of the New York City Mechanical Code.
428.1 Scope. | This section shall apply to the construction, alteration, and use of buildings or spaces for radioactive materials and radiation-producing equipment. | 428.1 Scope. | Higher education laboratories complying with the requirements of Sections 428.1 through 428.4 shall be permitted to exceed the maximum allowable quantities of hazardous materials in control areas set forth in Tables 307.1(1) and 307.1(2) without requiring classification as a Group H occupancy. Except as specified in Section 428, such laboratories shall comply with all applicable provisions of this code and the International Fire Code.
428.2 City, state and federal regulations. | In addition to the requirements of this section, occupancies involving radioactive materials and radiation-producing equipment shall also com­ply with applicable requirements of the New York City Health Code, and applicable state and federal regulations. | 428.2 Application. | The provisions of Section 428 shall be applied as exceptions or additions to applicable requirements of this code. Unless specifically modified by Section 428, the storage, use and handling of hazardous materials shall comply with all other provisions in Chapters 38 and 50 through 67 of the International Fire Code and this code for quantities not exceeding the maximum allowable quantity.
428.3 Laboratories. | All laboratories utilizing radioactive materials or radiation-producing equipment required to register under the requirements of the New York City Health Code shall comply with the requirements of Sections 428.3.1 through 428.3.7. | 428.3 Laboratory suite construction. | Where laboratory suites are provided, they shall be constructed in accordance with this section and Chapter 38 of the International Fire Code. The number of laboratory suites and percentage of maximum allowable quantities of hazardous materials in laboratory suites shall be in accordance with Table 428.3.
428.3.1 Construction. | All buildings in which such laboratories occur shall be of Type I or II construction. | 428.3.1 Separation from other nonlaboratory areas. | Laboratory suites shall be separated from other portions of the building in accordance with the most restrictive of the following: 1. Fire barriers and horizontal assemblies as required in Table 428.3. Fire barriers shall be constructed in ac-cordance with Section 707 and horizontal assemblies constructed in accordance with Section 711. Exception: Where an individual laboratory suite occupies more than one story, the fire-resistance rating of intermediate floors contained within the laboratory suite shall comply with the requirements of this code. 2. Separations as required by Section 508.
428.3.2 Floors. | All floors shall comply with the fire resistance requirements for the class of construction, and provide the degree of radioactive resistance required by applicable city, state, and federal regulations. A finished material shall be applied to provide a continuous nonporous surface, which may be readily removed. | 428.3.2 Separation from other laboratory suites. | Laboratory suites shall be separated from other laboratory suites in accordance with Table 428.3.
428.3.3 Interior finish. | All insulation of acoustical treatments and interior partitions shall be of noncombustible material. Walls and ceilings shall have nonporous finishes of Class A rating. | 428.3.3 Floor assembly fire resistance. | The floor assembly supporting laboratory suites and the construction supporting the floor of laboratory suites shall have a fire-resistance rating of not less than 2 hours. Exception: The floor assembly of the laboratory suites and the construction supporting the floor of the laboratory suites are allowed to be 1-hour fire-resistance rated in buildings of Types IIA, IIIA and VA construction, provided that the building is three or fewer stories.
428.3.4 Sprinkler protection. | Automatic sprinkler protection complying with the construction provisions of Chapter 9 of the New York City Building Code shall be provided, and such protection shall be designed for the type of combustible materials wherever such material is used, and for the radioactive material that may be expected to melt, vaporize, or oxidize under fire conditions. Laboratory equipment susceptible to damage from water or other materials used in the sprinkler system may be shielded by hoods except when the equipment provides a source of combustion. Where sprinkler protection uses water, or small water-spray installations are used to fight small isolated fires, floors shall be provided with drainage so that water may be carried to retention tanks for later disposal as required by the New York City Health Code when contamination of the water is to be anticipated. | 428.3.4 Maximum number. | The maximum number of laboratory suites shall be in accordance with Table 428.3. Where a building contains both laboratory suites and control areas, the total number of laboratory suites and control areas within a building shall not exceed the maximum number of laboratory suites in accordance with Table 428.3.
428.3.5 Electrical controls. | Electrical controls and equipment shall be installed in accordance with the requirements of the New York City Electrical Code. | 428.3.5 Means of egress. | Means of egress shall be in accordance with Chapter 10.
428.3.6 Ventilation. | Exhaust air from areas in which radioactive materials are used or stored shall be exhausted to the outdoors in such manner as not to create a health hazard, and shall not be recirculated to other areas of the building. Air pressure in rooms in which radioactive materials are used or stored shall be maintained below the air pressure of adjoining rooms, so that there is no flow of radioactive gases or dusts into adjoining rooms. | 428.3.6 Standby or emergency power. | Standby or emergency power shall be provided in accordance with Section 414.5.2 where laboratory suites are located above the sixth story above grade plane or located in a story below grade plane.
428.3.6.1 Ducts. | Ducts shall be of sheet steel of not less than No. 16 manufacturers’ standard gauge or of other equivalent noncombustible material having a melting point above 1800°F (982°C). Exhaust ducts within the building, on the discharge side of the fan, shall be welded airtight. Exhaust ducts within the building, on the suction side of the fan, shall have laps in the direction of airflow with smoke-tight joints, and shall be subjected to a smoke test in accordance with the requirements for chimneys in the New York City Mechanical Code. Access hatches with tight-closing covers shall be provided for cleaning and for fire-fighting in the exhaust system ducts.
428.3.6.2 Fume hoods. | Fume hoods shall be exhausted to the outdoors. Controls for hood fans shall be interlocked so that contaminated air cannot be drawn into any space from a hood where the exhaust fan is not in operation.
428.3.6.3 Fans. | Fan equipment other than the impeller and impeller housing shall be located outside the exhaust stream.
428.3.6.4 Exhaust. | When the degree of contamination of the exhaust stream exceeds the concentration limits permitted by the health code, the duct system shall be equipped with devices to decontaminate the air to a safe level before discharging to the outdoor air.
428.3.7 Plumbing. | Drainage lines from sinks used for radioactive wastes shall be without traps, and shall lead to retention tanks when required by the provisions of the New York City Health Code. | 428.3.7 Ventilation. | Ventilation shall be in accordance with Chapter 7 of NFPA 45, and the International Mechanical Code.
428.4 Radiation machines. | Radiation machines or particle accelerators, linear accelerators, cyclotrons, synchrotons, betatrons, or bevatrons shall be located only in buildings of Type I or II construction; however, this requirement shall not apply to conventional medical, dental, research, or industrial x-ray machines of less than one million-volt capacity.
428.5 Storage. | Radioactive materials shall be stored in sealed containers. When required by the commissioner to avoid too concentrated an exposure within any one space, radioactive materials shall be stored in vaults designed in accordance with the radiation shielding or other requirements for the materials to be stored, and with the requirements of Sections 428.5.1 through 428.5.3.
428.5.1 Fire protection. | When any materials are subject to melting, vaporization, or oxidation under fire conditions, the storage vaults shall be constructed of walls having a fire-resistance rating of at least 4 hours, and the vaults shall be equipped with automatic sprinklers complying with the construction requirements of Chapter 9 and shall be vented through devices to decontaminate the air to a safe level.
428.5.2 Doors. | Doors opening into storage vaults shall meet shielding requirements and have a fire-protection rating of not less than 3 hours.
428.5.3 Bins, shelving, partitions and pallets. | All bins, shelving, partitions, and pallets in storage vaults shall be of noncombustible materials. Other methods of storage permitted by the health department or applicable state and federal regulations, such as storage under water, may be used.
|  | 402.4.2.2.1 Openings between anchor building and mall. | Except for the separation between Group R-1 sleeping units and the mall, openings between anchor buildings of Type IA, IB, IIA or IIB construction and the mall need not be protected.
|  | 403.2.1.1 Type of construction. | The following reductions in the minimum fire-resistance rating of the building elements in TABLE 601 shall be permitted as follows: |  | See BC06 Tables&Figures
|  | 403.2.1.2 Shaft enclosures. | For buildings not greater than 420 feet (128 m) in building height, the required fire-resistance rating of the fire barriers enclosing vertical shafts, other than interior exit stairway and elevator hoistway enclosures, is permitted to be reduced to 1 hour where automatic sprinklers are installed within the shafts at the top and at alternate floor levels.
|  | 403.2.2.1 Wall assembly materials—soft body impact. | The panels making up the enclosures for interior exit stairways and elevator hoistway enclosures shall meet or exceed Soft Body Impact Classification Level 2 as measured by the test method described in ASTM C1629/C1629M.
|  | 403.2.2.2 Wall assembly materials—hard body impact. | The panels making up the enclosures for interior exit stairways and elevator hoistway enclosures that are not exposed to the interior of the enclosures for interior exit stairways or elevator hoistway enclosure shall be in accordance with one of the following:
|  | 403.2.2.3 Concrete and masonry walls. | Concrete or masonry walls shall be deemed to satisfy the requirements of Sections 403.2.2.1 and 403.2.2.2.
|  | 403.2.2.4 Other wall assemblies. | Any other wall assembly that provides impact resistance equivalent to that required by Sections 403.2.2.1 and 403.2.2.2 for Hard Body Impact Classification Level 3, as measured by the test method described in ASTM C1629/C1629M, shall be permitted.
|  | 403.4.8.4 Emergency power loads. | The following are classified as emergency power loads:
|  | 404.11 Interior exit stairway discharge. | Discharge of interior exit stairways through an atrium shall be in accordance with Section 1028.
|  | 405.4.2 Smoke barrier penetration. | The compartments shall be separated from each other by a smoke barrier in accordance with Section 709. Penetrations between the two compartments shall be limited to plumbing and electrical piping and conduit that are firestopped in accordance with Section 714. Doorways shall be protected by fire door assemblies that comply with Section 716, automatic-closing by smoke detection in accordance with Section 716.2.6.6 and installed in accordance with NFPA 105 and Section 716.2.2.1. Where provided, each compartment shall have an air supply and an exhaust system independent of the other compartments.
|  | 406.2.1 Automatic garage door openers and vehicular gates. | Automatic garage door openers shall be listed and labeled in accordance with UL 325. Where provided, automatic vehicular gates shall comply with Section 3110.
|  | 406.2.2 Clear height. | The clear height of each floor level in vehicle and pedestrian traffic areas shall be not less than 7 feet (2134 mm). Canopies under which fuels are dispensed shall have a clear height in accordance with Section 406.7.2.
|  | 406.2.3 Accessible parking spaces. | Where parking is provided, accessible parking spaces, access aisles and vehicular routes serving accessible parking shall be provided in accordance with Section 1106.
|  | 406.2.4 Floor surfaces. | Floor surfaces shall be of concrete or similar approved noncombustible and nonabsorbent materials. The area of floor used for the parking of automobiles or other vehicles shall be sloped to facilitate the movement of liquids to a drain or toward the main vehicle entry doorway. The surface of vehicle fueling pads in motor fuel-dispensing facilities shall be in accordance with Section 406.7.1.
|  | 406.2.5 Sleeping rooms. | Openings between a motor vehicle-related occupancy and a room used for sleeping purposes shall not be permitted.
|  | 406.2.6 Fuel dispensing. | The dispensing of fuel shall only be permitted in motor fuel-dispensing facilities in accordance with Section 406.7.
|  | 406.2.7 Electric vehicle charging stations and systems. | Where provided, electric vehicle charging systems shall be installed in accordance with NFPA 70. Electric vehicle charging system equipment shall be listed and labeled in accordance with UL 2202. Electric vehicle supply equipment shall be listed and labeled in accordance with UL 2594. Accessibility to electric vehicle charging stations shall be provided in accordance with Section 1108.
|  | 406.2.8 Mixed occupancies and uses. | Mixed uses shall be allowed in the same building as public parking garages and repair garages in accordance with Section 508.1. Mixed uses in the same building as an open parking garage are subject to Sections 402.4.2.3, 406.5.11, 508.1, 510.3, 510.4 and 510.7.
|  | 406.2.9 Equipment and appliances. | Equipment and appliances shall be installed in accordance with Sections 406.2.9.1 through 406.2.9.3 and the International Mechanical Code, International Fuel Gas Code and NFPA 70.
|  | 406.2.9.1 Elevation of ignition sources. | Equipment and appliances having an ignition source and located in hazardous locations and public garages, private garages, repair garages, automotive motor fuel-dispensing facilities and parking garages shall be elevated such that the source of ignition is not less than 18 inches (457 mm) above the floor surface on which the equipment or appliance rests. For the purpose of this section, rooms or spaces that are not part of the living space of a dwelling unit and that communicate directly with a private garage through openings shall be considered to be part of the private garage.
|  | 406.2.9.1.1 Parking garages. | Connection of a parking garage with any room in which there is a fuel-fired appliance shall be by means of a vestibule providing a two-doorway separation, except that a single door is permitted where the sources of ignition in the appliance are elevated in accordance with Section 406.2.9.
|  | 406.2.9.2 Public garages. | Appliances located in public garages, motor fuel-dispensing facilities, repair garages or other areas frequented by motor vehicles shall be installed not less than 8 feet (2438 mm) above the floor. Where motor vehicles are capable of passing under an appliance, the appliance shall be installed at the clearances required by the appliance manufacturer and not less than 1 foot (305 mm) higher than the tallest vehicle garage door opening.
|  | 406.2.9.3 Private garages. | Appliances located in private garages and carports shall be installed with a minimum clearance of 6 feet (1829 mm) above the floor.
|  | 406.3.2.1 Dwelling unit separation. | The private garage shall be separated from the dwelling unit and its attic area by means of gypsum board, not less than 1/2 inch (12.7 mm) in thickness, applied to the garage side. Garages beneath habitable rooms shall be separated from all habitable rooms above by not less than a 5/8-inch (15.9 mm) Type X gypsum board or equivalent and 1/2-inch (12.7 mm) gypsum board applied to structures supporting the separation from habitable rooms above the garage. Door openings between a private garage and the dwelling unit shall be equipped with either solid wood doors or solid or honeycomb core steel doors not less than 13/8 inches (34.9 mm) in thickness, or doors in compliance with Section 716.2.2.1 with a fire protection rating of not less than 20 minutes. Doors shall be self-closing and self-latching.
|  | 406.3.2.2 Ducts. | Ducts in a private garage and ducts penetrating the walls or ceilings separating the dwelling unit from the garage, including its attic area, shall be constructed of sheet steel of not less than 0.019 inch (0.48 mm) in thickness and shall not have openings into the garage.
|  | 406.3.3.1 Carport separation. | A separation is not required between a Group R-3 and U carport, provided that the carport is entirely open on two or more sides and there are not enclosed areas above.
|  | 406.4.1 Guards. | Guards shall be provided in accordance with Section 1015. Guards serving as vehicle barriers shall comply with Sections 406.4.2 and 1015.
|  | 406.4.2 Vehicle barriers. | Vehicle barriers not less than 2 feet 9 inches (835 mm) in height shall be placed where the vertical distance from the floor of a drive lane or parking space to the ground or surface directly below is greater than 1 foot (305 mm). Vehicle barriers shall comply with the loading requirements of Section 1607.10.
|  | 406.4.3 Ramps. | Vehicle ramps shall not be considered as required exits unless pedestrian facilities are provided. Vehicle ramps that are utilized for vertical circulation as well as for parking shall not exceed a slope of 1 unit vertical in 15 units horizontal (6.67-percent slope).
|  | 406.5.3 Mixed occupancies and uses. | Mixed uses shall be allowed in the same building as an open parking garage subject to the provisions of Sections 402.4.2.3, 406.5.11, 508.1, 510.3, 510.4 and 510.7.
|  | 406.5.8 Standpipe system. | An open parking garage shall be equipped with a standpipe system as required by Section 905.3.
|  | 406.6.4 Mechanical-access enclosed parking garages. | Mechanical-access enclosed parking garages shall be in accordance with Sections 406.6.4.1 through 406.6.4.4.
|  | 406.6.4.1 Separation. | Mechanical-access enclosed parking garages shall be separated from other occupancies and accessory uses by not less than 2-hour fire barriers constructed in accordance with Section 707 or by not less than 2-hour horizontal assemblies constructed in accordance with Section 711, or both.
|  | 406.6.4.2 Smoke removal. | A mechanical smoke removal system, installed in accordance with Section 910.4, shall be provided for all areas containing a mechanical-access enclosed parking garage.
|  | 406.6.4.3 Fire control equipment room. | Fire control equipment, consisting of the fire alarm control unit, mechanical ventilation controls and an emergency shutdown switch, shall be provided in a room located where the equipment is able to be accessed by the fire service from a secured exterior door of the building. The room shall be not less than 50 square feet (4.65 m2) in area and shall be in a location that is approved by the fire code official.
|  | 406.6.4.3.1 Emergency shutdown switch. | The mechanical parking system shall be provided with a manually activated emergency shutdown switch for use by emergency personnel. The switch shall be clearly identified and shall be in a location approved by the fire code official.
|  | 406.6.4.4 Fire department access doors. | Access doors shall be provided in accordance with Section 3206.7 of the International Fire Code.
|  | 406.8.1 Ventilation. | Repair garages shall be mechanically ventilated in accordance with the International Mechanical Code. The ventilation system shall be controlled at the entrance to the garage.
|  | 406.8.2 Gas detection system. | Repair garages used for repair of vehicles fueled by nonodorized gases including but not limited to hydrogen and nonodorized LNG, shall be provided with a gas detection system that complies with Section 916. The gas detection system shall be designed to detect leakage of nonodorized gaseous fuel. Where lubrication or chassis service pits are provided in garages used for repairing nonodorized LNG-fueled vehicles, gas sensors shall be provided in such pits.
|  | 406.8.2.1 System activation. | Activation of a gas detection alarm shall result in all of the following:
|  | 406.8.2.2 Failure of the gas detection system. | Failure of the gas detection system shall automatically deactivate the heating system, activate the mechanical ventilation system where the system is interlocked with the gas detection system, and cause a trouble signal to sound at an approved location.
|  | 406.8.3 Automatic sprinkler system. | A repair garage shall be equipped with an automatic sprinkler system in accordance with Section 903.2.9.1.
|  | 407.2.7 Domestic cooking appliances. | In Group I-2 occupancies, installation of cooking appliances used in domestic cooking facilities shall comply with all of the following:
|  | 407.3.1.1 Door construction. | Doors in corridors not required to have a fire protection rating shall comply with the following:
|  | 407.5.1 Smoke compartment size. | Stories shall be divided into smoke compartments with an area of not more than 22,500 square feet (2092 m2) in Group I-2 occupancies. Exceptions: 1. A smoke compartment in Group I-2, Condition 2 is permitted to have an area of not more than 40,000 square feet (3716 m2) provided that all patient sleeping rooms within that smoke compartment are config-ured for single patient occupancy and any suite within the smoke compartment complies with Section 407.4.4. 2. A smoke compartment in Group I-2, Condition 2 without patient sleeping rooms is permitted to have an area of not more than 40,000 square feet (3716 m2).
|  | 407.5.2 Exit access travel distance. | The distance of travel from any point in a smoke compartment to a smoke barrier door shall be not greater than 200 feet (60 960 mm).
|  | 407.5.3 Refuge area. | Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:
|  | 407.5.4 Independent egress. | A means of egress shall be provided from each smoke compartment created by smoke barriers without having to return through the smoke compartment from which means of egress originated. Smoke compartments that do not contain an exit shall be provided with direct access to not less than two adjacent smoke compartments.
|  | 407.5.5 Horizontal assemblies. | Horizontal assemblies supporting smoke barriers required by this section shall be designed to resist the movement of smoke. Elevator lobbies shall be in accordance with Section 3006.2.
|  | 407.6 Automatic-closing doors. | Automatic-closing doors with hold-open devices shall comply with Sections 709.5 and 716.2.
|  | 407.6.1 Activation of automatic-closing doors. | Automatic-closing doors on hold-open devices in accordance with Section 716.2.6.6 shall also close upon activation of a fire alarm system, an automatic sprinkler system, or both. The automatic release of the hold-open device on one door shall release all such doors within the same smoke compartment.
|  | 407.11 Electrical systems. | In Group I-2 occupancies, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of Chapter 27 and NFPA 99.
|  | 410.2 Stages. | Stage construction shall comply with Sections 410.2.1 through 410.2.7.
|  | 410.2.1 Stage construction. | Stages shall be constructed of materials as required for floors for the type of construction of the building in which such stages are located. Exception: Stages need not be constructed of the same materials as required for the type of construction provided that the construction complies with one of the following: 1. Stages of Type IIB or IV construction with a nominal 2-inch (51 mm) wood deck, provided that the stage is separated from other areas in accordance with Section 410.2.4. 2. In buildings of Type IIA, IIIA and VA construction, a fire-resistance-rated floor is not required, provided that the space below the stage is equipped with an automatic sprinkler system or fire-extinguishing system in accordance with Section 903 or 904. 3. In all types of construction, the finished floor shall be constructed of wood or approved noncombustible materials. Openings through stage floors shall be equipped with tight-fitting, solid wood trap doors with ap-proved safety locks.
|  | 410.2.1.1 Stage height and area. | Stage areas shall be measured to include the entire performance area and adjacent backstage and support areas not separated from the performance area by fire-resistance-rated construction. Stage height shall be measured from the lowest point on the stage floor to the highest point of the roof or floor deck above the stage.
|  | 410.2.2 Technical production areas: galleries, gridirons and catwalks. | Beams designed only for the attachment of portable or fixed theater equipment, gridirons, galleries and catwalks shall be constructed of approved materials consistent with the requirements for the type of construction of the building; and a fire-resistance rating shall not be required. These areas shall not be considered to be floors, stories, mezzanines or levels in applying this code. Exception: Floors of fly galleries and catwalks shall be constructed of any approved material.
|  | 410.2.3 Exterior stage doors. | Where protection of openings is required, exterior exit doors shall be protected with fire door assemblies that comply with Section 716. Exterior openings that are located on the stage for means of egress or loading and unloading purposes, and that are likely to be open during occupancy of the theater, shall be constructed with vestibules to prevent air drafts into the auditorium.
|  | 410.2.4 Proscenium wall. | Where the stage height is greater than 50 feet (15 240 mm), all portions of the stage shall be completely separated from the seating area by a proscenium wall with not less than a 2-hour fire-resistance rating extending continuously from the foundation to the roof.
|  | 410.2.5 Proscenium curtain. | Where a proscenium wall is required to have a fire-resistance rating, the stage opening shall be provided with a fire curtain complying with NFPA 80, horizontal sliding doors complying with Section 716 having a fire protection rating of not less than 1 hour, or an approved water curtain complying with Section 903.3.1.1 or, in facilities not utilizing the provisions of smoke-protected assembly seating in accordance with Section 1030.6.2, a smoke control system complying with Section 909 or natural ventilation designed to maintain the smoke level not less than 6 feet (1829 mm) above the floor of the means of egress.
|  | 410.2.6 Scenery. | Combustible materials used in sets and scenery shall meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701, in accordance with Section 806 and the International Fire Code. Foam plastics and materials containing foam plastics shall comply with Section 2603 and the International Fire Code.
|  | 410.2.7 Stage ventilation. | Emergency ventilation shall be provided for stages larger than 1,000 square feet (93 m2) in floor area, or with a stage height greater than 50 feet (15 240 mm). Such ventilation shall comply with Section 410.2.7.1 or 410.2.7.2.
|  | 410.2.7.1 Roof vents. | Two or more vents constructed to open automatically by approved heat-activated devices and with an aggregate clear opening area of not less than 5 percent of the area of the stage shall be located near the center and above the highest part of the stage area. Supplemental means shall be provided for manual operation of the ventilator. Curbs shall be provided as required for skylights in Section 2610.2. Vents shall be labeled.
|  | 410.2.7.2 Smoke control. | Smoke control in accordance with Section 909 shall be provided to maintain the smoke layer interface not less than 6 feet (1829 mm) above the highest level of the assembly seating or above the top of the proscenium opening where a proscenium wall is provided in compliance with Section 410.2.4.
|  | 410.3 Platform construction. | Permanent platforms shall be constructed of materials as required for the type of construction of the building in which the permanent platform is located. Permanent platforms are permitted to be constructed of fire-retardant-treated wood for Types I, II and IV construction where the platforms are not more than 30 inches (762 mm) above the main floor, and not more than one-third of the room floor area and not more than 3,000 square feet (279 m2) in area. Where the space beneath the permanent platform is used for storage or any purpose other than equipment, wiring or plumbing, the floor assembly shall be not less than 1-hour fire-resistance-rated construction. Where the space beneath the permanent platform is used only for equipment, wiring or plumbing, the underside of the permanent platform need not be protected.
|  | 410.3.1 Temporary platforms. | Platforms installed for a period of not more than 30 days are permitted to be constructed of any materials permitted by this code. The space between the floor and the platform above shall only be used for plumbing and electrical wiring to platform equipment.
|  | 410.4 Dressing and appurtenant rooms. | Dressing and appurtenant rooms shall comply with Sections 410.4.1 and 410.4.2.
|  | 410.4.1 Separation from stage. | The stage shall be separated from dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage and other parts of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours for stage heights greater than 50 feet (15 240 mm) and not less than 1 hour for stage heights of 50 feet (15 240 mm) or less.
|  | 410.4.2 Separation from each other. | Dressing rooms, scene docks, property rooms, workshops, storerooms and compartments appurtenant to the stage shall be separated from each other by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
|  | 410.5 Means of egress. | Except as modified or as provided for in this section, the provisions of Chapter 10 shall apply.
|  | 410.5.1 Arrangement. | Where two or more exits or exit access doorways from the stage are required in accordance with Section 1006.2, not fewer than one exit or exit access doorway shall be provided on each side of a stage.
|  | 410.5.2 Stairway and ramp enclosure. | Exit access stairways and ramps serving a stage or platform are not required to be enclosed. Exit access stairways and ramps serving technical production areas are not required to be enclosed.
|  | 410.5.3 Technical production areas. | Technical production areas shall be provided with means of egress and means of escape in accordance with Sections 410.5.3.1 through 410.5.3.5.
|  | 410.5.3.1 Number of means of egress. | Not fewer than one means of egress shall be provided from technical production areas.
|  | 410.5.3.2 Exit access travel distance. | The exit access travel distance shall be not greater than 300 feet (91 440 mm) for buildings without a sprinkler system and 400 feet (122 mm) for buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
|  | 410.5.3.3 Two means of egress. | Where two means of egress are required, the common path of travel shall be not greater than 100 feet (30 480 mm). Exception: A means of escape to a roof in place of a second means of egress is permitted.
|  | 410.5.3.4 Path of egress travel. | The following exit access components are permitted where serving technical production areas:
|  | 410.5.3.5 Width. | The path of egress travel within and from technical support areas shall be not less than 22 inches (559 mm).
|  | 410.6 Automatic sprinkler system. | Stages shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. Sprinklers shall be installed under the roof and gridiron and under all catwalks and galleries over the stage. Sprinklers shall be installed in dressing rooms, performer lounges, shops and storerooms accessory to such stages. Exceptions: 1. Sprinklers are not required under stage areas less than 4 feet (1219 mm) in clear height that are utilized exclu-sively for storage of tables and chairs, provided that the concealed space is separated from the adjacent spaces by Type X gypsum board not less than 5/8-inch (15.9 mm) in thickness. 2. Sprinklers are not required for stages 1,000 square feet (93 m2) or less in area and 50 feet (15 240 mm) or less in height where curtains, scenery or other combustible hangings are not retractable vertically. Combustible hangings shall be limited to a single main curtain, borders, legs and a single backdrop. 3. Sprinklers are not required within portable orchestra enclosures on stages.
|  | 410.7 Standpipes. | Standpipe systems shall be provided in accordance with Section 905.
|  | 411.2 Automatic sprinkler system. | Buildings containing special amusement areas shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. Where the special amusement area is temporary, the sprinkler water supply shall be of an approved temporary means. Exception: Automatic sprinklers are not required where the total floor area of a temporary special amusement area is less than 1,000 square feet (93 m2) and the exit access travel distance from any point in the special amusement area to an exit is less than 50 feet (15 240 mm).
|  | 411.3 Fire alarm system. | Buildings containing special amusement areas shall be equipped with an automatic smoke detection system in accordance with Section 907.2.13.
|  | 411.4 Emergency voice/alarm communications system. | An emergency voice/alarm communications system shall be provided in accordance with Section 907.2.12.
|  | 411.5 Puzzle room exiting. | Puzzle room exiting shall comply with one of the following:
|  | 411.6 Exit marking. | Exit signs shall be installed at the required exit or exit access doorways serving special amusement areas in accordance with this section and Section 1013. Approved directional exit markings shall be provided. Where mirrors, mazes or other designs are utilized that disguise the path of egress travel such that they are not apparent, approved and listed low-level exit signs that comply with Section 1013.5, and directional path markings listed in accordance with UL 1994, shall be provided and located not more than 8 inches (203 mm) above the walking surface and on or near the path of egress travel. Such markings shall become visible in an emergency. The directional exit marking shall be activated by the automatic smoke detection system and the automatic sprinkler system in accordance with Section 907.2.12.
|  | 411.6.1 Photoluminescent exit signs. | Where photoluminescent exit signs are installed, activating light source and viewing distance shall be in accordance with the listing and markings of the signs.
|  | 411.7 Interior finish. | The interior finish in special amusement areas shall be Class A in accordance with Section 803.1.
|  | 412.2 Airport traffic control towers. | The provisions of Sections 412.2.1 through 412.2.6 shall apply to airport traffic control towers occupied only for the following uses:
|  | 412.2.1 Construction. | The construction of airport traffic control towers shall comply with the provisions of Sections 412.2.1.1 through 412.2.1.3.
|  | 412.2.1.1 Type of construction. | Airport traffic control towers shall be constructed to comply with the height limitations of Table 412.2.1.1. |  | See BC04 Tables&Figures
|  | 412.2.1.2 Structural integrity of interior exit stairways and elevator hoistway enclosures. | Enclosures for interior exit stairways and elevator hoistway enclosures shall comply with Section 403.2.2 in airport traffic control towers where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access.
|  | 412.2.1.3 Sprayed fire-resistant materials (SFRM). | The bond strength of the SFRM installed in airport traffic control towers shall be in accordance with Section 403.2.3 where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access.
|  | 412.2.2 Means of egress and evacuation. | The means of egress in airport traffic control towers shall comply with Sections 412.2.2.1 through 412.2.2.3.
|  | 412.2.2.1 Stairways. | Stairways in airport traffic control towers shall be in accordance with Section 1011. Exit stairways shall be smokeproof enclosures complying with one of the alternatives provided in Section 909.20. Exception: Stairways in airport traffic control towers are not required to comply with Section 1011.12.
|  | 412.2.2.2 Exit access. | From observation levels, airport traffic control towers shall be permitted to have a single means of exit access for a distance of travel not greater than 100 feet (30 480 mm). Exit access stairways from the observation level need not be enclosed.
|  | 412.2.2.3 Number of exits. | Not less than one exit stairway shall be permitted for airport traffic control towers of any height provided that the occupant load per floor is not greater than 15 and the area per floor does not exceed 1,500 square feet (140 m2).
|  | 412.2.2.3.1 Interior finish. | Where an airport traffic control tower is provided with only one exit stairway, interior wall and ceiling finishes shall be either Class A or Class B.
|  | 412.2.2.3.2 Exit separation. | Where an airport traffic control tower is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and two exits are required, the exit separation distance required by Section 1007 shall be not less than one-fourth of the length of the maximum overall dimension of the area served.
|  | 412.2.3 Emergency systems. | The detection, alarm and emergency systems of airport traffic control towers shall comply with Sections 412.2.3.1 through 412.2.3.3.
|  | 412.2.3.1 Automatic smoke detection systems. | Airport traffic control towers shall be provided with an automatic smoke detection system installed in accordance with Section 907.2.22.
|  | 412.2.3.2 Fire command center. | A fire command center shall be provided in airport traffic control towers where the control cab is located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access. The fire command center shall comply with Section 911. Exceptions: 1. The fire command center shall be located in the airport control tower or an adjacent contiguous build-ing where building functions are interdependent. 2. The room shall be not less than 150 square feet (14 m2) in area with a minimum dimension of 10 feet (3048 mm). 3. The following features shall not be required in an airport traffic control tower fire command center. 3.1. Emergency voice/alarm control unit. 3.2. Public address system. 3.3. Status indicators and controls for the air distributions centers. 3.4. Generator supervision devices, manual start and transfer features. 3.5. Elevator emergency or standby power switches where emergency or standby power is provid-ed.
|  | 412.2.3.3 Smoke removal. | Smoke removal in airport traffic control towers shall be provided in accordance with Section 403.4.7.
|  | 412.2.4 Automatic sprinkler system. | Where an occupied floor is located more than 35 feet (10 668 mm) above the lowest level of fire department vehicle access, airport traffic control towers shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1.
|  | 412.2.4.1 Fire pump room. | Fire pumps shall be located in rooms that are separated from all other areas of the building by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both. Exception: Separation is not required for fire pumps physically separated in accordance with NFPA 20.
|  | 412.2.5 Protection of elevator wiring and cables. | Wiring and cables serving elevators in airport traffic control towers shall be protected in accordance with Section 3007.8.1.
|  | 412.2.5.1 Elevators for occupant evacuation. | Where provided in addition to an exit stairway, occupant evacuation elevators shall be in accordance with Section 3008.
|  | 412.2.6 Accessibility. | Airport traffic control towers shall be accessible except as specified in Section 1104.4.
|  | 412.3 Aircraft hangars. | Aircraft hangars shall be in accordance with Sections 412.3.1 through 412.3.6.
|  | 412.3.1 Exterior walls. | Exterior walls located less than 30 feet (9144 mm) from lot lines or a public way shall have a fire-resistance rating not less than 2 hours.
|  | 412.3.2 Basements. | Where hangars have basements, floors over basements shall be of Type IA construction and shall be made tight against seepage of water, oil or vapors. There shall not be openings or communication between basements and the hangar. Access to basements shall be from outside only.
|  | 412.3.3 Floor surface. | Floors shall be graded and drained to prevent water or fuel from remaining on the floor. Floor drains shall discharge through an oil separator to the sewer or to an outside vented sump. Exception: Aircraft hangars with individual lease spaces not exceeding 2,000 square feet (186 m2) each in which servicing, repairing or washing is not conducted and fuel is not dispensed shall have floors that are graded toward the door, but shall not require a separator.
|  | 412.3.4 Heating equipment. | Heating equipment shall be placed in another room separated by 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Entrance shall be from the outside or by means of a vestibule providing a two-doorway separation. Exceptions: 1. Unit heaters and vented infrared radiant heating equipment suspended not less than 10 feet (3048 mm) above the upper surface of wings or engine enclosures of the highest aircraft that are permitted to be housed in the hangar need not be located in a separate room provided that they are mounted not less than 8 feet (2438 mm) above the floor in shops, offices and other sections of the hangar communicating with storage or service areas. 2. Entrance to the separated room shall be permitted by a single interior door provided that the sources of ig-nition in the appliances are not less than 18 inches (457 mm) above the floor.
|  | 412.3.5 Finishing. | The process of “doping,” involving use of a volatile flammable solvent, or of painting, shall be carried on in a separate detached building equipped with automatic fire-extinguishing equipment in accordance with Section 903.
|  | 412.3.6 Fire suppression. | Aircraft hangars shall be provided with a fire suppression system designed in accordance with NFPA 409, based on the classification for the hangar given in Table 412.3.6. Exception: Where a fixed base operator has separate repair facilities on site, Group II hangars operated by a fixed base operator used for storage of transient aircraft only shall have a fire suppression system, but the system is ex-empt from foam requirements. |  | See BC04 Tables&Figures
|  | 412.3.6.1 Hazardous operations. | Any Group III aircraft hangar according to Table 412.3.6 that contains hazardous operations including, but not limited to, the following shall be provided with a Group I or II fire suppression system in accordance with NFPA 409 as applicable: |  | See BC04 Tables&Figures
|  | 412.3.6.2 Separation of maximum single fire areas. | Maximum single fire areas established in accordance with hangar classification and construction type in Table 412.3.6 shall be separated by 2-hour fire walls constructed in accordance with Section 706. In determining the maximum single fire area as set forth in Table 412.3.6, ancillary uses that are separated from aircraft servicing areas by a fire barrier of not less than 1 hour, constructed in accordance with Section 707, shall not be included in the area. |  | See BC04 Tables&Figures
|  | 412.4 Residential aircraft hangars. | Residential aircraft hangars shall comply with Sections 412.4.1 through 412.4.5.
|  | 412.4.1 Fire separation. | A hangar shall not be attached to a dwelling unless separated by a fire barrier having a fire-resistance rating of not less than 1 hour. Such separation shall be continuous from the foundation to the underside of the roof and unpierced except for doors leading to the dwelling unit. Doors into the dwelling unit shall be equipped with self-closing devices and conform to the requirements of Section 716 with a noncombustible raised sill not less than 4 inches (102 mm) in height. Openings from a hangar directly into a room used for sleeping purposes shall not be permitted.
|  | 412.4.2 Egress. | A hangar shall provide two means of egress. One of the doors into the dwelling shall be considered as meeting only one of the two means of egress.
|  | 412.4.3 Smoke alarms. | Smoke alarms shall be provided within the hangar in accordance with Section 907.2.22.
|  | 412.4.4 Independent systems. | Electrical, mechanical and plumbing drain, waste and vent (DWV) systems installed within the hangar shall be independent of the systems installed within the dwelling. Building sewer lines shall be permitted to be connected outside the structures. Exception: Smoke detector wiring and feed for electrical subpanels in the hangar.
|  | 412.4.5 Height and area limits. | Residential aircraft hangars shall be not greater than 2,000 square feet (186 m2) in area and 20 feet (6096 mm) in building height.
|  | 412.5 Aircraft paint hangars. | Aircraft painting operations shall be conducted in an aircraft paint hangar that complies with the provisions of Sections 412.5.1 through 412.5.8. Buildings and structures, or parts thereof, used for the application of flammable finishes shall comply with the applicable provisions of Section 416.
|  | 412.5.1 Occupancy classification. | Aircraft paint hangars shall be classified in accordance with the provisions of Section 307.1. Aircraft paint hangars shall comply with the applicable requirements of this code and the International Fire Code for such occupancy.
|  | 412.5.2 Construction. | Aircraft paint hangars shall be of Type I or II construction.
|  | 412.5.3 Spray equipment cleaning operations. | Spray equipment cleaning operations shall be conducted in a liquid use, dispensing and mixing room.
|  | 412.5.4 Operations. | Only those flammable liquids necessary for painting operations shall be permitted in quantities less than the maximum allowable quantities per control area in Table 307.1(1). Spray equipment cleaning operations exceeding the maximum allowable quantities per control area in Table 307.1(1) shall be conducted in a liquid use, dispensing and mixing room. |  | See BC03 Tables&Figures
|  | 412.5.5 Storage. | Storage of flammable or combustible liquids exceeding the maximum allowable quantities per control area in Table 307.1(1) shall be in a liquid storage room. |  | See BC03 Tables&Figures
|  | 412.5.6 Fire suppression. | Aircraft paint hangars shall be provided with fire suppression as required by NFPA 409.
|  | 412.5.7 Ventilation. | Aircraft paint hangars shall be provided with ventilation as required in the International Mechanical Code.
|  | 412.5.8 Electrical. | Electrical equipment and devices within the aircraft paint hangar shall comply with NFPA 70.
|  | 412.5.8.1 Class I, Division I hazardous locations. | The area within 10 feet (3048 mm) horizontally from aircraft surfaces and from the floor to 10 feet (3048 mm) above the aircraft surface shall be classified as a Class I, Division I location.
|  | 412.5.8.2 Class I, Division 2 hazardous locations. | The area horizontally from aircraft surfaces between 10 feet (3048 mm) and 30 feet (9144 mm) and from the floor to 30 feet (9144 mm) above the aircraft surface shall be classified as a Class I, Division 2 location.
|  | 412.6 Aircraft manufacturing facilities. | In buildings used for the manufacturing of aircraft, exit access travel distances indicated in Section 1017.1 shall be increased in accordance with the following:
|  | 412.6.1 Ancillary areas. | Rooms, areas and spaces ancillary to the primary manufacturing area shall be permitted to egress through such area having a minimum height as indicated in Table 412.6. Exit access travel distance within the ancillary room, area or space shall not exceed that indicated in Table 1017.2 based on the occupancy classification of that ancillary area. Total exit access travel distance shall not exceed that indicated in Table 412.6. |  | See BC04 Tables&Figures
|  | 412.7 Heliports and helistops. | Heliports and helistops shall be permitted to be erected on buildings or other locations where they are constructed in accordance with Sections 412.7.1 through 412.7.5.
|  | 412.7.1 Size. | The landing area for helicopters less than 3,500 pounds (1588 kg) shall be not less than 20 feet (6096 mm) in length and width. The landing area shall be surrounded on all sides by a clear area having an average width at roof level of 15 feet (4572 mm), and all widths shall be not less than 5 feet (1524 mm).
|  | 412.7.2 Design. | Helicopter landing areas and the supports thereof on the roof of a building shall be noncombustible construction. Landing areas shall be designed to confine any flammable liquid spillage to the landing area itself and provisions shall be made to drain such spillage away from any exit or stairway serving the helicopter landing area or from a structure housing such exit or stairway. For structural design requirements, see Section 1607.6.
|  | 412.7.3 Means of egress. | The means of egress from heliports and helistops shall comply with the provisions of Chapter 10. Landing areas located on buildings or structures shall have two or more exits or access to exits. For landing areas less than 60 feet (18 288 mm) in length or less than 2,000 square feet (186 m2) in area, the second means of egress is permitted to be a fire escape, alternating tread device or ladder leading to the floor below.
|  | 412.7.4 Rooftop heliports and helistops. | Rooftop heliports and helistops shall comply with NFPA 418.
|  | 412.7.5 Standpipe system. | In buildings equipped with a standpipe system, the standpipe shall extend to the roof level in accordance with Section 905.3.6.
|  | 414.1.2.1 Aerosol products, aerosol cooking spray products and plastic aerosol 3 products. | Level 2 and 3 aerosol products, aerosol cooking spray products and plastic aerosol 3 products shall be stored and displayed in accordance with the International Fire Code. See Section 311.2 and the International Fire Code for occupancy group requirements.
|  | 414.2.4 Fire-resistance rating requirements. | The required fire-resistance rating for fire barriers shall be in accordance with Table 414.2.2. The floor assembly of the control area and the construction supporting the floor of the control area shall have a fire-resistance rating of not less than 2 hours. Exception: The floor assembly of the control area and the construction supporting the floor of the control area are allowed to be 1-hour fire-resistance-rated in buildings of Types IIA, IIIA, IV and VA construction, provided that both of the following conditions exist: 1. The building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The building is three or fewer stories above grade plane. |  | See BC04 Tables&Figures
|  | 414.2.5.1 Nonflammable solids and nonflammable and noncombustible liquids. | The aggregate quantity of nonflammable solid and nonflammable or noncombustible liquid hazardous materials permitted within a single control area of a Group M display and storage area, a Group S storage area or an outdoor control area is permitted to exceed the maximum allowable quantities per control area specified in Tables 307.1(1) and 307.1(2) without classifying the building or use as a Group H occupancy, provided that the materials are displayed and stored in accordance with the International Fire Code and quantities do not exceed the maximum allowable specified in Table 414.2.5(1). |  | See BC04 Tables&Figures
|  | 414.2.5.2 Flammable and combustible liquids. | In Group M occupancy wholesale and retail sales uses, indoor storage of flammable and combustible liquids shall not exceed the maximum allowable quantities per control area as indicated in Table 414.2.5(2), provided that the materials are displayed and stored in accordance with the International Fire Code. |  | See BC04 Tables&Figures
|  | 414.2.5.3 Aerosol products, aerosol cooking spray products or plastic aerosol 3 products. | The maximum quantity of aerosol products, aerosol cooking spray products or plastic aerosol 3 products in Group M occupancy retail display areas, storage areas adjacent to retail display areas and retail storage areas shall be in accordance with the International Fire Code.
|  | 415.1 General. | The provisions of Sections 415.1 through 415.11 shall apply to the storage and use of hazardous materials in excess of the maximum allowable quantities per control area listed in Section 307.1.
|  | 415.2 Compliance. | Buildings and structures with an occupancy in Group H shall comply with the applicable provisions of Section 414 and the International Fire Code.
|  | 415.6.1 Rooms for flammable or combustible liquid use, dispensing or mixing in open systems. | Rooms for flammable or combustible liquid use, dispensing or mixing in open systems having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the International Fire Code and NFPA 30.
|  | 415.6.2 Liquid storage rooms and rooms for flammable or combustible liquid use in closed systems. | Liquid storage rooms and rooms for flammable or combustible liquid use in closed systems, having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the International Fire Code and NFPA 30.
|  | 415.6.3 Spray paint booths. | Spray paint booths that comply with the International Fire Code need not be located on the outer perimeter.
|  | 415.6.4 Group H occupancy minimum fire separation distance. | Regardless of any other provisions, buildings containing Group H occupancies shall be set back to the minimum fire separation distance as set forth in Sections 415.6.4.1 through 415.6.4.4. Distances shall be measured from the walls enclosing the occupancy to lot lines, including those on a public way. Distances to assumed lot lines established for the purpose of determining exterior wall and opening protection are not to be used to establish the minimum fire separation distance for buildings on sites where explosives are manufactured or used where separation is provided in accordance with the quantity distance tables specified for explosive materials in the International Fire Code.
|  | 415.6.4.1 Group H-1. | Group H-1 occupancies shall be set back not less than 75 feet (22 860 mm) and not less than required by the International Fire Code. Exception: Fireworks manufacturing buildings separated in accordance with NFPA 1124.
|  | 415.6.4.2 Group H-2. | Group H-2 occupancies shall be set back not less than 30 feet (9144 mm) where the area of the occupancy is greater than 1,000 square feet (93 m2) and it is not required to be located in a detached building.
|  | 415.6.4.3 Groups H-2 and H-3. | Group H-2 and H-3 occupancies shall be set back not less than 50 feet (15 240 mm) where a detached building is required (see Table 415.6.5). |  | See BC04 Tables&Figures
|  | 415.6.4.4 Explosive materials. | Group H-2 and H-3 occupancies containing materials with explosive characteristics shall be separated as required by the International Fire Code. Where separations are not specified, the distances required shall be determined by a technical report issued in accordance with Section 414.1.3.
|  | 415.6.5 Detached buildings for Group H-1, H-2 or H-3 occupancy. | The storage or use of hazardous materials in excess of those amounts specified in Table 415.6.5 shall be in accordance with the applicable provisions of Sections 415.7 and 415.8. |  | See BC04 Tables&Figures
|  | 415.6.5.1 Wall and opening protection. | Where a detached building is required by Table 415.6.5, wall and opening protection based on fire separation distance is not required. |  | See BC04 Tables&Figures
|  | 415.9.1.3 Tanks. | Storage tanks shall be approved tanks conforming to the requirements of the International Fire Code.
|  | 415.9.2 Liquefied petroleum gas facilities. | The construction and installation of liquefied petroleum gas facilities shall be in accordance with the requirements of this code, the International Fire Code, the International Fuel Gas Code, the International Mechanical Code and NFPA 58.
|  | 415.10.4 Separation of highly toxic solids and liquids. | Highly toxic solids and liquids not stored in approved hazardous materials storage cabinets shall be isolated from other hazardous materials storage by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
|  | 415.11.4 Emergency alarm system. | Emergency alarm systems shall be provided in accordance with this section and Sections 415.5.1 and 415.5.2. The maximum allowable quantity per control area provisions shall not apply to emergency alarm systems required for HPM.
|  | 415.11.4.1 Service corridors. | An emergency alarm system shall be provided in service corridors, with not fewer than one alarm device in each service corridor.
|  | 415.11.4.2 Corridors and interior exit stairways and ramps. | Emergency alarms for corridors, interior exit stairways and ramps and exit passageways shall comply with Section 415.5.2.
|  | 415.11.4.3 Liquid storage rooms, HPM rooms and gas rooms. | Emergency alarms for liquid storage rooms, HPM rooms and gas rooms shall comply with Section 415.5.1.
|  | 415.11.4.4 Alarm-initiating devices. | An approved emergency telephone system, local alarm manual pull stations, or other approved alarm-initiating devices are allowed to be used as emergency alarm-initiating devices.
|  | 415.11.4.5 Alarm signals. | Activation of the emergency alarm system shall sound a local alarm and transmit a signal to the emergency control station.
|  | 415.11.5 Storage of hazardous production materials. | Storage of hazardous production materials (HPM) in fabrication areas shall be within approved or listed storage cabinets or gas cabinets or within a workstation. The storage of HPM in quantities greater than those specified in Section 5004.2 of the International Fire Code shall be in liquid storage rooms, HPM rooms or gas rooms as appropriate for the materials stored. The storage of other hazardous materials shall be in accordance with other applicable provisions of this code and the International Fire Code.
|  | 415.11.6 HPM rooms, gas rooms, liquid storage room construction. | HPM rooms, gas rooms and liquid shall be constructed in accordance with Sections 415.11.6.1 through 415.11.6.9.
|  | 415.11.6.1 HPM rooms and gas rooms. | HPM rooms and gas rooms shall be separated from other areas by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than 2 hours where the area is 300 square feet (27.9 m2) or more and not less than 1 hour where the area is less than 300 square feet (27.9 m2).
|  | 415.11.6.2 Liquid storage rooms. | Liquid storage rooms shall be constructed in accordance with the following requirements:
|  | 415.11.6.3 Floors. | Except for surfacing, floors of HPM rooms and liquid storage rooms shall be of noncombustible liquid-tight construction. Raised grating over floors shall be of noncombustible materials.
|  | 415.11.6.4 Location. | Where HPM rooms, liquid storage rooms and gas rooms are provided, they shall have not fewer than one exterior wall and such wall shall be not less than 30 feet (9144 mm) from lot lines, including lot lines adjacent to public ways.
|  | 415.11.6.5 Explosion control. | Explosion control shall be provided where required by Section 414.5.1.
|  | 415.11.6.6 Exits. | Where two exits are required from HPM rooms, liquid storage rooms and gas rooms, one shall be directly to the outside of the building.
|  | 415.11.6.7 Doors. | Doors in a fire barrier wall, including doors to corridors, shall be self-closing fire door assemblies having a fire protection rating of not less than 3/4 hour.
|  | 415.11.6.8 Ventilation. | Mechanical exhaust ventilation shall be provided in liquid storage rooms, HPM rooms and gas rooms at the rate of not less than 1 cubic foot per minute per square foot (0.044 L/s/m2) of floor area or six air changes per hour.
|  | 415.11.6.9 Emergency alarm system. | An approved emergency alarm system shall be provided for HPM rooms, liquid storage rooms and gas rooms.
|  | 415.11.7 Piping and tubing. | Hazardous production materials piping and tubing shall comply with this section and ASME B31.3.
|  | 415.11.7.1 HPM having a health-hazard ranking of 3 or 4. | Systems supplying HPM liquids or gases having a health-hazard ranking of 3 or 4 shall be welded throughout, except for connections, to the systems that are within a ventilated enclosure if the material is a gas, or an approved method of drainage or containment is provided for the connections if the material is a liquid.
|  | 415.11.7.2 Location in service corridors. | Hazardous production materials supply piping or tubing in service corridors shall be exposed to view.
|  | 415.11.7.3 Excess flow control. | Where HPM gases or liquids are carried in pressurized piping above 15 pounds per square inch gauge (psig) (103.4 kPa), excess flow control shall be provided. Where the piping originates from within a liquid storage room, HPM room or gas room, the excess flow control shall be located within the liquid storage room, HPM room or gas room. Where the piping originates from a bulk source, the excess flow control shall be located as close to the bulk source as practical.
|  | 415.11.7.4 Installations in corridors and above other occupancies. | The installation of HPM piping and tubing within the space defined by the walls of corridors and the floor or roof above, or in concealed spaces above other occupancies, shall be in accordance with Sections 415.11.7.1 through 415.11.7.3 and the following conditions: 1. Automatic sprinklers shall be installed within the space unless the space is less than 6 inches (152 mm) in the least dimension. 2. Ventilation not less than six air changes per hour shall be provided. The space shall not be used to convey air from any other area. 3. Where the piping or tubing is used to transport HPM liquids, a receptor shall be installed below such piping or tubing. The receptor shall be designed to collect any discharge or leakage and drain it to an approved lo-cation. The 1-hour enclosure shall not be used as part of the receptor. 4. HPM supply piping and tubing and nonmetallic waste lines shall be separated from the corridor and from occupancies other than Group H-5 by fire barriers or by an approved method or assembly that has a fire-resistance rating of not less than 1 hour. Access openings into the enclosure shall be protected by approved fire-protection-rated assemblies. 5. Readily accessible manual or automatic remotely activated fail-safe emergency shutoff valves shall be in-stalled on piping and tubing other than waste lines at the following locations: 5.1. At branch connections into the fabrication area. 5.2. At entries into corridors. Exception: Transverse crossings of the corridors by supply piping that is enclosed within a ferrous pipe or tube for the width of the corridor need not comply with Items 1 through 5.
|  | 415.11.7.5 Identification. | Piping, tubing and HPM waste lines shall be identified in accordance with ANSI A13.1 to indicate the material being transported.
|  | 415.11.8 Gas detection systems. | A gas detection system complying with Section 916 shall be provided for HPM gases where the physiological warning threshold level of the gas is at a higher level than the accepted permissible exposure limit (PEL) for the gas and for flammable gases in accordance with Sections 415.11.8.1 through 415.11.8.2.
|  | 415.11.8.1 Where required. | A gas detection system shall be provided in the areas identified in Sections 415.11.8.1.1 through 415.11.8.1.4.
|  | 415.11.8.1.1 Fabrication areas. | A gas detection system shall be provided in fabrication areas where HPM gas is used in the fabrication area.
|  | 415.11.8.1.2 HPM rooms. | A continuous gas detection system shall be provided in HPM rooms where HPM gas is used in the room.
|  | 415.11.8.1.3 Gas cabinets, exhausted enclosures and gas rooms. | A gas detection system shall be provided in gas cabinets and exhausted enclosures for HPM gas. A gas detection system shall be provided in gas rooms where HPM gases are not located in gas cabinets or exhausted enclosures.
|  | 415.11.8.1.4 Corridors. | Where HPM gases are transported in piping placed within the space defined by the walls of a corridor and the floor or roof above the corridor, a gas detection system shall be provided where piping is located and in the corridor. Exception: A gas detection system is not required for occasional transverse crossings of the corridors by supply piping that is enclosed in a ferrous pipe or tube for the width of the corridor.
|  | 415.11.8.2 Gas detection system operation. | The gas detection system shall be capable of monitoring the room, area or equipment in which the HPM gas is located at or below all the following gas concentrations:
|  | 415.11.8.2.1 Alarms. | The gas detection system shall initiate a local alarm and transmit a signal to the emergency control station when a short-term hazard condition is detected. The alarm shall be both visual and audible and shall provide warning both inside and outside the area where the gas is detected. The audible alarm shall be distinct from all other alarms.
|  | 415.11.8.2.2 Shutoff of gas supply. | The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for which gas is detected when a short-term hazard condition is detected. Automatic closure of shutoff valves shall comply with the following: 1. Where the gas detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close. 2. Where the gas detection sampling point initiating the gas detection system alarm is within a room and compressed gas containers are not in gas cabinets or an exhausted enclosure, the shutoff valves on all gas lines for the specific gas detected shall automatically close. 3. Where the gas detection sampling point initiating the gas detection system alarm is within a piping dis-tribution manifold enclosure, the shutoff valve supplying the manifold for the compressed gas contain-er of the specific gas detected shall automatically close. Exception: Where the gas detection sampling point initiating the gas detection system alarm is at the use lo-cation or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve for the branch line located in the piping distribution manifold enclosure shall automatically close.
|  | 415.11.9 Manual fire alarm system. | An approved manual fire alarm system shall be provided throughout buildings containing Group H-5. Activation of the alarm system shall initiate a local alarm and transmit a signal to the emergency control station. The fire alarm system shall be designed and installed in accordance with Section 907.
|  | 415.11.10 Emergency control station. | An emergency control station shall be provided in accordance with Sections 415.11.10.1 through 415.11.10.3.
|  | 415.11.10.1 Location. | The emergency control station shall be located on the premises at an approved location outside the fabrication area.
|  | 415.11.10.2 Staffing. | Trained personnel shall continuously staff the emergency control station.
|  | 415.11.10.3 Signals. | The emergency control station shall receive signals from emergency equipment and alarm and detection systems. Such emergency equipment and alarm and detection systems shall include, but not be limited to, the following where such equipment or systems are required to be provided either in this chapter or elsewhere in this code:
|  | 415.11.11 Emergency power system. | An emergency power system shall be provided in Group H-5 occupancies in accordance with Section 2702. The emergency power system shall supply power automatically to the electrical systems specified in Section 415.11.11.1 when the normal electrical supply system is interrupted.
|  | 415.11.11.1 Required electrical systems. | Emergency power shall be provided for electrically operated equipment and connected control circuits for the following systems:
|  | 415.11.11.2 Exhaust ventilation systems. | Exhaust ventilation systems are allowed to be designed to operate at not less than one-half the normal fan speed on the emergency power system where it is demonstrated that the level of exhaust will maintain a safe atmosphere.
|  | 415.11.12 Automatic sprinkler system protection in exhaust ducts for HPM. | An approved automatic sprinkler system shall be provided in exhaust ducts conveying gases, vapors, fumes, mists or dusts generated from HPM in accordance with Sections 415.11.12.1 through 415.11.12.3 and the International Mechanical Code.
|  | 415.11.12.1 Metallic and noncombustible nonmetallic exhaust ducts. | An approved automatic sprinkler system shall be provided in metallic and noncombustible nonmetallic exhaust ducts where all of the following conditions apply:
|  | 415.11.12.2 Combustible nonmetallic exhaust ducts. | Automatic sprinkler system protection shall be provided in combustible nonmetallic exhaust ducts where the largest cross-sectional diameter of the duct is equal to or greater than 10 inches (254 mm). Exception: Ducts need not be provided with automatic sprinkler protection as follows: 1. Ducts listed or approved for applications without automatic sprinkler system protection. 2. Ducts not more than 12 feet (3658 mm) in length installed below ceiling level.
|  | 415.11.12.3 Automatic sprinkler locations. | Sprinkler systems shall be installed at 12-foot (3658 mm) intervals in horizontal ducts and at changes in direction. In vertical ducts, sprinklers shall be installed at the top and at alternate floor levels.
|  | 416.2.1 Construction. | Walls and ceilings of spray rooms shall be constructed of noncombustible materials or the interior surface shall be completely covered with noncombustible materials. Aluminum shall not be used.
|  | 416.2.2 Surfaces. | The interior surfaces of spray rooms shall be smooth and shall be so constructed to permit the free passage of exhaust air from all parts of the interior and to facilitate washing and cleaning, and shall be so designed to confine residues within the room.
|  | 416.2.3 Ventilation. | Mechanical ventilation and interlocks with the spraying operation shall be in accordance with the International Fire Code and International Mechanical Code.
|  | 419.1 Artificial decorative vegetation. | Artificial decorative vegetation exceeding 6 feet (1830 mm) in height and permanently installed outdoors within 5 feet (1524 mm) of a building, or on the roof of a building, shall comply with Section 321.1 of the International Fire Code. Exception: Artificial decorative vegetation located more than 30 feet (9144 mm) from the exterior wall of a building.
|  | 420.4 Automatic sprinkler system. | Group R occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.8. Group I-1 occupancies shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.2.6. Quick-response or residential automatic sprinklers shall be installed in accordance with Section 903.3.2.
|  | 420.5 Fire alarm systems and smoke alarms. | Fire alarm systems and smoke alarms shall be provided in Group I-1, R-1 and R-2 occupancies in accordance with Sections 907.2.6, 907.2.8 and 907.2.9, respectively. Single- or multiple-station smoke alarms shall be provided in Groups I-1, R-2, R-3 and R-4 in accordance with Section 907.2.11.
|  | 420.6 Smoke barriers in Group I-1, Condition 2. | Smoke barriers shall be provided in Group I-1, Condition 2 to subdivide every story used by persons receiving care, treatment or sleeping and to provide other stories with an occupant load of 50 or more persons, into not fewer than two smoke compartments. Such stories shall be divided into smoke compartments with an area of not more than 22,500 square feet (2092 m2) and the distance of travel from any point in a smoke compartment to a smoke barrier door shall not exceed 200 feet (60 960 mm). The smoke barrier shall be in accordance with Section 709.
|  | 420.6.1 Refuge area. | Refuge areas shall be provided within each smoke compartment. The size of the refuge area shall accommodate the occupants and care recipients from the adjoining smoke compartment. Where a smoke compartment is adjoined by two or more smoke compartments, the minimum area of the refuge area shall accommodate the largest occupant load of the adjoining compartments. The size of the refuge area shall provide the following:
|  | 420.7 Group I-1 assisted living housing units. | In Group I-1 occupancies, where a fire-resistance corridor is provided in areas where assisted living residents are housed, shared living spaces, group meeting or multipurpose therapeutic spaces open to the corridor shall be in accordance with all of the following criteria:
|  | 420.8 Group I-1 cooking facilities. | In Group I-1 occupancies, rooms or spaces that contain a cooking facility with domestic cooking appliances shall be permitted to be open to the corridor where all of the following criteria are met:
|  | 420.9 Domestic cooking appliances. | In Group I-1 occupancies, installation of cooking appliance used in domestic cooking facilities shall comply with all of the following:ovens, cooktops, ranges, warmers and microwaves. 2. Domestic cooking hoods installed and constructed in accordance with Section 505 of the International Mechani-cal Code shall be provided over cooktops or ranges. 3. Cooktops and ranges shall be protected in accordance with Section 904.14. 4. A shutoff for the fuel and electrical supply to the cooking equipment shall be provided in a location to which on-ly staff has access. 5. A timer shall be provided that automatically deactivates the cooking appliances within a period of not more than 120 minutes. 6. A portable fire extinguisher shall be provided. Installation shall be in accordance with Section 906 and the extin-guisher shall be located within a 30-foot (9144 mm) distance of travel from each domestic cooking appliance. Exceptions: 1. Cooking facilities provided within care recipients’ individual dwelling units are not required to comply with this section. 2. Cooktops and ranges used for care-recipient training or nutritional counseling are not required to comply with Item 3 of this section
|  | 420.10 Group R cooking facilities. | In Group R occupancies, cooking appliances used for domestic cooking operations shall be in accordance with Section 917.2 of the International Mechanical Code.
|  | 420.11 Group R-2 dormitory cooking facilities. | Domestic cooking appliances for use by residents of Group R-2 college dormitories shall be in accordance with Sections 420.11.1 and 420.11.2.
|  | 420.11.1 Cooking appliances. | Where located in Group R-2 college dormitories, domestic cooking appliances for use by residents shall be in compliance with all of the following:
|  | 420.11.2 Cooking appliances in sleeping rooms. | Cooktops, ranges and ovens shall not be installed or used in sleeping rooms.
|  | 421.7 Standby power. | Mechanical ventilation and gas detection systems shall be provided with a standby power system in accordance with Section 2702.
|  | 422.6 Electrical systems. | In ambulatory care facilities, the essential electrical system for electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of Chapter 27 and NFPA 99.
|  | 422.7 Domestic cooking. | Installation of cooking appliances used in domestic cooking facilities shall comply with all of the following:
|  | 423.2 Construction. | Storm shelters shall be constructed in accordance with this code and ICC 500 and shall be designated as hurricane shelters, tornado shelters, or combined hurricane and tornado shelters. Buildings or structures that are also designated as emergency shelters shall also comply with Table 1604.5 as Risk Category IV structures.
|  | 423.3 Occupancy classification. | The occupancy classification for a storm shelter shall be determined in accordance with this section.
|  | 423.3.1 Dedicated storm shelters. | A facility designed to be occupied solely as a storm shelter shall be classified as Group A-3 for the determination of requirements other than those covered in ICC 500. Exceptions: 1. The occupancy category for dedicated storm shelters with an occupant load of fewer than 50 persons as de-termined in accordance with ICC 500 shall be in accordance with Section 303. 2. The occupancy category for a dedicated residential storm shelter shall be the Group R occupancy served.
|  | 423.3.2 Storm shelters within host buildings. | Where designated storm shelters are constructed as a room or space within a host building that will normally be occupied for other purposes, the requirements of this code for the occupancy of the building, or the individual rooms or spaces thereof, shall apply unless otherwise required by ICC 500.
|  | 423.4 Critical emergency operations. | In areas where the shelter design wind speed for tornados in accordance with Figure 304.2(1) of ICC 500 is 250 mph, 911 call stations, emergency operation centers and fire, rescue, ambulance and police stations shall comply with Table 1604.5 as a Risk Category IV structure and shall be provided with a storm shelter constructed in accordance with ICC 500.
|  | 423.5 Group E occupancies. | In areas where the shelter design wind speed for tornados is 250 mph in accordance with Figure 304.2(1) of ICC 500, all Group E occupancies with an occupant load of 50 or more shall have a storm shelter constructed in accordance with ICC 500. Exceptions: 1. Group E day care facilities. 2. Group E occupancies accessory to places of religious worship. 3. Buildings meeting the requirements for shelter design in ICC 500.
|  | 423.5.1 Required occupant capacity. | The required occupant capacity of the storm shelter shall include all of the buildings on the site and shall be the greater of the following: 1. The total occupant load of the classrooms, vocational rooms and offices in the Group E occupancy. 2. The occupant load of the largest indoor assembly space that is associated with the Group E occupancy. Exceptions: 1. Where a new building is being added on an existing Group E site, and where the new building is not of sufficient size to accommodate the required occupant capacity of the storm shelter for all of the build-ings on the site, the storm shelter shall at a minimum accommodate the required occupant capacity for the new building. 2. Where approved by the building official, the required occupant capacity of the shelter shall be permit-ted to be reduced by the occupant capacity of any existing storm shelters on the site.
|  | 423.5.2 Location. | Storm shelters shall be located within the buildings they serve or shall be located where the maximum distance of travel from not fewer than one exterior door of each building to a door of the shelter serving that building does not exceed 1,000 feet (305 m).
|  | 424.1 General. | Play structures installed inside all occupancies covered by this code that exceed 10 feet (3048 mm) in height or 150 square feet (14 m2) in area shall comply with Sections 424.2 through 424.5.
|  | 424.5.1 Design. | Play structures exceeding 600 square feet (56 m2) in area or 10 feet (3048 mm) in height shall be designed in accordance with Chapter 16.
|  | 426.1 General. | The provisions of Sections 426.1.1 through 426.1.7 shall apply to buildings in which materials that produce combustible dusts are stored or handled. Buildings that store or handle combustible dusts shall comply with the applicable provisions of the International Fire Code. Where required by the fire code official, NFPA 652 and the applicable provisions of NFPA 61, NFPA 85, NFPA 120, NFPA 484, NFPA 654, NFPA 655 and NFPA 664 shall apply.
|  | 427.2.1 One-hour exterior room. | A 1-hour exterior room shall be a room or enclosure separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, with a fire-resistance rating of not less than 1 hour. Openings between the room or enclosure and interior spaces shall be provided with self-closing smoke- and draft-control assemblies having a fire protection rating of not less than 1 hour. Rooms shall have not less than one exterior wall that is provided with not less than two vents. Each vent shall have a minimum free air opening of not less than 36 square inches (232 cm2) for each 1,000 cubic feet (28 m3) at normal temperature and pressure (NTP) of gas stored in the room and shall be not less than 72 square inches (465 cm2) in aggregate free opening area. One vent shall be within 6 inches (152 mm) of the floor and one shall be within 6 inches (152 mm) of the ceiling. Rooms shall be provided with not fewer than one automatic fire sprinkler to provide container cooling in case of fire.
|  | 427.2.2 One-hour interior room. | Where an exterior wall cannot be provided for the room, a 1-hour interior room shall be provided and shall be a room or enclosure separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, with a fire-resistance rating of not less than 1 hour. Openings between the room or enclosure and interior spaces shall be provided with self-closing smoke- and draft-control assemblies having a fire protection rating of not less than 1 hour. An automatic sprinkler system shall be installed within the room. The room shall be exhausted through a duct to the exterior. Supply and exhaust ducts shall be enclosed in a 1-hour rated shaft enclosure from the room to the exterior. Approved mechanical ventilation shall comply with the International Mechanical Code and be provided with a minimum rate of 1 cubic foot per minute per square foot (0.00508 m3/s/m2) of the area of the room.
|  | 427.2.3 Gas cabinets. | Gas cabinets shall be constructed in accordance with Section 5003.8.6 of the International Fire Code and shall comply with the following:
|  | 428.3.8 Liquid-tight floor. | Portions of laboratory suites where hazardous materials are present shall be provided with a liquid-tight floor.
|  | 428.3.9 Automatic sprinkler systems. | Buildings containing laboratory suites shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
|  | 428.4 Percentage of maximum allowable quantity in each laboratory suite. | The percentage of maximum allowable quantities of hazardous materials in each laboratory suite shall be in accordance with Table 428.3. |  | See BC04 Tables&Figures
Very Cool | Error

## BC5
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
501.1 Scope. | The provisions of this chapter control the height and area of structures hereafter erected and additions to existing structures, including separation of occupancies. | 501.1 Scope. | The provisions of this chapter control the height and area of structures hereafter erected and additions to existing structures.
501.2 Address identification. | Buildings shall be provided with address numbers or letters in accordance with Section 3-505 of the Administrative Code and the rules issued thereunder by the borough president of the borough in which the property is located. Except as otherwise provided by the rules of the borough president in which the property is located, characters shall be a minimum 4 inches (102 mm) high and a minimum of 0.5 inch (12.7 mm) wide. They shall be installed on a contrasting background and be plainly visible from the street or road fronting the property. Where access is by means of a private road and the building address cannot be viewed from the public way, an appropriately placed monument, pole or sign or any other means authorized by the borough president of the borough in which the property is located shall be used to identify the structure.
501.3 Fire Department access. | Access shall be provided to the Fire Department in accordance with Sections 501.3.1 and 501.3.2.
503.1 General. | Unless otherwise specifically modified in Chapter 4, building height, number of stories and building area shall not exceed the limits specified in Sections 504 and 506, based on the type of construction as determined by Section 602, and the occupancies as determined by Section 302, except as modified hereafter in this chapter. Building height, number of stories and building area provisions shall be applied independently. Each portion of a building separated by one or more fire walls complying with Section 706 shall be considered to be a separate building. | 503.1 General. | Unless otherwise specifically modified in Chapter 4 and this chapter, building height, number of stories and building area shall not exceed the limits specified in Sections 504 and 506 based on the type of construction as determined by Section 602 and the occupancies as determined by Section 302 except as modified hereafter. Building height, number of stories and building area provisions shall be applied independently. For the purposes of determining area limitations, height limitations and type of construction, each portion of a building separated by one or more fire walls complying with Section 706 shall be considered to be a separate building.
501.3.1 Frontage. | Every building, exclusive of accessory buildings, shall have at least 8 percent of the total perimeter of the building adjoining a street or frontage space. For the purposes of this section, building perimeter shall be measured at that story having the maximum enclosed floor area; and buildings provided with a front yard or front setback no deeper than 30 feet (9144 mm) in compliance with the New York City Zoning Resolution shall be considered as adjoining the street or frontage space.
503.1.1 Special industrial occupancies. | Buildings and structures of Type I and II construction designed to house special industrial processes that require large areas and unusual building heights to accommodate craneways or special machinery and equipment, including, among others, rolling mills; structural metal fabrication shops and foundries; or the production and distribution of electric, gas or steam power, shall be exempt from the building height, number of stories and building area limitations specified in Sections 504 and 506. Mezzanines within such buildings or structures shall comply with Section 505.2. Documents and plans describing the special industrial processes shall be submitted to the commissioner for approval. | 503.1.1 Special industrial occupancies. | Buildings and structures designed to house special industrial processes that require large areas and unusual building heights to accommodate craneways or special machinery and equipment, including, among others, rolling mills; structural metal fabrication shops and foundries; or the production and distribution of electric, gas or steam power, shall be exempt from the building height, number of stories and building area limitations specified in Sections 504 and 506.
501.3.2 Building access. | Provisions shall be made for access by the Fire Department to every building in accordance with the New York City Fire Code and Section 903.2.11.1 of this code. In addition, multiple dwellings shall comply with Section 54 of the New York State Multiple Dwelling Law, as applicable.
502.1 Definitions. | The following terms are defined in Chapter 2:
503.1.3 Type I construction. | Buildings of Type I construction permitted to be of unlimited tabular building heights and areas are not subject to the special requirements that allow unlimited area buildings in Section 507 or unlimited building height in Sections 503.1.1 and 504.3 or increased building heights and areas for other types of construction. | 503.1.3 Type I construction. | Buildings of Type I construction permitted to be of unlimited tabular building heights and areas are not subject to the special requirements that allow unlimited area buildings in Section 507 or unlimited building height in Sections 503.1.1 and 504.3 or increased building heights and areas for other types of construction.
503.1.2 Buildings on the same tax lot. | Two or more buildings on the same tax lot and under the same ownership and control shall be regulated as separate buildings, or, at the option of the owner, shall be considered as portions of one building where the building height, number of stories of each building and the aggregate building area of the combined buildings are within the limitations specified in Sections 504 and 506. The provisions of this code applicable to the aggregate building shall be applicable to each building.
504.1 General. | The height, in feet, and the number of stories of a building shall be determined based on the type of construction, occupancy classification and whether there is an automatic sprinkler system installed throughout the building. Exception: The building height of one-story aircraft hangars, aircraft paint hangars and buildings used for the manufacturing of aircraft shall not be limited where the building is provided with an automatic sprinkler system or automatic fire-extinguishing system in accordance with Chapter 9 and is entirely surrounded by public ways or yards not less in width than one and one-half times the building height. | 504.1 General. | The height, in feet, and the number of stories of a building shall be determined based on the type of construction, occupancy classification and whether there is an automatic sprinkler system installed throughout the building. Exception: The building height of one-story aircraft hangars, aircraft paint hangars and buildings used for the manufacturing of aircraft shall not be limited where the building is provided with an automatic sprinkler system or automatic fire-extinguishing system in accordance with Chapter 9 and is entirely surrounded by public ways or yards not less in width than one and one-half times the building height.
504.1.1 Unlimited area buildings. | The height of unlimited area buildings shall be designed in accordance with Section 507. | 504.1.1 Unlimited area buildings. | The height of unlimited area buildings shall be designed in accordance with Section 507.
504.1.2 Special provisions. | The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable heights of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510. | 504.1.2 Special provisions. | The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable heights of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510.
504.2 Mixed occupancy. | In a building containing mixed occupancies in accordance with Section 508, no individual occupancy shall exceed the height and number of story limits specified in Section 504 for the applicable occupancies. | 504.2 Mixed occupancy. | In a building containing mixed occupancies in accordance with Section 508, no individual occupancy shall exceed the height and number of story limits specified in this section for the applicable occupancies.
504.4 Number of stories. | The maximum number of stories of a building shall not exceed the limits specified in Table 504.4. | 504.4 Number of stories. | The maximum number of stories above grade plane of a building shall not exceed the limits specified in Table 504.4. |  | See BC05 Tables&Figures
504.3 Height in feet and number of stories. | The maximum height, in feet, of a building shall not exceed the limits specified in Table 504.3. The maximum number of stories of a building shall not exceed the limits specified in Table 504.4. Exceptions: 1. Rooftop structures including but not limited to roof tanks and their supports, ventilating, air conditioning, combined heat and power systems and similar building service equipment, bulkheads, penthouses, greenhouses, chimneys, and parapet walls 4 feet (1219 mm) or less in height shall not be included in the building height of the building or considered an additional story unless the aggregate area of all such structures, exclusive of any solar thermal and solar (photovoltaic) collectors and/or panels and their supporting equipment, exceeds 331/3 percent of the area of the roof of the building upon which they are erected. Rooftop structures shall be constructed in accordance with Section 1510. 2. Solar thermal and solar electric (photovoltaic) collectors and/or panels and their supporting equipment that exceed 331/3 percent of the area of the roof of the building upon which they are erected shall not be included in the height of a building or considered an additional story. 3. Noncombustible steeples, minarets, spires, domes, cupolas and other similar architectural elements, not used for occupancy or storage, shall not be included in the building height of the building or considered an extra story, and may be unlimited in height. |  |  |  | See BC05 Tables&Figures
505.1 General. | Mezzanines shall comply with Section 505.2. Equipment platforms shall comply with Section 505.3. | 505.1 General. | Mezzanines shall comply with Section 505.2. Equipment platforms shall comply with Section 505.3.
505.2 Mezzanines. | A mezzanine or mezzanines in compliance with Section 505.2 shall be considered a portion of the story below. Such mezzanines shall not contribute to either the building area or number of stories as regulated by Section 503.1. The area of the mezzanine shall be included in determining the fire area. The clear height above and below the mezzanine floor construction shall be not less than 7 feet (2134 mm). Exception: The clear height of habitable spaces above or below mezzanines within dwelling units shall be not less than 8 feet (2438 mm). | 505.2 Mezzanines. | A mezzanine or mezzanines in compliance with Section 505.2 shall be considered a portion of the story below. Such mezzanines shall not contribute to either the building area or number of stories as regulated by Section 503.1. The area of the mezzanine shall be included in determining the fire area. The clear height above and below the mezzanine floor construction shall be not less than 7 feet (2134 mm).
505.2.1 Area limitation. | The aggregate area of a mezzanine or mezzanines within a room or space shall be not greater than one-third of the floor area of that room or space in which they are located. The enclosed portions of a room or space shall not be included in determining the permissible floor area of the mezzanine. In determining the allowable mezzanine area, the area of the mezzanine shall not be included in the floor area of the room in which it is contained. Where a room contains both a mezzanine and an equipment platform, the aggregate area of the two raised floor levels shall be not greater than two-thirds of the floor area of that room or space in which they are located. Exceptions: 1. The aggregate area of mezzanines in buildings and structures of Type I or II construction for special industrial occupancies in accordance with Section 503.1.1 shall be not greater than two-thirds of the area of the room in which the mezzanines are located. 2. The aggregate area of a mezzanine or mezzanines within a dwelling unit shall not exceed one-third of the net floor area of such dwelling unit, whether or not portions of such dwelling unit are enclosed. The area of the mezzanine shall not contribute to the determination of the floor area of the dwelling unit in which it is contained. | 505.2.1 Area limitation. | The aggregate area of a mezzanine or mezzanines within a room shall be not greater than one-third of the floor area of that room or space in which they are located. The enclosed portion of a room shall not be included in a determination of the floor area of the room in which the mezzanine is located. In determining the allowable mezzanine area, the area of the mezzanine shall not be included in the floor area of the room. Exceptions: 1. The aggregate area of mezzanines in buildings and structures of Type I or II construction for special industrial occupancies in accordance with Section 503.1.1 shall be not greater than two-thirds of the floor area of the room. 2. The aggregate area of mezzanines in buildings and structures of Type I or II construction shall be not greater than one-half of the floor area of the room in buildings and structures equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 and an approved emergency voice/alarm communication system in accordance with Section 907.5.2.2. 3. The aggregate area of a mezzanine within a dwelling unit that is located in a building equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 shall not be greater than one-half of the floor area of the room, provided that: 3.1. Except for enclosed closets and bathrooms, the mezzanine shall be open to the room in which such mezzanine is located; 3.2. The opening to the room shall be unobstructed except for walls not more than 42 inches (1067 mm) in height, columns and posts; and 3.3. Exceptions to Section 505.2.3 shall not be permitted.
505.2.2 Means of egress. | Each occupant of a mezzanine shall have access to at least two independent means of egress where the common path of egress travel exceeds the limitations of Section 1006.2. Where a stairway provides a means of exit access from a mezzanine, the maximum travel distance includes the distance traveled on the stairway measured in the plane of the tread nosing. Accessible means of egress shall be provided in accordance with Section 1009. Exception: A single means of egress shall be permitted in accordance with Section 1006.2. | 505.2.2 Means of egress. | The means of egress for mezzanines shall comply with the applicable provisions of Chapter 10.
505.2.3 Openness. | A mezzanine shall be open and unobstructed to the room in which such mezzanine is located except for walls or railings not more than 42 inches (1067 mm) in height, columns and posts. Exceptions: 1. Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the occupant load of the aggregate area of the enclosed space is not greater than 10. 2. A mezzanine having two or more means of egress is not required to be open to the room in which the mezzanine is located, if at least one of the means of egress provides direct access to an exit located on the mezzanine level. 3. Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the aggregate floor area of the enclosed space is‡ not greater than 10 percent of the mezzanine area. 4. In industrial facilities, mezzanines used for control equipment are permitted to be glazed on all sides. 5. A mezzanine having two or more means of egress shall not be required to be open to the room in which the mezzanine is located in occupancies, other than Groups H and I, that comply with Items 5.1 through 5.4. 5.1. Such occupancy is no more than two stories above grade plane, 5.2. Such occupancy is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, 5.3. An approved fire alarm system is installed throughout the entire building or structure in which such occupancy is located, and 5.4. Notification appliances are installed throughout the mezzanine in accordance with NFPA 72. | 505.2.3 Openness. | A mezzanine shall be open and unobstructed to the room in which such mezzanine is located except for walls not more than 42 inches (1067 mm) in height, columns and posts. Exceptions: 1. Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the occupant load of the aggregate area of the enclosed space is not greater than 10. 2. A mezzanine having two or more exits or access to exits is not required to be open to the room in which the mezzanine is located. 3. Mezzanines or portions thereof are not required to be open to the room in which the mezzanines are located, provided that the aggregate floor area of the enclosed space is not greater than 10 percent of the mezzanine area. 4. In industrial facilities, mezzanines used for control equipment are permitted to be glazed on all sides. 5. In occupancies other than Groups H and I, which are no more than two stories above grade plane and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, a mezzanine having two or more exits or access to exits shall not be required to be open to the room in which the mezzanine is located.
505.3 Equipment platforms. | Equipment platforms in buildings shall not be considered as a portion of the floor below. Such equipment platforms shall not contribute to either the building area or the number of stories as regulated by Section 503.1. The area of the equipment platform shall not be included in determining the fire area in accordance with Section 903. Equipment platforms shall not be a part of any mezzanine and such platforms and the walkways, stairways, alternating tread devices and ladders providing access to an equipment platform shall not serve as a part of the means of egress from the building. | 505.3 Equipment platforms. | Equipment platforms in buildings shall not be considered as a portion of the floor below. Such equipment platforms shall not contribute to either the building area or the number of stories as regulated by Section 503.1. The area of the equipment platform shall not be included in determining the fire area in accordance with Section 903. Equipment platforms shall not be a part of any mezzanine and such platforms and the walkways, stairways, alternating tread devices and ladders providing access to an equipment platform shall not serve as a part of the means of egress from the building.
5.1.
5.1.
505.3.1 Area limitation. | The aggregate area of all industrial equipment platforms within a room shall be not greater than two-thirds of the area of the room in which they occur. Where an equipment platform is located in the same room as a mezzanine, the area of the mezzanine shall be determined by Section 505.2.1 and the combined aggregate area of the equipment platforms and mezzanines shall be not greater than two-thirds of the room in which they are located. | 505.3.1 Area limitation. | The aggregate area of all equipment platforms within a room shall be not greater than two-thirds of the area of the room in which they are located. Where an equipment platform is located in the same room as a mezzanine, the area of the mezzanine shall be determined by Section 505.2.1 and the combined aggregate area of the equipment platforms and mezzanines shall be not greater than two-thirds of the room in which they are located. The area of the mezzanine shall not exceed the area determined in accordance with Section 505.2.1.
5.2.
5.2.
5.3.
5.3.
505.3.3 Guards. | Equipment platforms shall have guards where required by Section 1015.2. | 505.3.3 Guards. | Equipment platforms shall have guards where required by Section 1015.2.
5.4.
506.1 General. | The floor area of a building shall be determined based on the type of construction, occupancy classification, whether there is an automatic sprinkler system installed throughout the building and the amount of building frontage on public way or open space. | 506.1 General. | The floor area of a building shall be determined based on the type of construction, occupancy classification, whether there is an automatic sprinkler system installed throughout the building and the amount of building frontage on public way or open space.
506.1.1 Unlimited area buildings. | Unlimited area buildings shall be designed in accordance with Section 507. | 506.1.1 Unlimited area buildings. | Unlimited area buildings shall be designed in accordance with Section 507.
506.1.2 Special provisions. | The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510. | 506.1.2 Special provisions. | The special provisions of Section 510 permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in Section 510.
505.3.2 Fire suppression. | Where located in a building that is required to be protected by an automatic sprinkler system, industrial equipment platforms shall be fully protected by sprinklers above and below the platform, where required by the standards referenced in Section 903.3.
506.2 Allowable area determination. | The allowable area of a building shall be determined in accordance with the applicable provisions of Sections 506.2.1 through 506.2.4, and Section 506.3. | 506.2 Allowable area determination. | The allowable area of a building shall be determined in accordance with the applicable provisions of Sections 506.2.1, 506.2.2 and 506.3.
506.2.2.1 Group H-2 or H-3 mixed occupancies. | For a building containing Group H-2 or H-3 occupancies, the allowable area shall be determined in accordance with Section 508.4.2, with the sprinkler system increase applicable only to the portions of the building not classified as Group H-2 or H-3. | 506.2.2.1 Group H-2 or H-3 mixed occupancies. | For a building containing Group H-2 or H-3 occupancies, the allowable area shall be determined in accordance with Section 508.4.2, with the sprinkler system increase applicable only to the portions of the building not classified as Group H-2 or H-3.
506.1.3 Basement and cellar. | A single basement or cellar need not be included in the total allowable building area, provided such basement or cellar does not exceed the area permitted for a building with no more than one story above grade plane.
506.3 Frontage increase. | Area factor increase shall be determined in accordance with Sections 506.3.1 through 506.3.3. | 506.3 Frontage increase. | Every building shall adjoin or have access to a public way to receive an area factor increase based on frontage. Area factor increase shall be determined in accordance with Sections 506.3.1 through 506.3.3.
506.3.1 Minimum percentage of perimeter. | To qualify for an area factor increase based on frontage, a building shall have not less than 25 percent of its perimeter on a public way or open space. Such open space shall be either on the same zoning lot or dedicated for public use and shall be accessed from a street or approved fire lane. | 506.3.1 Minimum percentage of perimeter. | To qualify for an area factor increase based on frontage, a building shall have not less than 25 percent of its perimeter on a public way or open space. Such open space shall be either on the same lot or dedicated for public use and shall be accessed from a street or approved fire lane.
506.2.1 Single-occupancy, one-story buildings. | The allowable area of a single-occupancy building with no more than one story above grade plane shall be determined in accordance with Equation 5-1:
506.3.2 Minimum frontage distance. | To qualify for an area factor increase based on frontage, the public way or open space adjacent to the building perimeter shall have a minimum distance (W) of 20 feet (6096 mm) measured at right angles from the building face to any of the following: Exception: Where a building meets the requirements of Section 507, as applicable, except for compliance with the minimum 60-foot (18 288 mm) public way or yard requirement, and the value of W is greater than 30 feet (9144 mm), the value of W shall not exceed 60 feet (18 288 mm). | 506.3.2 Minimum frontage distance. | To qualify for an area factor increase based on frontage, the public way or open space adjacent to the building perimeter shall have a minimum distance (W) of 20 feet (6096 mm) measured at right angles from the building face to any of the following:
506.2.2 Mixed-occupancy, one-story buildings. | The allowable area of a mixed-occupancy building with no more than one story above grade plane shall be determined in accordance with the applicable provisions of Section 508.1 based on Equation 5-1 for each applicable occupancy.
506.3.3 Amount of increase. | The area factor increase based on frontage shall be determined in accordance with Equation 5-5: | 506.3.3 Amount of increase. | The area factor increase based on frontage shall be determined in accordance with Table 506.3.3. |  | See BC05 Tables&Figures
506.2.3 Single-occupancy, multistory buildings. | The allowable area of a single-occupancy building with more than one story above grade plane shall be determined in accordance with Equation 5-2:
507.1 General. | The area of buildings of the occupancies and configurations specified in Sections 507.1 through 507.18 shall not be limited, except that only one cellar or one basement shall be permissible. | 507.1 General. | The area of buildings of the occupancies and configurations specified in Sections 507.1 through 507.13 shall not be limited. Basements not more than one story below grade plane shall be permitted.
506.2.4 Mixed-occupancy, multistory buildings. | Each story of a mixed-occupancy building with more than one story above grade plane shall individually comply with the applicable requirements of Section 508.1. For buildings with more than three stories above grade plane, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories, determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed three.Exception: For buildings designed as separated occupancies under Section 508.4 and equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed four.
507.1.1 Accessory occupancies. | Accessory occupancies shall be permitted in unlimited area buildings in accordance with the provisions of Section 508.2, otherwise the requirements of Sections 507.3 through 507.18 shall be applied, where applicable. | 507.1.1 Accessory occupancies. | Accessory occupancies shall be permitted in unlimited area buildings in accordance with the provisions of Section 508.2, otherwise the requirements of Sections 507.3 through 507.13 shall be applied, where applicable.
506.2.4.1 Group H-2 or H-3 mixed occupancies. | For a building containing Group H-2 or H-3 occupancies, the allowable area shall be determined in accordance with Section 508.4.2, with the sprinkler system increase applicable only to the portions of the building not classified as Group H-2 or H-3.
507.2 Measurement of open spaces. | Where Sections 507.3 through 507.18 require buildings to be surrounded and adjoined by public ways and yards, those open spaces shall be determined as follows: | 507.2 Measurement of open spaces. | Where Sections 507.3 through 507.13 require buildings to be surrounded and adjoined by public ways and yards, those open spaces shall be determined as follows:
507.2.1 Reduced open space. | The public ways or yards of 60 feet (18 288 mm) in width required in Sections 507.3, 507.4, 507.5 and 507.6 shall be permitted to be reduced to not less than 40 feet (12 192 mm) in width provided all of the following requirements are met: | 507.2.1 Reduced open space. | The public ways or yards of 60 feet (18 288 mm) in width required in Sections 507.3, 507.4, 507.5, 507.6 and 507.12 shall be permitted to be reduced to not less than 40 feet (12 192 mm) in width, provided that the following requirements are met:
507.3 Nonsprinklered, one-story buildings. | The area of a Group F-2 or S-2 building no more than one story in height, of other than Type V construction, shall not be limited when the building is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width. | 507.3 Nonsprinklered, one-story buildings. | The area of a Group F-2 or S-2 building not more than one story in height shall not be limited where the building is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width.
507.4 Sprinklered, one-story buildings. | The area of a Group A-4 building no more than one story in height above grade plane of other than Type V construction, or the area of a Group B, F, M or S building no more than one story in height of any construction type, shall not be limited where the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width. Exceptions: 1. In Group F-2 and S-2 occupancies, one-story rack storage facilities of Type II construction that are not accessible to the public shall not be limited in height provided that such buildings conform to the requirements of the New York City Fire Code, and Sections 507.4 and 903.3.1.1 of this code. 2. The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, swimming and equestrian activities, in occupancies in Group A-4, provided that both of the following criteria are met: 2.1. Exit doors directly to the outside are provided for occupants of the participant sports areas. 2.2. The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 907. | 507.4 Sprinklered, one-story buildings. | The area of a Group A-4 building not more than one story above grade plane of other than Type V construction, or the area of a Group B, F, M or S building no more than one story above grade plane of any construction type, shall not be limited where the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width. Exceptions: 1. Buildings and structures of Type I or II construction for rack storage facilities that do not have access by the public shall not be limited in height, provided that such buildings conform to the requirements of Sections 507.4 and 903.3.1.1 and Chapter 32 of the International Fire Code. 2. The automatic sprinkler system shall not be required in areas occupied for indoor participant sports, such as tennis, skating, swimming and equestrian activities in occupancies in Group A-4, provided that the following criteria are met: 2.1. Exit doors directly to the outside are provided for occupants of the participant sports areas. 2.2. The building is equipped with a fire alarm system with manual fire alarm boxes installed in accordance with Section 907. 2.3. An automatic sprinkler system is provided in storage rooms, press boxes, concession booths or other spaces ancillary to the sport activity space.
507.4.1 Mixed occupancy buildings with Groups A-1 and A-2. | Group A-1 and A-2 occupancies of other than Type V construction shall be permitted within mixed occupancy buildings of unlimited area complying with Section 507.4, provided all of the following criteria are met: | 507.4.1 Mixed occupancy buildings with Groups A-1 and A-2. | Group A-1 and A-2 occupancies of other than Type V construction shall be permitted within mixed occupancy buildings of unlimited area complying with Section 507.4, provided that the following criteria are met:
507.8.1 Allowable area. | The aggregate floor area of Group H occupancies located in an unlimited area building shall not exceed 10 percent of the area of the building and shall not exceed the area limitations for the Group H occupancies as specified in Section 506 based on the perimeter of each Group H floor area that fronts on a public way or open space. | 507.8.1 Allowable area. | The aggregate floor area of Group H occupancies located in an unlimited area building shall not exceed 10 percent of the area of the building or the area limitations for the Group H occupancies as specified in Section 506 based on the perimeter of each Group H floor area that fronts on a public way or open space.
507.8.1.1 Located within the building. | The aggregate floor area of Group H occupancies not located at the perimeter of the building shall not exceed 25 percent of the area limitations for the Group H occupancies as specified in Section 506. | 507.8.1.1 Located within the building. | The aggregate floor area of Group H occupancies not located at the perimeter of the building shall not exceed 25 percent of the area limitations for the Group H occupancies as specified in Section 506.
507.5 Sprinklered, two-story buildings. | The area of a Group B, F, M or S building no more than two stories in height shall not be limited when the building is provided with an automatic sprinkler system in accordance with Section 903.3.1.1 throughout, and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width.
507.6 Group A buildings. | The area of a Group A-1, A-2, A-3, or A-4 building of Type IIA, IIIA or IV construction shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The area of a one-story, Group A-3 building used as a house of worship, community hall, dance hall, exhibition hall, gymnasium, lecture hall, indoor swimming pool or tennis court of Type IIB construction shall not be limited when all of the following criteria are met:
507.8.1.1.3 Spray paint booths. | Spray paint booths that comply with the New York City Fire Code need not be located on the outer perimeter. | 507.8.1.1.3 Spray paint booths. | Spray paint booths that comply with the International Fire Code need not be located on the outer perimeter.
507.7 Reserved.
507.8.2 Located on building perimeter. | Except as provided for in Section 507.8.1.1, Group H occupancies shall be located on the perimeter of the building. In Group H-2 and H-3 occupancies, not less than 25 percent of the perimeter of such occupancies shall be an exterior wall. | 507.8.2 Located on building perimeter. | Except as provided for in Section 507.8.1.1, Group H occupancies shall be located on the perimeter of the building. In Group H-2 and H-3 occupancies, not less than 25 percent of the perimeter of such occupancies shall be an exterior wall.
507.8 Group H occupancies. | Group H-2, H-3 and H-4 fire occupancies shall be permitted in unlimited area buildings containing Group F or S occupancies in accordance with Sections 507.4 and 507.5 and the provisions of Sections 507.8.1 through 507.8.4.
507.8.3 Occupancy separations. | Group H occupancies shall be separated from the remainder of the unlimited area building and from each other in accordance with Table 508.4. | 507.8.3 Occupancy separations. | Group H occupancies shall be separated from the remainder of the unlimited area building and from each other in accordance with Table 508.4. |  | See BC05 Tables&Figures
507.8.4 Height limitations. | For two-story, unlimited area buildings, Group H occupancies shall not be located more than one story above grade plane unless permitted based on the allowable height and number of stories and feet as set forth in Section 504 based on the type of construction of the unlimited area building. | 507.8.4 Height limitations. | For two-story, unlimited area buildings, Group H occupancies shall not be located more than one story above grade plane unless permitted based on the allowable height and number of stories and feet as specified in Section 504 based on the type of construction of the unlimited area building.
507.9 Unlimited mixed occupancy buildings with Group H-5. | The area of a Group B, F, H-5, M or S building no more than two stories above grade plane shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width, provided all of the following criteria are met: 1. Buildings containing Group H-5 occupancy shall be of Type I or II construction. 2. Each area used for Group H-5 occupancy shall be separated from other occupancies as required in Sections 415.11 and 508.4. 3. Each area used for Group H-5 occupancy shall not exceed the maximum allowable area permitted for such occupancies in Section 503.1 including modifications of Section 506. Exception: Where the Group H-5 occupancy exceeds the maximum allowable area, the Group H-5 shall be subdivided into areas that are separated by 2-hour fire barriers. | 507.9 Unlimited mixed occupancy buildings with Group H-5. | The area of a Group B, F, H-5, M or S building not more than two stories above grade plane shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width, provided that the following criteria are met: 1. Buildings containing Group H-5 occupancy shall be of Type I or II construction. 2. Each area used for Group H-5 occupancy shall be separated from other occupancies as required in Sections 415.11 and 508.4. 3. Each area used for Group H-5 occupancy shall not exceed the maximum allowable area permitted for such occupancies in Section 503.1 including modifications of Section 506. Exception: Where the Group H-5 occupancy exceeds the maximum allowable area, the Group H-5 shall be subdivided into areas that are separated by 2-hour fire barriers.
507.8.1.1.1 Liquid use, dispensing and mixing rooms. | Liquid use, dispensing and mixing rooms having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the New York City Fire Code and NFPA 30.
507.10 Aircraft paint hangar. | The area of a Group H-2 aircraft paint hangar no more than one story above grade plane shall not be limited where such aircraft paint hangar complies with the provisions of Section 412.6 and is surrounded and adjoined by public ways or yards not less in width than one and one-half times the building height. | 507.10 Aircraft paint hangar. | The area of a Group H-2 aircraft paint hangar not more than one story above grade plane shall not be limited where such aircraft paint hangar complies with the provisions of Section 412.5 and is surrounded and adjoined by public ways or yards not less in width than one and one-half times the building height.
507.8.1.1.2 Liquid storage rooms. | Liquid storage rooms having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the New York City Fire Code and NFPA 30.
507.11 Group E buildings. | The area of a Group E building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. The area of a one-story Group E building of Type IIB construction shall not be limited when the following criteria are met: | 507.11 Group E buildings. | The area of a Group E building not more than one story above grade plane, of Type II, IIIA or IV construction, shall not be limited provided that the following criteria are met:
507.12 Motion picture theaters. | In buildings of Type II, IIIA and IV construction, the area of a motion picture theater located on the first story above grade plane shall not be limited when the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined on all sides by public ways or yards not less than 60 feet (18 288 mm) in width. | 507.12 Motion picture theaters. | In buildings of Type II construction, the area of a motion picture theater located on the first story above grade plane shall not be limited where the building is provided with an automatic sprinkler system throughout in accordance with Section 903.3.1.1 and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width.
507.13 Covered and open mall buildings and anchor buildings. | The area of covered and open mall buildings and anchor buildings not exceeding three stories in height that comply with Section 402 shall not be limited. | 507.13 Covered and open mall buildings and anchor buildings. | The area of covered and open mall buildings and anchor buildings not exceeding three stories in height that comply with Section 402 shall not be limited.
508.1 General. | Each portion of a building shall be individually classified in accordance with Section 302.1. Where a building contains more than one occupancy group, the building or portion thereof shall comply with the applicable provisions of Section 508.2, 508.3 or 508.4, or a combination of these sections. Exceptions: 1. Occupancies separated in accordance with Section 510. 2. Where required by Table 415.6.2, areas of Group H-1, H-2 and H-3 occupancies shall be located in a detached building or structure. 3. Where identified in Table 509, rooms or spaces shall be treated as incidental uses. 4. Where not identified in Table 509, mechanical and/or electrical equipment rooms shall be permitted to be classified as the occupancy within which they are located, or at the option of the applicant, classified as Group F-2 occupancy in accordance with Section 306.3. 5. Commercial kitchens classified as Group F-2 need not be separated by fire separations from adjoining dining spaces, provided that the conditions of Items 5.1, 5.2, and 5.3 are met: 5.1. The cooking equipment is vented directly to the outdoors; 5.2. A draft curtain of noncombustible material, at least 24 inches (609 mm) down from the ceiling, is provided to separate the opening between the cooking facilities and the dining spaces; and 5.3. A fire protection system is installed and located as set forth in Item 5.3.1 or 5.3.2. 5.3.1. A fire protection system in accordance with Sections 903 and 904 is installed within the cooking facilities. Additionally, sprinkler heads protecting the opening between the cooking facilities and the dining spaces shall be located within 24 inches (609 mm) of the curtain on the cooking facilities side; or 5.3.2. A fire protection system in accordance with Section 903 is located along any opening between the cooking facilities and the dining space on the cooking facilities side, with sprinkler heads located within 24 inches (609 mm) of the opening and, if the opening is more than 60 inches (1524 mm) wide, the sprinkler heads are spaced not more than 48 inches (1219 mm) on center. Where the conditions of Items 5.1, 5.2, and 5.3 cannot be satisfied, such commercial kitchen shall be separated from adjoining dining spaces in accordance with Table 508.4, footnote f. | 508.1 General. | Each portion of a building shall be individually classified in accordance with Section 302.1. Where a building contains more than one occupancy group, the building or portion thereof shall comply with the applicable provisions of Section 508.2, 508.3, 508.4 or 508.5, or a combination of these sections. Exceptions: 1. Occupancies separated in accordance with Section 510. 2. Where required by Table 415.6.5, areas of Group H-1, H-2 and H-3 occupancies shall be located in a detached building or structure. |  | See BC05 Tables&Figures
508.2 Accessory occupancies. | Accessory occupancies are those occupancies that are ancillary to the main occupancy of the building or portion thereof. Accessory occupancies shall comply with the provisions of Sections 508.2.1 through 508.2.4. | 508.2 Accessory occupancies. | Accessory occupancies are those occupancies that are ancillary to the main occupancy of the building or portion thereof. Accessory occupancies shall comply with the provisions of Sections 508.2.1 through 508.2.4.
508.2.1 Occupancy classification. | Accessory occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space. | 508.2.1 Occupancy classification. | Accessory occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space.
508.2.2 Allowable building height. | The allowable height and number of stories of the building containing accessory occupancies shall be in accordance with Section 504 for the main occupancy of the building. | 508.2.2 Allowable building height. | The allowable height and number of stories of the building containing accessory occupancies shall be in accordance with Section 504 for the main occupancy of the building.
508.2.3 Allowable building area. | The allowable area of the building shall be based on the applicable provisions of Section 506 for the main occupancy of the building. Aggregate accessory occupancies shall not occupy more than 10 percent of the building area of the story in which they are located and shall not exceed the tabular values for nonsprinklered buildings in Table 506.2 for each such accessory occupancy. Exceptions: 1. The following accessory occupancies are permitted to occupy more than 10 percent of the floor area of the story in which they are located: 1.1. Accessory assembly areas having a floor area less than 750 square feet (69.7 m2). 1.2. Assembly areas that are accessory to Group E occupancies. 1.3. Accessory religious educational rooms and religious auditoriums with occupant loads of less than 100. 2. Rooms or spaces within Group H-2, H-3, H-4 or H-5 occupancy shall not be considered accessory occupancies and shall be treated as separated occupancies. | 508.2.3 Allowable building area. | The allowable area of the building shall be based on the applicable provisions of Section 506 for the main occupancy of the building. Aggregate accessory occupancies shall not occupy more than 10 percent of the floor area of the story in which they are located and shall not exceed the tabular values for nonsprinklered buildings in Table 506.2 for each such accessory occupancy. |  | See BC05 Tables&Figures
508.2.4 Separation of occupancies. | No separation is required between accessory occupancies and the main occupancy. Exceptions: 1. Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4. 2. Separated tenancies in accordance with the requirements of Section 510. | 508.2.4 Separation of occupancies. | No separation is required between accessory occupancies and the main occupancy. Exceptions: 1. Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4. 2. Group I-1, R-1, R-2 and R-3 dwelling units and sleeping units shall be separated from other dwelling or sleeping units and from accessory occupancies contiguous to them in accordance with the requirements of Section 420.
508.3 Nonseparated occupancies. | Buildings or portions of buildings that comply with the provisions of this section shall be considered as nonseparated occupancies. | 508.3 Nonseparated occupancies. | Buildings or portions of buildings that comply with the provisions of this section shall be considered as nonseparated occupancies.
507.14 Group B buildings. | Notwithstanding the provisions of Sections 507.3 and 507.4, the area of a Group B building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.
508.3.1 Occupancy classification. | Nonseparated occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space. In addition, the most restrictive provisions of Chapter 9 that apply to the nonseparated occupancies shall apply to the total nonseparated occupancy area. Where nonseparated occupancies occur in a high-rise building, the most restrictive requirements of Section 403 that apply to the nonseparated occupancies shall apply throughout the high-rise building. | 508.3.1 Occupancy classification. | Nonseparated occupancies shall be individually classified in accordance with Section 302.1. The requirements of this code shall apply to each portion of the building based on the occupancy classification of that space. In addition, the most restrictive provisions of Chapter 9 that apply to the nonseparated occupancies shall apply to the total nonseparated occupancy area.
507.15 Group F-2 buildings. | Notwithstanding the provisions of Sections 507.3 and 507.4, the area of a Group F-2 building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.
507.16 Group M buildings. | Notwithstanding the provisions of Sections 507.3 and 507.4, the area of a Group M building of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.
507.17 Group R buildings. | The area of Group R-1 and R-2 buildings of Type IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, as applicable.
507.18 Group S-2 buildings. | Notwithstanding the provisions of Sections 507.3 and 507.4, the area of a Group S-2 building of Type IB, IIA, IIIA or IV construction shall not be limited where the building is protected throughout with an approved auto­matic sprinkler system in accordance with Section 903.3.1.1.
508.3.3 Separation. | No separation is required between nonseparated occupancies. Exceptions: 1. Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4. 2. Separated tenancies in accordance with Section 510.10. 3. Commercial kitchens shall be separated in accordance with Section 508.1, Exception 5. | 508.3.3 Separation. | No separation is required between nonseparated occupancies. Exceptions: 1. Group H-2, H-3, H-4 and H-5 occupancies shall be separated from all other occupancies in accordance with Section 508.4. 2. Group I-1, R-1, R-2 and R-3 dwelling units and sleeping units shall be separated from other dwelling or sleeping units and from other occupancies contiguous to them in accordance with the requirements of Section 420.
508.4 Separated occupancies. | Buildings or portions of buildings that comply with the provisions of this section shall be considered as separated occupancies. | 508.4 Separated occupancies. | Buildings or portions of buildings that comply with the provisions of this section shall be considered as separated occupancies.
508.4.1 Occupancy classification. | Separated occupancies shall be individually classified in accordance with Section 302.1. Each separated space shall comply with this code based on the occupancy classification of that portion of the building. | 508.4.1 Occupancy classification. | Separated occupancies shall be individually classified in accordance with Section 302.1. Each separated space shall comply with this code based on the occupancy classification of that portion of the building. The most restrictive provisions of Chapter 9 that apply to the separate occupancies shall apply to the total nonfire-barrier-separated occupancy areas. Occupancy separations that serve to define fire area limits established in Chapter 9 for requiring a fire protection system shall also comply with Section 901.7.
508.4.2 Allowable building area. | In each story, the building area shall be such that the sum of the ratios of the actual building area of each separated occupancy divided by the allowable building area of each separated occupancy shall not exceed 1. | 508.4.2 Allowable building area. | In each story, the building area shall be such that the sum of the ratios of the actual building area of each separated occupancy divided by the allowable building area of each separated occupancy shall not exceed 1.
5.3.1.
508.4.4 Separation. | Individual occupancies shall be separated from adjacent occupancies in accordance with Table 508.4. Exception: Fire separations of Group H and I-2 occupancies shall not be permitted any reductions in fire-resistance ratings. | 508.4.4 Separation. | Individual occupancies shall be separated from adjacent occupancies in accordance with Table 508.4. |  | See BC05 Tables&Figures
5.3.2.
508.4.4.1 Construction. | Required separations shall be fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, so as to completely separate adjacent occupancies. | 508.4.4.1 Construction. | Required separations shall be fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, so as to completely separate adjacent occupancies. Mass timber elements serving as fire barriers or horizontal assemblies to separate occupancies in Type IV-B or IV-C construction shall be separated from the interior of the building with an approved thermal barrier consisting of gypsum board that is not less than 1/2 inch (12.7 mm) in thickness or a material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275.
508.3.2 Allowable building area and height. | The allowable building area and height of the building or portion thereof shall be based on the most restrictive allowances for the occupancy groups under consideration for the type of construction of the building in accordance with Section 503.1.
508.4.3 Allowable height. | Each separated occupancy shall comply with the building height limitations based on the type of construction of the building in accordance with Section 503.1. Exception: Special provisions of Section 510 shall permit occupancies at building heights other than provided in Section 503.1.
509.2 Occupancy classification. | Incidental uses shall not be individually classified in accordance with Section 302.1. Incidental uses shall be included in the building occupancies within which they are located. | 509.2 Occupancy classification. | Incidental uses shall not be individually classified in accordance with Section 302.1. Incidental uses shall be included in the building occupancies within which they are located.
509.3 Area limitations. | Incidental uses shall not occupy more than 10 percent of the building in which they are located. | 509.3 Area limitations. | Incidental uses shall not occupy more than 10 percent of the building area of the story in which they are located.
509.1 General. | Incidental uses listed in Table 509 and located within single occupancy or mixed occupancy buildings shall comply with the provisions of this section. Incidental uses are ancillary functions associated with a given occupancy that generally pose a greater level of risk to that occupancy and are limited to those uses listed in Table 509. Exception: Incidental uses within and serving a dwelling unit are not required to comply with this section. |  |  |  | See BC05 Tables&Figures
509.4 Separation and protection. | The incidental uses listed in Table 509 shall be separated from the remainder of the building or equipped with an automatic sprinkler system, or both, in accordance with the provisions of that table. | 509.4 Separation and protection. | The incidental uses specified in Table 509.1 shall be separated from the remainder of the building or equipped with an automatic sprinkler system, or both, in accordance with the provisions of that table. |  | See BC05 Tables&Figures
509.4.1 Separation. | Where Table 509 specifies a fire-resistance-rated separation, the incidental uses shall be separated from the remainder of the building by a fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section 711, or both. Construction supporting 1-hour fire barriers or horizontal assemblies used for incidental use separations in buildings of Type IIB, IIIB and VB construction is not required to be fire-resistance rated unless required by other sections of this code. | 509.4.1 Separation. | Where Table 509.1 specifies a fire-resistance-rated separation, the incidental uses shall be separated from the remainder of the building by a fire barrier constructed in accordance with Section 707 or a horizontal assembly constructed in accordance with Section 711, or both. Construction supporting 1-hour fire barriers or horizontal assemblies used for incidental use separations in buildings of Type IIB, IIIB and VB construction is not required to be fire-resistance rated unless required by other sections of this code. |  | See BC05 Tables&Figures
509.4.2 Protection. | Where Table 509 permits an automatic sprinkler system without a fire barrier, the incidental uses shall be separated from the remainder of the building by construction capable of resisting the passage of smoke. The walls shall extend from the top of the foundation or floor assembly below to the underside of the ceiling that is a component of a fire-resistance-rated floor assembly or roof assembly above or to the underside of the floor or roof sheathing, deck or slab above. Doors shall be self- or automatic-closing upon detection of smoke in accordance with Section 716.5.9.3. Doors shall not have air transfer openings and shall not be undercut in excess of the clearance permitted in accordance with NFPA 80. Walls surrounding the incidental use shall not have air transfer openings unless provided with smoke dampers in accordance with Section 710.8. | 509.4.2 Protection. | Where Table 509.1 permits an automatic sprinkler system without a fire barrier, the incidental uses shall be separated from the remainder of the building by construction capable of resisting the passage of smoke. The walls shall extend from the top of the foundation or floor assembly below to the underside of the ceiling that is a component of a fire-resistance-rated floor assembly or roof assembly above or to the underside of the floor or roof sheathing, deck or slab above. Doors shall be self- or automatic-closing upon detection of smoke in accordance with Section 716.2.6.6. Doors shall not have air transfer openings and shall not be undercut in excess of the clearance permitted in accordance with NFPA 80. Walls surrounding the incidental use shall not have air transfer openings unless provided with smoke dampers in accordance with Section 710.8. |  | See BC05 Tables&Figures
509.4.2.1 Protection limitation. | Except as specified in Table 509 for certain incidental uses, where an automatic sprinkler system is provided in accordance with Table 509, only the space occupied by the incidental use need be equipped with such a system. | 509.4.2.1 Protection limitation. | Where an automatic sprinkler system is provided in accordance with Table 509.1, only the space occupied by the incidental use need be equipped with such a system. |  | See BC05 Tables&Figures
510.1 General. | The provisions in Sections 510.2 through 510.10 shall permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable building heights and areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in this section for such condition and other applicable requirements of this code. The provisions of Sections 510.2 through 510.8 are to be considered independent and separate from each other. | 510.1 General. | The provisions in Sections 510.2 through 510.9 shall permit the use of special conditions that are exempt from, or modify, the specific requirements of this chapter regarding the allowable building heights and areas of buildings based on the occupancy classification and type of construction, provided the special condition complies with the provisions specified in this section for such condition and other applicable requirements of this code. The provisions of Sections 510.2 through 510.8 are to be considered independent and separate from each other.
510.2 Horizontal building separation allowance. | Buildings shall be considered as separate and distinct from each other for the purpose of determining area limitations, continuity of fire walls, limitation of number of stories and type of construction, where all of the following conditions are met: 1. The buildings are separated with a horizontal floor assembly having a fire-resistance rating of not less than 3 hours. 2. The building below the horizontal assembly is of Type IA construction. 3. Shaft, stairway, ramp or escalator enclosures through the horizontal floor assembly shall have not less than a 2-hour fire-resistance rating with opening protectives in accordance with Section 716.5. Exception: Where the enclosure walls below the horizontal floor assembly have not less than a 3-hour fire-resistance rating with opening protectives in accordance with Section 716.5, the enclosure walls extending above the horizontal floor assembly shall be permitted to have a 1-hour fire-resistance rating, provided: 1. The building above the horizontal floor assembly is not required to be of Type I construction; 2. The enclosure connects fewer than four stories; and 3. The enclosure opening protectives above the horizontal floor assembly have a fire protection rating of not less than 1 hour. 4. The building or buildings above the horizontal assembly shall be permitted to have multiple Group A occupancy uses, each with an occupant load of less than 300, or Group B, M, R or S occupancies. 5. The building below the horizontal assembly shall be protected throughout by an approved automatic sprinkler system in accordance with Section 903.3.1.1, and shall be permitted to be any occupancy allowed by this code except Group H. 6. The maximum building height in feet (mm) as measured from the grade plane shall not exceed the limits set forth in Section 504.3 for the building having the smaller allowable height as measured from the grade plane. | 510.2 Horizontal building separation allowance. | A building shall be considered as separate and distinct buildings for the purpose of determining area limitations, continuity of fire walls, limitation of number of stories and type of construction where the following conditions are met: 1. The buildings are separated with a horizontal assembly having a fire-resistance rating of not less than 3 hours. Where vertical offsets are provided as part of a horizontal assembly, the vertical offset and the structure supporting the vertical offset shall have a fire-resistance rating of not less than 3 hours. 2. The building below, including the horizontal assembly, is of Type IA construction. 3. Shaft, stairway, ramp and escalator enclosures through the horizontal assembly shall have not less than a 2-hour fire-resistance rating with opening protectives in accordance with Section 716. Exception: Where the enclosure walls below the horizontal assembly have not less than a 3-hour fire-resistance rating with opening protectives in accordance with Section 716, the enclosure walls extending above the horizontal assembly shall be permitted to have a 1-hour fire-resistance rating, provided that the following conditions are met: 1. The building above the horizontal assembly is not required to be of Type I construction. 2. The enclosure connects fewer than four stories. 3. The enclosure opening protectives above the horizontal assembly have a fire protection rating of not less than 1 hour. 4. Interior exit stairways located within the Type IA building are permitted to be of combustible materials where the following requirements are met: 4.1. The building above the Type IA building is of Type III, IV, or V construction. 4.2. The stairway located in the Type IA building is enclosed by 3-hour fire-resistance-rated construction with opening protectives in accordance with Section 716. 5. The building or buildings above the horizontal assembly shall be permitted to have multiple Group A occupancy uses, each with an occupant load of less 300, or Group B, M, R or S occupancies. 6. The building below the horizontal assembly shall be protected throughout by an approved automatic sprinkler system in accordance with Section 903.3.1.1, and shall be permitted to be any occupancy allowed by this code except Group H. 7, The maximum building height in feet (mm) shall not exceed the limits set forth in Section 504.3 for the building having the smaller allowable height as measured from the grade plane.
510.3 Group S-2 enclosed parking garage with Group S-2 open parking garage above. | A Group S-2 enclosed parking garage with not more than one story above grade plane and located below a Group S-2 open parking garage shall be classified as a separate and distinct building for the purpose of determining the type of construction where all of the following conditions are met: | 510.3 Group S-2 enclosed parking garage with Group S-2 open parking garage above. | A Group S-2 enclosed parking garage with not more than one story above grade plane and located below a Group S-2 open parking garage shall be classified as a separate and distinct building for the purpose of determining the type of construction where the following conditions are met:
510.4 Parking beneath Group R. | Where a maximum one story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The horizontal floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.4. | 510.4 Parking beneath Group R. | Where a maximum one story above grade plane Group S-2 parking garage, enclosed or open, or combination thereof, of Type I construction or open of Type IV construction, with grade entrance, is provided under a building of Group R, the number of stories to be used in determining the minimum type of construction shall be measured from the floor above such a parking area. The floor assembly between the parking garage and the Group R above shall comply with the type of construction required for the parking garage and shall also provide a fire-resistance rating not less than the mixed occupancy separation required in Section 508.4.
510.5 Reserved.
510.7 Open parking garage beneath Groups A, I, B, M and R. | Open parking garages constructed under Groups A, I, B, M and R shall not exceed the height and area limitations permitted under Section 406.5. The height and area of the portion of the building above the open parking garage shall not exceed the limitations in Section 503 for the upper occupancy. The height, in both feet and stories, of the portion of the building above the open parking garage shall be measured from grade plane and shall include both the open parking garage and the portion of the building above the parking garage. | 510.7 Open parking garage beneath Groups A, I, B, M and R. | Open parking garages constructed under Groups A, I, B, M and R shall not exceed the height and area limitations permitted under Section 406.5. The height and area of the portion of the building above the open parking garage shall not exceed the limitations in Section 503 for the upper occupancy. The height, in both feet and stories, of the portion of the building above the open parking garage shall be measured from grade plane and shall include both the open parking garage and the portion of the building above the parking garage.
510.6 Group R-2 buildings of Type IIA construction. | The height limitation for buildings of Type IIA construction in Group R-2 shall be increased to nine stories and 100 feet (30 480 mm) where the building is separated by not less than 50 feet (15 240 mm) from any other building on the lot and from lot lines, the exits are segregated in an area enclosed by a 2-hour fire-resistance-rated fire wall and the first floor assembly has a fire-resistance rating of not less than 11/2 hours.
510.7.1 Fire separation. | Fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 between the parking occupancy and the upper occupancy shall correspond to the required fire-resistance rating prescribed in Table 508.4 for the occupancies involved. The type of construction shall apply to each occupancy individually, except that structural members, including main bracing within the open parking structure, which is necessary to support the upper occupancy, shall be protected with the more restrictive fire-resistance-rated assemblies of the groups involved as shown in Table 601. Means of egress for the upper occupancy shall conform to Chapter 10 and shall be separated from the parking occupancy by fire barriers having not less than a 2-hour fire-resistance rating as required by Section 707, with self-closing doors complying with Sec­tion 716 or horizontal assemblies having not less than a 2-hour fire-resistance rating as required by Section 711, with self-closing doors complying with Section 716. Means of egress from the open parking garage shall comply with Section 406.5. | 510.7.1 Fire separation. | Fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 between the parking occupancy and the upper occupancy shall correspond to the required fire-resistance rating prescribed in Table 508.4 for the uses involved. The type of construction shall apply to each occupancy individually, except that structural members, including main bracing within the open parking structure, which is necessary to support the upper occupancy, shall be protected with the more restrictive fire-resistance-rated assemblies of the groups involved as shown in Table 601. Means of egress for the upper occupancy shall conform to Chapter 10 and shall be separated from the parking occupancy by fire barriers having not less than a 2-hour fire-resistance rating as required by Section 707 with self-closing doors complying with Section 716 or horizontal assemblies having not less than a 2-hour fire-resistance rating as required by Section 711, with self-closing doors complying with Section 716. Means of egress from the open parking garage shall comply with Section 406.5. |  | See BC06 Tables&Figures | See BC05 Tables&Figures
510.8 Industrial uses in buildings containing Group R. | No space classified as Factory Industrial Group F shall be located above the second story of any building of Type III, IV or V construction containing a space classified as Residential Group R-1 or R-2.
510.9 Multiple buildings above Group S-2 parking garages. | Where two or more buildings are provided above the horizontal assembly separating a Group S-2 open or closed parking garage from the buildings above in accordance with the special provisions in Section 510.2, 510.3 or 510.8, the buildings above the horizontal assembly shall be regarded as separate and distinct buildings from each other and shall comply with all other provisions of this code as applicable to each separate and distinct building.
510.10 Separation of different tenancies. | Spaces or dwelling units occupied by different tenants shall be separated by fire barriers having at least 1-hour fire-resistance ratings. Exceptions: 1. Nonresidential spaces occupied by different tenants located in buildings that are sprinklered throughout. 2. Tenant spaces in covered mall buildings complying with Section 402.
|  | 502.1 Address identification. | New and existing buildings shall be provided with approved address identification. The address identification shall be legible and placed in a position that is visible from the street or road fronting the property. Address identification characters shall contrast with their background. Address numbers shall be Arabic numbers or alphabetical letters. Numbers shall not be spelled out. Each character shall be a minimum of 4 inches (102 mm) high with a minimum stroke width of 1/2 inch (12.7 mm). Where required by the fire code official, address identification shall be provided in additional approved locations to facilitate emergency response. Where access is by means of a private road and the building address cannot be viewed from the public way, a monument, pole or other approved sign or means shall be used to identify the structure. Address identification shall be maintained.
|  | 503.1.2 Buildings on same lot. | Two or more buildings on the same lot shall be regulated as separate buildings or shall be considered as portions of one building where the building height, number of stories of each building and the aggregate building area of the buildings are within the limitations specified in Sections 504 and 506. The provisions of this code applicable to the aggregate building shall be applicable to each building.
|  | 503.1.4 Occupied roofs. | A roof level or portion thereof shall be permitted to be used as an occupied roof provided the occupancy of the roof is an occupancy that is permitted by Table 504.4 for the story immediately below the roof. The area of the occupied roofs shall not be included in the building area as regulated by Section 506. An occupied roof shall not be included in the building height or number of stories as regulated by Section 504, provided that the penthouses and other enclosed rooftop structures comply with Section 1511. Exceptions: 1. The occupancy located on an occupied roof shall not be limited to the occupancies allowed on the story immediately below the roof where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and occupant notification in accordance with Sections 907.5.2.1 and 907.5.2.3 is provided in the area of the occupied roof. Emergency voice/alarm communication system notification per Section 907.5.2.2 shall also be provided in the area of the occupied roof where such system is required elsewhere in the building. 2. Assembly occupancies shall be permitted on roofs of open parking spaces of Type I or Type II construction, in accordance with the exception to Section 903.2.1.6. |  | See BC05 Tables&Figures
|  | 503.1.4.1 Enclosures over occupied roof areas. | Elements or structures enclosing the occupied roof areas shall not extend more than 48 inches (1220 mm) above the surface of the occupied roof. Exception: Penthouses constructed in accordance with Section 1511.2 and towers, domes, spires and cupolas constructed in accordance with Section 1511.5.
|  | 504.3 Height in feet. | The maximum height, in feet, of a building shall not exceed the limits specified in Table 504.3. Exception: Towers, spires, steeples and other rooftop structures shall be constructed of materials consistent with the required type of construction of the building except where other construction is permitted by Section 1511.2.4. Such structures shall not be used for habitation or storage. The structures shall be unlimited in height where of noncombustible materials and shall not extend more than 20 feet (6096 mm) above the allowable building height where of combustible materials (see Chapter 15 for additional requirements). |  | See BC05 Tables&Figures
|  | 505.2.1.1 Aggregate area of mezzanines and equipment platforms. | Where a room contains both a mezzanine and an equipment platform, the aggregate area of the two raised floor levels shall be not greater than two-thirds of the floor area of that room or space in which they are located. The area of the mezzanine shall not exceed the area determined in accordance with Section 505.2.1.
|  | 505.3.2 Automatic sprinkler system. | Where located in a building that is required to be protected by an automatic sprinkler system, equipment platforms shall be fully protected by sprinklers above and below the platform, where required by the standards referenced in Section 903.3.
|  | 506.1.3 Basements. | Basements need not be included in the total allowable floor area of a building provided the total area of such basements does not exceed the area permitted for a one-story above grade plane building.
|  | 506.2.1 Single-occupancy buildings. | The allowable area of each story of a single-occupancy building shall be determined in accordance with Equation 5-1:
|  | 506.2.2 Mixed-occupancy buildings. | The allowable area of each story of a mixed-occupancy building shall be determined in accordance with the applicable provisions of, Section 508.3.2 for nonseparated occupancies and Section 508.4.2 for separated occupancies. For buildings with more than three stories above grade plane, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories, determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed three. Aa = [At + (NS × If)] (Equation 5-3) Aa = Allowable area (square feet). At = Tabular allowable area factor (NS, S13R, S13D or SM value, as applicable) in accordance with Table 506.2. NS = Tabular allowable area factor in accordance with Table 506.2 for a nonsprinklered building, regardless of whether the building is sprinklered. If = Area factor increase due to frontage (percent) as calculated in accordance with Section 506.3. Exception: For buildings designed as separated occupancies under Section 508.4 and equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.2, the total building area shall be such that the aggregate sum of the ratios of the actual area of each story divided by the allowable area of such stories determined in accordance with Equation 5-3 based on the applicable provisions of Section 508.1, shall not exceed four. |  | See BC05 Tables&Figures
|  | 506.3.3.1 Section 507 buildings. | Where a building meets the requirements of Section 507, as applicable, except for compliance with the minimum 60-foot (18 288 mm) public way or yard requirement, the area factor increase based on frontage shall be determined in accordance with Table 506.3.3.1. |  | See BC05 Tables&Figures
|  | 507.5 Two-story buildings. | The area of a Group B, F, M or S building not more than two stories above grade plane shall not be limited where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width.
|  | 507.6 Group A-3 buildings of Type II construction. | The area of a Group A-3 building not more than one story above grade plane, used as a place of religious worship, community hall, dance hall, exhibition hall, gymnasium, lecture hall, indoor swimming pool or tennis court of Type II construction, shall not be limited provided that the following criteria are met:
|  | 507.7 Group A-3 buildings of Type III and IV construction. | The area of a Group A-3 building of Type III or IV construction, with not more than one story above grade plane and used as a place of religious worship, community hall, dance hall, exhibition hall, gymnasium, lecture hall, indoor swimming pool or tennis court, shall not be limited provided that the following criteria are met:
|  | 507.8 Group H-2, H-3 and H-4 occupancies. | Group H-2, H-3 and H-4 occupancies shall be permitted in unlimited area buildings containing Group F or S occupancies in accordance with Sections 507.4 and 507.5 and the provisions of Sections 507.8.1 through 507.8.4.
|  | 507.8.1.1.1 Rooms for flammable or combustible liquid use, dispensing or mixing in open systems. | Rooms for flammable or combustible liquid use, dispensing or mixing in open systems having a floor area of not more than 500 square feet (46.5 m2) need not be located on the outer perimeter of the building where they are in accordance with the International Fire Code and NFPA 30.
|  | 507.8.1.1.2 Liquid storage rooms and rooms for flammable or combustible liquid use in closed systems. | Liquid storage rooms and rooms for flammable or combustible liquid use in closed systems having a floor area of not more than 1,000 square feet (93 m2) need not be located on the outer perimeter where they are in accordance with the International Fire Code and NFPA 30.
|  | 508.3.1.1 High-rise buildings. | Where nonseparated occupancies occur in a high-rise building, the most restrictive requirements of Section 403 that apply to the nonseparated occupancies shall apply throughout the high-rise building.
|  | 508.3.1.2 Group I-2, Condition 2 occupancies. | Where one of the nonseparated occupancies is Group I-2, Condition 2, the most restrictive requirements of Sections 407, 509 and 712 shall apply throughout the fire area containing the Group I-2 occupancy. The most restrictive requirements of Chapter 10 shall apply to the path of egress from the Group I-2, Condition 2 occupancy up to and including the exit discharge.
|  | 508.3.2 Allowable building area, height and number of stories. | The allowable building area, height and number of stories of the building or portion thereof shall be based on the most restrictive allowances for the occupancy groups under consideration for the type of construction of the building in accordance with Section 503.1.
|  | 508.4.3 Allowable building height and number of stories. | Each separated occupancy shall comply with the building height limitations and story limitations based on the type of construction of the building in accordance with Section 503.1. Exception: Special provisions of Section 510 shall permit occupancies at building heights and number of stories other than provided in Section 503.1.
|  | 508.5 Live/work units A live/work unit shall comply with Sections 508. | 5 through 508.5.11. Exception: Dwelling or sleeping units that include an office that is less than 10 percent of the area of the dwelling unit are permitted to be classified as dwelling units with accessory occupancies in accordance with Section 508.2.
|  | 508.5.1 Limitations. | The following shall apply to live/work areas:
|  | 508.5.2 Occupancies. | Live/work units shall be classified as a Group R-2 occupancy. Separation requirements found in Sections 420 and 508 shall not apply within the live/work unit where the live/work unit is in compliance with Section 508.5. Nonresidential uses that would otherwise be classified as either a Group H or S occupancy shall not be permitted in a live/work unit. Exception: Storage shall be permitted in the live/work unit provided that the aggregate area of storage in the nonresidential portion of the live/work unit shall be limited to 10 percent of the space dedicated to nonresidential activities.
|  | 508.5.3 Means of egress. | Except as modified by this section, the means of egress components for a live/work unit shall be designed in accordance with Chapter 10 for the function served.
|  | 508.5.4 Egress capacity. | The egress capacity for each element of the live/work unit shall be based on the occupant load for the function served in accordance with Table 1004.5.
|  | 508.5.5 Spiral stairways. | Spiral stairways that conform to the requirements of Section 1011.10 shall be permitted.
|  | 508.5.6 Vertical openings. | Floor openings between floor levels of a live/work unit are permitted without enclosure.
|  | 508.5.7 Fire protection. | The live/work unit shall be provided with a monitored fire alarm system where required by Section 907.2.9 and an automatic sprinkler system in accordance with Section 903.2.8.
|  | 508.5.8 Structural. | Floors within a live/work unit shall be designed for the live loads in Table 1607.1, based on the function within the space.
|  | 508.5.9 Accessibility. | Accessibility shall be designed in accordance with Chapter 11 for the function served.
|  | 508.5.10 Ventilation. | The applicable ventilation requirements of the International Mechanical Code shall apply to each area within the live/work unit for the function within that space.
|  | 508.5.11 Plumbing facilities. | The nonresidential area of the live/work unit shall be provided with minimum plumbing facilities as specified by Chapter 29, based on the function of the nonresidential area. Where the nonresidential area of the live/work unit is required to be accessible by Section 1108.6.2.1, the plumbing fixtures specified by Chapter 29 shall be accessible.
|  | 509.1 General Incidental uses located within single occupancy or mixed occupancy buildings shall comply with the provisions of this section. | Incidental uses are ancillary functions associated with a given occupancy that generally pose a greater level of risk to that occupancy and are limited to those uses specified in Table 509.1. Exception: Incidental uses within and serving a dwelling unit are not required to comply with this section. |  | See BC05 Tables&Figures
|  | 509.4.1.1 Type IV-B and IV-C construction. | Where Table 509.1 specifies a fire-resistance-rated separation, mass timber elements serving as fire barriers or horizontal assemblies in Type IV-B or IV-C construction shall be separated from the interior of the incidental use with an approved thermal barrier consisting of gypsum board that is not less than 1/2 inch (12.7 mm) in thickness or a material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275. |  | See BC05 Tables&Figures
|  | 510.5 Group R-1 and R-2 buildings of Type IIIA construction. | For buildings of Type IIIA construction in Groups R-1 and R-2, the maximum allowable height in Table 504.3 shall be increased by 10 feet (3048 mm) and the maximum allowable number of stories in Table 504.4 shall be increased by one where the first-floor assembly above the basement has a fire-resistance rating of not less than 3 hours and the floor area is subdivided by 2-hour fire-resistance-rated fire walls into areas of not more than 3,000 square feet (279 m2). |  | See BC05 Tables&Figures
|  | 510.6 Group R-1 and R-2 buildings of Type IIA construction. | The height limitation for buildings of Type IIA construction in Groups R-1 and R-2 shall be increased to nine stories and 100 feet (30 480 mm) where the building is separated by not less than 50 feet (15 240 mm) from any other building on the lot and from lot lines, the exits are segregated in an area enclosed by a 2-hour fire-resistance-rated fire wall and the first floor assembly has a fire-resistance rating of not less than 11/2 hours.
|  | 510.8 Group B or M buildings with Group S-2 open parking garage above. | Group B or M occupancies located below a Group S-2 open parking garage of a lesser type of construction shall be considered as a separate and distinct building from the Group S-2 open parking garage for the purpose of determining the type of construction where the following conditions are met: 1. The buildings are separated with a horizontal assembly having a fire-resistance rating of not less than 2 hours. 2. The occupancies in the building below the horizontal assembly are limited to Groups B and M. 3. The occupancy above the horizontal assembly is limited to a Group S-2 open parking garage. 4. The building below the horizontal assembly is of Type IA construction. Exception: The building below the horizontal assembly shall be permitted to be of Type IB or II construction, but not less than the type of construction required for the Group S-2 open parking garage above, where the building below is not greater than one story in height above grade plane. 5. The height and area of the building below the horizontal assembly does not exceed the limits set forth in Section 503. 6. The height and area of the Group S-2 open parking garage does not exceed the limits set forth in Section 406.5. The height, in both feet and stories, of the Group S-2 open parking garage shall be measured from grade plane and shall include the building below the horizontal assembly. 7. Exits serving the Group S-2 open parking garage discharge at grade with direct and unobstructed access to a street or public way and are separated from the building below the horizontal assembly by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both.
|  | 510.9 Multiple buildings above a horizontal assembly. | Where two or more buildings are provided above the horizontal assembly separating a Group S-2 parking garage or building below from the buildings above in accordance with the special provisions in Section 510.2, 510.3 or 510.8, the buildings above the horizontal assembly shall be regarded as separate and distinct buildings from each other and shall comply with all other provisions of this code as applicable to each separate and distinct building.

## BC6
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
601.1 Scope. | The provisions of this chapter shall control the classification of buildings as to type of construction. | 601.1 Scope. | The provisions of this chapter shall control the classification of buildings as to type of construction.
602.1 General. | Buildings and structures erected or to be erected, altered or extended in height or area shall be classified in one of the five construction types defined in Sections 602.2 through 602.5. The building elements shall have a fire-resistance rating not less than that specified in Table 601 and exterior walls shall have a fire-resistance rating not less than that specified in Table 602. Where required to have a fire-resistance rating by Table 601, building elements shall comply with the applicable provisions of Section 703.2. The protection of openings, ducts and air transfer openings in building elements shall not be required unless required by other provisions of this code. Buildings constructed or altered inside the fire district shall further comply with Appendix D. | 602.1 General. | Buildings and structures erected or to be erected, altered or extended in height or area shall be classified in one of the five construction types defined in Sections 602.2 through 602.5. The building elements shall have a fire-resistance rating not less than that specified in Table 601 and exterior walls shall have a fire-resistance rating not less than that specified in Table 705.5. Where required to have a fire-resistance rating by Table 601, building elements shall comply with the applicable provisions of Section 703.2. The protection of openings, ducts and air transfer openings in building elements shall not be required unless required by other provisions of this code. |  | See BC06 Tables&Figures | See BC07 Tables&Figures
602.1.1 Minimum requirements. | A building or portion thereof shall not be required to conform to the details of a type of construction higher than that type which meets the minimum requirements based on occupancy even though certain features of such a building actually conform to a higher type of construction. Classification shall be that of the minimum requirement unless all of the requirements for the higher type of construction are met. Exception: Portions of buildings that cantilever over an adjacent building or tax lot shall also comply with the fire-resistance ratings of Section 705.12. | 602.1.1 Minimum requirements. | A building or portion thereof shall not be required to conform to the details of a type of construction higher than that type which meets the minimum requirements based on occupancy even though certain features of such a building actually conform to a higher type of construction.
602.2 Types I and II. | Types I and II construction are those types of construction in which the building elements listed in Table 601 are of noncombustible materials, except as permitted in Section 603 and elsewhere in this code. | 602.2 Types I and II. | Types I and II construction are those types of construction in which the building elements specified in Table 601 are of noncombustible materials, except as permitted in Section 603 and elsewhere in this code. |  | See BC06 Tables&Figures
602.3 Type III. | Type III construction is that type of construction in which the exterior walls are of noncombustible materials and the interior building elements are of any material permitted by this code. Fire-retardant-treated wood framing complying with Section 2303.2 shall be permitted within exterior wall assemblies of a 2-hour rating or less. Exceptions: 1. In Group I-1, R-1, and R-2 occupancies, all exterior walls, fire walls, exit passageways, and shaft enclosures shall be noncombustible. 2. In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a “fireproof building” as such term is defined in Section 264 of such law. 3. Inside the fire district, exterior load-bearing walls shall be constructed of noncombustible material. 4. Inside the fire district, exterior nonload-bearing walls may be constructed with fire-retardant-treated wood complying with Section 2303.2 where the building is equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 through 903.3.1.3, unless otherwise prohibited by Exception 1 or 2 above. | 602.3 Type III. | Type III construction is that type of construction in which the exterior walls are of noncombustible materials and the interior building elements are of any material permitted by this code. Fire-retardant-treated wood framing and sheathing complying with Section 2303.2 shall be permitted within exterior wall assemblies of a 2-hour rating or less.
602.4 Type IV. | Type IV construction is that type of construction in which the exterior walls are of noncombustible materials or other materials permitted by Section 602.4.1 or 602.4.2, and the interior building elements are of solid wood, glue-laminated timber, heavy timber (HT), structural composite lumber (SCL), or cross-laminated timber (CLT) without concealed spaces. The minimum dimensions for permitted materials including solid timber, glued-laminated timber, SCL, and CLT and details of Type IV construction shall comply with the provisions of Section 2304.11 and this section. Interior walls and partitions not less than 1-hour fire-resistance rating or heavy timber complying with Section 2304.11.2.2 shall be permitted. Buildings of Type IV construction utilizing SCL or CLT shall be equipped throughout with an automatic sprinkler system where required by Section 903.2.13. In buildings of Type IV construction utilizing SCL or CLT, a fire watch shall be maintained in accordance with Section 901.7.2 of the New York City Fire Code and Section 3303.3 of this code. Exceptions: 1. In Group I-1, R-1, and R-2 occupancies, all exterior walls, fire walls, exit passageways, and shaft enclosures shall be noncombustible. 2. In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a "fireproof building" as defined in Section 264 of such law. 3. Inside the fire district, exterior load-bearing walls shall be constructed of noncombustible material. 4. Inside the fire district, exterior non-bearing walls may be constructed with fire-retardant-treated wood complying with Section 2303.2 of this code where the building is equipped throughout with an automatic sprinkler system in accordance with Sections 903.3.1.1 through 903.3.1.3, unless otherwise prohibited by Exception 1 or 2 above. 5. Inside the fire district, exterior non-bearing walls are permitted to be constructed with cross-laminated timber (CLT) complying with Section 602.4.2 of this code, unless otherwise prohibited by Exception 1 or 2 above. | 602.4 Type IV. | Type IV construction is that type of construction in which the building elements are mass timber or noncombustible materials and have fire-resistance ratings in accordance with Table 601. Mass timber elements shall meet the fire-resistance-rating requirements of this section based on either the fire-resistance rating of the noncombustible protection, the mass timber, or a combination of both and shall be determined in accordance with Section 703.2. The minimum dimensions and permitted materials for building elements shall comply with the provisions of this section and Section 2304.11. Mass timber elements of Types IV-A, IV-B and IV-C construction shall be protected with noncombustible protection applied directly to the mass timber in accordance with Sections 602.4.1 through 602.4.3. The time assigned to the noncombustible protection shall be determined in accordance with Section 703.6 and comply with Section 722.7. Cross-laminated timber shall be labeled as conforming to ANSI/APA PRG 320 as referenced in Section 2303.1.4. Exterior load-bearing walls and nonload-bearing walls shall be mass timber construction, or shall be of noncombus-tible construction. Exception: Exterior load-bearing walls and nonload-bearing walls of Type IV-HT Construction in accordance with Section 602.4.4. The interior building elements , including nonload-bearing walls and partitions, shall be of mass timber construction or of noncombustible construction. Exception: Interior building elements and nonload-bearing walls and partitions of Type IV-HT construction in ac-cordance with Section 602.4.4. Combustible concealed spaces are not permitted except as otherwise indicated in Sections 602.4.1 through 602.4.4. Combustible stud spaces within light frame walls of Type IV-HT construction shall not be considered concealed spaces, but shall comply with Section 718. In buildings of Type IV-A, IV-B, and IV-C construction with an occupied floor located more than 75 feet (22 860 mm) above the lowest level of fire department access, up to and including 12 stories or 180 feet (54 864 mm) above grade plane, mass timber interior exit and elevator hoistway enclosures shall be protected in accordance with Section 602.4.1.2. In buildings greater than 12 stories or 180 feet (54 864 mm) above grade plane, interior exit and elevator hoistway enclosures shall be constructed of noncombustible materials. |  | See BC06 Tables&Figures
|  | 602.4.1 Type IV-A. | Building elements in Type IV-A construction shall be protected in accordance with Sections 602.4.1.1 through 602.4.1.6. The required fire-resistance rating of noncombustible elements and protected mass timber elements shall be determined in accordance with Section 703.2.
|  | 602.4.1.1 Exterior protection. | The outside face of exterior walls of mass timber construction shall be protected with noncombustible protection with a minimum assigned time of 40 minutes, as specified in Table 722.7.1(1). Components of the exterior wall covering shall be of noncombustible material except water-resistive barriers having a peak heat release rate of less than 150kW/m2, a total heat release of less than 20 MJ/m2 and an effective heat of combustion of less than 18MJ/kg as determined in accordance with ASTM E1354 and having a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E84 or UL 723. The ASTM E1354 test shall be conducted on specimens at the thickness intended for use, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2. |  | See BC07 Tables&Figures
|  | 602.4.1.2 Interior protection. | Interior faces of all mass timber elements, including the inside faces of exterior mass timber walls and mass timber roofs, shall be protected with materials complying with Section 703.3.
|  | 602.4.1.2.1 Protection time. | Noncombustible protection shall contribute a time equal to or greater than times assigned in Table 722.7.1(1), but not less than 80 minutes. The use of materials and their respective protection contributions specified in Table 722.7.1(2) shall be permitted to be used for compliance with Section 722.7.1. |  | See BC07 Tables&Figures
|  | 602.4.1.3 Floors. | The floor assembly shall contain a noncombustible material not less than 1 inch (25 mm) in thickness above the mass timber. Floor finishes in accordance with Section 804 shall be permitted on top of the noncombustible material. The underside of floor assemblies shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.1.4 Roofs. | The interior surfaces of roof assemblies shall be protected in accordance with Section 602.4.1.2. Roof coverings in accordance with Chapter 15 shall be permitted on the outside surface of the roof assembly.
|  | 602.4.1.5 Concealed spaces. | Concealed spaces shall not contain combustibles other than electrical, mechanical, fire protection, or plumbing materials and equipment permitted in plenums in accordance with Section 602 of the International Mechanical Code, and shall comply with all applicable provisions of Section 718. Combustible construction forming concealed spaces shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.1.6 Shafts. | Shafts shall be permitted in accordance with Sections 713 and 718. Both the shaft side and room side of mass timber elements shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.2 Type IV-B. | Building elements in Type IV-B construction shall be protected in accordance with Sections 602.4.2.1 through 602.4.2.6. The required fire-resistance rating of noncombustible elements or mass timber elements shall be determined in accordance with Section 703.2.
|  | 602.4.2.1 Exterior protection. | The outside face of exterior walls of mass timber construction shall be protected with noncombustible protection with a minimum assigned time of 40 minutes, as specified in Table 722.7.1(1). Components of the exterior wall covering shall be of noncombustible material except water-resistive barriers having a peak heat release rate of less than 150kW/m2, a total heat release of less than 20 MJ/m2 and an effective heat of combustion of less than 18MJ/kg as determined in accordance with ASTM E1354, and having a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E84 or UL 723. The ASTM E1354 test shall be conducted on specimens at the thickness intended for use, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2. |  | See BC07 Tables&Figures
|  | 602.4.2.2 Interior protection. | Interior faces of all mass timber elements, including the inside face of exterior mass timber walls and mass timber roofs, shall be protected, as required by this section, with materials complying with Section 707.3.
|  | 602.4.2.2.1 Protection time. | Noncombustible protection shall contribute a time equal to or greater than times assigned in Table 722.7.1(1), but not less than 80 minutes. The use of materials and their respective protection contributions specified in Table 722.7.1(2) shall be permitted to be used for compliance with Section 722.7.1. |  | See BC07 Tables&Figures
|  | 602.4.2.2.2 Protected area. | Interior faces of mass timber elements, including the inside face of exterior mass timber walls and mass timber roofs, shall be protected in accordance with Section 602.4.2.2.1. Exceptions: Unprotected portions of mass timber ceilings and walls complying with Section 602.4.2.2.4 and the following: 1. Unprotected portions of mass timber ceilings and walls complying with one of the following: 1.1. Unprotected portions of mass timber ceilings, including attached beams, shall be permitted and shall be limited to an area equal to 20 percent of the floor area in any dwelling unit or fire area. 1.2. Unprotected portions of mass timber walls, including attached columns, shall be permitted and shall be limited to an area equal to 40 percent of the floor area in any dwelling unit or fire area. 1.3. Unprotected portions of both walls and ceilings of mass timber, including attached columns and beams, in any dwelling unit or fire area shall be permitted in accordance with Section 602.4.2.2.3. 2. Mass timber columns and beams that are not an integral portion of walls or ceilings, respectively, shall be permitted to be unprotected without restriction of either aggregate area or separation from one an-other.
|  | 602.4.2.2.3 Mixed unprotected areas. | In each dwelling unit or fire area, where both portions of ceilings and portions of walls are unprotected, the total allowable unprotected area shall be determined in accordance with Equation 6-1. (Utc/Uac)  (Utw/Uaw)  1 (Equation 6-1) where: Utc = Total unprotected mass timber ceiling areas. Uac = Allowable unprotected mass timber ceiling area conforming to Exception 1.1 of Section 602.4.2.2.2. Utw = Total unprotected mass timber wall areas. Uaw = Allowable unprotected mass timber wall area conforming to Exception 1.2 of Section 602.4.2.2.2.
|  | 602.4.2.2.4 Separation distance between unprotected mass timber elements. | In each dwelling unit or fire area, unprotected portions of mass timber walls and ceilings shall be not less than 15 feet (4572 mm) from unprotected portions of other walls and ceilings, measured horizontally along the ceiling and from other unprotected portions of walls measured horizontally along the floor.
|  | 602.4.2.3 Floors. | The floor assembly shall contain a noncombustible material not less than 1 inch (25 mm) in thickness above the mass timber. Floor finishes in accordance with Section 804 shall be permitted on top of the noncombustible material. The underside of floor assemblies shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.2.4 Roofs. | The interior surfaces of roof assemblies shall be protected in accordance with Section 602.4.2.2 except, in nonoccupiable spaces, they shall be treated as a concealed space with no portion left unprotected. Roof coverings in accordance with Chapter 15 shall be permitted on the outside surface of the roof assembly.
|  | 602.4.2.5 Concealed spaces. | Concealed spaces shall not contain combustibles other than electrical, mechanical, fire protection, or plumbing materials and equipment permitted in plenums in accordance with Section 602 of the International Mechanical Code, and shall comply with all applicable provisions of Section 718. Combustible construction forming concealed spaces shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.2.6 Shafts. | Shafts shall be permitted in accordance with Sections 713 and 718. Both the shaft side and room side of mass timber elements shall be protected in accordance with Section 602.4.1.2.
|  | 602.4.3 Type IV-C. | Building elements in Type IV-C construction shall be protected in accordance with Sections 602.4.3.1 through 602.4.3.6. The required fire-resistance rating of building elements shall be determined in accordance with Section 703.2.
|  | 602.4.3.1 Exterior protection. | The exterior side of walls of combustible construction shall be protected with noncombustible protection with a minimum assigned time of 40 minutes, as determined in Table 722.7.1(1). Components of the exterior wall covering shall be of noncombustible material except water-resistive barriers having a peak heat release rate of less than 150 kW/m2, a total heat release of less than 20 MJ/m2 and an effective heat of combustion of less than 18 MJ/kg as determined in accordance with ASTM E1354 and having a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E84 or UL 723. The ASTM E1354 test shall be conducted on specimens at the thickness intended for use, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2. |  | See BC07 Tables&Figures
|  | 602.4.3.2 Interior protection. | Mass timber elements are permitted to be unprotected.
|  | 602.4.3.3 Floors. | Floor finishes in accordance with Section 804 shall be permitted on top of the floor construction.
|  | 602.4.3.4 Roof coverings. | Roof coverings in accordance with Chapter 15 shall be permitted on the outside surface of the roof assembly.
|  | 602.4.3.5 Concealed spaces. | Concealed spaces shall not contain combustibles other than electrical, mechanical, fire protection, or plumbing materials and equipment permitted in plenums in accordance with Section 602 of the International Mechanical Code, and shall comply with all applicable provisions of Section 718. Combustible construction forming concealed spaces shall be protected with noncombustible protection with a minimum assigned time of 40 minutes, as specified in Table 722.7.1(1). |  | See BC07 Tables&Figures
|  | 602.4.3.6 Shafts. | Shafts shall be permitted in accordance with Sections 713 and 718. Shafts and elevator hoistway and interior exit stairway enclosures shall be protected with noncombustible protection with a minimum assigned time of 40 minutes, as specified in Table 722.7.1(1), on both the inside of the shaft and the outside of the shaft. |  | See BC07 Tables&Figures
|  | 602.4.4 Type IV-HT. | Type IV-HT (Heavy Timber) construction is that type of construction in which the exterior walls are of noncombustible materials and the interior building elements are of solid wood, laminated heavy timber or structural composite lumber (SCL), without concealed spaces or with concealed spaces complying with Section 602.4.4.3. The minimum dimensions for permitted materials including solid timber, glued-laminated timber, SCL and cross-laminated timber (CLT) and the details of Type IV construction shall comply with the provisions of this section and Section 2304.11. Exterior walls complying with Section 602.4.4.1 or 602.4.4.2 shall be permitted. Interior walls and partitions not less than 1-hour fire-resistance rated or heavy timber conforming with Section 2304.11.2.2 shall be permitted.
|  | 602.4.4.1 Fire-retardant-treated wood in exterior walls. | Fire-retardant-treated wood framing and sheathing complying with Section 2303.2 shall be permitted within exterior wall assemblies with a 2-hour rating or less.
|  | 602.4.4.2 Cross-laminated timber in exterior walls. | Cross-laminated timber (CLT) not less than 4 inches (102 mm) in thickness complying with Section 2303.1.4 shall be permitted within exterior wall assemblies with a 2-hour rating or less. Heavy timber structural members appurtenant to the CLT exterior wall shall meet the requirements of Table 2304.11 and be fire-resistance rated as required for the exterior wall. The exterior surface of the cross-laminated timber and heavy timber elements shall be protected by one the following:
|  | 602.4.4.3 Concealed spaces. | Concealed spaces shall not contain combustible materials other than building elements and electrical, mechanical, fire protection, or plumbing materials and equipment permitted in plenums in accordance with Section 602 of the International Mechanical Code. Concealed spaces shall comply with applicable provisions of Section 718. Concealed spaces shall be protected in accordance with one or more of the following: 1. The building shall be sprinklered throughout in accordance with Section 903.3.1.1 and automatic sprinklers shall also be provided in the concealed space. 2. The concealed space shall be completely filled with noncombustible insulation. 3. Surfaces within the concealed space shall be fully sheathed with not less than 5/8-inch Type X gypsum board. Exception: Concealed spaces within interior walls and partitions with a 1-hour or greater fire-resistance rating complying with Section 2304.11.2.2 shall not require additional protection.
|  | 602.4.4.4 Exterior structural members. | Where a horizontal separation of 20 feet (6096 mm) or more is provided, wood columns and arches conforming to heavy timber sizes complying with Section 2304.11 shall be permitted to be used externally.
602.5 Type V. | Type V construction is that type of construction in which the structural elements, exterior walls and interior walls are of any materials permitted by this code. Type V construction shall not be permitted inside the fire district unless otherwise permitted by Section D105.1. Exception: In Group F occupancies subject to Section 270(1) of the New York State Labor Law, all exterior wall assemblies and all structural elements shall meet the requirements for a “fireproof building” as defined in Section 264 of such law. | 602.5 Type V. | Type V construction is that type of construction in which the structural elements, exterior walls and interior walls are of any materials permitted by this code.
603.1 Allowable materials. | Combustible materials shall be permitted in buildings of Type I or II construction in the following applications and in accordance with Sections 603.1.1 through 603.1.3: 1. Fire-retardant-treated wood, complying with Section 2303.2, shall be permitted in: 1.1. Nonbearing interior partitions where the required fire-resistance rating is 1 hour or less. Exception: Public corridors and exits shall be constructed of noncombustible materials. 1.2. Roof construction as permitted in Table 601, Note b. 2. Thermal and acoustical insulation, other than foam plastics, having a flame spread index of not more than 25. Exceptions: 1. Insulation placed between two layers of noncombustible materials without an intervening airspace shall be allowed to have a flame spread index of not more than 100. 2. Insulation installed between a finished floor and solid decking without intervening airspace shall be allowed to have a flame spread index of not more than 200. 3. Foam plastics in accordance with Chapter 26. 4. Roof coverings that have an A or B classification as defined in Section 1505. 5. Interior floor finish and floor covering materials installed in accordance with Section 804. 6. Millwork such as doors, door frames, window sashes and frames. 7. Interior wall and ceiling finishes installed in accordance with Sections 801 and 803. 8. Trim installed in accordance with Section 806. 9. Where not installed greater than 15 feet (4572 mm) above grade, show windows, nailing or furring strips and wooden bulkheads below show windows, including their frames, aprons and show cases. 10. Finish flooring installed in accordance with Section 805. 11. Partitions dividing portions of stores, offices or similar places occupied by one tenant only and that do not establish a corridor serving an occupant load of 30 or more shall be permitted to be constructed of fire-retardant-treated wood, 1-hour fire-resistance-rated construction or of wood panels or similar light construction up to 6 feet (1828.8 mm) in height. 12. Stages and platforms constructed in accordance with Sections 410.3 and 410.4, respectively. 13. Combustible exterior wall coverings, balconies and similar projections and bay or oriel windows in accordance with Chapter 14. 14. Blocking such as for handrails, millwork, cabinets and window and door frames. 15. Light-transmitting plastics as permitted by Chapter 26. 16. Mastics and caulking materials applied to provide flexible seals between components of exterior wall construction. 17. Exterior plastic veneer installed in accordance with Section 2605.2. 18. Nailing or furring strips as permitted by Section 803.13. 19. Heavy timber as permitted by Note c to Table 601 and Section 602.4.3. 20. Aggregates, component materials and admixtures as permitted by Section 703.2.2. 21. Sprayed fire-resistant materials and intumescent and mastic fire-resistant coatings, determined on the basis of fire resistance tests in accordance with Section 703.2 and installed in accordance with Sections 1705.14 and 1705.15, respectively. 22. Materials used to protect penetrations in fire-resistance-rated assemblies in accordance with Section 714. 23. Materials used to protect joints in fire-resistance-rated assemblies in accordance with Section 715. 24. Materials allowed in the concealed spaces of buildings of Types I and II construction in accordance with Section 718.5. 25. Materials exposed within plenums complying with Section 602 of the New York City Mechanical Code. 26. Bleachers, grandstands, and folding and telescopic seating within an assembly space in accordance with Section 1029.1.1 of this code. | 603.1 Allowable materials. | Combustible materials shall be permitted in buildings of Type I or II construction in the following applications and in accordance with Sections 603.1.1 through 603.1.3: 1. Fire-retardant-treated wood shall be permitted in: 1.1. Nonbearing partitions where the required fire-resistance rating is 2 hours or less except in shaft enclo-sures within Group I-2 occupancies and ambulatory care facilities. 1.2. Nonbearing exterior walls where fire-resistance-rated construction is not required. 1.3. Roof construction, including girders, trusses, framing and decking. Exceptions: 1. In buildings of Type IA constr-uction exceeding two stories above grade plane, fire-retardant-treated wood is not permitted in roof construction where the vertical distance from the upper floor to the roof is less than 20 feet (6096 mm). 2. Group I-2, roof construction containing fire-retardant-treated wood shall be covered by not less than a Class A roof covering or roof assembly, and the roof assembly shall have a fire-resistance rating where required by the construction type. 1.4. Balconies, porches, decks and exterior stairways not used as required exits on buildings three stories or less above grade plane. 2. Thermal and acoustical insulation, other than foam plastics, having a flame spread index of not more than 25. Exceptions: 1. Insulation placed between two layers of noncombustible materials without an intervening airspace shall be allowed to have a flame spread index of not more than 100. 2. Insulation installed between a finished floor and solid decking without intervening airspace shall be al-lowed to have a flame spread index of not more than 200. 3. Foam plastics in accordance with Chapter 26. 4. Roof coverings that have an A, B or C classification. 5. Interior floor finish and floor covering materials installed in accordance with Section 804. 6. Millwork such as doors, door frames, window sashes and frames. 7. Interior wall and ceiling finishes installed in accordance with Section 803. 8. Trim installed in accordance with Section 806. 9. Where not installed greater than 15 feet (4572 mm) above grade, show windows, nailing or furring strips and wooden bulkheads below show windows, including their frames, aprons and show cases. 10. Finish flooring installed in accordance with Section 805. 11. Partitions dividing portions of stores, offices or similar places occupied by one tenant only and that do not estab-lish a corridor serving an occupant load of 30 or more shall be permitted to be constructed of fire-retardant-treated wood, 1-hour fire-resistance-rated construction or of wood panels or similar light construction up to 6 feet (1829 mm) in height. 12. Stages and platforms constructed in accordance with Sections 410.2 and 410.3, respectively. 13. Combustible exterior wall coverings, balconies and similar projections and bay or oriel windows in accordance with Chapter 14 and Section 705.2.3.1. 14. Blocking such as for handrails, millwork, cabinets and window and door frames. 15. Light-transmitting plastics as permitted by Chapter 26. 16. Mastics and caulking materials applied to provide flexible seals between components of exterior wall construc-tion. 17. Exterior plastic veneer installed in accordance with Section 2605.2. 18. Nailing or furring strips as permitted by Section 803.15. 19. Heavy timber as permitted by Note c to Table 601 and Sections 602.4.4.4 and 705.2.3.1. 20. Aggregates, component materials and admixtures as permitted by Section 703.2.1.2. 21. Sprayed fire-resistant materials and intumescent and mastic fire-resistant coatings, determined on the basis of fire resistance tests in accordance with Section 703.2 and installed in accordance with Sections 1705.15 and 1705.16, respectively. 22. Materials used to protect penetrations in fire-resistance-rated assemblies in accordance with Section 714. 23. Materials used to protect joints in fire-resistance-rated assemblies in accordance with Section 715. 24. Materials allowed in the concealed spaces of buildings of Types I and II construction in accordance with Section 718.5. 25. Materials exposed within plenums complying with Section 602 of the International Mechanical Code. 26. Wall construction of freezers and coolers of less than 1,000 square feet (92.9 m2), in size, lined on both sides with noncombustible materials and the building is protected throughout with an automatic sprinkler system in ac-cordance with Section 903.3.1.1. 27. Wood nailers for parapet flashing and roof cants. |  | See BC06 Tables&Figures
603.1.1 Ducts. | The use of nonmetallic ducts shall be permitted where installed in accordance with the limitations of the New York City Mechanical Code. | 603.1.1 Ducts. | The use of nonmetallic ducts shall be permitted where installed in accordance with the limitations of the International Mechanical Code.
603.1.2 Piping. | The use of combustible piping materials shall be permitted where installed in accordance with the limitations of the New York City Mechanical Code and the New York City Plumbing Code. | 603.1.2 Piping. | The use of combustible piping materials shall be permitted where installed in accordance with the limitations of the International Mechanical Code and the International Plumbing Code.
603.1.3 Electrical. | The use of electrical wiring methods with combustible insulation, tubing, raceways and related components shall be permitted where installed in accordance with the limitations of the New York City Electrical Code. | 603.1.3 Electrical. | The use of electrical wiring methods with combustible insulation, tubing, raceways and related components shall be permitted where installed in accordance with the limitations of this code.
602.4.1 Fire-retardant-treated wood in exterior walls. | Fire-retardant-treated wood framing and sheathing complying with Section 2303.2 shall be permitted within exterior wall assemblies not less than 6 inches (152.4 mm) in thickness with a 2-hour rating or less.
602.4.2 Cross-laminated timber in exterior walls. | Cross-laminated timber (CLT) complying with Section 2303.1.4 shall be permitted within exterior wall assemblies not less than 6 inches (152.4 mm) in thickness with a 2-hour rating or less, provided the exterior surface of the cross-laminated timber (CLT) is protected by one of the following:
602.4.3 Exterior structural members. | Where a horizontal separation of 20 feet (6096 mm) or more is provided, wood columns and arches conforming to heavy timber sizes in accordance with Section 2304.11 shall be permitted to be used externally. Exception: Where prohibited by Exceptions 1, 2 or 3 of Section 602.4.

## BC7
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
701.1 Scope. | The provisions of this chapter shall govern the materials and assemblies used for structural fire resistance and fire-resistance-rated construction separation of adjacent spaces to safeguard against the spread of fire and smoke within a building and the spread of fire to or from buildings. | 701.1 Scope. | The provisions of this chapter shall govern the materials, systems and assemblies used for structural fire resistance and fire-resistance-rated construction separation of adjacent spaces to safeguard against the spread of fire and smoke within a building and the spread of fire to or from buildings.
|  | 702.1 Multiple-use fire assemblies. | Fire assemblies that serve multiple purposes in a building shall comply with all of the requirements that are applicable for each of the individual fire assemblies.
703.1 Scope. | Materials prescribed herein for fire resistance shall conform to the requirements of this chapter. | 703.1 Scope. | Materials prescribed herein for fire resistance shall conform to the requirements of this chapter.
|  | 703.2 Fire resistance. | The fire-resistance rating of building elements, components or assemblies shall be determined in accordance with Section 703.2.1 or 703.2.2 without the use of automatic sprinklers or any other fire suppression system being incorporated, or in accordance with Section 703.2.3.
|  | 703.2.1 Tested assemblies. | A fire-resistance rating of building elements, components or assemblies shall be determined by the test procedures set forth in ASTM E119 or UL 263. The fire-resistance rating of penetrations and fire-resistant joint systems shall be determined in accordance with Sections 714 and 715, respectively.
|  | 703.2.1.1 Nonsymmetrical wall construction. | Interior walls and partitions of nonsymmetrical construction shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests conducted in compliance with ASTM E119 or UL 263. Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the building official, the wall need not be subjected to tests from the opposite side (see Section 705.5 for exterior walls).
|  | 703.2.1.2 Combustible components. | Combustible aggregates are permitted in gypsum and Portland cement concrete mixtures for fire-resistance-rated construction. Any component material or admixture is permitted in assemblies if the resulting tested assembly meets the fire-resistance test requirements of this code.
|  | 703.2.1.3 Restrained classification. | Fire-resistance-rated assemblies tested under ASTM E119 or UL 263 shall not be considered to be restrained unless evidence satisfactory to the building official is furnished by the registered design professional showing that the construction qualifies for a restrained classification in accordance with ASTM E119 or UL 263. Restrained construction shall be identified on the construction documents.
|  | 703.2.1.4 Supplemental features. | Where materials, systems or devices that have not been tested as part of a fire-resistance-rated assembly are incorporated into the building element, component or assembly, sufficient data shall be made available to the building official to show that the required fire-resistance rating is not reduced.
|  | 703.2.1.5 Exterior bearing walls. | In determining the fire-resistance rating of exterior bearing walls, compliance with the ASTM E119 or UL 263 criteria for unexposed surface temperature rise and ignition of cotton waste due to passage of flame or gases is required only for a period of time corresponding to the required fire-resistance rating of an exterior nonbearing wall with the same fire separation distance, and in a building of the same group. Where the fire-resistance rating determined in accordance with this exception exceeds the fire-resistance rating determined in accordance with ASTM E119 or UL 263, the fire exposure time period, water pressure and application duration criteria for the hose stream test of ASTM E119 or UL 263 shall be based on the fire-resistance rating determined in accordance with this section.
|  | 703.2.2 Analytical methods. | The fire resistance of building elements , components or assemblies established by an analytical method shall be by any of the methods listed in this section, based on the fire exposure and acceptance criteria specified in ASTM E119 or UL 263.
|  | 703.2.3 Approved alternate method. | The fire resistance of building elements, components or assemblies not complying with Section 703.2.1 or 703.2.2 shall be permitted to be established by an alternative protection method in accordance with Section 104.11.
|  | 703.3 Noncombustibility tests. | The tests indicated in Section 703.3.1 shall serve as criteria for acceptance of building materials as set forth in Sections 602.2, 602.3 and 602.4 in Types I, II, III and IV construction. The term “noncombustible” does not apply to the flame spread characteristics of interior finish or trim materials. A material shall not be classified as a noncombustible building construction material if it is subject to an increase in combustibility or flame spread beyond the limitations herein established through the effects of age, moisture or other atmospheric conditions.
|  | 703.3.1 Noncombustible materials. | Materials required to be noncombustible shall be tested in accordance with ASTM E136. Alternately, materials required to be noncombustible shall be tested in accordance with ASTM E2652 using the acceptance criteria prescribed by ASTM E136. Exception: Materials having a structural base of noncombustible material as determined in accordance with ASTM E136, or with ASTM E2652 using the acceptance criteria prescribed by ASTM E136, with a surfacing of not more than 0.125 inch (3.18 mm) in thickness having a flame spread index not greater than 50 when tested in accordance with ASTM E84 or UL 723 shall be acceptable as noncombustible. |  | See BC07 Tables&Figures
|  | 703.4 Fire-resistance-rated glazing. | Fire-resistance-rated glazing, when tested in accordance with ASTM E119 or UL 263 and complying with the requirements of Section 707, shall be permitted. Fire-resistance-rated glazing shall bear a label marked in accordance with Table 716.1(1) issued by an agency and shall be permanently identified on the glazing. |  | See BC07 Tables&Figures
|  | 703.5 Marking and identification. | Where there is an accessible concealed floor, floor-ceiling or attic space, fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions or any other wall required to have protected openings or penetrations shall be effectively and permanently identified with signs or stenciling in the concealed space. Such identification shall:
|  | 703.6 Determination of noncombustible protection time contribution. | The time, in minutes, contributed to the fire-resistance rating by the noncombustible protection of mass timber building elements, components, or assemblies, shall be established through a comparison of assemblies tested using procedures set forth in ASTM E119 or UL 263. The test assemblies shall be identical in construction, loading and materials, other than the noncombustible protection. The two test assemblies shall be tested to the same criteria of structural failure with the following conditions:
704.1 Requirements. | The fire-resistance ratings of structural members and assemblies shall comply with this section and the requirements for the type of construction as specified in Table 601. The fire-resistance ratings shall be not less than the ratings required for the fire-resistance-rated assemblies supported by the structural members. Exception: Fire barriers, fire partitions, smoke barriers and horizontal assemblies as provided in Sections 707.5, 708.4 and 711.2, respectively. | 704.1 Requirements. | The fire-resistance ratings of structural members and assemblies shall comply with this section and the requirements for the type of construction as specified in Table 601. The fire-resistance ratings shall be not less than the ratings required for the fire-resistance-rated assemblies supported by the structural members. Exception: Fire barriers, fire partitions, smoke barriers and horizontal assemblies as provided in Sections 707.5, 708.4, 709.4 and 711.2, respectively. |  | See BC07 Tables&Figures
|  | 703.7 Sealing of adjacent mass timber elements. | In buildings of Types IV-A, IV-B and IV-C construction, sealant or adhesive shall be provided to resist the passage of air in the following locations: 1. At abutting edges and intersections of mass timber building elements required to be fire-resistance rated. 2. At abutting intersections of mass timber building elements and building elements of other materials where both are required to be fire-resistance rated. Sealants shall meet the requirements of ASTM C920. Adhesives shall meet the requirements of ASTM D3498. Exception: Sealants or adhesives need not be provided where they are not a required component of a tested fire-resistance-rated assembly.
704.2 Column protection. | Where columns are required to have protection to achieve a fire-resistance rating, the entire column shall be provided individual encasement protection by protecting it on all sides for the full column height, including connections to other structural members, with materials having the required fire-resistance rating. Where the column extends through a ceiling, the encasement protection shall be continuous from the top of the foundation or floor/ceiling assembly below through the ceiling space to the top of the column. | 704.2 Column protection. | Where columns are required to have protection to achieve a fire-resistance rating, the entire column shall be provided individual encasement protection by protecting it on all sides for the full column height, including connections to other structural members, with materials having the required fire-resistance rating. Where the column extends through a ceiling, the encasement protection shall be continuous from the top of the foundation or floor/ceiling assembly below through the ceiling space to the top of the column. Exception: Columns that meet the limitations of Section 704.4.1.
704.3 Protection of the primary structural frame other than columns. | Members of the primary structural frame other than columns that are required to have protection to achieve a fire-resistance rating and support more than one floor or one floor and roof, or support a load-bearing wall or a nonload-bearing wall more than one story high, shall be provided individual encasement protection by protecting them on all sides for the full length, including connections to other structural members, with materials having the required fire-resistance rating. Exception: Individual encasement protection may be omitted on those exposed sides where the extent of protection is in accordance with the required fire-resistance rating, as determined in Section 703. | 704.3 Protection of the primary structural frame other than columns. | Members of the primary structural frame other than columns that are required to have protection to achieve a fire-resistance rating and support more than two floors or one floor and roof, or support a load-bearing wall or a nonload-bearing wall more than two stories high, shall be provided individual encasement protection by protecting them on all sides for the full length, including connections to other structural members, with materials having the required fire-resistance rating. Exception: Individual encasement protection on all sides shall be permitted on all exposed sides provided that the extent of protection is in accordance with the required fire-resistance rating, as determined in Section 703.
704.4.1 Light-frame construction. | Studs and boundary elements that are integral elements in load-bearing walls of light-frame construction shall be permitted to have required fire-resistance ratings provided by the membrane protection provided for the load-bearing wall. | 704.4.1 Light-frame construction. | Studs, columns and boundary elements that are integral elements in walls of light-frame construction and are located entirely between the top and bottom plates or tracks shall be permitted to have required fire-resistance ratings provided by the membrane protection provided for the wall.
|  | 704.4 Protection of secondary structural members. | Secondary structural members that are required to have protection to achieve a fire-resistance rating shall be protected by individual encasement protection.
704.4.2 Horizontal assemblies. | Horizontal assemblies are permitted to be protected with a membrane or ceiling where the membrane or ceiling provides the required fire-resistance rating and is installed in accordance with Section 711. | 704.4.2 Horizontal assemblies. | Horizontal assemblies are permitted to be protected with a membrane or ceiling where the membrane or ceiling provides the required fire-resistance rating and is installed in accordance with Section 711.
704.5 Truss protection. | The required thickness and construction of fire-resistance-rated assemblies enclosing trusses shall be based on the results of full-scale tests or combinations of tests on truss components or on approved calculations based on such tests that satisfactorily demonstrate that the assembly has the required fire resistance. | 704.5 Truss protection. | The required thickness and construction of fire-resistance-rated assemblies enclosing trusses shall be based on the results of full-scale tests or combinations of tests on truss components or on approved calculations based on such tests that satisfactorily demonstrate that the assembly has the required fire resistance.
704.6 Attachments to structural members. | The edges of lugs, brackets, rivets and bolt heads attached to structural members shall be protected to the highest required fire-resistance rating of the members connected. | 704.6 Attachments to structural members. | The edges of lugs, brackets, rivets and bolt heads attached to structural members shall be permitted to extend to within 1 inch (25 mm) of the surface of the fire protection.
704.7 Reinforcing. | Thickness of protection for concrete or masonry reinforcement shall be measured to the outside of the reinforcement, including stirrups, ties and spiral reinforcing ties. | 704.7 Reinforcing. | Thickness of protection for concrete or masonry reinforcement shall be measured to the outside of the reinforcement except that stirrups and spiral reinforcement ties are permitted to project not more than 0.5 inch (12.7 mm) into the protection.
704.8 Embedments and enclosures. | Pipes, wires, conduits, ducts or other service facilities shall not be embedded in the required fire protective covering of a structural member that is required to be individually encased. Exception: Pipes, wires, and con¬duits may be installed in the space between the required fire protection and the structural member protected, provided that where such facilities pierce the required fire protection: 1. The area of the penetration does not exceed two percent of the area of the fire protection on any one face, 2. The penetrations are closed off with close-fitting metal escutcheons or plates, and 3. The concealed space is firestopped at each story. | 704.8 Embedments and enclosures. | Pipes, wires, conduits, ducts or other service facilities shall not be embedded in the required fire protective covering of a structural member that is required to be individually encased.
|  | 704.6.1 Secondary attachments to structural members. | Where primary and secondary structural steel members require fire protection, secondary steel attachments to those structural members shall be protected with the same fire-resistive material and thickness as required for the structural member. The protection shall extend away from the structural member a distance of not less than 12 inches (305 mm), or shall be applied to the entire length where the attachment is less than 12 inches (305 mm) long. Where an attachment is hollow and the ends are open, the fire-resistive material and thickness shall be applied to both exterior and interior of the hollow steel attachment.
704.9 Impact protection. | Where the fire protective covering of a structural member is subject to impact damage from moving vehicles, the handling of merchandise or other activity, the fire protective covering shall be protected by corner guards or by a substantial jacket of metal or other noncombustible material to a height adequate to provide full protection, but not less than 5 feet (1524 mm) from the finished floor. Exception: Corner protection is not required on concrete columns in open or enclosed parking garages. | 704.9 Impact protection. | Where the fire protective covering of a structural member is subject to impact damage from moving vehicles, the handling of merchandise or other activity, the fire protective covering shall be protected by corner guards or by a substantial jacket of metal or other noncombustible material to a height adequate to provide full protection, but not less than 5 feet (1524 mm) from the finished floor. Exception: Corner protection is not required on concrete columns in parking garages.
704.10 Exterior structural members. | Load-bearing structural members located within the exterior walls, or exposed to the outside of a building or structure shall be provided with the highest fire-resistance rating as determined in accordance with the following: | 704.10 Exterior structural members. | Load-bearing structural members located within the exterior walls or on the outside of a building or structure shall be provided with the highest fire-resistance rating as determined in accordance with the following:
704.11 Bottom flange protection. | Fire protection is not required at the bottom flange of lintels, shelf angles and plates spanning not more than 6 feet 4 inches (1930.4 mm), whether part of the primary structural frame or not, and from the bottom flange of lintels, shelf angles and plates not part of the structural frame, regardless of span. | 704.11 Bottom flange protection. | Fire protection is not required at the bottom flange of lintels, shelf angles and plates, spanning not more than 6 feet 4 inches (1931 mm) whether part of the primary structural frame or not, and from the bottom flange of lintels, shelf angles and plates not part of the structural frame, regardless of span.
704.12 Seismic isolation systems. | Fire-resistance ratings for the isolation system shall meet the fire-resistance rating required for the columns, walls or other structural elements in which the isolation system is installed in accordance with Table 601 of this code. Isolation systems required to have a fire-resistance rating shall be protected with approved materials or construction assemblies designed to provide the same degree of fire resistance as the structural element in which the system is installed when tested in accordance with ASTM E 119 or UL 263 (see Section 703.2 of this code). | 704.12 Seismic isolation systems. | Fire-resistance ratings for the isolation system shall meet the fire-resistance rating required for the columns, walls or other structural elements in which the isolation system is installed in accordance with Table 601. Isolation systems required to have a fire-resistance rating shall be protected with approved materials or construction assemblies designed to provide the same degree of fire resistance as the structural element in which the system is installed when tested in accordance with ASTM E119 or UL 263 (see Section 703.2). |  | See BC07 Tables&Figures
704.13 Sprayed fire-resistant materials (SFRM). | Sprayed fire-resistant materials (SFRM) shall comply with Sections 704.13.1 through 704.13.5. | 704.13 Sprayed fire-resistant materials (SFRM). | Sprayed fire-resistant materials (SFRM) shall comply with Sections 704.13.1 through 704.13.5.
704.13.1 Fire-resistance rating. | The application of SFRM shall be consistent with the fire-resistance rating and the listing, including, but not limited to, minimum thickness and dry density of the applied SFRM, method of application, substrate surface conditions and the use of bonding adhesives, sealants, reinforcing or other materials. | 704.13.1 Fire-resistance rating. | The application of SFRM shall be consistent with the fire-resistance rating and the listing, including, but not limited to, minimum thickness and dry density of the applied SFRM, method of application, substrate surface conditions and the use of bonding adhesives, sealants, reinforcing or other materials.
704.13.2 Manufacturer’s installation instructions. | The application of SFRM shall be in accordance with the manufacturer’s installation instructions. The instructions shall include, but are not limited to, substrate temperatures and surface conditions and SFRM handling, storage, mixing, conveyance, method of application, curing and ventilation. | 704.13.2 Manufacturer’s installation instructions. | The application of SFRM shall be in accordance with the manufacturer’s installation instructions. The instructions shall include, but are not limited to, substrate temperatures and surface conditions and SFRM handling, storage, mixing, conveyance, method of application, curing and ventilation.
704.13.3 Substrate condition. | The SFRM shall be applied to a substrate in compliance with Sections 704.13.3.1 through 704.13.3.2. | 704.13.3 Substrate condition. | The SFRM shall be applied to a substrate in compliance with Sections 704.13.3.1 and 704.13.3.2.
704.13.3.1 Surface conditions. | Substrates to receive SFRM shall be free of dirt, oil, grease, release agents, loose scale and any other condition that prevents adhesion. The substrates shall be free of primers, paints and encapsulants other than those fire tested and listed by a nationally recognized testing agency. Primed, painted or encapsulated steel shall be allowed, provided that testing has demonstrated that required adhesion is maintained. | 704.13.3.1 Surface conditions. | Substrates to receive SFRM shall be free of dirt, oil, grease, release agents, loose scale and any other condition that prevents adhesion. The substrates shall be free of primers, paints and encapsulants other than those fire tested and listed by a nationally recognized testing agency. Primed, painted or encapsulated steel shall be allowed, provided that testing has demonstrated that required adhesion is maintained.
704.13.3.2 Primers, paints and encapsulants. | Where the SFRM is to be applied over primers, paints or encapsulants other than those specified in the listing, the material shall be field tested in accordance with ASTM E 736. Where testing of the SFRM with primers, paints or encapsulants demonstrates that required adhesion is maintained, SFRM shall be permitted to be applied to primed, painted or encapsulated wide flange steel shapes subject to the following conditions: | 704.13.3.2 Primers, paints and encapsulants. | Where the SFRM is to be applied over primers, paints or encapsulants other than those specified in the listing, the material shall be field tested in accordance with ASTM E736. Where testing of the SFRM with primers, paints or encapsulants demonstrates that required adhesion is maintained, SFRM shall be permitted to be applied to primed, painted or encapsulated wide flange steel shapes in accordance with the following conditions:
704.13.4 Temperature. | A minimum ambient and substrate temperature of 40°F (4.44°C) shall be maintained during and for not fewer than 24 hours after the application of the SFRM, unless the manufacturer’s instructions allow otherwise. | 704.13.4 Temperature. | A minimum ambient and substrate temperature of 40°F (4.44°C) shall be maintained during and for not fewer than 24 hours after the application of the SFRM, unless the manufacturer’s instructions allow otherwise.
704.13.5 Finished condition. | The finished condition of SFRM applied to structural members or assemblies shall not, upon complete drying or curing, exhibit cracks, voids, spalls, delamination or any exposure of the substrate. Surface irregularities of SFRM shall be deemed acceptable. | 704.13.5 Finished condition. | The finished condition of SFRM applied to structural members or assemblies shall not, upon complete drying or curing, exhibit cracks, voids, spalls, delamination or any exposure of the substrate. Surface irregularities of SFRM shall be deemed acceptable.
705.1 General. | Exterior walls shall comply with this section. Exterior wall construction shall comply with the provisions of Chapter 14 and Appendix D where applicable. | 705.1 General. | Exterior walls shall comply with this section.
705.2 Projections. | Cornices, eave overhangs, exterior balconies and similar projections, including but not limited to, fascias, belt courses, pilasters, surrounds, gutters, leaders, half-timber work, shutters, and trellises, extending beyond the exterior wall shall conform to the requirements of this section and Section 1406, provided that any such projection, if removed, altered or destroyed, will not reduce the structural stability of the building enclosure, and that such projection is installed so as not to reduce the required fire-resistance rat­ing of the building enclosure. Exterior egress balconies and exterior exit stairways and ramps shall comply with the requirements of this section and Sections 1021 and 1027, respectively. Projections shall not extend any closer to the line used to determine the fire separation distance Table 705.2. Exterior wall coverings and cladding at exterior balconies and similar projections shall comply with Section 1406.3. Exception: Buildings on the same tax lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with this section. | 705.2 Projections. | Cornices, eave overhangs, exterior balconies and similar projections extending beyond the exterior wall shall conform to the requirements of this section and Section 1405. Exterior egress balconies and exterior exit stairways and ramps shall comply with Sections 1021 and 1027, respectively. Projections shall not extend any closer to the line used to determine the fire separation distance than shown in Table 705.2. Exception: Buildings on the same lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with this section for projections between the buildings. |  | See BC07 Tables&Figures
705.2.2 Type III, IV or V construction. | Projections from walls of Type III, IV or V construction shall be of any approved material. Projections located where openings are not permitted or where protection of openings is required shall be constructed of the following: | 705.2.2 Type III, IV or V construction. | Projections from walls of Type III, IV or V construction shall be of any approved material.
|  | 705.2.1 Types I and II construction. | Projections from walls of Type I or II construction shall be of noncombustible materials or combustible materials as allowed by Sections 705.2.3.1 and 705.2.4.
|  | 705.2.3 Projection protection. | Projections extending to within 5 feet (1524 mm) of the line used to determine the fire separation distance shall be one of the following: 1. Noncombustible materials. 2. Combustible materials of not less than 1-hour fire-resistance-rated construction. 3. Heavy timber construction complying with Section 2304.11. 4. Fire-retardant-treated wood. 5. As permitted by Section 705.2.3.1. Exception: Type VB construction shall be allowed for combustible projections in Group R-3 and U occupancies with a fire separation distance greater than or equal to 5 feet (1524 mm).
705.4 Materials. | Exterior walls shall be of materials permitted by the building type of construction. | 705.4 Materials. | Exterior walls shall be of materials permitted by the building’s type of construction.
|  | 705.2.3.1 Balconies and similar projections. | Balconies and similar projections of combustible construction other than fire-retardant-treated wood shall be fire-resistance rated where required by Table 601 for floor construction or shall be of heavy timber construction in accordance with Section 2304.11. The aggregate length of the projections shall not exceed 50 percent of the building’s perimeter on each floor. Exceptions: 1. On buildings of Types I and II construction, three stories or less above grade plane, fire-retardant-treated wood shall be permitted for balconies, porches, decks and exterior stairways not used as re-quired exits. 2. Untreated wood and plastic composites that comply with ASTM D7032 and Section 2612 are permitted for pickets, rails and similar guard components that are limited to 42 inches (1067 mm) in height. 3. Balconies and similar projections on buildings of Types III, IV and V construction shall be permitted to be of Type V construction and shall not be required to have a fire-resistance rating where sprinkler protection is extended to these areas. 4. Where sprinkler protection is extended to the balcony areas, the aggregate length of the balcony on each floor shall not be limited. |  | See BC07 Tables&Figures
705.5 Fire-resistance ratings. | Exterior walls shall be fire-resistance-rated in accordance with Tables 601 and 602 and Appendix D where applicable. The required fire-resistance rating of exterior walls with a fire separation distance of greater than 10 feet (3048 mm) shall be rated for exposure to fire from the inside. The required fire-resistance rating of exterior walls with a fire separation distance of less than or equal to 10 feet (3048 mm) shall be rated for exposure to fire from both sides. | 705.5 Fire-resistance ratings. | Exterior walls shall be fire-resistance rated in accordance with Table 601, based on the type of construction, and Table 705.5, based on the fire separation distance. The required fire-resistance rating of exterior walls with a fire separation distance of greater than 10 feet (3048 mm) shall be rated for exposure to fire from the inside. The required fire-resistance rating of exterior walls with a fire separation distance of less than or equal to 10 feet (3048 mm) shall be rated for exposure to fire from both sides. |  | See BC07 Tables&Figures
|  | 705.2.4 Bay and oriel windows. | Bay and oriel windows constructed of combustible materials shall conform to the type of construction required for the building to which they are attached. Exception: Fire-retardant-treated wood shall be permitted on buildings three stories or less above grade plane of Type I, II, III or IV construction.
705.6 Structural stability. | Exterior walls shall extend to the height required by Section 705.11. Interior structural elements that brace the exterior wall but that are not located within the plane of the exterior wall shall have the minimum fire-resistance rating required in Table 601 for that structural element. Structural elements that brace the exterior wall but are located outside of the exterior wall or wholly or partly within the plane of the exterior wall shall have the minimum fire-resistance rating required in Tables 601 and 602 for the exterior wall. | 705.6 Structural stability. | Exterior walls shall extend to the height required by Section 705.11. Interior structural elements that brace the exterior wall but that are not located within the plane of the exterior wall shall have the minimum fire-resistance rating required in Table 601 for that structural element. Structural elements that brace the exterior wall but are located outside of the exterior wall or within the plane of the exterior wall shall have the minimum fire-resistance rating required in Table 601 and Table 705.5 for the exterior wall. |  | See BC07 Tables&Figures
|  | 705.3 Buildings on the same lot. | For the purposes of determining the required wall and opening protection, projections and roof-covering requirements, buildings on the same lot shall be assumed to have an imaginary line between them. Exceptions: 1. Two or more buildings on the same lot shall be either regulated as separate buildings or shall be considered as portions of one building if the aggregate area of such buildings is within the limits specified in Chapter 5 for a single building. Where the buildings contain different occupancy groups or are of different types of construc-tion, the area shall be that allowed for the most restrictive occupancy or construction. 2. Where an S-2 parking garage of Construction Type I or IIA is erected on the same lot as a Group R-2 building, and there is no fire separation distance between these buildings, then the adjoining exterior walls between the buildings are permitted to have occupant use openings in accordance with Section 706.8. However, opening protectives in such openings shall only be required in the exterior wall of the S-2 parking garage, not in the ex-terior wall openings in the R-2 building, and these opening protectives in the exterior wall of the S-2 parking garage shall be not less than 11/2-hour fire protection rating.
705.7 Unexposed surface temperature. | Where protected openings are not limited by Section 705.8, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E 119 or UL 263 shall not apply. Where protected openings are limited by Section 705.8 of this code, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E 119 or UL 263 shall not apply provided that a correction is made for radiation from the unexposed exterior wall surface in accordance with the following formula: | 705.7 Unexposed surface temperature. | Where protected openings are not limited by Section 705.8, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E119 or UL 263 shall not apply. Where protected openings are limited by Section 705.8, the limitation on the rise of temperature on the unexposed surface of exterior walls as required by ASTM E119 or UL 263 shall not apply provided that a correction is made for radiation from the unexposed exterior wall surface in accordance with the following formula:
705.8 Openings. | Openings in exterior walls shall comply with Sections 705.8.1 through 705.8.6. | 705.8 Openings. | Openings in exterior walls shall comply with Sections 705.8.1 through 705.8.6.
705.8.1 Allowable area of openings. | The maximum area of unprotected and protected openings permitted in an exterior wall in any story of a building shall not exceed the percentages specified in Table 705.8. Exceptions: 1. In other than Group H occupancies, unlimited unprotected openings are permitted in the first story above grade plane either: 1.1. Where the wall faces a street and has a fire separation distance of more than 15 feet (4572 mm); or 1.2. Where the wall faces an unoccupied space, the unoccupied space shall be on the same tax lot or dedicated for public use, shall be not less than 30 feet (9144 mm) in width and shall have access from a street by a posted fire lane in accordance with the New York City Fire Code. 2. Buildings whose exterior bearing walls, exterior nonbearing walls and exterior primary structural frame are not required to be fire-resistance-rated shall be permitted to have unlimited unprotected openings. | 705.8.1 Allowable area of openings. | The maximum area of unprotected and protected openings permitted in an exterior wall in any story of a building shall not exceed the percentages specified in Table 705.8 based on the fire separation distance of each individual story. Exceptions: 1. In other than Group H occupancies, unlimited unprotected openings are permitted in the first story above grade plane where the wall faces one of the following: 1.1. A street and has a fire separation distance of more than 15 feet (4572 mm). 1.2. An unoccupied space. The unoccupied space shall be on the same lot or dedicated for public use, shall be not less than 30 feet (9144 mm) in width and shall have access from a street by a posted fire lane in accordance with the International Fire Code. 2. Buildings whose exterior bearing walls, exterior nonbearing walls and exterior primary structural frame are not required to be fire-resistance rated shall be permitted to have unlimited unprotected openings. |  | See BC07 Tables&Figures
705.8.2 Protected openings. | Where openings are required to be protected, fire doors and fire shutters shall comply with Section 716.5 and fire window assemblies shall comply with Section 716.6. Exception: Opening protectives are not required where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and the exterior openings are protected by a water curtain using automatic sprinklers approved for that use. The sprinklers and the water curtain shall be installed in accordance with NFPA 13, as modified by Appendix Q of this code. | 705.8.2 Protected openings. | Where openings are required to be protected, opening protectives shall comply with Section 716. Exception: Opening protectives are not required where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and the exterior openings are protected by a water curtain using automatic sprinklers approved for that use.
705.8.3 Unprotected openings. | Where unprotected openings are permitted, windows and doors shall be constructed of any approved materials. Glazing shall conform to the requirements of Chapters 24 and 26. | 705.8.3 Unprotected openings. | Where unprotected openings are permitted, windows and doors shall be constructed of any approved materials. Glazing shall conform to the requirements of Chapters 24 and 26.
705.8.4 Mixed openings. | Where both unprotected and protected openings are located in the exterior wall in any story of a building, the total area of the openings shall be determined in accordance with the following formula: | 705.8.4 Mixed openings. | Where both unprotected and protected openings are located in the exterior wall in any story of a building, the total area of openings shall be determined in accordance with the following:
705.8.5 Vertical separation of openings. | Openings in exterior walls in adjacent stories shall be separated vertically to protect against fire spread on the exterior of the buildings where the openings are within 5 feet (1524 mm) of each other horizontally. Such openings shall be separated vertically not less than 3 feet (914.4 mm) by spandrel girders, exterior walls or other similar assemblies that have a fire-resistance rating of not less than 1 hour, rated for exposure to fire from both sides, or by flame barriers that extend horizontally not less than 30 inches (762 mm) beyond the exterior wall and that are at least as wide as the opening. Flame barriers shall have a fire-resistance rating of not less than 1 hour. The unexposed surface temperature limitations specified in ASTM E 119 or UL 263 shall not apply to the flame barriers or vertical separation unless otherwise required by the provisions of this code. Where a curtain wall assembly is used on the exterior wall, the intersection between the floor assembly and curtain wall assembly shall be protected in accordance with Section 713.4 of this code. Exceptions: 1. This section shall not apply to buildings that are three stories or less above grade plane. 2. This section shall not apply to buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 3. This section shall not apply to open parking garages. 4. This section shall not apply to Occupancy Group A, E, I or R. 5. This section shall not apply where the opening in the lower story is a protected opening with a fire protection rating of at least ¾ hour. | 705.8.5 Vertical separation of openings. | Openings in exterior walls in adjacent stories shall be separated vertically to protect against fire spread on the exterior of the buildings where the openings are within 5 feet (1524 mm) of each other horizontally and the opening in the lower story is not a protected opening with a fire protection rating of not less than 3/4 hour. Such openings shall be separated vertically not less than 3 feet (914 mm) by spandrel girders, exterior walls or other similar assemblies that have a fire-resistance rating of not less than 1 hour, rated for exposure to fire from both sides, or by flame barriers that extend horizontally not less than 30 inches (762 mm) beyond the exterior wall. Flame barriers shall have a fire-resistance rating of not less than 1 hour. The unexposed surface temperature limitations specified in ASTM E119 or UL 263 shall not apply to the flame barriers unless otherwise required by the provisions of this code. Exceptions: 1. This section shall not apply to buildings that are three stories or less above grade plane. 2. This section shall not apply to buildings equipped throughout with an automatic sprinkler system in ac-cordance with Section 903.3.1.1 or 903.3.1.2. 3. Open parking garages.
705.8.6 Vertical exposure. | For buildings on the same tax lot, opening protectives shall be provided in every opening that is less than 15 feet (4572 mm) vertically above the roof of an adjacent building or structure based on assuming an imaginary line between them. The opening protectives are required where the fire separation distance between the imaginary line and the adjacent building or structure is less than 15 feet (4572 mm). Exceptions: 1. Opening protectives are not required where the roof assembly of the adjacent building or structure has a fire-resistance rating of not less than 1 hour for a minimum distance of 10 feet (3048 mm) from the exterior wall facing the imaginary line and the entire length and span of the supporting elements for the fire-resistance-rated roof assembly has a fire-resistance rating of not less than 1 hour. 2. Buildings on the same tax lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with Section 705.8.6. | 705.8.6 Vertical exposure. | For buildings on the same lot, opening protectives having a fire protection rating of not less than 3/4 hour shall be provided in every opening that is less than 15 feet (4572 mm) vertically above the roof of an adjacent building or structure based on assuming an imaginary line between them. The opening protectives are required where the fire separation distances from the imaginary line to each building or structure are less than 15 feet (4572 mm). Exceptions: 1. Opening protectives are not required where the roof assembly of the adjacent building or structure has a fire-resistance rating of not less than 1 hour for a minimum distance of 10 feet (3048 mm) from the exteri-or wall facing the imaginary line and the entire length and span of the supporting elements for the fire-resistance-rated roof assembly has a fire-resistance rating of not less than 1 hour. 2. Buildings on the same lot and considered as portions of one building in accordance with Section 705.3 are not required to comply with Section 705.8.6.
705.9 Joints. | Joints made in or between exterior walls required by this section to have a fire-resistance rating shall comply with Section 715. Exception: Joints in exterior walls that are permitted to have unprotected openings. | 705.9 Joints. | Joints made in or between exterior walls required by this section to have a fire-resistance rating shall comply with Section 715. Exception: Joints in exterior walls that are permitted to have unprotected openings.
705.9.1 Voids. | The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 715.4. | 705.9.1 Voids. | The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 715.4.
705.10 Ducts and air transfer openings. | Penetrations by air ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings shall comply with Section 717. Exception: Foundation vents installed in accordance with this code are permitted. | 705.10 Ducts and air transfer openings. | Penetrations by air ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings shall comply with Section 717. Exception: Foundation vents installed in accordance with this code are permitted.
705.11 Parapets. | Parapets shall be provided on exterior walls of buildings. Exceptions: A parapet need not be provided on an exterior wall where any of the following conditions exist: 1. The wall is not required to be fire-resistance-rated in accordance with Table 602 because of fire separation distance. 2. The building has an area of not more than 1,000 square feet (92.9 m²) on any floor. 3. Walls that terminate at roofs of not less than 2-hour fire-resistance-rated construction. 4. One-hour fire-resistance-rated exterior walls that terminate at the underside of the roof sheathing, deck or slab, provided that the entire building is covered with a Class A roof covering. Such roof shall not have openings located within 10 feet (3048 mm) of the 1-hour fire-resistance-rated exterior wall and not within 5 feet (1524 mm) for Groups R and U. 4.1. Where the roof/ceiling framing elements are parallel to the walls, such framing and elements supporting such framing shall not be of less than 1-hour fire- resistance-rated construction for a width of 4 feet (1220 mm) for Groups R and U and 10 feet (3048 mm) for other occupancies, measured from the interior side of the wall. 4.2. Where roof/ceiling framing elements are not parallel to the wall, the entire span of such framing and elements supporting such framing shall not be of less than 1-hour fire-resistance-rated construction. 5. In occupancies of Groups R-2 and R-3, where both are provided with a Class A or B roof covering, the exterior wall shall be permitted to terminate at the underside of the roof sheathing or deck in Type III, IV and V construction, provided one or both of the following criteria is met: 5.1. The roof sheathing or deck is constructed of approved noncombustible materials or of fire-retardant-treated wood for a distance of 4 feet (1220 mm) from the perimeter; or 5.2. The roof is protected with 0.625-inch (15.9 mm) Type X gypsum board directly beneath the underside of the roof sheathing or deck, supported by not less than nominal 2-inch (50.8 mm) ledgers attached to the sides of the roof framing members for a minimum distance of 4 feet (1220 mm). 6. Where the wall is permitted to have not less than 25 percent of the exterior wall areas containing unprotected openings based on fire separation distance as determined in accordance with Section 705.8. | 705.11 Parapets. | Parapets shall be provided on exterior walls of buildings. Exceptions: A parapet need not be provided on an exterior wall where any of the following conditions exist: 1. The wall is not required to be fire-resistance rated in accordance with Table 705.5 because of fire separation distance. 2. The building has an area of not more than 1,000 square feet (93 m2) on any floor. 3. Walls that terminate at roofs of not less than 2-hour fire-resistance-rated construction or where the roof, in-cluding the deck or slab and supporting construction, is constructed entirely of noncombustible materials. 4. One-hour fire-resistance-rated exterior walls that terminate at the underside of the roof sheathing, deck or slab, provided that: 4.1. Where the roof/ceiling framing elements are parallel to the walls, such framing and elements supporting such framing shall not be of less than 1-hour fire-resistance-rated construction for a width of 4 feet (1220 mm) for Groups R and U and 10 feet (3048 mm) for other occupancies, measured from the inte-rior side of the wall. 4.2. Where roof/ceiling framing elements are not parallel to the wall, the entire span of such framing and el-ements supporting such framing shall not be of less than 1-hour fire-resistance-rated construction. 4.3. Openings in the roof shall not be located within 5 feet (1524 mm) of the 1-hour fire-resistance-rated ex-terior wall for Groups R and U and 10 feet (3048 mm) for other occupancies, measured from the interi-or side of the wall. 4.4. The entire building shall be provided with not less than a Class B roof covering. 5. In Groups R-2 and R-3 where the entire building is provided with a Class C roof covering, the exterior wall shall be permitted to terminate at the underside of the roof sheathing or deck in Types III, IV and V construc-tion, provided that one or both of the following criteria is met: 5.1. The roof sheathing or deck is constructed of approved noncombustible materials or of fire-retardant-treated wood for a distance of 4 feet (1220 mm). 5.2. The roof is protected with 0.625-inch (16 mm) Type X gypsum board directly beneath the underside of the roof sheathing or deck, supported by not less than nominal 2-inch (51 mm) ledgers attached to the sides of the roof framing members for a minimum distance of 4 feet (1220 mm). 6. Where the wall is permitted to have not less than 25 percent of the exterior wall areas containing unprotected openings based on fire separation distance as determined in accordance with Section 705.8. |  | See BC07 Tables&Figures
705.11.1 Parapet construction. | Parapets shall have the same fire-resistance rating as that required for the supporting wall, and on any side adjacent to a roof surface, shall have noncombustible faces for the uppermost 18 inches (457.2 mm), including counterflashing and coping materials. The height of the parapet shall be not less than 30 inches (762 mm) above the point where the roof surface and the wall intersect. Where the roof slopes toward a parapet at a slope greater than two units vertical in 12 units horizontal (16.7-percent slope), the parapet shall extend to the same height as any portion of the roof within a fire separation distance where protection of wall openings is required, but in no case shall the height be less than 30 inches (762 mm). | 705.11.1 Parapet construction. | Parapets shall have the same fire-resistance rating as that required for the supporting wall, and on any side adjacent to a roof surface, shall have noncombustible faces for the uppermost 18 inches (457 mm), including counterflashing and coping materials. The height of the parapet shall be not less than 30 inches (762 mm) above the point where the roof surface and the wall intersect. Where the roof slopes toward a parapet at a slope greater than 2 units vertical in 12 units horizontal (16.7-percent slope), the parapet shall extend to the same height as any portion of the roof within a fire separation distance where protection of wall openings is required, but the height shall be not less than 30 inches (762 mm).
706.1 General. | Each portion of a building separated by one or more fire walls that comply with the provisions of this section shall be considered a separate building. The extent and location of such fire walls shall provide a complete separation. Where a fire wall also separates occupancies that are required to be separated by a fire barrier wall, the most restrictive requirements of each separation shall apply. Concealed spaces in cornices and eaves shall comply with the provisions of Section 705.2.2. | 706.1 General. | Fire walls shall be constructed in accordance with Sections 706.2 through 706.11. The extent and location of such fire walls shall provide a complete separation. Where a fire wall separates occupancies that are required to be separated by a fire barrier wall, the most restrictive requirements of each separation shall apply.
706.1.1 Party walls. | Any wall located on a property line between adjacent buildings, which is used or adapted for joint service between the two buildings, shall be constructed as a fire wall in accordance with Section 706, and shall create separate buildings. Exception: Openings in a party wall separating an anchor building and a mall shall be in accordance with Section 402.4.2.2. | 706.1.1 Party walls. | Any wall located on a lot line between adjacent buildings, which is used or adapted for joint service between the two buildings, shall be constructed as a fire wall in accordance with Section 706. Party walls shall be constructed without openings and shall create separate buildings. Exceptions: 1. Openings in a party wall separating an anchor building and a mall shall be in accordance with Section 402.4.2.2.1. 2. Party walls and fire walls are not required on lot lines dividing a building for ownership purposes where the aggregate height and area of the portions of the building located on both sides of the lot line do not exceed the maximum height and area requirements of this code. For the building official’s review and approval, the official shall be provided with copies of dedicated access easements and contractual agreements that permit the owners of portions of the building located on either side of the lot line access to the other side for pur-poses of maintaining fire and life safety systems necessary for the operation of the building.
706.2 Structural stability. | Fire walls shall be designed and constructed to allow collapse of the structure on either side without collapse of the wall under fire conditions. Fire walls designed and constructed in accordance with NFPA 221 shall be deemed to comply with this section. | 706.2 Structural stability. | Fire walls shall be designed and constructed to allow collapse of the structure on either side without collapse of the wall under fire conditions. Fire walls designed and constructed in accordance with NFPA 221 shall be deemed to comply with this section. Exception: In Seismic Design Categories D through F, where double fire walls are used in accordance with NFPA 221, floor and roof sheathing not exceeding 3/4 inch (19.05 mm) thickness shall be permitted to be continuous through the wall assemblies of light frame construction.
706.3 Materials. | Fire walls shall be constructed of any approved noncombustible materials. | 706.3 Materials. | Fire walls shall be of any approved noncombustible materials. Exception: Buildings of Type V construction.
706.4 Fire-resistance rating. | Fire walls shall have a fire-resistance rating of not less than that required by Table 706.4. | 706.4 Fire-resistance rating. | Fire walls shall have a fire-resistance rating of not less than that required by Table 706.4. |  | See BC07 Tables&Figures
706.5 Horizontal continuity. | Fire walls shall be continuous from exterior wall to exterior wall and shall extend not less than 18 inches (457.2 mm) beyond the exterior surface of exterior walls. Exceptions: 1. Fire walls shall be permitted to terminate at the interior surface of combustible exterior sheathing or siding provided the exterior wall has a fire-resistance rating of not less than 1 hour for a horizontal distance of not less than 4 feet (1220 mm) on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. 2. Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing, exterior siding or other noncombustible exterior finishes provided the sheathing, siding or other exterior noncombustible finish extends a horizontal distance of not less than 4 feet (1220 mm) on both sides of the fire wall. 3. Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing where the building on each side of the fire wall is protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 706.5 Horizontal continuity. | Fire walls shall be continuous from exterior wall to exterior wall and shall extend not less than 18 inches (457 mm) beyond the exterior surface of exterior walls. Exceptions: 1. Fire walls shall be permitted to terminate at the interior surface of combustible exterior sheathing or siding provided that the exterior wall has a fire-resistance rating of not less than 1 hour for a horizontal distance of not less than 4 feet (1220 mm) on both sides of the fire wall. Openings within such exterior walls shall be pro-tected by opening protectives having a fire protection rating of not less than 3/4 hour. 2. Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing, exterior siding or other noncombustible exterior finishes provided that the sheathing, siding or other exterior noncom-bustible finish extends a horizontal distance of not less than 4 feet (1220 mm) on both sides of the fire wall. 3. Fire walls shall be permitted to terminate at the interior surface of noncombustible exterior sheathing where the building on each side of the fire wall is protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.
706.5.1 Exterior walls. | Where the fire wall intersects exterior walls, the fire-resistance rating and opening protection of the exterior walls shall comply with one of the following: | 706.5.1 Exterior walls. | Where the fire wall intersects exterior walls, the fire-resistance rating and opening protection of the exterior walls shall comply with one of the following:
706.5.2 Horizontal projecting elements. | Fire walls shall extend to the outer edge of horizontal projecting elements such as balconies, roof overhangs, canopies, marquees and similar projections that are within 4 feet (1220 mm) of the fire wall. Exceptions: 1. Horizontal projecting elements without concealed spaces, provided the exterior wall behind and below the projecting element has not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting element on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. 2. Noncombustible horizontal projecting elements with concealed spaces, provided a minimum 1-hour fire-resistance-rated wall extends through the concealed space. The projecting element shall be separated from the building by not less than 1-hour fire-resistance-rated construction for a distance on each side of the fire wall equal to the depth of the projecting element. The wall is not required to extend under the projecting element where the building exterior wall is not less than 1-hour fire-resistance-rated for a distance on each side of the fire wall equal to the depth of the projecting element. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. 3. For combustible horizontal projecting elements with concealed spaces, the fire wall need only extend through the concealed space to the outer edges of the projecting elements. The exterior wall behind and below the projecting element shall be of not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting elements on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire-protection rating of not less than 3/4 hour. | 706.5.2 Horizontal projecting elements. | Fire walls shall extend to the outer edge of horizontal projecting elements such as balconies, roof overhangs, canopies, marquees and similar projections that are within 4 feet (1220 mm) of the fire wall. Exceptions: 1. Horizontal projecting elements without concealed spaces, provided that the exterior wall behind and below the projecting element has not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting element on both sides of the fire wall. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. 2. Noncombustible horizontal projecting elements with concealed spaces, provided that a minimum 1-hour fire-resistance-rated wall extends through the concealed space. The projecting element shall be separated from the building by not less than 1-hour fire-resistance-rated construction for a distance on each side of the fire wall equal to the depth of the projecting element. The wall is not required to extend under the pro-jecting element where the building exterior wall is not less than 1-hour fire-resistance rated for a distance on each side of the fire wall equal to the depth of the projecting element. Openings within such exterior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. 3. For combustible horizontal projecting elements with concealed spaces, the fire wall need only extend through the concealed space to the outer edges of the projecting elements. The exterior wall behind and be-low the projecting element shall be of not less than 1-hour fire-resistance-rated construction for a distance not less than the depth of the projecting elements on both sides of the fire wall. Openings within such exte-rior walls shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour.
706.6 Vertical continuity. | Fire walls shall extend from the foundation through the roof, to form a parapet not less than 30 inches (762 mm) in height. Exceptions: 1. Where a 2-hour fire wall is permitted in accordance with Table 706.4, such wall shall be permitted to ter¬minate at the underside of the roof sheathing, deck or slab provided: 1.1. The lower roof assembly within 4 feet (1220 mm) of the wall has not less than a 1-hour fire-resistance rating and the entire length and span of supporting elements for the rated roof assembly has a fire-resistance rating of not less than 1 hour; and 1.2. Openings in the roof shall not be located within 4 feet (1220 mm) of the fire wall; and 1.3. Each building shall be provided with not less than a Class A roof covering. 2. In buildings of Type I or II construction, fire walls shall be permitted to terminate at the underside of noncombustible roof sheathing, deck, or slabs where both buildings are provided with not less than a Class A roof covering. Openings in the roof shall not be located within 4 feet (1220 mm) of the fire wall. 3. In buildings of Type III, IV and V construction, fire walls shall be permitted to terminate at the underside of noncombustible roof sheathing or decks provided: 3.1. There are no openings in the roof within 4 feet (1220 mm) of the fire wall; and 3.2. The roof is covered with a minimum Class A roof covering. 4. In buildings designed in accordance with Section 510.2, fire walls located above the 3-hour horizontal assembly required by Section 510.2, Item 1 shall be permitted to extend from the top of this horizontal assembly. 5. Where a fire wall serves as an interior wall for a building, and the roof on one side or both sides of the fire wall slopes toward the fire wall at a slope greater than two units vertical in 12 units horizontal (2:12), the fire wall shall extend to a height equal to the height of the roof located 4 feet (1220 mm) from the fire wall plus 30 inches (762 mm). In no case shall the extension of the fire wall be less than 30 inches (762 mm). | 706.6 Vertical continuity. | Fire walls shall extend from the foundation to a termination point not less than 30 inches (762 mm) above both adjacent roofs. Exceptions: 1. Stepped buildings in accordance with Section 706.6.1. 2. Two-hour fire-resistance-rated walls shall be permitted to terminate at the underside of the roof sheathing, deck or slab, provided that: 2.1. The lower roof assembly within 4 feet (1220 mm) of the wall has not less than a 1-hour fire-resistance rating and the entire length and span of supporting elements for the rated roof assembly has a fire-resistance rating of not less than 1 hour. 2.2. Openings in the roof shall not be located within 4 feet (1220 mm) of the fire wall. 2.3. Each building shall be provided with not less than a Class B roof covering. 3. Walls shall be permitted to terminate at the underside of noncombustible roof sheathing, deck or slabs where both buildings are provided with not less than a Class B roof covering. Openings in the roof shall not be locat-ed within 4 feet (1220 mm) of the fire wall. 4. In buildings of Types III, IV and V construction, walls shall be permitted to terminate at the underside of com-bustible roof sheathing or decks, provided that all of the following requirements are met: 4.1. Roof openings are not less than 4 feet (1220 mm) from the fire wall. 4.2. The roof is covered with a minimum Class B roof covering. 4.3. The roof sheathing or deck is constructed of fire-retardant-treated wood for a distance of 4 feet (1220 mm) on both sides of the wall or the roof is protected with 5/8-inch (15.9 mm) Type X gypsum board di-rectly beneath the underside of the roof sheathing or deck, supported by not less than 2-inch (51 mm) nominal ledgers attached to the sides of the roof framing members for a distance of not less than 4 feet (1220 mm) on both sides of the fire wall. 5. In buildings designed in accordance with Section 510.2, fire walls located above the 3-hour horizontal assem-bly required by Section 510.2, Item 1 shall be permitted to extend from the top of this horizontal assembly. 6. Buildings with sloped roofs in accordance with Section 706.6.2. |  | See BC07 Tables&Figures
706.6.1 Stepped buildings. | Where a fire wall serves as an exterior wall for a building and separates buildings having different roof levels, such wall shall terminate at a point not less than 30 inches (762 mm) above the lower roof level, provided the exterior wall for a height of 60 feet (18 288 mm) above the lower roof is not less than 1-hour fire-resistance-rated construction from both sides with openings protected by fire assemblies having a fire protection rating of not less than ¾ hour. Exception: Where the fire wall terminates at the underside of the roof sheathing, deck or slab of the lower roof, provided: 1. The lower roof assembly within 10 feet (3048 mm) of the wall has not less than a 1-hour fire-resistance rating and the entire length and span of supporting elements for the rated roof assembly has a fire-resistance rating of not less than 1 hour. 2. Openings in the lower roof shall not be located within 10 feet (3048 mm) of the fire wall. | 706.6.1 Stepped buildings. | Where a fire wall also serves as an exterior wall for a building and separates buildings having different roof levels, such wall shall terminate at a point not less than 30 inches (762 mm) above the lower roof level. Exterior walls above the fire wall extending more than 30 inches (762 mm) above the lower roof shall be of not less than 1-hour fire-resistance-rated construction from both sides with openings protected by fire assemblies having a fire protection rating of not less than 3/4 hour. Portions of the exterior walls greater than 15 feet (4572 mm) above the lower roof shall be of nonfire-resistance-rated construction unless otherwise rated construction is required by other provisions of this code. Exception: A fire wall serving as part of an exterior wall that separates buildings having different roof levels shall be permitted to terminate at the underside of the roof sheathing, deck or slab of the lower roof, provided that Items 1, 2 and 3 are met. The exterior wall above the fire wall is not required to be of fire-resistance-rated construction unless required by other provisions of this code. 1. The lower roof assembly within 10 feet (3048 mm) of the fire wall has not less than a 1-hour fire-resistance rating. 2. The entire length and span of supporting elements for the rated roof assembly shall have a fire-resistance rating of not less than 1 hour. 3. Openings in the lower roof shall not be located within 10 feet (3048 mm) of the fire wall.
|  | 706.6.2 Buildings with sloped roofs. | Where a fire wall serves as an interior wall for a building, and the roof on one side or both sides of the fire wall slopes toward the fire wall at a slope greater than 2 units vertical in 12 units horizontal (2:12), the fire wall shall extend to a height equal to the height of the roof located 4 feet (1219 mm) from the fire wall plus 30 inches (762 mm). The extension of the fire wall shall be not less than 30 inches (762 mm).
706.7 Combustible framing in fire walls. | Adjacent combustible members entering into a concrete or masonry fire wall from opposite sides shall not have less than a 4-inch (101.6 mm) distance between embedded ends. Where combustible members frame into hollow walls or walls of hollow units, hollow spaces shall be solidly filled for the full thickness of the wall and for a distance not less than 4 inches (101.6 mm) above, below and between the structural members, with noncombustible materials approved for fireblocking. | 706.7 Combustible framing in fire walls. | Adjacent combustible members entering into a concrete or masonry fire wall from opposite sides shall not have less than a 4-inch (102 mm) distance between embedded ends. Where combustible members frame into hollow walls or walls of hollow units, hollow spaces shall be solidly filled for the full thickness of the wall and for a distance not less than 4 inches (102 mm) above, below and between the structural members, with noncombustible materials approved for fireblocking.
706.8 Openings. | Each opening through a fire wall or a party wall shall be protected in accordance with Section 716.5 and shall not exceed 156 square feet (14.5 m²). The aggregate width of openings at any floor level shall not exceed 25 percent of the length of the wall. Exception: Openings shall not be limited to 156 square feet (14.5 m²) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. However, the aggregate width of all openings at any one floor level shall not exceed 25 percent of the length of the wall. | 706.8 Openings. | Each opening through a fire wall shall be protected in accordance with Section 716 and shall not exceed 156 square feet (15 m2). The aggregate width of openings at any floor level shall not exceed 25 percent of the length of the wall. Exceptions: 1. Openings are not permitted in party walls constructed in accordance with Section 706.1.1. 2. Openings shall not be limited to 156 square feet (15 m2) where both buildings are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.
706.9 Penetrations. | Penetrations of fire walls shall comply with Section 714. | 706.9 Penetrations. | Penetrations of fire walls shall comply with Section 714.
706.10 Joints. | Joints made in or between fire walls shall comply with Section 715. | 706.10 Joints. | Joints made in or between fire walls shall comply with Section 715.
706.11 Ducts and air transfer openings. | Ducts and air transfer openings shall not penetrate fire walls. Exception: Penetrations by ducts and air transfer openings of fire walls that are not on a lot line shall be allowed provided the penetrations comply with Section 717. The size and aggregate width of all openings shall not exceed the limitations of Section 706.8. | 706.11 Ducts and air transfer openings. | Ducts and air transfer openings shall not penetrate fire walls. Exception: Penetrations by ducts and air transfer openings of fire walls that are not on a lot line shall be allowed pro-vided that the penetrations comply with Section 717. The size and aggregate width of all openings shall not exceed the limitations of Section 706.8.
707.1 General. | Fire barriers installed as required elsewhere in this code or the New York City Fire Code, shall comply with this section. | 707.1 General. | Fire barriers installed as required elsewhere in this code or the International Fire Code shall comply with this section.
707.2 Materials. | Fire barriers shall be of materials permitted by the building type of construction. | 707.2 Materials. | Fire barriers shall be of materials permitted by the building type of construction.
707.3 Fire-resistance rating. | The fire-resistance rating of fire barriers shall comply with this section. | 707.3 Fire-resistance rating. | The fire-resistance rating of fire barriers shall comply with this section.
707.3.1 Shaft enclosures. | The fire-resistance rating of the fire barrier separating building areas from a shaft shall comply with Section 713.4. | 707.3.1 Shaft enclosures. | The fire-resistance rating of the fire barrier separating building areas from a shaft shall comply with Section 713.4.
707.3.2 Interior exit stairway and ramp construction. | The fire-resistance rating of the fire barrier separating building areas from an interior exit stairway or ramp shall comply with Section 1023.1. | 707.3.2 Interior exit stairway and ramp construction. | The fire-resistance rating of the fire barrier separating building areas from an interior exit stairway or ramp shall comply with Section 1023.1.
707.3.3 Enclosures for exit access stairways. | The fire-resistance rating of the fire barrier separating building areas from an exit access stairway or ramp shall comply with Section 713.4. | 707.3.3 Enclosures for exit access stairways. | The fire-resistance rating of the fire barrier separating building areas from an exit access stairway or ramp shall comply with Section 713.4.
707.3.4 Exit passageway. | The fire-resistance rating of the fire barrier separating building areas from an exit passageway shall comply with Section 1024.3. | 707.3.4 Exit passageway. | The fire-resistance rating of the fire barrier separating building areas from an exit passageway shall comply with Section 1024.3.
707.3.5 Horizontal exit. | The fire-resistance rating of the separation between building areas connected by a horizontal exit shall comply with Section 1026.1. | 707.3.5 Horizontal exit. | The fire-resistance rating of the separation between building areas connected by a horizontal exit shall comply with Section 1026.1.
707.3.6 Atriums. | The fire-resistance rating of the fire barrier separating atriums shall comply with Section 404.6. | 707.3.6 Atriums. | The fire-resistance rating of the fire barrier separating atriums shall comply with Section 404.6.
707.3.7 Incidental uses. | The fire barrier separating incidental uses from other spaces in the building shall have a fire-resistance rating of not less than that indicated in Table 509. | 707.3.7 Incidental uses. | The fire barrier separating incidental uses from other spaces in the building shall have a fire-resistance rating of not less than that indicated in Table 509.1. |  | See BC07 Tables&Figures
707.3.8 Control areas. | Fire barriers separating control areas shall have a fire-resistance rating of not less than that required in Section 414.2.4. | 707.3.8 Control areas. | Fire barriers separating control areas shall have a fire-resistance rating of not less than that required in Section 414.2.4.
707.3.9 Separated occupancies. | Where the provisions of Section 508.4 are applicable, the fire barrier separating mixed occupancies shall have a fire-resistance rating of not less than that indicated in Table 508.4 based on the occupancies being separated. | 707.3.9 Separated occupancies. | Where the provisions of Section 508.4 are applicable, the fire barrier separating mixed occupancies shall have a fire-resistance rating of not less than that indicated in Table 508.4 based on the occupancies being separated. |  | See BC05 Tables&Figures
707.3.10 Fire areas. | The fire barriers or horizontal assemblies, or both, separating a single occupancy into different fire areas shall have a fire-resistance rating of not less than that indicated in Table 707.3.10. The fire barriers or horizontal assemblies, or both, separating fire areas of mixed occupancies shall have a fire-resistance rating of not less than the highest value indicated in Table 707.3.10 for the occupancies under consideration. Exception: For fire-resistance ratings of public corridors, see Section 707.3.11. | 707.3.10 Fire areas. | The fire barriers, fire walls, horizontal assemblies or combinations thereof separating a single occupancy into different fire areas shall have a fire-resistance rating of not less than that indicated in Table 707.3.10. The fire barriers, fire walls, horizontal assemblies or combinations thereof separating fire areas of mixed occupancies shall have a fire-resistance rating of not less than the highest value indicated in Table 707.3.10 for the occupancies under consideration. |  | See BC07 Tables&Figures
707.4 Exterior walls. | Where exterior walls serve as a part of a required fire-resistance-rated shaft, stairway or ramp enclosure, or separation, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure or separation requirements shall not apply. Exception: Exterior walls required to be fire-resistance-rated in accordance with Section 1021 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps. | 707.4 Exterior walls. | Where exterior walls serve as a part of a required fire-resistance-rated shaft, or separation or enclosure for a stairway, ramp or exit passageway, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure or separation requirements shall not apply. Exceptions: 1. Exterior walls required to be fire-resistance rated in accordance with Section 1021 for exterior egress balco-nies, Section 1023.7 for interior exit stairways and ramps, Section 1024.8 for exit passageways and Section 1027.6 for exterior exit stairways and ramps. 2. Exterior walls required to be fire-resistance rated in accordance with Section 1207 of the International Fire Code for enclosure of energy storage systems.
707.5 Continuity. | Fire barriers shall extend from the top of the floor/ceiling assembly below to the underside of the floor or roof sheathing, slab or deck above and shall be securely attached thereto. Such fire barriers shall be continuous through concealed spaces, such as the space above a suspended ceiling. Joints and voids at intersections shall comply with Sections 707.8 and 707.9. Exceptions: 1. Shaft enclosures shall be permitted to terminate at a top enclosure complying with Section 713.12. 2. Interior exit stairway and ramp enclosures required by Section 1023 and exit access stairway and ramp enclosures required by Section 1019 shall be permitted to terminate at a top enclosure complying with Section 713.12. | 707.5 Continuity. | Fire barriers shall extend from the top of the foundation or floor/ceiling assembly below to the underside of the floor or roof sheathing, slab or deck above and shall be securely attached thereto. Such fire barriers shall be continuous through concealed space, such as the space above a suspended ceiling. Joints and voids at intersections shall comply with Sections 707.8 and 707.9 Exceptions: 1. Shaft enclosures shall be permitted to terminate at a top enclosure complying with Section 713.12. 2. Interior exit stairway and ramp enclosures required by Section 1023 and exit access stairway and ramp enclo-sures required by Section 1019 shall be permitted to terminate at a top enclosure complying with Section 713.12. 3. An exit passageway enclosure required by Section 1024.3 that does not extend to the underside of the roof sheathing, slab or deck above shall be enclosed at the top with construction of the same fire-resistance rating as required for the exit passageway. 707.5.1 Supporting construction. The supporting construction for a fire barrier shall be protected to afford the re-qui
707.5.1 Supporting construction. | The supporting construction for a fire barrier shall be protected to afford the required fire-resistance rating of the fire barrier supported. Hollow vertical spaces within a fire barrier shall be fireblocked in accordance with Section 718.2 at every floor level. Exceptions: 1. The maximum required fire-resistance rating for assemblies supporting fire barriers separating tank storage as provided for in Section 415.9.1.2 shall be 2 hours, but not less than required by Table 601 for the building construction type. 2. Supporting construction for 1-hour fire barriers required by Table 509 in buildings of Type IIB, IIIB and VB construction is not required to be fire-resistance-rated unless required by other sections of this code. | 707.5.1 Supporting construction. | The supporting construction for a fire barrier shall be protected to afford the required fire-resistance rating of the fire barrier supported. Hollow vertical spaces within a fire barrier shall be fireblocked in accordance with Section 718.2 at every floor level. Exceptions: 1. The maximum required fire-resistance rating for assemblies supporting fire barriers separating tank stor-age as provided for in Section 415.9.1.2 shall be 2 hours, but not less than required by Table 601 for the building construction type. 2. Supporting construction for 1-hour fire barriers required by Table 509.1 in buildings of Types IIB, IIIB and VB construction is not required to be fire-resistance rated unless required by other sections of this code. |  | See BC05 Tables&Figures
707.6 Openings. | Openings in a fire barrier shall be protected in accordance with Section 716. Openings shall be limited to a maximum aggregate width of 25 percent of the length of the wall, and the maximum area of any single opening shall not exceed 156 square feet (14.5 m2). Openings in enclosures for exit access stairways and ramps, interior exit stairways and ramps and exit passageways shall also comply with Sections 1019, 1023.4 and 1024.5, respectively. Exceptions: 1. Openings shall not be limited to 156 square feet (14.5 m²) where adjoining floor areas are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Openings shall not be limited to 156 square feet (14.5 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door serving enclosures for exit access stairways and ramps, and/or interior exit stairways and ramps. 3. Openings shall not be limited to 156 square feet (14.5 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective has been tested in accordance with ASTM E 119 or UL 263 and has a minimum fire-resistance rating not less than the fire-resistance rating of the wall. 4. Fire window assemblies permitted in atrium separation walls shall not be limited to a maximum aggregate width of 25 percent of the length of the wall. 5. Openings shall not be limited to 156 square feet (14.5 m²) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door assembly in a fire barrier separating an enclosure for exit access stairways and ramps, and/or interior exit stairways and ramps from an exit passageway in accordance with Section 1023.3.1. 6. Openings permitted in atrium enclosures shall comply with the provisions of Section 404.5. | 707.6 Openings. | Openings in a fire barrier shall be protected in accordance with Section 716. Openings shall be limited to a maximum aggregate width of 25 percent of the length of the wall, and the maximum area of any single opening shall not exceed 156 square feet (15 m2). Openings in enclosures for exit access stairways and ramps, interior exit stairways and ramps and exit passageways shall also comply with Sections 1019, 1023.4 and 1024.5, respectively. Exceptions: 1. Openings shall not be limited to 156 square feet (15 m2) where adjoining floor areas are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Openings shall not be limited to 156 square feet (15 m2) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door serving enclosures for exit access stairways and ramps, and interior exit stairways and ramps. 3. Openings shall not be limited to 156 square feet (15 m2) or an aggregate width of 25 percent of the length of the wall where the opening protective has been tested in accordance with ASTM E119 or UL 263 and has a minimum fire-resistance rating not less than the fire-resistance rating of the wall. 4. Fire window assemblies permitted in atrium separation walls shall not be limited to a maximum aggregate width of 25 percent of the length of the wall. 5. Openings shall not be limited to 156 square feet (15 m2) or an aggregate width of 25 percent of the length of the wall where the opening protective is a fire door assembly in a fire barrier separating an enclosure for exit access stairways and ramps, and interior exit stairways and ramps from an exit passageway in accordance with Section 1023.3.1.
707.7 Penetrations. | Penetrations of fire barriers shall comply with Section 714. | 707.7 Penetrations. | Penetrations of fire barriers shall comply with Section 714.
707.7.1 Prohibited penetrations. | Penetrations into enclosures for exit access stairways and ramps, interior exit stairways and ramps, and exit passageways shall be allowed only where permitted by Sections 1019, 1023.5 and 1024.6, respectively. | 707.7.1 Prohibited penetrations. | Penetrations into enclosures for exit access stairways and ramps, interior exit stairways and ramps, and exit passageways shall be allowed only where permitted by Sections 1019, 1023.5 and 1024.6, respectively.
707.8 Joints. | Joints made in or between fire barriers, and joints made at the intersection of fire barriers with underside of a fire-resistance-rated floor or roof sheathing, slab or deck above, and the exterior vertical wall intersection shall comply with Section 715. | 707.8 Joints. | Joints made in or between fire barriers, and joints made at the intersection of fire barriers with underside of a fire-resistance-rated floor or roof sheathing, slab or deck above, and the exterior vertical wall intersection shall comply with Section 715.
707.9 Voids at intersections. | The voids created at the intersection of a fire barrier and a nonfire-resistance-rated roof assembly or a nonfire-resistance-rated exterior wall assembly shall be filled. An approved material or system, or a material consistent with the construction requirements of the fire barrier, shall be used to fill the void, and shall be securely installed in or on the intersection for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to retard the passage of fire and hot gases. | 707.9 Voids at intersections. | The voids created at the intersection of a fire barrier and a nonfire-resistance-rated roof assembly or a nonfire-resistance-rated exterior wall assembly shall be filled. An approved material or system shall be used to fill the void, and shall be securely installed in or on the intersection for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to retard the passage of fire and hot gases.
707.10 Ducts and air transfer openings. | Penetrations in a fire barrier by ducts and air transfer openings shall comply with Section 717. | 707.10 Ducts and air transfer openings. | Penetrations in a fire barrier by ducts and air transfer openings shall comply with Section 717.
708.1 General. | The following wall assemblies shall comply with this section. | 708.1 General. | The following wall assemblies shall comply with this section:
708.2 Materials. | The walls shall be of materials permitted by the building type of construction. | 708.2 Materials. | The walls shall be of materials permitted by the building type of construction.
708.3 Fire-resistance rating. | Fire partitions shall have a fire-resistance rating of not less than 1 hour. Exception: Interior corridor walls as permitted by Table 1020.1. | 708.3 Fire-resistance rating. | Fire partitions shall have a fire-resistance rating of not less than 1 hour. Exceptions: 1. Corridor walls permitted to have a 1/2-hour fire-resistance rating by Table 1020.2. 2. Dwelling unit and sleeping unit separations in buildings of Types IIB, IIIB and VB construction shall have fire-resistance ratings of not less than 1/2 hour in buildings equipped throughout with an automatic sprinkler sys-tem in accordance with Section 903.3.1.1. |  | See BC10 Tables&Figures
708.4 Continuity. | Fire partitions shall extend from the top of the foundation or floor/ceiling assembly below to the underside of the floor or roof sheathing, slab or deck above or to the fire-resistance-rated floor/ceiling or roof/ceiling assembly above, and shall be securely attached thereto. If the fire partitions are not continuous to the sheathing, deck or slab, the space between the ceiling and the sheathing, deck or slab above shall be fire blocked or draft stopped in accordance with Sections 718.2 and 718.3 at the partition line. The supporting construction shall be protected to afford the required fire-resistance rating of the wall supported. Exceptions: 1. The fire partitions separating tenant spaces in a covered or open mall building, complying with Section 402.4.2.1, are not required to extend beyond the underside of a ceiling that is not part of a fire-resistance-rated assembly. A wall is not required in attic or ceiling spaces above tenant separation walls. However, fireblocking or draftstopping shall be provided in accordance with Section 718. 2. Attic fireblocking or draftstopping is not required at the partition line in Group R-2 buildings that do not exceed four stories above grade plane, provided the attic space is subdivided by draftstopping into areas not exceeding 3,000 square feet (278.8 m2) or above every two dwelling units, whichever is smaller. 3. Fireblocking or draftstopping is not required at the partition line in buildings equipped with an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1 or 903.3.1.2, provided that automatic sprinklers are installed in combustible floor/ceiling and roof/ceiling spaces. | 708.4 Continuity. | Fire partitions shall extend from the top of the foundation or floor/ceiling assembly below and be securely attached to one of the following: 1. The underside of the floor or roof sheathing, deck or slab above. 2. The underside of a floor/ceiling or roof/ceiling assembly having a fire-resistance rating that is not less than the fire-resistance rating of the fire partition. Exceptions: 1. Fire partitions shall not be required to extend into a crawl space below where the floor above the crawl space has a minimum 1-hour fire-resistance rating. 2. Fire partitions serving as a corridor wall shall not be required to extend above the lower membrane of a corri-dor ceiling provided that the corridor ceiling membrane is equivalent to corridor wall membrane, and either of the following conditions is met: 2.1. The room-side membrane of the corridor wall extends to the underside of the floor or roof sheathing, deck or slab of a fire-resistance-rated floor or roof above. 2.2. The building is equipped with an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1 or 903.3.1.2, including automatic sprinklers installed in the space between the top of the fire partition and underside of the floor or roof sheathing, deck or slab above. 3. Fire partitions serving as a corridor wall shall be permitted to terminate at the upper membrane of the corri-dor ceiling assembly where the corridor ceiling is constructed as required for the corridor wall. 4. Fire partitions separating tenant spaces in a covered or open mall building complying with Section 402.4.2.1 shall not be required to extend above the underside of a ceiling. Such ceiling shall not be required to be part of a fire-resistance-rated assembly, and the attic or space above the ceiling at tenant separation walls shall not be required to be subdivided by fire partitions.
|  | 708.4.1 Supporting construction. | The supporting construction for a fire partition shall have a fire-resistance rating that is equal to or greater than the required fire-resistance rating of the supported fire partition. Exception: In buildings of Types IIB, IIIB and VB construction, the supporting construction requirement shall not apply to fire partitions separating tenant spaces in covered and open mall buildings, fire partitions separating dwelling units, fire partitions separating sleeping units, fire partitions serving as corridor walls, fire partitions separating ambulatory care facilities from adjacent spaces or corridors, fire partitions separating dwelling and sleeping units from Group R-1 and R-2 occupancies and fire partitions separating vestibules from the level of exit discharge.
|  | 708.4.2 Fireblocks and draftstops in combustible construction. | In combustible construction where fire partitions do not extend to the underside of the floor or roof sheathing, deck or slab above, the space above and along the line of the fire partition shall be provided with one of the following: 1. Fireblocking up to the underside of the floor or roof sheathing, deck or slab above using materials complying with Section 718.2.1. 2. Draftstopping up to the underside of the floor or roof sheathing, deck or slab above using materials complying with Section 718.3.1 for floors or Section 718.4.1 for attics. Exceptions: 1. Buildings equipped with an automatic sprinkler system installed throughout in accordance with Section 903.3.1.1, or in accordance with Section 903.3.1.2 provided that protection is provided in the space be-tween the top of the fire partition and underside of the floor or roof sheathing, deck or slab above as re-quired for systems complying with Section 903.3.1.1. 2. Where corridor walls provide a sleeping unit or dwelling unit separation, draftstopping shall only be re-quired above one of the corridor walls. 3. In Group R-2 occupancies with fewer than four dwelling units, fireblocking and draftstopping shall not be required. 4. In Group R-2 occupancies up to and including four stories in height in buildings not exceeding 60 feet (18 288 mm) in height above grade plane, the attic space shall be subdivided by draftstops into areas not ex-ceeding 3,000 square feet (279 m2) or above every two dwelling units, whichever is smaller. 5. In Group R-3 occupancies with fewer than three dwelling units, fireblocking and draftstopping shall not be required in floor assemblies.
708.5 Exterior walls. | Where exterior walls serve as a part of a required fire-resistance-rated separation, such walls shall comply with the requirements of Section 705 for exterior walls, and the fire-resistance-rated separation requirements shall not apply. Exception: Exterior walls required to be fire-resistance-rated in accordance with Section 1021.2 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps. | 708.5 Exterior walls. | Where exterior walls serve as a part of a required fire-resistance-rated separation, such walls shall comply with the requirements of Section 705 for exterior walls, and the fire-resistance-rated separation requirements shall not apply. Exception: Exterior walls required to be fire-resistance rated in accordance with Section 1021.2 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps.
708.6 Openings. | Openings in a fire partition shall be protected in accordance with Section 716. | 708.6 Openings. | Openings in a fire partition shall be protected in accordance with Section 716.
708.7 Penetrations. | Penetrations through fire partitions shall comply with Section 714. | 708.7 Penetrations. | Penetrations of fire partitions shall comply with Section 714.
708.8 Joints. | Joints made in or between fire partitions shall comply with Section 715. | 708.8 Joints. | Joints made in or between fire partitions shall comply with Section 715.
708.9 Ducts and air transfer openings. | Penetrations in a fire partition by ducts and air transfer openings shall comply with Section 717. | 708.9 Ducts and air transfer openings. | Penetrations in a fire partition by ducts and air transfer openings shall comply with Section 717.
709.1 General. | Vertical and horizontal smoke barriers shall comply with this section. | 709.1 General. | Vertical and horizontal smoke barriers shall comply with this section.
709.2 Materials. | Smoke barriers shall be of materials permitted by the building type of construction. | 709.2 Materials. | Smoke barriers shall be of materials permitted by the building type of construction.
709.3 Fire-resistance rating. | A 1-hour fire-resistance rating is required for smoke barriers. Exception: Smoke barriers constructed of minimum 0.10-inch (2.5 mm) thick steel in Group I-3 buildings. | 709.3 Fire-resistance rating. | A 1-hour fire-resistance rating is required for smoke barriers. Exception: Smoke barriers constructed of minimum 0.10-inch-thick (2.5 mm) steel in Group I-3 buildings.
709.4 Continuity. | Smoke barriers shall form an effective membrane continuous from the top of the foundation or floor/ceiling assembly below to the underside of the floor or roof sheathing, deck or slab above, including continuity through concealed spaces, such as those found above sus­pended ceilings, and interstitial structural and mechanical spaces. The supporting construction shall be protected to afford the required fire-resistance rating of the wall or floor supported in buildings of other than Type IIB, IIIB or VB construction. Smoke barrier walls used to separate smoke compartments shall comply with Section 709.4.1. Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4 or to enclose elevator lobbies in accordance with Section 405.4.3, 3007.6.2, or 3008.7.2 shall also comply with Section 709.4.2. Exception: Smoke barrier walls are not required in intersti¬tial spaces where such spaces are designed and constructed with ceilings or exterior walls that provide resistance to the passage of fire and smoke equivalent to that provided by the smoke barrier walls. | 709.4 Continuity. | Smoke barriers shall form an effective membrane continuous from the top of the foundation or floor/ceiling assembly below to the underside of the floor or roof sheathing, deck or slab above, including continuity through concealed spaces, such as those found above suspended ceilings, and interstitial structural and mechanical spaces. The supporting construction shall be protected to afford the required fire-resistance rating of the wall or floor supported in buildings of other than Type IIB, IIIB or VB construction. Smoke-barrier walls used to separate smoke compartments shall comply with Section 709.4.1. Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4 or to enclose elevator lobbies in accordance with Section 405.4.3, 3007.6.2, or 3008.6.2 shall comply with Section 709.4.2. Exception: Smoke-barrier walls are not required in interstitial spaces where such spaces are designed and construct-ed with ceilings or exterior walls that provide resistance to the passage of fire and smoke equivalent to that provided by the smoke-barrier walls.
|  | 709.4.1 Smoke-barrier assemblies separating smoke compartments. | Smoke-barrier assemblies used to separate smoke compartments shall form an effective membrane enclosure that is continuous from an outside wall or smoke barrier wall to an outside wall or another smoke barrier wall and to the horizontal assemblies.
709.4.2 Smoke-barrier walls enclosing areas of refuge or elevator lobbies. | Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4, or to enclose elevator lobbies in accordance with Sections 405.4.3, 3007.6.2, or 3008.7.2, shall form an effective membrane enclosure that terminates at a fire barrier wall, provided such fire barrier wall has a level of fire protection rating not less than 1 hour, or that terminates at another smoke barrier wall or an outside wall. A smoke and draft control door assembly as specified in Section 716.5.3.1 shall not be required at each elevator hoistway door opening or at each exit doorway between an area of refuge and the enclosure of interior exit stairways or ramps or exit passageways. | 709.4.2 Smoke-barrier walls enclosing areas of refuge or elevator lobbies. | Smoke-barrier walls used to enclose areas of refuge in accordance with Section 1009.6.4, or to enclose elevator lobbies in accordance with Section 405.4.3, 3007.6.2, or 3008.6.2, shall form an effective membrane enclosure that terminates at a fire barrier wall having a level of fire protection rating not less than 1 hour, another smoke barrier wall or an outside wall. A smoke and draft control door assembly as specified in Section 716.2.2.1.1 shall not be required at each elevator hoistway door opening or at each exit doorway between an area of refuge and the exit enclosure.
709.5 Openings. | Openings in a smoke barrier shall be protected in accordance with Section 716. Exceptions: 1. In Group I-1, Group I-2 and Group B ambulatory care facilities, where a pair of opposite-swinging doors are installed across a corridor in accordance with Section 709.5.1, the doors shall not be required to be protected in accordance with Section 716. The doors shall be close fitting within operational tolerances, and shall not have a center mullion or undercuts in excess of ¾-inch (19.1 mm), louvers or grilles. The doors shall have head and jamb stops, and astragals or rabbets at meeting edges. Where permitted by the door manufacturer’s listing, positive-latching devices are not required. 2. In Group I-1, Group I-2 and Group B and ambulatory care facilities, horizontal sliding doors installed in accordance with Section 1010.1.4.3 and protected in accordance with Section 716. | 709.5 Openings. | Openings in a smoke barrier shall be protected in accordance with Section 716. Exceptions: 1. In Group I-1, Condition 2, Group I-2 and ambulatory care facilities, where a pair of opposite-swinging doors are installed across a corridor in accordance with Section 709.5.1, the doors shall not be required to be pro-tected in accordance with Section 716. The doors shall be close fitting within operational tolerances, and shall not have a center mullion or undercuts in excess of 3/4 inch (19.1 mm), louvers or grilles. The doors shall have head and jamb stops, and astragals or rabbets at meeting edges. Where permitted by the door manufacturer’s listing, positive-latching devices are not required. Factory-applied or field-applied protective plates are not re-quired to be labeled. 2. In Group I-1, Condition 2, Group I-2 and ambulatory care facilities, special purpose horizontal sliding, accor-dion or folding doors installed in accordance with Section 1010.3.3 and protected in accordance with Section 716.
709.5.1 Group I-2 and ambulatory care facilities. | In Group I-2 and Group B ambulatory care facilities, where doors are installed across a corridor, the doors shall be automatic-closing by smoke detection in accordance with Section 716.5.9.3 and shall have a vision panel with fire-protection-rated glazing materials in fire-protection-rated frames, the area of which shall not exceed that tested. | 709.5.1 Group I-2 and ambulatory care facilities. | In Group I-2 and ambulatory care facilities, where doors protecting openings in smoke barriers are installed across a corridor and have hold-open devices, the doors shall be automatic-closing in accordance with Section 716.2.6.6. Such doors shall have a vision panel with fire-protection-rated glazing materials in fire-protection-rated frames, the area of which shall not exceed that tested.
709.6 Penetrations. | Penetrations through smoke barriers shall comply with Section 714. | 709.6 Penetrations. | Penetrations of smoke barriers shall comply with Section 714.
709.7 Joints. | Joints made in or between smoke barriers shall comply with Section 715. | 709.7 Joints. | Joints made in or between smoke barriers shall comply with Section 715.
|  | 709.8 Ducts and air transfer openings. | Penetrations in a smoke barrier by ducts and air transfer openings shall comply with Section 717.
710.1 General. | Smoke partitions installed as required elsewhere in the code shall comply with this section. | 710.1 General. | Smoke partitions installed as required elsewhere in the code shall comply with this section.
710.2 Materials. | Smoke partitions shall be constructed of noncombustible materials. Glazing may be used provided it is heat-strengthened or tempered glazing complying and shall otherwise comply with Chapter 24, and shall be protected by sprinkler heads installed in a maximum of 6 feet (1828.8 mm) on center on each side of the smoke partition. | 710.2 Materials. | The walls shall be of materials permitted by the building type of construction.
710.3 Fire-resistance rating. | Unless required elsewhere in the code, smoke partitions are not required to have a fire-resistance rating. | 710.3 Fire-resistance rating. | Unless required elsewhere in the code, smoke partitions are not required to have a fire-resistance rating.
710.4 Continuity. | Smoke partitions shall extend from the top of the foundation or floor below to the underside of the floor or roof sheathing, deck or slab above or to the under­side of the ceiling above where the ceiling membrane is con­structed to limit the transfer of smoke. | 710.4 Continuity. | Smoke partitions shall extend from the top of the foundation or floor below to the underside of the floor or roof sheathing, deck or slab above or to the underside of the ceiling above where the ceiling membrane is constructed to limit the transfer of smoke.
710.5 Openings. | Openings in smoke partitions shall comply with Sections 710.5.1 and 710.5.2. | 710.5 Openings. | Openings in smoke partitions shall comply with Sections 710.5.1 through 710.5.3.
710.5.1 Windows. | Windows in smoke partitions shall be sealed to resist the free passage of smoke or be automatic-closing upon detection of smoke. | 710.5.1 Windows. | Windows in smoke partitions shall be sealed to resist the free passage of smoke or be automatic-closing upon detection of smoke.
710.5.2 Doors. | Doors in smoke partitions shall comply with Sections 710.5.2.1 through 710.5.2.3. | 710.5.2 Doors. | Doors in smoke partitions shall comply with Sections 710.5.2.1 through 710.5.2.3.
710.5.2.1 Louvers. | Doors in smoke partitions shall not include louvers. | 710.5.2.1 Louvers. | Doors in smoke partitions shall not include louvers. Exception: Where permitted in accordance with Section 407.3.1.1.
|  | 710.5.2.2 Smoke and draft control doors. | Where required elsewhere in the code, doors in smoke partitions shall meet the requirements for a smoke and draft control door assembly tested in accordance with UL 1784. The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature test and the elevated temperature exposure test. Installation of smoke doors shall be in accordance with NFPA 105.
710.5.2.2.1 Smoke and draft control door labeling. | Smoke and draft control doors complying only with UL 1784 shall be permitted to show the letter “S” on the manufacturer’s labeling. | 710.5.2.2.1 Smoke and draft control door labeling. | Smoke and draft control doors complying only with UL 1784 shall be permitted to show the letter “S” on the manufacturer’s labeling.
|  | 710.5.2.3 Self- or automatic-closing doors. | Where required elsewhere in the code, doors in smoke partitions shall be self- or automatic-closing by smoke detection in accordance with Section 716.2.6.6.
|  | 710.5.3 Pass-through openings in Group I-2, Condition 2. | Where pass-through openings are provided in smoke partitions in Group I-2, Condition 2 occupancies, such openings shall comply with the following:
710.6 Penetrations. | The space around penetrating items shall be filled with an approved material to limit the free passage of smoke. | 710.6 Penetrations. | The space around penetrating items shall be filled with an approved material to limit the free passage of smoke.
710.7 Joints. | Joints shall be filled with an approved material to limit the free passage of smoke. | 710.7 Joints. | Joints shall be filled with an approved material to limit the free passage of smoke.
710.8 Ducts and air transfer openings. | The space around a duct penetrating a smoke partition shall be filled with an approved material to limit the free passage of smoke. Air transfer openings in smoke partitions shall be provided with a smoke damper complying with Section 717.3.2.2. Exception: Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized. | 710.8 Ducts and air transfer openings. | The space around a duct penetrating a smoke partition shall be filled with an approved material to limit the free passage of smoke. Air transfer openings in smoke partitions shall be provided with a smoke damper complying with Section 717.3.2.2. Exception: Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized.
711.1 General. | Horizontal assemblies shall comply with Section 711.2. Nonfire-resistance-rated floor and roof assemblies shall comply with Section 711.3. | 711.1 General. | Horizontal assemblies shall comply with Section 711.2. Nonfire-resistance-rated floor and roof assemblies shall comply with Section 711.3.
711.2 Horizontal assemblies. | Horizontal assemblies shall comply with Sections 711.2.1 through 711.2.6. | 711.2 Horizontal assemblies. | Horizontal assemblies shall comply with Sections 711.2.1 through 711.2.6.
711.2.1 Materials. | Horizontal assemblies shall be of materials permitted by the building type of construction. | 711.2.1 Materials. | Assemblies shall be of materials permitted by the building type of construction.
711.2.2 Continuity. | Assemblies shall be continuous without vertical openings, except as permitted by this section and Section 712. | 711.2.2 Continuity. | Assemblies shall be continuous without vertical openings, except as permitted by this section and Section 712.
711.2.3 Supporting construction. | The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported. Exception: In buildings of Type IIB, IIIB or VB construction, the construction supporting the horizontal assembly is not required to be fire-resistance-rated at the following: 1. Horizontal assemblies at the separations of incidental uses as specified by Table 509 provided the required fire-resistance rating does not exceed 1 hour. 2. Horizontal assemblies at the separations of dwelling units and sleeping units as required by Section 420.3. 3. Horizontal assemblies at smoke barriers constructed in accordance with Section 709. | 711.2.3 Supporting construction. | The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported. Exception: In buildings of Type IIB, IIIB or VB construction, the construction supporting the horizontal assembly is not required to be fire-resistance rated at the following: 1. Horizontal assemblies at the separations of incidental uses as specified by Table 509.1 provided that the required fire-resistance rating does not exceed 1 hour. 2. Horizontal assemblies at the separations of dwelling units and sleeping units as required by Section 420.3. 3. Horizontal assemblies at smoke barriers constructed in accordance with Section 709. |  | See BC05 Tables&Figures
711.2.4 Fire-resistance rating. | The fire-resistance rating of horizontal assemblies shall comply with Sections 711.2.4.1 through 711.2.4.6 but shall be not less than that required by the building type of construction. | 711.2.4 Fire-resistance rating. | The fire-resistance rating of horizontal assemblies shall comply with Sections 711.2.4.1 through 711.2.4.6 but shall be not less than that required by the building type of construction.
711.2.4.1 Separating mixed occupancies. | Where the horizontal assembly separates mixed occupancies, the assembly shall have a fire-resistance rating of not less than that required by Section 508.4 based on the occupancies being separated. | 711.2.4.1 Separating mixed occupancies. | Where the horizontal assembly separates mixed occupancies, the assembly shall have a fire-resistance rating of not less than that required by Section 508.4 based on the occupancies being separated.
711.2.4.2 Separating fire areas. | Where the horizontal assembly separates a single occupancy into different fire areas, the assembly shall have a fire-resistance rating of not less than that required by Section 707.3.10. | 711.2.4.2 Separating fire areas. | Where the horizontal assembly separates a single occupancy into different fire areas, the assembly shall have a fire-resistance rating of not less than that required by Section 707.3.10.
711.2.4.3 Dwelling units and sleeping units. | Horizontal assemblies serving as dwelling or sleeping unit separations in accordance with Section 420.3, located in Group I-1 and R occupancies, shall be not less than 1-hour fire-resistance-rated construction. | 711.2.4.3 Dwelling units and sleeping units. | Horizontal assemblies serving as dwelling or sleeping unit separations in accordance with Section 420.3 shall be not less than 1-hour fire-resistance-rated construction. Exception: Horizontal assemblies separating dwelling units and sleeping units shall be not less than 1/2-hour fire-resistance-rated construction in a building of Types IIB, IIIB and VB construction, where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
711.2.4.4 Separating smoke compartments. | Where the horizontal assembly is required to be a smoke barrier, the assembly shall comply with Section 709. | 711.2.4.4 Separating smoke compartments. | Where the horizontal assembly is required to be a smoke barrier, the assembly shall comply with Section 709.
711.2.4.5 Separating incidental uses. | Where the horizontal assembly separates incidental uses from the remainder of the building, the assembly shall have a fire-resistance rating of not less than that required by Section 509. | 711.2.4.5 Separating incidental uses. | Where the horizontal assembly separates incidental uses from the remainder of the building, the assembly shall have a fire-resistance rating of not less than that required by Section 509.
711.2.4.6 Other separations. | Where a horizontal assembly is required by other sections of this code, the most restrictive fire-resistance rating shall govern. | 711.2.4.6 Other separations. | Where a horizontal assembly is required by other sections of this code, the assembly shall have a fire-resistance rating of not less than that required by that section.
711.2.5 Ceiling panels. | Where the weight of lay-in ceiling panels, used as part of fire-resistance-rated floor/ceiling or roof/ceiling assemblies, is not adequate to resist an upward force of 1 pound per square foot (47.8 Pa), wire or other approved devices shall be installed above the panels to prevent vertical displacement under such upward force. | 711.2.5 Ceiling panels. | Where the weight of lay-in ceiling panels, used as part of fire-resistance-rated floor/ceiling or roof/ceiling assemblies, is not adequate to resist an upward force of 1 pound per square foot (48 Pa), wire or other approved devices shall be installed above the panels to prevent vertical displacement under such upward force.
|  | 711.2.6 Unusable space. | In 1-hour fire-resistance-rated floor/ceiling assemblies, the ceiling membrane is not required to be installed over unusable crawl spaces. In 1-hour fire-resistance-rated roof assemblies, the floor membrane is not required to be installed where unusable attic space occurs above.
711.3 Nonfire-resistance-rated floor and roof assemblies. | Nonfire-resistance-rated floor, floor/ceiling, roof and roof/ceiling assemblies shall comply with Sections 711.3.1 and 711.3.2. | 711.3 Nonfire-resistance-rated floor and roof assemblies. | Nonfire-resistance-rated floor, floor/ceiling, roof and roof/ceiling assemblies shall comply with Sections 711.3.1 and 711.3.2.
711.3.1 Materials. | Assemblies shall be of materials permitted by the building type of construction. | 711.3.1 Materials. | Assemblies shall be of materials permitted by the building type of construction.
711.3.2 Continuity. | Assemblies shall be continuous without vertical openings, except as permitted by Section 712. | 711.3.2 Continuity. | Assemblies shall be continuous without vertical openings, except as permitted by Section 712.
712.1 General. | Each vertical opening shall comply in accordance with one of the protection methods in Sections 712.1.1 through 712.1.16. | 712.1 General. | Each vertical opening shall comply in accordance with one of the protection methods in Sections 712.1.1 through 712.1.16.
712.1.1 Shaft enclosures. | Vertical openings contained entirely within a shaft enclosure complying with Section 713 shall be permitted. | 712.1.1 Shaft enclosures. | Vertical openings contained entirely within a shaft enclosure complying with Section 713 shall be permitted.
712.1.2 Individual dwelling unit. | Unconcealed vertical openings totally within an individual residential dwelling unit and connecting four stories or less, where such dwelling unit is fully sprinklered in accordance with Sections 903.3.1.1, 903.3.1.2 or 903.3.1.3, shall be permitted. | 712.1.2 Individual dwelling unit. | Unconcealed vertical openings totally within an individual residential dwelling unit and connecting four stories or less shall be permitted.
712.1.3 Escalator openings. | Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, vertical openings for escalators shall be permitted where protected in accordance with Section 712.1.3.1 or 712.1.3.2. | 712.1.3 Escalator openings. | Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, vertical openings for escalators shall be permitted where protected in accordance with Section 712.1.3.1 or 712.1.3.2.
712.1.3.1 Opening size. | Protection by a draft curtain and closely spaced sprinklers in accordance with NFPA 13, as modified by Appendix Q of this code, shall be permitted where the area of the vertical opening between stories does not exceed twice the horizontal projected area of the escalator or stairway. In other than Groups B and M, this application is limited to openings that do not connect more than four stories. | 712.1.3.1 Opening size. | Protection by a draft curtain and closely spaced sprinklers in accordance with NFPA 13 shall be permitted where the area of the vertical opening between stories does not exceed twice the horizontal projected area of the escalator. In other than Groups B and M, this application is limited to openings that do not connect more than four stories.
712.1.3.2 Automatic shutters. | Protection of the vertical opening by approved shutters at every penetrated floor shall be permitted in accordance with this section. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector installed in accordance with Section 907.3.1 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release there from. | 712.1.3.2 Automatic shutters. | Protection of the vertical opening by approved shutters at every penetrated floor shall be permitted in accordance with this section. The shutters shall be of noncombustible construction and have a fire-resistance rating of not less than 1.5 hours. The shutter shall be so constructed as to close immediately upon the actuation of a smoke detector installed in accordance with Section 907.3.1 and shall completely shut off the well opening. Escalators shall cease operation when the shutter begins to close. The shutter shall operate at a speed of not more than 30 feet per minute (152.4 mm/s) and shall be equipped with a sensitive leading edge to arrest its progress where in contact with any obstacle, and to continue its progress on release therefrom.
712.1.4 Penetrations. | Penetrations, concealed and unconcealed, shall be permitted where protected in accordance with Section 714. | 712.1.4 Penetrations. | Penetrations, concealed and unconcealed, shall be permitted where protected in accordance with Section 714.
712.1.5 Joints. | Joints shall be permitted where complying with Section 712.1.5.1 or 712.1.5.2, as applicable. | 712.1.5 Joints. | Joints shall be permitted where complying with Section 712.1.5.1 or 712.1.5.2, as applicable.
712.1.5.1 Joints in or between horizontal assemblies. | Joints made in or between horizontal assemblies shall comply with Section 715. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be permitted where protected in accordance with Section 715.4. | 712.1.5.1 Joints in or between horizontal assemblies. | Joints made in or between horizontal assemblies shall comply with Section 715. The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be permitted where protected in accordance with Section 715.4.
712.1.5.2 Joints in or between nonfire-resistance-rated floor assemblies. | Joints in or between floor assemblies without a required fire-resistance rating shall be permitted where they comply with one of the following: 1. The joint shall be concealed within the cavity of a wall. 2. The joint shall be located above a ceiling. 3. The joint shall be sealed, treated or covered with an approved material or system to resist the free passage of flame and the products of combustion. Exception: Joints meeting one of the exceptions listed in Section 715.1. | 712.1.5.2 Joints in or between nonfire-resistance-rated floor assemblies. | Joints in or between floor assemblies without a required fire-resistance rating shall be permitted where they comply with one of the following: 1. The joint shall be concealed within the cavity of a wall. 2. The joint shall be located above a ceiling. 3. The joint shall be sealed, treated or covered with an approved material or system to resist the free passage of flame and the products of combustion. Exception: Joints meeting one of the exceptions specified in Section 715.3.
712.1.6 Ducts and air transfer openings. | Penetrations by ducts and air transfer openings shall be protected in accordance with Section 717. Grease ducts shall be protected in accordance with the New York City Mechanical Code. | 712.1.6 Ducts and air transfer openings. | Penetrations by ducts and air transfer openings shall be protected in accordance with Section 717. Grease ducts shall be protected in accordance with the International Mechanical Code.
712.1.7 Atriums. | In other than Group H occupancies, atriums complying with Section 404 shall be permitted. | 712.1.7 Atriums. | Atriums complying with Section 404 that connect two or more stories in Group I-2 or I-3 occupancies or three or more stories in other occupancies shall be permitted. Exceptions: 1. Atriums shall not be permitted within Group H occupancies. 2. Balconies or stories within Groups A-1, A-4 and A-5 and mezzanines that comply with Section 505 shall not be considered a story as it applies to this section
712.1.8 Masonry chimney. | Approved vertical openings for masonry chimneys shall be permitted where the annular space is fireblocked at each floor level in accordance with Section 718.2.5. | 712.1.8 Masonry chimney. | Approved vertical openings for masonry chimneys shall be permitted where the annular space is fireblocked at each floor level in accordance with Section 718.2.5.
712.1.9 Two-story openings. | In other than Groups I-2 and I-3, a vertical opening that is not used as one of the applications listed in this section shall be permitted if the opening complies with all of the items below: | 712.1.9 Two-story openings. | In other than Groups I-2 and I-3, a vertical opening that is not used as one of the applications specified in this section shall be permitted if the opening complies with all of the following items:
712.1.10 Parking garages. | Vertical openings in parking garages for automobile ramps, elevators and duct systems shall comply with Section 712.1.10.1, 712.1.10.2 or 712.1.10.3, as applicable. | 712.1.10 Parking garages. | Vertical openings in parking garages for automobile ramps, elevators and duct systems shall comply with Section 712.1.10.1, 712.1.10.2 or 712.1.10.3, as applicable.
712.1.10.1 Automobile ramps. | Vertical openings for automobile ramps in open and enclosed parking garages shall be permitted where constructed in accordance with Sections 406.5 and 406.6, respectively. | 712.1.10.1 Automobile ramps. | Vertical openings for automobile ramps in parking garages shall be permitted where constructed in accordance with Sections 406.5 and 406.6.
712.1.10.2 Elevators. | Vertical openings for elevator hoistways in open and enclosed parking garages that serve only the parking garage, and complying with Sections 406.5 and 406.6, respectively, shall be permitted. | 712.1.10.2 Elevators. | Vertical openings for elevator hoistways in parking garages that serve only the parking garage, and complying with Sections 406.5 and 406.6, respectively, shall be permitted.
712.1.10.3 Duct systems. | Vertical openings for mechanical exhaust or supply duct systems in open or enclosed parking garages complying with Sections 406.5 and 406.6, respectively, shall be permitted to be unenclosed where such duct system is contained within and serves only the parking garage. | 712.1.10.3 Duct systems. | Vertical openings for mechanical exhaust or supply duct systems in parking garages complying with Sections 406.5 and 406.6, respectively, shall be permitted to be unenclosed where such duct system is contained within and serves only the parking garage.
712.1.11 Mezzanine. | Vertical openings between a mezzanine complying with Section 505 and the floor below shall be permitted. | 712.1.11 Mezzanine. | Vertical openings between a mezzanine complying with Section 505 and the floor below shall be permitted.
712.1.12 Exit access stairways and ramps. | Vertical openings containing exit access stairways or ramps in accordance with Section 1019 shall be permitted. | 712.1.12 Exit access stairways and ramps. | Vertical openings containing exit access stairways or ramps in accordance with Section 1019 shall be permitted.
712.1.13 Openings. | Vertical openings for floor fire doors and access doors shall be permitted where protected by Section 712.1.13.1 or 712.1.13.2. | 712.1.13 Openings. | Vertical openings for floor fire doors and access doors shall be permitted where protected by Section 712.1.13.1 or 712.1.13.2.
712.1.13.1 Horizontal fire door assemblies. | Horizontal fire door assemblies used to protect openings in fire-resistance-rated horizontal assemblies shall be tested in accordance with NFPA 288, and shall achieve a fire-resistance rating not less than the assembly being penetrated. Horizontal fire door assemblies shall be labeled by an approved agency. The label shall be permanently affixed and shall specify the manufacturer, the test standard and the fire-resistance rating. | 712.1.13.1 Horizontal fire door assemblies. | Horizontal fire door assemblies used to protect openings in fire-resistance-rated horizontal assemblies shall be tested in accordance with NFPA 288, and shall achieve a fire-resistance rating not less than the assembly being penetrated. Horizontal fire door assemblies shall be labeled by an approved agency. The label shall be permanently affixed and shall specify the manufacturer, the test standard and the fire-resistance rating.
712.1.13.2 Access doors. | Access doors shall be permitted in ceilings of fire-resistance-rated floor/ceiling and roof/ceiling assemblies, provided such doors are tested in accordance with ASTM E 119 or UL 263 as horizontal assemblies and labeled by an approved agency for such purpose. | 712.1.13.2 Access doors. | Access doors shall be permitted in ceilings of fire-resistance-rated floor/ceiling and roof/ceiling assemblies, provided that such doors are tested in accordance with ASTM E119 or UL 263 as horizontal assemblies and labeled by an approved agency for such purpose.
712.1.14 Group I-3. | In Group I-3 occupancies, vertical openings shall be permitted in accordance with Section 408.5. | 712.1.14 Group I-3. | In Group I-3 occupancies, vertical openings shall be permitted in accordance with Section 408.5.
712.1.15 Skylights. | Skylights and other penetrations through a fire-resistance-rated roof deck or slab are permitted to be unprotected, provided that the structural integrity of the fire-resistance-rated roof assembly is maintained. Unprotected skylights shall not be permitted in roof assemblies required to be fire-resistance-rated in accordance with Section 705.8.6. The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported. | 712.1.15 Skylights. | Skylights and other penetrations through a fire-resistance-rated roof deck or slab are permitted to be unprotected, provided that the structural integrity of the fire-resistance-rated roof assembly is maintained. Unprotected skylights shall not be permitted in roof assemblies required to be fire-resistance rated in accordance with Section 705.8.6. The supporting construction shall be protected to afford the required fire-resistance rating of the horizontal assembly supported.
712.1.16 Openings otherwise permitted. | Vertical openings shall be permitted where allowed by other sections of this code. | 712.1.16 Openings otherwise permitted. | Vertical openings shall be permitted where allowed by other sections of this code.
713.1 General. | The provisions of this section shall apply to shafts required to protect openings and penetrations through floor/ceiling and roof/ceiling assemblies. Interior exit stairways and ramps shall be enclosed in accordance with Section 1023. | 713.1 General. | The provisions of this section shall apply to shafts required to protect openings and penetrations through floor/ceiling and roof/ceiling assemblies. Interior exit stairways and ramps shall be enclosed in accordance with Section 1023.
713.2 Construction. | Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies in accordance with Section 711, or both. | 713.2 Construction. | Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies in accordance with Section 711, or both.
713.3 Materials. | The shaft enclosure shall be of materials permitted by the building type of construction. Exception: Noncombustible materials shall be used for shaft enclosures in Group I-1, R-1 and R-2 buildings irre¬spective of the building type of construction. | 713.3 Materials. | Shaft enclosures shall be of materials permitted by the building type of construction.
713.4 Fire-resistance rating. | Shaft enclosures shall have a fire-resistance rating of not less than 2 hours where penetrating three stories or more, and not less than 1 hour where penetrating fewer than three stories. The number of stories connected by the shaft enclosure shall include any basements or cellars, but not any mezzanines. Shaft enclosures shall have a fire-resistance rating not less than the floor assem­bly penetrated, but need not exceed 2 hours. Shaft enclosures shall meet the requirements of Section 703.2.1. | 713.4 Fire-resistance rating. | Shaft enclosures shall have a fire-resistance rating of not less than 2 hours where connecting four stories or more, and not less than 1 hour where connecting less than four stories. The number of stories connected by the shaft enclosure shall include any basements but not any mezzanines. Shaft enclosures shall have a fire-resistance rating not less than the floor assembly penetrated, but need not exceed 2 hours. Shaft enclosures shall meet the requirements of Section 703.2.1.1.
713.5 Continuity. | Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Where the roof construction is of combusti­ble materials, shaft enclosure walls shall extend through the roof construction not less than 30 inches (762 mm) above the roof. Where the roof construction is of noncombustible materials, shaft enclosure walls shall extend from the top of the floor/ceil­ing assembly below to the underside of the floor or roof slab or deck above and shall be securely attached thereto. These walls shall be continuous through concealed spaces such as the space above a suspended ceiling. The supporting construction shall be protected to afford the required fire-resistance rating of the element supported. Hollow vertical spaces within the shaft enclosure construction wall shall be firestopped at every floor level. Exception: A shaft enclosure of a refuse or laundry chute shall extend through combustible or noncombustible roof construction not less than 6 feet (1828.9 mm) above the roof. | 713.5 Continuity. | Shaft enclosures shall be constructed as fire barriers in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, and shall have continuity in accordance with Section 707.5 for fire barriers or Section 711.2.2 for horizontal assemblies, as applicable.
713.6 Exterior walls. | Where exterior walls serve as a part of a required shaft enclosure, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure requirements of Section 713.4 shall not apply. Exception: Exterior walls required to be fire-resistance-rated in accordance with Section 1021.2 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps. | 713.6 Exterior walls. | Where exterior walls serve as a part of a required shaft enclosure, such walls shall comply with the requirements of Section 705 for exterior walls and the fire-resistance-rated enclosure requirements shall not apply. Exception: Exterior walls required to be fire-resistance rated in accordance with Section 1021.2 for exterior egress balconies, Section 1023.7 for interior exit stairways and ramps and Section 1027.6 for exterior exit stairways and ramps.
713.7 Openings. | Openings in a shaft enclosure shall be pro­tected in accordance with Section 716 as required for fire barriers. Doors shall be self- or automatic-closing by smoke detection in accordance with Section 716.5.9.3. Automatic-closing by smoke detection is not permitted for doors serving interior exit stairways or ramps. Exception: For no more than one interior exit stairway or ramp in a building, doors serving such enclosure may be automatic-closing by smoke detection provided that all the following conditions are satisfied: 1. The building contains no Group H space and: 1.1. Is not a high-rise building pursuant to Section 403.1 of this code, or for the purposes of prior code buildings, Section 27-232 of the Administrative Code, and is equipped with a fire alarm system; or 1.2. Is equipped with fire alarm systems and automatic sprinkler systems throughout; or 1.3. Is a high-rise office building, as such term is defined in Section 27-232 of the Administrative Code, that is 100 feet (30 480 mm) or more in height, equipped with a fire alarm system and subdivided into compartments pursuant to subdivision c of Section 27-339 of the Administrative Code. 2. Such doors serve no more than three levels within such vertical exit enclosure, which must be consecutive levels. 3. All levels served by such doors are served by not less than one other exit. 4. Such doors are connected to a fire alarm system and installed in accordance with NFPA 80 and Section 716.5.9.3 of this code. 5. The hold-open devices of such doors: 5.1. Are capable of manual release at the fire command center, or if a fire command center is not required, at a fire alarm control panel that is near the main building entrance; and 5.2. Are capable of manual release by pulling the doors to the closed position. | 713.7 Openings. | Openings in a shaft enclosure shall be protected in accordance with Section 716 as required for fire barriers. Doors shall be self- or automatic-closing by smoke detection in accordance with Section 716.2.6.6.
713.7.1 Prohibited openings. | Openings other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures. | 713.7.1 Prohibited openings. | Openings other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures.
713.8 Penetrations. | Penetrations in a shaft enclosure shall be protected in accordance with Section 714 as required for fire barriers. Structural elements, such as beams or joists, where protected in accordance with Section 714 shall be permitted to penetrate a shaft enclosure. | 713.8 Penetrations. | Penetrations in a shaft enclosure shall be protected in accordance with Section 714 as required for fire barriers. Structural elements, such as beams or joists, where protected in accordance with Section 714 shall be permitted to penetrate a shaft enclosure.
713.8.1 Prohibited penetrations. | Penetrations other than those necessary for the purpose of the shaft shall not be per­mitted in shaft enclosures. | 713.8.1 Prohibited penetrations. | Penetrations other than those necessary for the purpose of the shaft shall not be permitted in shaft enclosures. Exception: Membrane penetrations shall be permitted on the outside of shaft enclosures. Such penetrations shall be protected in accordance with Section 714.4.2.
713.9 Joints. | Joints in a shaft enclosure shall comply with Section 715. | 713.9 Joints. | Joints in a shaft enclosure shall comply with Section 715.
713.10 Duct and air transfer openings. | Penetrations of a shaft enclosure by ducts and air transfer openings shall comply with Section 717. | 713.10 Duct and air transfer openings. | Penetrations of a shaft enclosure by ducts and air transfer openings shall comply with Section 717.
713.11 Enclosure at the bottom. | Shafts that do not extend to the bottom of the building or structure shall comply with one of the following: 1. They shall be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure. 2. They shall terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the remainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating and opening protectives shall be not less than the protection required for the shaft enclosure. Exceptions: 1. The fire-resistance-rated room separation is not required, provided there are no openings in or penetrations of the shaft enclosure to the inte¬rior of the building except at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 718.3.1 for draftstopping, or the room shall be provided with an approved automatic sprinkler system. 2. A shaft enclosure containing a waste or linen chute shall not be used for any other purpose and shall discharge into a room protected in accordance with Section 713.13.4. 3. The fire-resistance-rated room separation and the protection at the bottom of the shaft are not required provided there are no combustibles in the shaft and there are no openings or other pen¬etrations through the shaft enclosure to the inte¬rior of the building. | 713.11 Enclosure at the bottom. | Shafts that do not extend to the bottom of the building or structure shall comply with one of the following: 1. Be enclosed at the lowest level with construction of the same fire-resistance rating as the lowest floor through which the shaft passes, but not less than the rating required for the shaft enclosure. 2. Terminate in a room having a use related to the purpose of the shaft. The room shall be separated from the re-mainder of the building by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating and opening protectives shall be not less than the protection required for the shaft enclosure. 3. Be protected by approved fire dampers installed in accordance with their listing at the lowest floor level within the shaft enclosure. Exceptions: 1. The fire-resistance-rated room separation is not required, provided that the only openings in or penetrations of the shaft enclosure to the interior of the building occur at the bottom. The bottom of the shaft shall be closed off around the penetrating items with materials permitted by Section 718.3.1 for draftstopping, or the room shall be provided with an approved automatic sprinkler system. 2. A shaft enclosure containing a waste or linen chute shall not be used for any other purpose and shall discharge in a room protected in accordance with Section 713.13.4. 3. The fire-resistance-rated room separation and the protection at the bottom of the shaft are not required provid-ed that there are no combustibles in the shaft and there are no openings or other penetrations through the shaft enclosure to the interior of the building.
|  | 713.12 Enclosure at top. | The top of shaft enclosures shall comply with one of the following:
|  | 713.12.1 Penthouse mechanical rooms. | A fire/smoke damper shall not be required at the penetration of the rooftop structure where shaft enclosures extend up through the roof assembly into a rooftop structure conforming to Section 1511. Ductwork in the shaft shall be connected directly to HVAC equipment.
|  | 713.13 Waste, recycling and linen chutes and incinerator rooms. | Waste, recycling and linen chutes shall comply with the provisions of NFPA 82, Chapter 6 and shall meet the requirements of Sections 712 and 713.13.1 through 713.13.6. Incinerator rooms shall meet the provisions of Sections 713.13.4 and 713.13.5. Exception: Chutes serving and contained within a single dwelling unit.
|  | 713.13.1 Waste, recycling and linen chute enclosures. | A shaft enclosure containing a recycling, waste or linen chute shall not be used for any other purpose and shall be enclosed in accordance with Section 713.4. A shaft enclosure shall be permitted to contain recycling and waste chutes. Openings into the shaft, from access rooms and discharge rooms, shall be protected in accordance with this section and Section 716. Openings into chutes shall not be located in corridors. Doors into chutes shall be self-closing. Discharge doors shall be self-or automatic-closing upon the actuation of a smoke detector in accordance with Section 716.2.6.6, except that heat-activated closing devices shall be permitted between the shaft and the discharge room.
713.13.2 Materials. | A shaft enclosure containing a waste, recycling, or linen chute shall be constructed of noncombustible materials. | 713.13.2 Materials. | A shaft enclosure containing a waste, recycling, or linen chute shall be constructed of materials as permitted by the building type of construction.
|  | 713.13.3 Chute access rooms. | Access openings for waste, recycling or linen chutes shall be located in rooms or compartments enclosed by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Openings into the access rooms shall be protected by opening protectives having a fire protection rating of not less than 3/4 hour. Doors shall be self- or automatic-closing upon the detection of smoke in accordance with Section 716.2.6.6. The room or compartment shall be configured to allow the access door to the room or compartment to close and latch with the access panel to the chute in any position.
713.13.4 Chute discharge room. | Waste or linen chutes shall discharge into an enclosed room separated by not less than 3-hour fire barriers constructed in accordance with Section 707 or by horizontal assemblies constructed in accordance with Section 711, or both. Openings into the discharge room from the remainder of the building shall be protected by opening protectives having a fire protection rating equal to the protection required for the shaft enclosure. Doors shall be self- or automatic-closing upon the detection of smoke in accordance with Section 716.5.9.3. Waste chutes shall not terminate in an incinerator room. Waste and linen rooms that are not provided with chutes need only comply with Table 509. Exception: Opening protectives shall not be required at a waste or linen chute opening to a discharge room. | 713.13.4 Chute discharge room. | Table 509.1Waste, recycling or linen chutes shall discharge into an enclosed room separated by fire barriers with a fire-resistance rating not less than the required fire rating of the shaft enclosure and constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Openings into the discharge room from the remainder of the building shall be protected by opening protectives having a fire protection rating equal to the protection required for the shaft enclosure. Doors shall be self- or automatic-closing upon the detection of smoke in accordance with Section 716.2.6.6. Waste chutes shall not terminate in an incinerator room. Waste and linen rooms that are not provided with chutes need only comply with Table 509.1. |  | See BC05 Tables&Figures
713.13.5 Incinerator room. | Incinerator rooms shall comply with Table 509. | 713.13.5 Incinerator room. | Incinerator rooms shall comply with Table 509.1. |  | See BC05 Tables&Figures
713.13.6 Automatic sprinkler system. | An approved automatic sprinkler system shall be installed in accordance with Section 903.2.11.6. | 713.13.6 Automatic sprinkler system. | An approved automatic sprinkler system shall be installed in accordance with Section 903.2.11.2.
713.14 Elevator, dumbwaiter and other hoistways. | Elevator, dumbwaiter and other hoistway enclosures shall be constructed in accordance with Chapter 30 and this section. | 713.14 Elevator, dumbwaiter and other hoistways. | Elevator, dumbwaiter and other hoistway enclosures shall be constructed in accordance with Sections 712 and 713, and Chapter 30.
714.1 Scope. | The provisions of this section shall govern the materials and methods of construction used to protect through-penetrations and membrane-penetrations of horizontal assemblies and fire-resistance-rated wall assemblies. | 714.1 Scope. | The provisions of this section shall govern the materials and methods of construction used to protect through penetrations and membrane penetrations of horizontal assemblies and fire-resistance-rated wall assemblies.
714.1.1 Ducts and air transfer openings. | Penetrations of fire-resistance-rated walls by ducts that are not protected with dampers shall comply with Sections 714.2 through 714.3.3. Penetrations of horizontal assemblies not protected with a shaft as permitted by Section 717.6, and not required to be protected with fire dampers by other sections of this code, shall comply with Sections 714.4 through 714.5.2. Ducts and air transfer openings that are protected with dampers shall comply with Section 717. | 714.1.1 Ducts and air transfer openings. | Penetrations of fire-resistance-rated walls by ducts that are not protected with dampers shall comply with Sections 714.3 through 714.4.3. Penetrations of horizontal assemblies not protected with a shaft as permitted by Section 717.6, and not required to be protected with fire dampers by other sections of this code, shall comply with Sections 714.5 through 714.6.2. Ducts and air transfer openings that are protected with dampers shall comply with Section 717.
|  | 714.2 Installation. | A listed penetration firestop system shall be installed in accordance with the manufacturer’s installation instructions and the listing criteria.
|  | 714.3 Installation details. | Where sleeves are used, they shall be securely fastened to the assembly penetrated. The space between the item contained in the sleeve and the sleeve itself and any space between the sleeve and the assembly penetrated shall be protected in accordance with this section. Insulation and coverings on or in the penetrating item shall not penetrate the assembly unless the specific material used has been tested as part of the assembly in accordance with this section.
|  | 714.4 Fire-resistance-rated walls. | Penetrations into or through fire walls, fire barriers, smoke barrier walls and fire partitions shall comply with Sections 714.4.1 through 714.4.3. Penetrations in smoke barrier walls shall also comply with Section 714.5.4.
|  | 714.4.1 Through penetrations. | Through penetrations of fire-resistance-rated walls shall comply with Section 714.4.1.1 or 714.4.1.2. Exception: Where the penetrating items are steel, ferrous or copper pipes, tubes or conduits, the annular space be-tween the penetrating item and the fire-resistance-rated wall is permitted to be protected by either of the following measures: 1. In concrete or masonry walls where the penetrating item is a maximum 6-inch (152 mm) nominal diameter and the area of the opening through the wall does not exceed 144 square inches (0.0929 m2), concrete, grout or mortar is permitted where installed the full thickness of the wall or the thickness required to maintain the fire-resistance rating. 2. The material used to fill the annular space shall prevent the passage of flame and hot gases sufficient to ig-nite cotton waste when subjected to ASTM E119 or UL 263 time-temperature fire conditions under a mini-mum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated.
|  | 714.4.1.1 Fire-resistance-rated assemblies. | Through penetrations shall be protected using systems installed as tested in the approved fire-resistance-rated assembly.
714.4.1.2 Through-penetration firestop system. | Through-penetrations shall be protected by an approved through-penetration firestop system installed and tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water. The system shall have both, an F rating (flame) and a T rating (temperature) of not less than 1 hour but not less than the required rating of the floor penetrated. Exceptions: 1. Floor penetrations contained and located within the cavity of a wall do not require a T rating. 2. Floor penetrations by floor drains, tub drains or shower drains contained and located within the concealed space of a horizontal assembly do not require a T rating. 3. Floor penetrations of maximum 4-inch (101.6 mm) nominal diameter penetrating directly into metal-enclosed electrical power switchgear do not require a T rating. | 714.4.1.2 Through-penetration firestop system. | Through penetrations shall be protected by an approved penetration firestop system installed as tested in accordance with ASTM E814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water and shall have an F rating of not less than the required fire-resistance rating of the wall penetrated.
714.4.2 Membrane penetrations. | Penetrations of membranes that are part of a horizontal assembly shall comply with Section 714.4.1.1 or 714.4.1.2. Where floor/ceiling assemblies are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced. Exceptions: 1. Membrane penetrations by steel, ferrous or copper conduits, pipes, tubes or vents, or concrete or masonry items where the annular space is protected either in accordance with Section 714.4.1 or to prevent the free passage of flame and the products of combustion. The aggregate area of the openings through the membrane shall not exceed 100 square inches (64 500 mm2) in any 100 square feet (9.3 m2) of ceiling area in assemblies tested without penetrations. 2. Ceiling membrane penetrations of maximum 2-hour horizontal assemblies by steel electrical boxes that do not exceed 16 square inches (10 323 mm2) in area, provided the aggregate area of such penetrations does not exceed 100 square inches (64 516 mm2) in any 100 square feet (9.3 m2) of ceiling area, and the annular space between the ceiling membrane and the box does not exceed 1/8 inch (3.2 mm). 3. Membrane penetrations by electrical boxes of any size or type that have been listed as part of an opening protective material system for use in horizontal assemblies and are installed in accordance with the instructions included in the listing. 4. Membrane penetrations by listed electrical boxes of any material, provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the ceiling membrane and the box shall not exceed 1/8 inch (3.2 mm) unless listed otherwise. 5. The annular space created by the penetration of a fire sprinkler, provided it is covered by a metal escutcheon plate. 6. Noncombustible items that are cast into concrete building elements and that do not penetrate both top and bottom surfaces of the element, provided such items are installed such that the required fire resistance will not be reduced. 7. The ceiling membrane of 1- and 2-hour fire-resistance-rated horizontal assemblies is permitted to be interrupted with the double wood top plate of a wall assembly that is sheathed with Type X gypsum wallboard, provided that all penetrating items through the double top plates are protected in accordance with Section 714.4.1.1 or 714.4.1.2 and the ceiling membrane is tight to the top plates. | 714.4.2 Membrane penetrations. | Membrane penetrations shall comply with Section 714.4.1. Where walls or partitions are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced. Exceptions: 1. Membrane penetrations of maximum 2-hour fire-resistance-rated walls and partitions by steel electrical boxes that do not exceed 16 square inches (0.0 103 m2) in area, provided that the aggregate area of the openings through the membrane does not exceed 100 square inches (0.0645 m2) in any 100 square feet (9.29 m2) of wall area. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.2 mm). Such boxes on opposite sides of the wall or partition shall be separated by one of the following: 1.1. By a horizontal distance of not less than 24 inches (610 mm) where the wall or partition is con-structed with individual noncommunicating stud cavities. 1.2. By a horizontal distance of not less than the depth of the wall cavity where the wall cavity is filled with cellulose loose-fill, rockwool or slag mineral wool insulation. 1.3. By solid fireblocking in accordance with Section 718.2.1. 1.4. By protecting both outlet boxes with listed putty pads. 1.5. By other listed materials and methods. 2. Membrane penetrations by listed electrical boxes of any material, provided that such boxes have been test-ed for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.2 mm) unless listed otherwise. Such boxes on opposite sides of the wall or partition shall be separated by one of the following: 2.1. By the horizontal distance specified in the listing of the electrical boxes. 2.2. By solid fireblocking in accordance with Section 718.2.1. 2.3. By protecting both boxes with listed putty pads. 2.4. By other listed materials and methods. 3. Membrane penetrations by electrical boxes of any size or type, that have been listed as part of a wall open-ing protective material system for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. 4. Membrane penetrations by boxes other than electrical boxes, provided that such penetrating items and the annular space between the wall membrane and the box, are protected by an approved membrane penetra-tion firestop system installed as tested in accordance with ASTM E814 or UL 1479, with a minimum posi-tive pressure differential of 0.01 inch (2.49 Pa) of water, and shall have an F and T rating of not less than the required fire-resistance rating of the wall penetrated and be installed in accordance with their listing. 5. The annular space created by the penetration of an automatic sprinkler, provided that it is covered by a metal escutcheon plate. 6. Membrane penetrations of maximum 2-hour fire-resistance-rated walls and partitions by steel electrical boxes that exceed 16 square inches (0.0 103 m2) in area, or steel electrical boxes of any size having an ag-gregate area through the membrane exceeding 100 square inches (0.0645 m2) in any 100 square feet (9.29 m2) of wall area, provided that such penetrating items are protected by listed putty pads or other listed ma-terials and methods, and installed in accordance with the listing.
|  | 714.4.3 Dissimilar materials. | Noncombustible penetrating items shall not connect to combustible items beyond the point of firestopping unless it can be demonstrated that the fire-resistance integrity of the wall is maintained.
|  | 714.5 Horizontal assemblies. | Penetrations of a fire-resistance-rated floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly not required to be enclosed in a shaft by Section 712.1 shall be protected in accordance with Sections 714.5.1 through 714.5.4.
|  | 714.5.1 Through penetrations. | Through penetrations of horizontal assemblies shall comply with Section 714.5.1.1 or 714.5.1.2. Exceptions: 1. Penetrations by steel, ferrous or copper conduits, pipes, tubes or vents or concrete or masonry items through a single fire-resistance-rated floor assembly where the annular space is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste when subjected to ASTM E119 or UL 263 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. Penetrating items with a maximum 6-inch (152 mm) nominal diameter shall not be limited to the penetration of a single fire-resistance-rated floor assembly, provided that the ag-gregate area of the openings through the assembly does not exceed 144 square inches (92 900 mm2) in any 100 square feet (9.3 m2) of floor area. 2. Penetrations in a single concrete floor by steel, ferrous or copper conduits, pipes, tubes or vents with a max-imum 6-inch (152 mm) nominal diameter, provided that the concrete, grout or mortar is installed the full thickness of the floor or the thickness required to maintain the fire-resistance rating. The penetrating items shall not be limited to the penetration of a single concrete floor, provided that the area of the opening through each floor does not exceed 144 square inches (92 900 mm2). 3. Penetrations by listed electrical boxes of any material, provided that such boxes have been tested for use in fire-resistance-rated assemblies and installed in accordance with the instructions included in the listing.
|  | 714.5.1.1 Fire-resistance-rated assemblies. | Through penetrations shall be protected using systems installed as tested in the approved fire-resistance-rated assembly.
|  | 714.5.1.2 Through-penetration firestop system. | Through penetrations shall be protected by an approved through-penetration firestop system installed and tested in accordance with ASTM E814 or UL 1479, with a minimum positive pressure differential of 0.01 inch of water (2.49 Pa). The system shall have an F rating/T rating of not less than 1 hour but not less than the required rating of the floor penetrated. Exceptions: 1. Floor penetrations contained and located within the cavity of a wall above the floor or below the floor do not require a T rating. 2. Floor penetrations by floor drains, tub drains or shower drains contained and located within the con-cealed space of a horizontal assembly do not require a T rating. 3. Floor penetrations of maximum 4-inch (102 mm) nominal diameter metal conduit or tubing penetrating directly into metal-enclosed electrical power switchgear do not require a T rating.
|  | 714.5.2 Membrane penetrations. | Penetrations of membranes that are part of a horizontal assembly shall comply with Section 714.5.1.1 or 714.5.1.2. Where floor/ceiling assemblies are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced. Exceptions: 1. Membrane penetrations by steel, ferrous or copper conduits, pipes, tubes or vents, or concrete or masonry items where the annular space is protected either in accordance with Section 714.5.1 or to prevent the free passage of flame and the products of combustion. The aggregate area of the openings through the membrane shall not exceed 100 square inches (64 500 mm2) in any 100 square feet (9.3 m2) of ceiling area in assem-blies tested without penetrations. 2. Ceiling membrane penetrations of maximum 2-hour horizontal assemblies by steel electrical boxes that do not exceed 16 square inches (10 323 mm2) in area, provided that the aggregate area of such penetrations does not exceed 100 square inches (44 500 mm2) in any 100 square feet (9.29 m2) of ceiling area, and the annular space between the ceiling membrane and the box does not exceed 1/8 inch (3.2 mm). 3. Membrane penetrations by electrical boxes of any size or type, that have been listed as part of an opening protective material system for use in horizontal assemblies and are installed in accordance with the instruc-tions included in the listing. 4. Membrane penetrations by listed electrical boxes of any material, provided that such boxes have been test-ed for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the ceiling membrane and the box shall not exceed 1/8 inch (3.2 mm) unless listed otherwise. 5. The annular space created by the penetration of a fire sprinkler, provided that it is covered by a metal es-cutcheon plate. 6. Noncombustible items that are cast into concrete building elements and that do not penetrate both top and bottom surfaces of the element. 7. The ceiling membrane of a maximum 2-hour fire-resistance-rated horizontal assembly is permitted to be in-terrupted with the double wood top plate of a wall assembly that is sheathed with Type X gypsum wall-board, provided that all penetrating items through the double top plates are protected in accordance with Section 714.5.1.1 or 714.5.1.2 and the ceiling membrane is tight to the top plates. 8. Ceiling membrane penetrations by listed luminaires (light fixtures) or by luminaires protected with listed materials, which have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing.
|  | 714.5.3 Dissimilar materials. | Noncombustible penetrating items shall not connect to combustible materials beyond the point of firestopping unless it can be demonstrated that the fire-resistance integrity of the horizontal assembly is maintained.
|  | 714.5.4 Penetrations in smoke barriers. | Penetrations in smoke barriers shall be protected by an approved through-penetration firestop system installed and tested in accordance with the requirements of UL 1479 for air leakage. The L rating of the system measured at 0.30 inch (7.47 Pa) of water in both the ambient temperature and elevated temperature tests shall not exceed either of the following:
|  | 714.6 Nonfire-resistance-rated assemblies. | Penetrations of nonfire-resistance-rated floor or floor/ceiling assemblies or the ceiling membrane of a nonfire-resistance-rated roof/ceiling assembly shall meet the requirements of Section 713 or shall comply with Section 714.6.1 or 714.6.2.
|  | 714.6.1 Noncombustible penetrating items. | Noncombustible penetrating items that connect not more than five stories are permitted, provided that the annular space is filled to resist the free passage of flame and the products of combustion with an approved noncombustible material or with a fill, void or cavity material that is tested and classified for use in through-penetration firestop systems.
|  | 714.6.2 Penetrating items. | Penetrating items that connect not more than two stories are permitted, provided that the annular space is filled with an approved material to resist the free passage of flame and the products of combustion.
715.1 General. | Joints installed in or between fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected by an approved fire-resistant joint system designed to resist the passage of fire for a time period not less than the required fire-resistance rating of the wall, floor or roof in or between which the system is installed. Fire-resistant joint systems shall be tested in accordance with Section 715.3. Exception: Fire-resistant joint systems shall not be required for joints in all of the following locations: 1. Floors within a single dwelling unit. 2. Floors where the joint is protected by a shaft enclosure in accordance with Section 713. 3. Floors within atriums where the space adjacent to the atrium is included in the volume of the atrium for smoke control purposes. 4. Joints between floors within malls and non-rated assemblies. 5. Floors and ramps within open and enclosed parking garages or structures constructed in accordance with Sections 406.5 and 406.6, respectively. 6. Mezzanine floors. 7. Walls that are permitted to have unprotected openings. 8. Roofs where openings are permitted. 9. Control joints not exceeding a maximum width of 0.625 inch (15.9 mm) and tested in accordance with ASTM E 119 or UL 263. | 715.1 General. | The provisions of this section shall govern the materials and methods of construction used to protect joints and voids in or between horizontal and vertical assemblies.
715.2 Installation. | A fire-resistant joint system shall be securely installed in accordance with the listing criteria in or on the joint for its entire length so as not to dislodge, loosen or otherwise impair the joint system’s ability to accommodate expected building movements and to resist the passage of fire and hot gases. | 715.2 Installation. | Systems or materials protecting joints and voids shall be securely installed in accordance with the manufacturer’s installation instructions in or on the joint or void for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to resist the passage of fire and hot gases. Fire-resistant joint systems or systems used to protect voids at exterior curtain walls and fire-resistance-rated floor intersections shall also be installed in accordance with the listing criteria.
|  | 715.3 Fire-resistance-rated assembly intersections. | Joints installed in or between fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected by an approved fire-resistant joint system designed to resist the passage of fire for a time period not less than the required fire-resistance rating of the wall, floor or roof in or between which the system is installed. Exception: Fire-resistant joint systems shall not be required for joints in the following locations: 1. Floors within a single dwelling unit. 2. Floors where the joint is protected by a shaft enclosure in accordance with Section 713. 3. Floors within atriums where the space adjacent to the atrium is included in the volume of the atrium for smoke control purposes. 4. Floors within malls. 5. Floors and ramps within parking garages or structures constructed in accordance with Sections 406.5 and 406.6. 6. Mezzanine floors. 7. Walls that are permitted to have unprotected openings. 8. Roofs where openings are permitted. 9. Control joints not exceeding a maximum width of 0.625 inch (15.9 mm) and tested in accordance with ASTM E119 or UL 263. 10. The intersection of exterior curtain wall assemblies and the roof slab or roof deck.
|  | 715.3.1 Fire test criteria. | Fire-resistant joint systems shall be tested in accordance with the requirements of either ASTM E1966 or UL 2079. Nonsymmetrical wall joint systems shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests. Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the building official, the wall need not be subjected to tests from the opposite side. Exception: For exterior walls with a horizontal fire separation distance greater than 10 feet (3048 mm), the joint system shall be required to be tested for interior fire exposure only.
|  | 715.4 Exterior curtain wall/fire-resistance-rated floor intersections. | Voids created at the intersection of exterior curtain wall assemblies and fire-resistance-rated floor or floor/ceiling assemblies shall be protected with an approved perimeter fire containment system to prevent the interior spread of fire. Such systems shall provide an F rating for a time period not less than the fire-resistance rating of the floor or floor/ceiling assembly.
|  | 715.4.1 Fire test criteria. | Perimeter fire containment systems shall be tested in accordance with the requirements of ASTM E2307. Exception: Voids created at the intersection of the exterior curtain wall assemblies and floor assemblies where the vision glass extends to the finished floor level shall be permitted to be protected with an approved material to pre-vent the interior spread of fire. Such material shall be securely installed and capable of preventing the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E119 time-temperature fire condi-tions under a minimum positive pressure differential of 0.01 inch (0.254 mm) of water column (2.5 Pa) for the time period not less than the fire-resistance rating of the floor assembly.
|  | 715.5 Exterior curtain wall/nonfire-resistance-rated floor assembly intersections. | Voids created at the intersection of exterior curtain wall assemblies and nonfire-resistance-rated floor or floor/ceiling assemblies shall be filled with an approved material or system to retard the interior spread of fire and hot gases between stories.
|  | 715.6 Exterior curtain wall/vertical fire barrier intersections. | Voids created at the intersection of nonfire-resistance-rated exterior curtain wall assemblies and vertical fire barriers shall be filled with an approved material or system to retard the interior spread of fire and hot gases.
|  | 715.7 Curtain wall spandrels. | Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 705.8.5. Where Section 705.8.5 does not require fire-resistance-rated curtain wall spandrels, the requirements of Sections 715.4 and 715.5 shall still apply to the intersection between the curtain wall spandrels and the floor.
|  | 715.8 Joints and voids in smoke barriers. | Fire-resistant joint systems protecting joints in smoke barriers, and perimeter fire containment systems protecting voids at the intersection of a horizontal smoke barrier and an exterior curtain wall, shall be tested in accordance with the requirements of UL 2079 for air leakage. The L rating of the joint system shall not exceed 5 cubic feet per minute per linear foot (0.00775 m3/s m) of joint at 0.30 inch (74.7 Pa) of water for both the ambient temperature and elevated temperature tests.
716.1 General. | Opening protectives required by other sections of this code shall comply with the provisions of this section. | 716.1 General. | Opening protectives required by other sections of this code shall comply with the provisions of this section and shall be installed in accordance with NFPA 80.
|  | 716.1.1 Alternative methods for determining fire protection ratings. | The application of any of the alternative methods specified in this section shall be based on the fire exposure and acceptance criteria specified in NFPA 252, NFPA 257, UL 9, UL 10B or UL 10C. The required fire resistance of an opening protective shall be permitted to be established by any of the following methods or procedures:
|  | 716.1.2 Glazing. | Glazing used in fire door assemblies and fire window assemblies shall comply with this section in addition to the requirements of Sections 716.2 and 716.3, respectively.
|  | 716.1.2.1 Safety glazing. | Fire-protection-rated glazing and fire-resistance-rated glazing installed in fire door assemblies and fire window assemblies shall comply with the safety glazing requirements of Chapter 24 where applicable.
|  | 716.1.2.2 Marking fire-rated glazing assemblies. | Fire-rated glazing assemblies shall be marked in accordance with Tables 716.1(1), 716.1(2) and 716.1(3).
|  | 716.1.2.2.1 Fire-rated glazing identification. | For fire-rated glazing, the label shall bear the identification required in Tables 716.1(1) and 716.1(2). “D” indicates that the glazing is permitted to be used in fire door assemblies and meets the fire protection requirements of NFPA 252, UL 10B or UL 10C. “H” indicates that the glazing meets the hose stream requirements of NFPA 252, UL 10B or UL 10C. “T” indicates that the glazing meets the temperature requirements of Section 716.2.2.3.1. The placeholder “XXX” represents the fire-rating period, in minutes.
|  | 716.1.2.2.2 Fire-protection-rated glazing identification. | For fire-protection-rated glazing, the label shall bear the following identification required in Tables 716.1(1) and 716.1(3): “OH – XXX.” “OH” indicates that the glazing meets both the fire protection and the hose-stream requirements of NFPA 257 or UL 9 and is permitted to be used in fire window openings. The placeholder “XXX” represents the fire-rating period, in minutes.
|  | 716.1.2.2.3 Fire-resistance-rated glazing identification. | For fire-resistance-rated glazing, the label shall bear the identification required in Section 703.4 and Table 716.1(1). |  | See BC07 Tables&Figures
|  | 716.1.2.2.4 Fire-rated glazing that exceeds the code requirements. | Fire-rated glazing assemblies marked as complying with hose stream requirements (H) shall be permitted in applications that do not require compliance with hose stream requirements. Fire-rated glazing assemblies marked as complying with temperature rise requirements (T) shall be permitted in applications that do not require compliance with temperature rise requirements. Fire-rated glazing assemblies marked with ratings (XXX) that exceed the ratings required by this code shall be permitted.
|  | 716.1.2.3 Fire-resistance-rated glazing. | Fire-resistance-rated glazing tested as part of a fire-resistance-rated wall or floor/ceiling assembly in accordance with ASTM E119 or UL 263 and labeled in accordance with Section 703.4 shall not otherwise be required to comply with this section where used as part of a wall or floor/ceiling assembly.
|  | 716.1.2.3.1 Glazing in fire door and fire window assemblies. | Fire-resistance-rated glazing shall be permitted in fire door and fire window assemblies where tested and installed in accordance with their listings and where in compliance with the requirements of this section.
|  | 716.2 Fire door assemblies. | Fire door assemblies required by other sections of this code shall comply with the provisions of this section. Fire door frames with transom lights, sidelights or both shall be permitted in accordance with Section 716.2.5.4.
|  | 716.2.1 Testing requirements. | Approved fire door and fire shutter assemblies shall be constructed of any material or assembly of component materials that conforms to the test requirements of Sections 716.2.1.1 through 716.2.1.4 and the fire protection rating indicated in Table 716.1(2). Exceptions: 1. Labeled protective assemblies that conform to the requirements of this section or UL 10A, UL 14B and UL 14C for tin-clad fire door assemblies. |  | See BC07 Tables&Figures
|  | 716.2.1.1 Side-hinged or pivoted swinging doors. | Fire door assemblies with side-hinged and pivoted swinging doors shall be tested in accordance with NFPA 252 or UL 10C. For tests conducted in accordance with NFPA 252, the fire test shall be conducted using the positive pressure method specified in the standard.
|  | 716.2.1.2 Other types of assemblies. | Fire door assemblies with other types of doors, including swinging elevator doors, horizontal sliding fire doors, rolling steel fire doors, fire shutters, bottom- and side-hinged chute intake doors, and top-hinged chute discharge doors, shall be tested in accordance with NFPA 252 or UL 10B. For tests conducted in accordance with NFPA 252, the neutral pressure plane in the furnace shall be maintained as nearly equal to the atmospheric pressure as possible at the top of the door, as specified in the standard.
|  | 716.2.1.3 Glazing in transoms lights and sidelights in corridors and smoke barriers. | Glazing material in any other part of the door assembly, including transom lights and sidelights, shall be tested in accordance with NFPA 257 or UL 9, including the hose stream test, in accordance with Section 716.3.1.1.
|  | 716.2.1.4 Smoke and draft control. | Fire door assemblies that serve as smoke and draft control assemblies shall be tested in accordance with UL 1784.
|  | 716.2.2 Performance requirements. | Fire door assemblies shall be installed in the assemblies specified in Table 716.1(2) and shall comply with the fire protection rating specified. |  | See BC07 Tables&Figures
|  | 716.2.2.1 Door assemblies in corridors and smoke barriers. | Fire door assemblies required to have a minimum fire protection rating of 20 minutes where located in corridor walls or smoke barrier walls having a fire-resistance rating in accordance with Table 716.1(2) shall be tested in accordance with NFPA 252 or UL 10C without the hose stream test. Exceptions: 1. Viewports that require a hole not larger than 1 inch (25 mm) in diameter through the door, have not less than a 0.25-inch-thick (6.4 mm) glass disc and the holder is of metal that will not melt out where sub-ject to temperatures of 1,700°F (927°C). 2. Corridor door assemblies in occupancies of Group I-2 shall be in accordance with Section 407.3.1. 3. Unprotected openings shall be permitted for corridors in multitheater complexes where each motion picture auditorium has not fewer than one-half of its required exit or exit access doorways opening di-rectly to the exterior or into an exit passageway. 4. Horizontal sliding doors in smoke barriers that comply with Sections 408.6 and 408.8.4 in occupancies in Group I-3. |  | See BC07 Tables&Figures
|  | 716.2.2.1.1 Smoke and draft control. | The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot (0.01524 m3/s × m2) of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature and elevated temperature tests. Louvers shall be prohibited. Terminated stops shall be prohibited on doors required by Section 405.4.3 to comply with Section 716.2.2.1 and prohibited on doors required by Item 3 of Section 3006.3, or Section 3007.6.3 or 3008.6.3 to comply with this section.
|  | 716.2.2.2 Door assemblies in other fire partitions. | Fire door assemblies required to have a minimum fire protection rating of 20 minutes where located in other fire partitions having a fire-resistance rating of 0.5 hour in accordance with Table 716.1(2) shall be tested in accordance with NFPA 252, UL 10B or UL 10C with the hose stream test. |  | See BC07 Tables&Figures
|  | 716.2.2.3 Doors in interior exit stairways and ramps and exit passageways. | Fire door assemblies in interior exit stairways and ramps and exit passageways shall have a maximum transmitted temperature rise of not more than 450°F (250°C) above ambient at the end of 30 minutes of standard fire test exposure. Exception: The maximum transmitted temperature rise is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.
|  | 716.2.2.3.1 Glazing in doors. | Fire-protection-rated glazing in excess of 100 square inches (0.065 m2) is not permitted. Fire-resistance-rated glazing in excess of 100 square inches (0.065 m2) shall be permitted in fire doors. Listed fire-resistance-rated glazing in a fire door shall have a maximum transmitted temperature rise in accordance with Section 716.2.2.3 when the fire door is tested in accordance with NFPA 252, UL 10B or UL 10C.
|  | 716.2.3 Fire doors Fire doors installed within a fire door assembly shall meet the fire rating indicated in Table 716. | 1(2). |  | See BC07 Tables&Figures
|  | 716.2.4 Fire door frames. | Fire door frames installed as part of a fire door assembly shall meet the fire rating indicated in Table 716.1(2). |  | See BC07 Tables&Figures
|  | 716.2.5 Glazing in fire door assemblies. | Fire-rated glazing conforming to the opening protection requirements in Section 716.2.1 shall be permitted in fire door assemblies.
|  | 716.2.5.1 Size limitations. | Fire-resistance-rated glazing shall comply with the size limitations in Section 716.2.5.1.1. Fire-protection-rated glazing shall comply with the size limitations of NFPA 80, and as provided in Section 716.2.5.1.2.
|  | 716.2.5.1.1 Fire-resistance-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. | Fire-resistance-rated glazing tested to ASTM E119 or UL 263 and NFPA 252, UL 10B or UL 10C shall be permitted in fire door assemblies located in fire walls and in fire barriers in accordance with Table 716.1(2) to the maximum size tested and in accordance with their listings. |  | See BC07 Tables&Figures
|  | 716.2.5.1.2 Fire-protection-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. | Fire-protection-rated glazing shall be prohibited in fire walls and fire barriers except as provided in Sections 716.2.5.1.2.1 and 716.2.5.1.2.2.
|  | 716.2.5.1.2.1 Horizontal exits. | Fire-protection-rated glazing shall be permitted as vision panels in self-closing swinging fire door assemblies serving as horizontal exits in fire walls where limited to 100 square inches (0.065 m2).
|  | 716.2.5.1.2.2 Fire barriers. | Fire-protection-rated glazing shall be permitted in fire doors having a 11/2-hour fire protection rating intended for installation in fire barriers, where limited to 100 square inches (0.065 m2).
|  | 716.2.5.2 Elevator, stairway and ramp protectives. | Approved fire-protection-rated glazing used in fire door assemblies in elevator, stairway and ramp enclosures shall be so located as to furnish clear vision of the passageway or approach to the elevator, stairway or ramp.
|  | 716.2.5.3 Glazing in door assemblies in corridors and smoke barriers. | In a 20-minute fire door assembly, the glazing material in the door itself shall have a minimum fire-protection-rated glazing of 20 minutes and shall be exempt from the hose stream test.
|  | 716.2.5.4 Fire door frames with transom lights and sidelights. | Fire-protection-rated glazing shall be permitted in door frames with transom lights, sidelights or both, where a 3/4-hour fire protection rating or less is required and in 2-hour fire-resistance-rated exterior walls in accordance with Table 716.1(2). Fire door frames with transom lights, sidelights or both, installed with fire-resistance-rated glazing tested as an assembly in accordance with ASTM E119 or UL 263 shall be permitted where a fire protection rating exceeding 3/4 hour is required in accordance with Table 716.1(2). |  | See BC07 Tables&Figures
|  | 716.2.5.4.1 Energy storage system separation. | Fire-protection-rated glazing shall not be permitted in fire door frames with transom lights and sidelights in fire barriers required by Section 1207 of the International Fire Code to enclose energy storage systems.
|  | 716.2.6 Fire door hardware and closures. | Fire door hardware and closures shall be installed on fire door assemblies in accordance with the requirements of this section.
|  | 716.2.6.1 Door closing. | Fire doors shall be latching and self- or automatic-closing in accordance with this section. Exceptions: 1. Fire doors located in common walls separating sleeping units in Group R-1 shall be permitted without automatic- or self-closing devices. 2. The elevator car doors and the associated hoistway enclosure doors at the floor level designated for re-call in accordance with Section 3003.2 shall be permitted to remain open during Phase I emergency re-call operation.
|  | 716.2.6.2 Latch required. | Unless otherwise specifically permitted, single side-hinged swinging fire doors and both leaves of pairs of side-hinged swinging fire doors shall be provided with an active latch bolt that will secure the door when it is closed.
|  | 716.2.6.3 Chute intake door latching. | Chute intake doors shall be positive latching, remaining latched and closed in the event of latch spring failure during a fire emergency.
|  | 716.2.6.4 Automatic-closing fire door assemblies. | Automatic-closing fire door assemblies shall be self-closing in accordance with NFPA 80.
|  | 716.2.6.5 Delayed-action closers. | Doors required to be self-closing and not required to be automatic closing shall be permitted to be equipped with delayed-action closers.
|  | 716.2.6.6 Smoke-activated doors. | Automatic-closing doors installed in the following locations shall be permitted to have hold-open devices. Doors shall automatically close by the actuation of smoke detectors installed in accordance with Section 907.3 or by loss of power to the smoke detector or hold-open device. Doors that are automatic-closing by smoke detection shall not have more than a 10-second delay before the door starts to close after the smoke detector is actuated. Automatic-closing doors that protect openings installed in the following locations shall comply with this section:
|  | 716.2.6.7 Doors in pedestrian ways. | Vertical sliding or vertical rolling steel fire doors in openings through which pedestrians travel shall be heat activated or activated by smoke detectors with alarm verification.
|  | 716.2.7 Swinging fire shutters. | Where fire shutters of the swinging type are installed in exterior openings, not less than one row in every three vertical rows shall be arranged to be readily opened from the outside, and shall be identified by distinguishing marks or letters not less than 6 inches (152 mm) high.
|  | 716.2.8 Rolling fire shutters. | Where fire shutters of the rolling type are installed, such shutters shall include approved automatic-closing devices.
|  | 716.2.9 Labeled protective assemblies. | Fire door assemblies shall be labeled by an approved agency. The labels shall comply with NFPA 80, and shall be permanently affixed to the door or frame.
|  | 716.2.9.1 Fire door labeling requirements. | Fire doors shall be labeled showing the name of the manufacturer or other identification readily traceable back to the manufacturer, the name or trademark of the third-party inspection agency, the fire protection rating and, where required for fire doors in interior exit stairways and ramps and exit passageways by Section 716.2.2.3, the maximum transmitted temperature end point. Smoke and draft control doors complying with UL 1784 shall be labeled as such and shall comply with Section 716.2.9.3. Labels shall be approved and permanently affixed. The label shall be applied at the factory or location where fabrication and assembly are performed.
|  | 716.2.9.1.1 Light kits, louvers and components. | Listed light kits and louvers and their required preparations shall be considered as part of the labeled door where such installations are done under the listing program of the third-party agency. Fire doors and fire door assemblies shall be permitted to consist of components, including glazing, vision light kits and hardware that are listed or classified and labeled for such use by different third-party agencies.
|  | 716.2.9.2 Oversized doors. | Oversized fire doors shall bear an oversized fire door label by an approved agency or shall be provided with a certificate of inspection furnished by an approved testing agency. Where a certificate of inspection is furnished by an approved testing agency, the certificate shall state that the door conforms to the requirements of design, materials and construction, but has not been subjected to the fire test.
|  | 716.2.9.3 Smoke and draft control door labeling requirements. | Smoke and draft control doors complying with UL 1784 shall be labeled in accordance with Section 716.2.9.1 and shall show the letter “S” on the fire-rating label of the door. This marking shall indicate that the door and frame assembly are in compliance where listed or labeled gasketing is installed.
|  | 716.2.9.4 Fire door frame labeling requirements. | Fire door frames shall be labeled showing the names of the manufacturer and the third-party inspection agency.
|  | 716.2.9.5 Labeling. | Fire-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard and information required in Table 716.1(1) that shall be issued by an approved agency and shall be permanently identified on the glazing. |  | See BC07 Tables&Figures
|  | 716.2.9.6 Fire door operator labeling requirements. | Fire door operators for horizontal sliding doors shall be labeled and listed for use with the assembly.
|  | 716.2.10 Installation of door assemblies in corridors and smoke barriers. | Installation of smoke doors shall be in accordance with NFPA 105.
|  | 716.3 Fire window assemblies. | Fire window assemblies required by other sections of this code shall comply with the provisions of this section.
|  | 716.3.1 Testing requirements. | Fire window assemblies shall be constructed of any material or assembly of component materials that conforms to the test requirements of Sections 716.3.1.1 and 716.3.1.2 and the fire protection rating indicated in Table 716.1(3). |  | See BC07 Tables&Figures
|  | 716.3.1.1 Testing under positive pressure. | NFPA 257 or UL 9 shall evaluate fire-protection-rated glazing under positive pressure. Within the first 10 minutes of a test, the pressure in the furnace shall be adjusted so not less than two-thirds of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.
|  | 716.3.1.2 Nonsymmetrical glazing systems. | Nonsymmetrical fire-protection-rated glazing systems in fire partitions, fire barriers or in exterior walls with a fire separation distance of 10 feet (3048 mm) or less pursuant to Section 705 shall be tested with both faces exposed to the furnace, and the assigned fire protection rating shall be the shortest duration obtained from the two tests conducted in compliance with NFPA 257 or UL 9.
|  | 716.3.2 Performance requirements. | Fire window assemblies shall be installed in the assemblies and comply with the fire protection rating specified in Table 716.1(3). |  | See BC07 Tables&Figures
|  | 716.3.2.1 Interior fire window assemblies. | Fire-protection-rated glazing used in fire window assemblies located in fire partitions and fire barriers shall be limited to use in assemblies with a maximum fire-resistance rating of 1 hour in accordance with this section.
|  | 716.3.2.1.1 Where 3/4-hour-fire-protection window assemblies permitted. | Fire-protection-rated glazing requiring 45-minute opening protection in accordance with Table 716.1(3) shall be limited to fire partitions designed in accordance with Section 708 and fire barriers utilized in the applications set forth in Sections 707.3.6, 707.3.7 and 707.3.9 where the fire-resistance rating does not exceed 1 hour. Fire-resistance-rated glazing assemblies tested in accordance with ASTM E119 or UL 263 shall not be subject to the limitations of this section. |  | See BC07 Tables&Figures
|  | 716.3.2.1.1.1 Energy storage system separation. | Fire-protection-rated glazing is not permitted for use in fire window assemblies in fire barriers required by Section 1207 of the International Fire Code to enclose energy storage systems.
|  | 716.3.2.1.2 Area limitations. | The total area of the glazing in fire-protection-rated window assemblies shall not exceed 25 percent of the area of a common wall with any room.
|  | 716.3.2.1.3 Where 1/3-hour-fire-protection window assemblies permitted. | Fire-protection-rated glazing shall be permitted in window assemblies tested to NFPA 257 or UL 9 in fire partitions requiring 1/3-hour opening protection in accordance with Table 716.1(3). |  | See BC07 Tables&Figures
717.1 General. | The provisions of this section shall govern the protection of duct penetrations and air transfer openings in assemblies required to be protected and duct penetrations in nonfire-resistance-rated floor assemblies. | 717.1 General. | The provisions of this section shall govern the protection of duct penetrations and air transfer openings in assemblies required to be protected and duct penetrations in nonfire-resistance-rated floor assemblies.
|  | 716.3.3 Fire window frames. | Fire window frames installed with a fire window assembly shall meet the fire-protection rating indicated in Table 716.1(3). |  | See BC07 Tables&Figures
717.1.1 Ducts and air transfer openings. | Ducts transitioning horizontally between shafts shall not require a shaft enclosure provided that the duct penetration into each associated shaft is protected with dampers complying with this section. | 717.1.1 Ducts and air transfer openings. | Ducts transitioning horizontally between shafts shall not require a shaft enclosure provided that the duct penetration into each associated shaft is protected with dampers complying with this section.
|  | 716.3.3.1 Window mullions. | Metal mullions that exceed a nominal height of 12 feet (3658 mm) shall be protected with materials to afford the same fire-resistance rating as required for the wall construction in which the protective is located.
717.1.2 Ducts that penetrate fire-resistance-rated assemblies without dampers. | Ducts that penetrate fire-resistance-rated assemblies and are not required by this section to have dampers shall comply with the requirements of Sections 714.2 through 714.3.3. Ducts that penetrate horizontal assemblies not required to be contained within a shaft and not required by this section to have dampers shall comply with the requirements of Sections 714.4 through 714.5.2. | 717.1.2 Ducts that penetrate fire-resistance-rated assemblies without dampers. | Ducts that penetrate fire-resistance-rated walls and are not required by this section to have fire dampers shall comply with the requirements of Sections 714.3 through 714.4.3. Ducts that penetrate horizontal assemblies not required to be contained within a shaft and not required by this section to have fire dampers shall comply with the requirements of Sections 714.5 through 714.6.2.
|  | 716.3.4 Fire-protection-rated glazing. | Glazing in fire window assemblies shall be fire protection rated in accordance with this section and Table 716.1(3). Fire-protection-rated glazing in fire window assemblies shall be tested in accordance with and shall meet the acceptance criteria of NFPA 257 or UL 9. Openings in nonfire-resistance-rated exterior wall assemblies that require protection in accordance with Section 705.3, 705.8, 705.8.5 or 705.8.6 shall have a fire protection rating of not less than 3/4 hour. Fire-protection-rated glazing in 1/2-hour fire-resistance-rated partitions is permitted to have a 20-minute fire protection rating. |  | See BC07 Tables&Figures
717.1.2.1 Ducts that penetrate nonfire-resistance-rated assemblies. | The space around a duct penetrating a nonfire-resistance-rated floor assembly shall comply with Section 717.6.3. | 717.1.2.1 Ducts that penetrate nonfire-resistance-rated assemblies. | The space around a duct penetrating a nonfire-resistance-rated floor assembly shall comply with Section 717.6.3.
|  | 716.3.4.1 Glass and glazing. | Glazing in fire window assemblies shall be fire-protection-rated glazing installed in accordance with and complying with the size limitations set forth in NFPA 80.
717.2 Installation. | Fire dampers, smoke dampers, combination fire/smoke dampers and ceiling radiation dampers located within air distribution and smoke control systems shall be installed in accordance with the requirements of this section, the New York City Mechanical Code, the manufacturer’s instructions and damper’s listing. | 717.2 Installation. | Fire dampers, smoke dampers, combination fire/smoke dampers and ceiling radiation dampers located within air distribution and smoke control systems shall be installed in accordance with the manufacturer’s instructions, the dampers’ listing and Sections 717.2.1 through 717.2.3.
|  | 716.3.5 Labeled protective assemblies. | Glazing in fire window assemblies shall be labeled by an approved agency. The labels shall comply with NFPA 80 and Section 716.3.5.2.
717.2.1 Smoke control system. | Where the installation of a fire damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized. Where mechanical systems including ducts and dampers utilized for normal building ventilation serve as part of the smoke control system, the expected performance of these systems in smoke control mode shall be addressed in the rational analysis required by Section 909.4. | 717.2.1 Smoke control system. | Where the installation of a fire damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized. Where mechanical systems including ducts and dampers utilized for normal building ventilation serve as part of the smoke control system, the expected performance of these systems in smoke control mode shall be addressed in the rational analysis required by Section 909.4.
|  | 716.3.5.1 Fire window frames. | Fire window frames shall be approved for the intended application.
|  | 716.3.5.2 Labeling requirements. | Fire-protection-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard and information required in Section 716.1.2.2.2 and Table 716.1(3) that shall be issued by an approved agency and permanently identified on the glazing. |  | See BC07 Tables&Figures
717.2.2 Hazardous exhaust ducts. | Fire dampers for hazardous exhaust duct systems shall comply with the New York City Mechanical Code. | 717.2.2 Hazardous exhaust ducts. | Fire dampers for hazardous exhaust duct systems shall comply with the International Mechanical Code.
|  | 716.3.6 Installation. | Fire window assemblies shall be installed in accordance with the provisions of this section.
|  | 716.3.6.1 Closure. | Fire-protection-rated glazing shall be in the fixed position or be automatic-closing and shall be installed in labeled frames.
717.3 Damper testing, ratings and actuation. | Damper testing, ratings and actuation shall be in accordance with Sections 717.3.1 through 717.3.3. | 717.3 Damper testing, ratings and actuation. | Damper testing, ratings and actuation shall be in accordance with Sections 717.3.1 through 717.3.3.
|  | 716.4 Fire protective curtain assembly. | Approved fire protective curtain assemblies shall be constructed of any materials or assembly of component materials tested without hose stream in accordance with UL 10D, and shall comply with the Sections 716.4.1 through 716.4.3
717.3.1 Damper testing. | Dampers shall be listed and labeled in accordance with the standards in this section. | 717.3.1 Damper testing. | Dampers shall be listed and labeled in accordance with the standards in this section.
|  | 716.4.1 Label. | Fire protective curtain assemblies used as opening protectives in fire-rated walls and smoke partitions shall be labeled in accordance with Section 716.2.9.
717.3.2 Damper rating. | Damper ratings shall be in accordance with Sections 717.3.2.1 through 717.3.2.3. | 717.3.2 Damper rating. | Damper ratings shall be in accordance with Sections 717.3.2.1 through 717.3.2.4.
|  | 716.4.2 Smoke and draft control. | Fire protective curtain assemblies used to protect openings where smoke and draft control assemblies are required shall comply with Section 716.2.1.4.
717.3.2.1 Fire damper ratings. | Fire dampers shall have the minimum fire protection rating specified in Table 717.3.2.1 for the type of penetration. | 717.3.2.1 Fire damper ratings. | Fire dampers shall have the minimum rating specified in Table 717.3.2.1. |  | See BC07 Tables&Figures
|  | 716.4.3 Installation. | Fire protective curtain assemblies shall be installed in accordance with NFPA 80.
717.3.2.2 Smoke damper ratings. | Smoke damper leakage ratings shall be Class I or II. Elevated temperature ratings shall be not less than 250°F (121.1°C). | 717.3.2.2 Smoke damper ratings. | Smoke damper leakage ratings shall be Class I or II. Elevated temperature ratings shall be not less than 250°F (121°C).
717.3.2.3 Combination fire/smoke damper ratings. | Combination fire/smoke dampers shall have the minimum fire protection rating specified for fire dampers in Table 717.3.2.1 for the type of penetration and shall have a minimum smoke damper rating as specified in Section 717.3.2.2. | 717.3.2.3 Combination fire/smoke damper ratings. | Combination fire/smoke dampers shall have the minimum rating specified for fire dampers in Table 717.3.2.1 and shall have the minimum rating specified for smoke dampers in Section 717.3.2.2. |  | See BC07 Tables&Figures
717.3.3 Damper actuation. | Damper actuation shall be in accordance with Sections 717.3.3.1 through 717.3.3.4 as applicable. | 717.3.3 Damper actuation. | Damper actuation shall be in accordance with Sections 717.3.3.1 through 717.3.3.5 as applicable.
717.3.3.2 Smoke damper actuation. | The smoke damper shall close upon actuation of a listed smoke detector or detectors installed in accordance with Section 907.3 and one of the following methods, as applicable: 1. Where a smoke damper is installed within a duct, a smoke detector shall be installed inside the duct or outside the duct with sampling tubes protruding into the duct. The detector or tubes within the duct shall be within 5 feet (1524 mm) of the damper. Air outlets and inlets shall not be located between the detector or tubes and the damper. The detector shall be listed for the air velocity, temperature and humidity anticipated at the point where it is installed. Other than in mechanical smoke control systems, dampers shall be closed upon fan shutdown where local smoke detectors require a minimum velocity to operate. Exceptions: 1. Duct smoke detectors will not be required at each fire smoke damper provided the supply fan shall shut down and all the fire smoke dampers associated with the supply system automatically close upon actuation of any automatic alarm initiating device on the floor(s). 2. Duct smoke detectors will be required within 5 feet (1.5 m) downstream of any electric duct reheat coil. 3. Non-ducted return air systems shall have a smoke detector located within 5 feet (1.5 m) upstream of each return air protected opening in a 2-hour fire-rated barrier. 4. Ducted return air systems shall have a duct smoke detector located within 5 feet (1.5 m) of a smoke damper; additional smoke detectors will not be required at fire smoke dampers located downstream where there are no additional return air inlets. 2. Where a smoke damper is installed above smoke barrier doors in a smoke barrier, a spot-type detector shall be installed on either side of the smoke barrier door opening. The detector shall be listed for releasing service if used for direct interface with the damper. 3. Where a smoke damper is installed within an unducted opening in a wall, a spot-type detector shall be installed within 5 feet (1524 mm) horizontally of the damper. The detector shall be listed for releasing service if used for direct interface with the damper. 4. Where a smoke damper is installed in a corridor wall or ceiling, the damper shall be permitted to be controlled by a smoke detection system installed in the corridor. 5. Where a smoke detection system is installed in all areas served by duct in which the damper will be located, the smoke dampers shall be permitted to be controlled by the smoke detection system. 6. Smoke dampers that are part of an engineered smoke control system shall be controlled in accordance with Section 607.3.3.2 of the New York City Mechanical Code. | 717.3.3.2 Smoke damper actuation. | The smoke damper shall close upon actuation of a listed smoke detector or detectors installed in accordance with Section 907.3 and one of the following methods, as applicable:
717.3.3.3 Combination fire/smoke damper actuation. | Combination fire/smoke damper actuation shall be in accordance with Sections 717.3.3.1 and 717.3.3.2. Combination fire/smoke dampers installed in smoke control system shaft penetrations shall not be activated by local area smoke detection unless it is secondary to the smoke management system controls. | 717.3.3.3 Combination fire/smoke damper actuation. | Combination fire/smoke damper actuation shall be in accordance with Sections 717.3.3.1 and 717.3.3.2. Combination fire/smoke dampers installed in smoke control system shaft penetrations shall not be activated by local area smoke detection unless it is secondary to the smoke management system controls.
717.3.3.4 Ceiling radiation damper actuation. | The operating temperature of a ceiling radiation damper actuation device shall be 50°F (10°C) above the normal temperature within the duct system, but not less than 160°F (71.1°C). | 717.3.3.4 Ceiling radiation damper actuation. | The operating temperature of a ceiling radiation damper actuation device shall be 50°F (27.8°C) above the normal temperature within the duct system, but not less than 160°F (71°C).
717.4 Access and identification. | Fire and smoke dampers shall be provided with an approved means of access that is large enough to permit inspection and maintenance of the damper and its operating parts. The access shall not affect the integrity of fire-resistance-rated assemblies. The access openings shall not reduce the fire-resistance rating of the assembly. Access points shall be permanently identified on the exterior by a label having letters not less than 1/2 inch (12.7 mm) in height reading: FIRE/SMOKE DAMPER, SMOKE DAMPER or FIRE DAMPER followed by an identification marking that is individual and unique to the damper accessed. | 717.4 Access and identification. | Access and identification of fire and smoke dampers shall comply with Sections 717.4.1 through 717.4.2.
|  | 717.2.3 Static dampers. | Fire dampers and ceiling radiation dampers that are listed for use in static systems shall only be installed in heating, ventilation and air-conditioning systems that are automatically shut down in the event of a fire.
717.5 Where required. | Fire dampers, smoke dampers, combination fire/smoke dampers, and ceiling radiation dampers shall be provided as specified in Sections 717.5.1 through 717.5.7 and 717.6. Where an assembly is required to have both fire dampers and smoke dampers, combination fire/smoke dampers or a fire damper and a smoke damper shall be provided. Exception: Ducts 20 square inches (12 903.2 mm2) or less passing through fire-resistance-rated assemblies shall not require fire dampers or fire smoke dampers. | 717.5 Where required. | Fire dampers, smoke dampers, combination fire/smoke dampers, ceiling radiation dampers and corridor dampers shall be provided at the locations prescribed in Sections 717.5.1 through 717.5.7 and 717.6. Where an assembly is required to have both fire dampers and smoke dampers, combination fire/smoke dampers or a fire damper and a smoke damper shall be provided.
717.5.1 Fire walls. | Ducts and air transfer openings permitted in fire walls in accordance with Section 706.11 shall be protected with listed fire dampers and smoke dampers installed in accordance with their listing. Exception: Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions. The air-handling system shall be continuously monitored to ensure continuous airflow at a constantly attended location and be inspected and maintained in accordance with the system manufacturer’s instructions. | 717.5.1 Fire walls. | Ducts and air transfer openings permitted in fire walls in accordance with Section 706.11 shall be protected with listed fire dampers installed in accordance with their listing.
717.5.1.1 Horizontal exits. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point that a duct or air transfer opening penetrates a fire wall that serves as a horizontal exit. | 717.5.1.1 Horizontal exits. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a fire wall that serves as a horizontal exit.
717.5.2 Fire barriers. | Ducts and air transfer openings that penetrate fire barriers (horizontal and wall assemblies) shall be protected with listed fire dampers installed in accordance with their listing. Ducts and air transfer openings shall not penetrate enclosures for interior exit stairways and ramps and exit passageways, except as permitted by Sections 1023.5 and 1024.6, respectively. In addition, smoke dampers shall be installed in penetrations of public corridor and horizontal exit walls in accordance with Sections 717.5.2.1 and 717.5.2.2. Exception: Fire dampers are not required at penetrations of fire barriers where any of the following apply: 1. Penetrations are tested in accordance with ASTM E 119 or UL 263 as part of the fire-resistance-rated assembly. 2. Ducts are used as part of an engineered smoke control system in accordance with Sections 717.2.1 and 909 of this code where the use of a fire damper would interfere with the operation of a smoke control system. 3. Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, are in areas of other than Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or Section 903.3.1.2 of this code. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals. | 717.5.2 Fire barriers. | Ducts and air transfer openings of fire barriers shall be protected with listed fire dampers installed in accordance with their listing. Ducts and air transfer openings shall not penetrate enclosures for interior exit stairways and ramps and exit passageways, except as permitted by Sections 1023.5 and 1024.6, respectively. Exceptions: Fire dampers are not required at penetrations of fire barriers where any of the following apply: 1. Penetrations are tested in accordance with ASTM E119 or UL 263 as part of the fire-resistance-rated assembly. 2. Ducts are used as part of an approved smoke control system in accordance with Section 909 and where the use of a fire damper would interfere with the operation of a smoke control system. 3. Such walls are penetrated by fully ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, are in areas of other than Group H and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a fully ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals. Nonmet-al flexible air connectors shall be permitted in the following locations: 3.1. At the duct connection to the air handling unit or equipment located within the mechanical room in ac-cordance with Section 603.9 of the International Mechanical Code. 3.2. From an overhead metal duct to a ceiling diffuser within the same room in accordance with Section 603.6.2 of the International Mechanical Code.
717.5.2.1 Horizontal exits. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a fire barrier that serves as a horizontal exit. | 717.5.2.1 Horizontal exits. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a fire barrier that serves as a horizontal exit.
717.5.3 Shaft enclosures. | Ducts and air transfer openings shall not penetrate a shaft serving as an exit enclosure except as permitted by Section 1023.5. Shaft enclosures that are permitted to be penetrated by ducts and air transfer openings shall be protected with approved fire and smoke dampers installed in accordance with their listing. | 717.5.3 Shaft enclosures. | Shaft enclosures that are permitted to be penetrated by ducts and air transfer openings shall be protected with listed fire and smoke dampers installed in accordance with their listing. Exceptions: 1. Fire dampers are not required at penetrations of shafts where any of the following criteria are met: 1.1. Steel exhaust subducts having a wall thickness of not less than 0.0187 inch (0.4712 mm) are extend-ed not less than 22 inches (559 mm) vertically in exhaust shafts, and an exhaust fan is installed at the upper terminus of the shaft that is powered continuously in accordance with Section 909.11, so as to maintain a continuous upward airflow to the outdoors. 1.2. Penetrations are tested in accordance with ASTM E119 or UL 263 as part of the fire-resistance-rated assembly. 1.3. Ducts are used as part of an approved smoke control system designed and installed in accordance with Section 909 and where the fire damper will interfere with the operation of the smoke control system. 1.4. The penetrations are in parking garage exhaust or supply shafts that are separated from other build-ing shafts by not less than 2-hour fire-resistance-rated construction. 2. In Group B and R occupancies equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, smoke dampers are not required at penetrations of shafts where all of the following crite-ria are met: 2.1. Kitchen, clothes dryer, bathroom and toilet room exhaust openings are installed with steel exhaust subducts, having a wall thickness of not less than 0.0187 inch (0.4712 mm). 2.2. The subducts extend not less than 22 inches (559 mm) vertically. 2.3. An exhaust fan is installed at the upper terminus of the shaft that is powered continuously in ac-cordance with the provisions of Section 909.11, so as to maintain a continuous upward airflow to the outdoors. 3. Smoke dampers are not required at penetration of exhaust or supply shafts in parking garages that are sepa-rated from other building shafts by not less than 2-hour fire-resistance-rated construction. 4. Smoke dampers are not required at penetrations of shafts where ducts are used as part of an approved me-chanical smoke control system designed in accordance with Section 909 and where the smoke damper will interfere with the operation of the smoke control system. 5. Fire dampers and combination fire/smoke dampers are not required in kitchen and clothes dryer exhaust systems where dampers are prohibited by the International Mechanical Code.
|  | 717.3.2.4 Corridor damper ratings. | Corridor dampers shall have the following minimum ratings:
717.5.4 Fire partitions. | Ducts and air transfer openings that penetrate fire partitions shall be protected with listed fire dampers installed in accordance with their listing. Exceptions: In occupancies other than Group H, fire dampers are not required where any of the following apply: 1. The fire partitions are for tenant separation or interior corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and the duct is protected as a through-penetration in accordance with Section 714. 2. The fire partitions are for tenant partitions in covered mall buildings where the walls are not required by provisions elsewhere in the code to extend to the underside of the floor or roof sheathing, slab or deck above. 3. The duct system is constructed of approved materials in accordance with the New York City Mechanical Code and the duct penetrating the wall complies with all of the following requirements: 3.1. The duct shall not exceed 100 square inches (64 516 mm2). 3.2. The duct shall be constructed of steel not less than 0.0217 inch (0.55 mm) in thickness. 3.3. The duct shall not have openings that communicate the corridor with adjacent spaces or rooms. 3.4. The duct shall be installed above a ceiling. 3.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall. 3.6. A minimum 12-inch-long (304.8 mm) by 0.060-inch (1.52 mm) thick steel sleeve shall be centered in each duct opening. The sleeve shall be secured to both sides of the wall and all four sides of the sleeve with minimum 11/2-inch by 11/2-inch by 0.060-inch (38.1 mm by 38.1 mm by 1.52 mm) steel retaining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and the wall opening shall be filled with mineral wool batting or approved equivalent on all sides. 4. Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals. | 717.5.4 Fire partitions. | Ducts and air transfer openings that penetrate fire partitions shall be protected with listed fire dampers installed in accordance with their listing. Exceptions: In occupancies other than Group H, fire dampers are not required where any of the following apply: 1. Corridor walls in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 and the duct is protected as a through penetration in accordance with Sec-tion 714. 2. Tenant partitions in covered and open mall buildings where the walls are not required by provisions else-where in the code to extend to the underside of the floor or roof sheathing, slab or deck above. 3. The duct system is constructed of approved materials in accordance with the International Mechanical Code and the duct penetrating the wall complies with all of the following requirements: 3.1. The duct shall not exceed 100 square inches (0.06 m2). 3.2. The duct shall be constructed of steel not less than 0.0217 inch (0.55 mm) in thickness. 3.3. The duct shall not have openings that communicate the corridor with adjacent spaces or rooms. 3.4. The duct shall be installed above a ceiling. 3.5. The duct shall not terminate at a wall register in the fire-resistance-rated wall. 3.6. A minimum 12-inch-long (305 mm) by 0.060-inch-thick (1.52 mm) steel sleeve shall be centered in each duct opening. The sleeve shall be secured to both sides of the wall and all four sides of the sleeve with minimum 11/2-inch by 11/2-inch by 0.060-inch (38 mm by 38 mm by 1.52 mm) steel re-taining angles. The retaining angles shall be secured to the sleeve and the wall with No. 10 (M5) screws. The annular space between the steel sleeve and the wall opening shall be filled with mineral wool batting on all sides. 4. Such walls are penetrated by ducted HVAC systems, have a required fire-resistance rating of 1 hour or less, and are in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. For the purposes of this exception, a ducted HVAC system shall be a duct system for conveying supply, return or exhaust air as part of the structure’s HVAC system. Such a duct system shall be constructed of sheet steel not less than No. 26 gage thickness and shall be continuous from the air-handling appliance or equipment to the air outlet and inlet terminals.
|  | 717.3.3.1 Fire damper actuation. | Primary heat responsive devices used to actuate fire dampers shall meet one of the following requirements:
717.5.5 Smoke barriers. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a smoke barrier. Smoke dampers and smoke damper actuation methods shall comply with Section 717.3.3.2. Exceptions: 1. Smoke dampers are not required where the openings in ducts are limited to a single smoke compartment and the ducts are constructed of steel. 2. Smoke dampers are not required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions. 3. Smoke dampers are not required in smoke barriers required by Section 407.5 for Group I-2, Condition 2 where the HVAC system is fully ducted in accordance with Section 603 of the New York City Mechanical Code and where buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and equipped with quick-response sprinklers in accordance with Section 903.3.2. | 717.5.5 Smoke barriers. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a smoke barrier. Smoke dampers and smoke damper actuation methods shall comply with Section 717.3.3.2. Exceptions: 1. Smoke dampers are not required where the openings in ducts are limited to a single smoke compartment and the ducts are constructed of steel. 2. Smoke dampers are not required in smoke barriers required by Section 407.5 for Group I-2, Condition 2—where the HVAC system is fully ducted in accordance with Section 603 of the International Mechanical Code and where buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 and equipped with quick-response sprinklers in accordance with Section 903.3.2.
717.5.6 Exterior walls. | Ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings in accordance with Section 705.10 shall be protected with listed fire dampers installed in accordance with their listing. | 717.5.6 Exterior walls. | Ducts and air transfer openings in fire-resistance-rated exterior walls required to have protected openings in accordance with Section 705.10 shall be protected with listed fire dampers installed in accordance with their listing.
717.5.7 Smoke partitions. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point that an air transfer opening penetrates a smoke partition. Smoke dampers and smoke damper actuation methods shall comply with Section 717.3.3.2. Exception: Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized. | 717.5.7 Smoke partitions. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point that an air transfer opening penetrates a smoke partition. Smoke dampers and smoke damper actuation methods shall comply with Section 717.3.3.2. Exception: Where the installation of a smoke damper will interfere with the operation of a required smoke control system in accordance with Section 909, approved alternative protection shall be utilized.
717.6 Horizontal assemblies. | Penetrations by ducts and air transfer openings of a floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly shall be protected by a shaft enclosure that complies with Section 713 or shall comply with Sections 717.6.1 through 717.6.3. | 717.6 Horizontal assemblies. | Penetrations by ducts and air transfer openings of a floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly shall be protected by a shaft enclosure that complies with Section 713 or shall comply with Sections 717.6.1 through 717.6.3.
|  | 717.3.3.5 Corridor damper actuation. | Corridor damper actuation shall be in accordance with Sections 717.3.3.1 and 717.3.3.2.
717.6.2 Membrane penetrations. | Ducts and air transfer openings constructed of approved materials in accordance with the New York City Mechanical Code that penetrate the ceiling membrane of a fire-resistance-rated floor/ceiling assembly or roof/ceiling assembly shall be protected with one of the following: | 717.6.2 Membrane penetrations. | Ducts and air transfer openings constructed of approved materials in accordance with the International Mechanical Code that penetrate the ceiling membrane of a fire-resistance-rated floor/ceiling or roof/ceiling assembly shall be protected with one of the following: 1. A shaft enclosure in accordance with Section 713. 2. A listed ceiling radiation damper installed at the ceiling line where a duct penetrates the ceiling of a fire-resistance-rated floor/ceiling or roof/ceiling assembly. Exceptions: 1. A fire-resistance-rated assembly tested in accordance with ASTM E119 or UL 263 showing that ceil-ing radiation dampers are not required in order to maintain the fire-resistance rating of the assembly. 2. Where exhaust duct or outdoor air duct penetrations protected in accordance with Section 714.5.2 are located within the cavity of a wall and do not pass through another dwelling unit or tenant space. 3. Where duct and air transfer openings are protected with a duct outlet penetration system tested as part of a fire-resistance-rated assembly in accordance with ASTM E119 or UL 263. 3. A listed ceiling radiation damper installed at the ceiling line where a diffuser with no duct attached penetrates the ceiling of a fire-resistance-rated floor/ceiling or roof/ceiling assembly. Exceptions: 1. A fire-resistance-rated assembly tested in accordance with ASTM E119 or UL 263 showing that ceil-ing radiation dampers are not required in order to maintain the fire-resistance rating of the assembly. 2. Where duct and air transfer openings are protected with a duct outlet penetration system tested as part of a fire-resistance-rated assembly in accordance with ASTM E119 or UL 263.
|  | 717.4.1 Access. | Fire and smoke dampers shall be provided with an approved means of access that is large enough to permit inspection and maintenance of the damper and its operating parts. Dampers equipped with fusible links, internal operators, or both shall be provided with an access door that is not less than 12 inches (305 mm) square or provided with a removable duct section.
|  | 717.4.1.1 Access openings. | The access shall not affect the integrity of fire-resistance-rated assemblies. The access openings shall not reduce the fire-resistance rating of the assembly. Access doors in ducts shall be tight fitting and suitable for the required duct construction.
717.6.3 Nonfire-resistance-rated floor assemblies. | Duct systems constructed of approved materials in accordance with the New York City Mechanical Code that penetrate nonfire-resistance-rated floor assemblies shall be protected by any of the following methods: 1. A shaft enclosure in accordance with Section 713. 2. The duct connects not more than two stories, and the annular space around the penetrating duct is protected with a listed noncombustible material that resists the free passage of flame and the products of combustion. 3. In floor assemblies composed of noncombustible materials, a shaft shall not be required where the duct connects not more than three stories, the annular space around the penetrating duct is protected with an approved noncombustible material that resists the free passage of flame and the products of combustion and a fire damper is installed at each floor line. Exception: Fire dampers are not required in ducts within individual residential dwelling units. | 717.6.3 Nonfire-resistance-rated floor assemblies. | Duct systems constructed of approved materials in accordance with the International Mechanical Code that penetrate nonfire-resistance-rated floor assemblies shall be protected by any of the following methods: 1. A shaft enclosure in accordance with Section 713. 2. The duct connects not more than two stories, and the annular space around the penetrating duct is protected with an approved noncombustible material that resists the free passage of flame and the products of combus-tion. 3. In floor assemblies composed of noncombustible materials, a shaft shall not be required where the duct con-nects not more than three stories, the annular space around the penetrating duct is protected with an approved noncombustible material that resists the free passage of flame and the products of combustion and a fire damper is installed at each floor line. Exception: Fire dampers are not required in ducts within individual residential dwelling units.
|  | 717.4.1.2 Restricted access. | Where space constraints or physical barriers restrict access to a damper for periodic inspection and testing, the damper shall be a single- or multi-blade type damper and shall comply with the remote inspection requirements of NFPA 80 or NFPA 105.
717.7 Flexible ducts and air connectors. | Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any wall, floor or ceiling. | 717.7 Flexible ducts and air connectors. | Flexible ducts and air connectors shall not pass through any fire-resistance-rated assembly. Flexible air connectors shall not pass through any wall, floor or ceiling.
|  | 717.4.2 Identification. | Access points shall be permanently identified on the exterior by a label having letters not less than 1/2 inch (12.7 mm) in height reading: FIRE/SMOKE DAMPER, SMOKE DAMPER or FIRE DAMPER.
718.1 General. | Fireblocking and draftstopping shall be installed in combustible and noncombustible concealed locations in accordance with this section. Fireblocking shall comply with Section 718.2. Draftstopping in floor/ceiling spaces and attic spaces shall comply with Sections 718.3 and 718.4, respectively. The permitted use of combustible materials in concealed spaces of buildings of Type I or II construction shall be limited to the applications indicated in Section 718.5. Installations of fireblocking and draftstopping shall comply with the special inspection requirements of Chapter 17. Exception: Concealed spaces that are sprinklered in accordance with Chapter 9 or are constructed as a shaft. | 718.1 General. | Fireblocking and draftstopping shall be installed in combustible concealed locations in accordance with this section. Fireblocking shall comply with Section 718.2. Draftstopping in floor/ceiling spaces and attic spaces shall comply with Sections 718.3 and 718.4, respectively. The permitted use of combustible materials in concealed spaces of buildings of Type I or II construction shall be limited to the applications indicated in Section 718.5.
718.2 Fireblocking. | In combustible and noncombustible construction, fireblocking shall be installed to cut off concealed draft openings (both vertical and horizontal) and shall form an effective barrier between floors, between a top story and a roof or attic space. Fireblocking shall be installed in the locations specified in Sections 718.2.2 through 718.2.7. | 718.2 Fireblocking. | In combustible construction, fireblocking shall be installed to cut off concealed draft openings (both vertical and horizontal) and shall form an effective barrier between floors, between a top story and a roof or attic space. Fireblocking shall be installed in the locations specified in Sections 718.2.2 through 718.2.7.
718.2.1 Fireblocking materials. | Fireblocking shall consist of the following materials: | 718.2.1 Fireblocking materials. | Fireblocking shall consist of the following materials:
718.2.1.1 Batts or blankets of mineral wool or mineral fiber. | Batts or blankets of mineral or glass fiber or other listed nonrigid materials shall be permitted for compliance with the 10-foot (3048 mm) horizontal fireblocking in walls constructed using parallel rows of studs or staggered studs. | 718.2.1.1 Batts or blankets of mineral wool or mineral fiber. | Batts or blankets of mineral wool or mineral fiber or other approved nonrigid materials shall be permitted for compliance with the 10-foot (3048 mm) horizontal fireblocking in walls constructed using parallel rows of studs or staggered studs.
718.2.1.2 Unfaced fiberglass. | Unfaced fiberglass batt insulation used as fireblocking shall fill the entire cross section of the wall cavity to a minimum height of 16 inches (406.4 mm) measured vertically. Where piping, conduit or similar obstructions are encountered, the insulation shall be packed tightly around the obstruction. | 718.2.1.2 Unfaced fiberglass. | Unfaced fiberglass batt insulation used as fireblocking shall fill the entire cross section of the wall cavity to a minimum height of 16 inches (406 mm) measured vertically. Where piping, conduit or similar obstructions are encountered, the insulation shall be packed tightly around the obstruction.
718.2.1.3 Loose-fill insulation material. | Loose-fill insulation material, insulating foam sealants and caulk materials shall not be used as a fireblock unless specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and to retard the spread of fire and hot gases. | 718.2.1.3 Loose-fill insulation material. | Loose-fill insulation material, insulating foam sealants and caulk materials shall not be used as a fireblock unless specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and to retard the spread of fire and hot gases.
718.2.1.4 Fireblocking integrity. | The integrity of fireblocks shall be maintained. | 718.2.1.4 Fireblocking integrity. | The integrity of fireblocks shall be maintained.
|  | 717.5.3.1 Continuous upward airflow. | Fire dampers and smoke dampers shall not be installed in shafts that are required to maintain a continuous upward airflow path where closure of the damper would result in the loss of the airflow.
718.2.1.5 Double stud walls. | Batts or blankets of mineral or glass fiber or other approved nonrigid materials shall be allowed as fireblocking in walls constructed using parallel rows of studs or staggered studs. | 718.2.1.5 Double stud walls. | Batts or blankets of mineral or glass fiber or other approved nonrigid materials shall be allowed as fireblocking in walls constructed using parallel rows of studs or staggered studs.
718.2.2 Concealed wall spaces. | Fireblocking shall be provided in concealed spaces of stud walls and partitions, including furred spaces, and parallel rows of studs or staggered studs, as follows: | 718.2.2 Concealed wall spaces. | Fireblocking shall be provided in concealed spaces of stud walls and partitions, including furred spaces, and parallel rows of studs or staggered studs, as follows:
|  | 717.5.4.1 Corridors. | Duct and air transfer openings that penetrate corridors shall be protected with dampers as follows: 1. A corridor damper shall be provided where corridor ceilings, constructed as required for the corridor walls as permitted in Section 708.4, Exception 3, are penetrated. 2. A ceiling radiation damper shall be provided where the ceiling membrane of a fire-resistance-rated floor-ceiling or roof-ceiling assembly, constructed as permitted in Section 708.4, Exception 2, is penetrated. 3. A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a corridor enclosure required to have smoke and draft control doors in accord-ance with Section 716.2.2.1. Exceptions: 1. Smoke dampers are not required where the building is equipped throughout with an approved smoke control system in accordance with Section 909, and smoke dampers are not necessary for the operation and control of the system. 2. Smoke dampers are not required in corridor penetrations where the duct is constructed of steel not less than 0.019 inch (0.48 mm) in thickness and there are no openings serving the corridor.
718.2.3 Connections between horizontal and vertical spaces. | Fireblocking shall be provided at interconnections between concealed vertical stud wall or partition spaces and concealed horizontal spaces created by an assembly of floor joists or trusses, and between concealed vertical and horizontal spaces such as occur at soffits, drop ceilings, cove ceilings and similar locations. | 718.2.3 Connections between horizontal and vertical spaces. | Fireblocking shall be provided at interconnections between concealed vertical stud wall or partition spaces and concealed horizontal spaces created by an assembly of floor joists or trusses, and between concealed vertical and horizontal spaces such as occur at soffits, drop ceilings, cove ceilings and similar locations.
718.2.4 Stairways. | Fireblocking shall be provided in concealed spaces between stair stringers at the top and bottom of the run. Enclosed spaces under stairways shall also comply with Section 1011.7.3. | 718.2.4 Stairways. | Fireblocking shall be provided in concealed spaces between stair stringers at the top and bottom of the run. Enclosed spaces under stairways shall comply with Section 1011.7.3.
718.2.5 Ceiling and floor openings. | Where required by Section 712.1.8, Exception 1 of Section 714.4.2 or Section 714.5, fireblocking of the annular space around vents, pipes, ducts, chimneys and fireplaces at ceilings and floor levels shall be installed with a material specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and resist the free passage of flame and the products of combustion. | 718.2.5 Ceiling and floor openings. | Where required by Section 712.1.8, Exception 1 of Section 714.5.1.2 or Section 714.6, fireblocking of the annular space around vents, pipes, ducts, chimneys and fireplaces at ceilings and floor levels shall be installed with a material specifically tested in the form and manner intended for use to demonstrate its ability to remain in place and resist the free passage of flame and the products of combustion.
718.2.5.1 Factory-built chimneys and fireplaces. | Factory-built chimneys and fireplaces shall be fireblocked in accordance with UL 103 and UL 127. | 718.2.5.1 Factory-built chimneys and fireplaces. | Factory-built chimneys and fireplaces shall be fireblocked in accordance with UL 103 and UL 127.
|  | 717.6.1 Through penetrations. | In occupancies other than Groups I-2 and I-3, a duct constructed of approved materials in accordance with the International Mechanical Code that penetrates a fire-resistance-rated floor/ceiling assembly that connects not more than two stories is permitted without shaft enclosure protection, provided that a listed fire damper is installed at the floor line or the duct is protected in accordance with Section 714.5. For air transfer openings, see Section 712.1.9. Exception: A duct is permitted to penetrate three floors or less without a fire damper at each floor, provided that such duct meets all of the following requirements: 1. The duct shall be contained and located within the cavity of a wall and shall be constructed of steel having a minimum wall thickness of 0.0187 inches (0.4712 mm) (No. 26 gage). 2. The duct shall open into only one dwelling unit or sleeping unit and the duct system shall be continuous from the unit to the exterior of the building. 3. The duct shall not exceed 4-inch (102 mm) nominal diameter and the total area of such ducts shall not ex-ceed 100 square inches (0.065 m2) in any 100 square feet (9.3 m2) of floor area. 4. The annular space around the duct is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E119 or UL 263 time-temperature condi-tions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. 5. Grille openings located in a ceiling of a fire-resistance-rated floor/ceiling or roof/ceiling assembly shall be protected with a listed ceiling radiation damper installed in accordance with Section 717.6.2.1.
|  | 717.6.2.1 Ceiling radiation dampers testing and installation. | Ceiling radiation dampers shall be tested in accordance with Section 717.3.1. Ceiling radiation dampers shall be installed in accordance with the details specified in the fire-resistance-rated assembly and the manufacturer’s instructions and the listing.
|  | 717.6.2.1.1 Dynamic systems. | Only ceiling radiation dampers labeled for use in dynamic systems shall be installed in heating, ventilation and air-conditioning systems designed to operate with fans on during a fire.
718.2.7 Concealed sleeper spaces. | Where wood sleepers are used for laying wood flooring on masonry or concrete fire-resistance-rated floors, the space between the floor slab and the underside of the wood flooring shall be filled with an approved material to resist the free passage of flame and products of combustion or fireblocked in such a manner that there will be no open spaces under the flooring that will exceed 20 square feet (1.86 m2) in area and such space shall be filled solidly under permanent partitions so that there is no communication under the flooring between adjoining rooms. Exceptions: 1. Fireblocking is not required for slab-on-grade floors in gymnasiums. 2. Fireblocking is required only at the juncture of each alternate lane and at the ends of each lane in a bowling facility. | 718.2.7 Concealed sleeper spaces. | Where wood sleepers are used for laying wood flooring on masonry or concrete fire-resistance-rated floors, the space between the floor slab and the underside of the wood flooring shall be filled with an approved material to resist the free passage of flame and products of combustion or fireblocked in such a manner that open spaces under the flooring shall not exceed 100 square feet (9.3 m2) in area and such space shall be filled solidly under permanent partitions so that communication under the flooring between adjoining rooms shall not occur. Exceptions: 1. Fireblocking is not required for slab-on-grade floors in gymnasiums. 2. Fireblocking is required only at the juncture of each alternate lane and at the ends of each lane in a bowl-ing facility.
|  | 717.6.2.1.2 Static systems. | Static ceiling radiation dampers shall be provided with systems that are not designed to operate during a fire. Exceptions: 1. Where a static ceiling radiation damper is installed at the opening of a duct, a smoke detector shall be installed inside the duct or outside the duct with sampling tubes protruding into the duct. The detector or tubes in the duct shall be within 5 feet (1524 mm) of the damper. Air outlets and inlets shall not be located between the detector or tubes and the damper. The detector shall be listed for the air velocity, temperature and humidity anticipated at the point where it is installed. Other than in mechanical smoke control systems, dampers shall be closed upon fan shutdown where local smoke detectors re-quire a minimum velocity to operate. 2. Where a static ceiling radiation damper is installed in a ceiling, the ceiling radiation damper shall be permitted to be controlled by a smoke detection system installed in the same room or area as the ceil-ing radiation damper. 3. A static ceiling radiation damper shall be permitted to be installed in a room where an occupant sensor is provided within the room that will shut down the system.
718.3 Draftstopping in floors. | In combustible and noncombustible construction, draftstopping shall be installed to subdivide floor/ceiling assemblies in the locations prescribed in Sections 718.3.2 through 718.3.3. | 718.3 Draftstopping in floors. | Draftstopping shall be installed to subdivide floor/ceiling assemblies where required by Section 708.4.2. In other than Group R occupancies, draftstopping shall be installed to subdivide combustible floor/ceiling assemblies so that horizontal floor areas do not exceed 1,000 square feet (93 m2). Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
718.3.1 Draftstopping materials. | In noncombustible con­struction, draftstopping shall be of noncombustible materials. In combustible construction, draftstopping materials shall be not less than 1/2-inch (12.7 mm) gypsum board, 3/8-inch (9.5 mm) wood structural panel, 3/8-inch (9.5 mm) particleboard, 1-inch (25 mm) nominal lumber, cement fiberboard, batts or blankets of mineral wool or glass fiber, or other approved materials adequately supported. The integrity of draftstops shall be maintained. | 718.3.1 Draftstopping materials. | Draftstopping materials shall be not less than 1/2-inch (12.7 mm) gypsum board, 3/8-inch (9.5 mm) wood structural panel, 3/8-inch (9.5 mm) particleboard, 1-inch (25-mm) nominal lumber, cement fiberboard, batts or blankets of mineral wool or glass fiber, or other approved materials adequately supported. The integrity of draftstops shall be maintained.
718.4 Draftstopping in attics. | In combustible and noncombustible construction, draftstopping shall be installed to subdivide attic spaces and concealed roof spaces in the loca­tions prescribed in Sections 718.4.2 and 718.4.3. Ventilation of concealed roof spaces shall be maintained in accordance with Section 1203.2. | 718.4 Draftstopping in attics. | Draftstopping shall be installed to subdivide attic spaces where required by Section 708.4.2. In other than Group R, draftstopping shall be installed to subdivide combustible attic spaces and combustible concealed roof spaces such that any horizontal area does not exceed 3,000 square feet (279 m2). Ventilation of concealed roof spaces shall be maintained in accordance with Section 1202.2.1. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
718.4.1 Draftstopping materials. | Materials utilized for draftstopping of attic spaces shall comply with Section 718.3.1. | 718.4.1 Draftstopping materials. | Materials utilized for draftstopping of attic spaces shall comply with Section 718.3.1.
718.4.1.1 Openings. | Openings in draftstop partitions provided in accordance with Section 1209.2 shall be pro­tected by self-closing doors with automatic latches con­structed as required for the partitions. | 718.4.1.1 Openings. | Openings in the partitions shall be protected by self-closing doors with automatic latches constructed as required for the partitions.
718.5 Combustible materials in concealed spaces in Type I or II construction. | Combustible materials shall not be permitted in concealed spaces of buildings of Type I or II construction. Exceptions: 1. Combustible materials in accordance with Section 603 of this code. 2. Combustible materials exposed within plenums complying with Section 602 of the New York City Mechanical Code. 3. Class A interior finish materials classified in accordance with Section 803 of this code. 4. Combustible piping within partitions or shaft enclosures installed in accordance with the provisions of this code. 5. Combustible piping within concealed ceiling spaces installed in accordance with the New York City Mechanical Code and the New York City Plumbing Code. 6. Combustible insulation and covering on pipe and tubing, installed in concealed spaces other than plenums, complying with Section 720.7 of this code. | 718.5 Combustible materials in concealed spaces in Type I or II construction. | Combustible materials shall not be permitted in concealed spaces of buildings of Type I or II construction. Exceptions: 1. Combustible materials in accordance with Section 603. 2. Combustible materials exposed within plenums complying with Section 602 of the International Mechanical Code. 3. Class A interior finish materials classified in accordance with Section 803. 4. Combustible piping within partitions or shaft enclosures installed in accordance with the provisions of this code. 5. Combustible piping within concealed ceiling spaces installed in accordance with the International Mechanical Code and the International Plumbing Code. 6. Combustible insulation and covering on pipe and tubing, installed in concealed spaces other than plenums, complying with Section 720.7.
719.1 Thickness of plaster. | The minimum thickness of gypsum plaster or portland cement plaster used in a fire-resistance-rated system shall be determined by the prescribed fire tests. The plaster thickness shall be measured from the face of the lath where applied to gypsum lath or metal lath. | 719.1 Thickness of plaster. | The minimum thickness of gypsum plaster or Portland cement plaster used in a fire-resistance-rated system shall be determined by the prescribed fire tests. The plaster thickness shall be measured from the face of the lath where applied to gypsum lath or metal lath.
719.2 Plaster equivalents. | For fire-resistance purposes, 1/2 inch (12.7 mm) of unsanded gypsum plaster shall be deemed equivalent to 3/4 inch (19.1 mm) of one-to-three gypsum sand plaster or 1 inch (25.4 mm) of portland cement sand plaster. | 719.2 Plaster equivalents. | For fire-resistance purposes, 1/2 inch (12.7 mm) of unsanded gypsum plaster shall be deemed equivalent to 3/4 inch (19.1 mm) of one-to-three gypsum sand plaster or 1 inch (25 mm) of Portland cement sand plaster.
719.3 Noncombustible furring. | In buildings of Type I and II construction, plaster shall be applied directly on concrete or masonry or on approved noncombustible plastering base and furring. | 719.3 Noncombustible furring. | In buildings of Types I and II construction, plaster shall be applied directly on concrete or masonry or on approved noncombustible plastering base and furring.
719.4 Double reinforcement. | Plaster protection more than 1 inch (25.4 mm) in thickness shall be reinforced with an additional layer of approved lath embedded not less than 3/4 inch (19.1 mm) from the outer surface and fixed securely in place. Exception: Solid plaster partitions or where otherwise determined by fire tests. | 719.4 Double reinforcement. | Plaster protection more than 1 inch (25 mm) in thickness shall be reinforced with an additional layer of approved lath embedded not less than 3/4 inch (19.1 mm) from the outer surface and fixed securely in place. Exception: Solid plaster partitions or where otherwise determined by fire tests.
719.5 Plaster alternatives for concrete. | In reinforced concrete construction, gypsum plaster or portland cement plaster is permitted to be substituted for 1/2 inch (12.7 mm) of the required poured concrete protection, except that a minimum thickness of 3/8 inch (9.5 mm) of poured concrete shall be provided in reinforced concrete floors and 1 inch (25.4 mm) in reinforced concrete columns in addition to the plaster finish. The concrete base shall be prepared in accordance with Section 2510.7. | 719.5 Plaster alternatives for concrete. | In reinforced concrete construction, gypsum plaster or Portland cement plaster is permitted to be substituted for 1/2 inch (12.7 mm) of the required poured concrete protection, except that a minimum thickness of 3/8 inch (9.5 mm) of poured concrete shall be provided in reinforced concrete floors and 1 inch (25 mm) in reinforced concrete columns in addition to the plaster finish. The concrete base shall be prepared in accordance with Section 2510.7.
720.1 General. | Insulating materials, including facings such as vapor retarders and vapor-permeable membranes, similar coverings, and all layers of single and multilayer reflective foil insulations, shall comply with the requirements of this section. Where a flame spread index or a smoke-development index is specified in this section, such index shall be determined in accordance with ASTM E 84 or UL 723. Any material that is subject to an increase in flame spread index or smoke-development index beyond the limits herein established through the effects of age, moisture or other atmospheric conditions shall not be permitted. Exceptions: 1. Fiberboard insulation shall comply with Chapter 23 of this code. 2. Foam plastic insulation shall comply with Chapter 26 of this code. 3. Duct and pipe insulation and duct and pipe coverings and linings in plenums shall comply with the New York City Mechanical Code. 4. EIFS shall comply with Chapters 14 and 26 of this code. | 720.1 General. | Insulating materials shall comply with the requirements of this section. Where a flame spread index or a smoke-developed index is specified in this section, such index shall be determined in accordance with ASTM E84 or UL 723. Any material that is subject to an increase in flame spread index or smoke-developed index beyond the limits herein established through the effects of age, moisture or other atmospheric conditions shall not be permitted. Insulating materials, when tested in accordance with the requirements of this section, shall include facings, when used, such as vapor retarders, vapor permeable membranes and similar coverings, and all layers of single and multilayer reflective foil insulation and similar materials. Exceptions: 1. Fiberboard insulation shall comply with Chapter 23. 2. Foam plastic insulation shall comply with Chapter 26. 3. Duct and pipe insulation and duct and pipe coverings and linings in plenums shall comply with the Interna-tional Mechanical Code. 4. All layers of single and multilayer reflective plastic core insulation shall comply with Section 2614.
|  | 718.2.6 Exterior wall coverings. | Fireblocking shall be installed within concealed spaces of exterior wall coverings and other exterior architectural elements where permitted to be of combustible construction as specified in Section 1405 or where erected with combustible frames. Fireblocking shall be installed at maximum intervals of 20 feet (6096 mm) in either dimension so that there will be no concealed space exceeding 100 square feet (9.3 m2) between fireblocking. Where wood furring strips are used, they shall be of approved wood of natural decay resistance or preservative-treated wood. If noncontinuous, such elements shall have closed ends, with not less than 4 inches (102 mm) of separation between sections. Exceptions: 1. Fireblocking of cornices is not required in single-family dwellings. Fireblocking of cornices of a two-family dwelling is required only at the line of dwelling unit separation. 2. Fireblocking shall not be required where the exterior wall covering is installed on noncombustible framing and the face of the exterior wall covering exposed to the concealed space is covered by one of the follow-ing materials: 2.1. Aluminum having a minimum thickness of 0.019 inch (0.5 mm). 2.2. Corrosion-resistant steel having a base metal thickness not less than 0.016 inch (0.4 mm) at any point. 2.3. Other approved noncombustible materials. 3. Fireblocking shall not be required where the exterior wall covering has been tested in accordance with, and complies with the acceptance criteria of, NFPA 285. The exterior wall covering shall be installed as tested in accordance with NFPA 285.
720.2 Concealed installation. | Insulating materials, where concealed as installed in buildings of any type construction, shall comply with Sections 720.1.1, 720.1 and 720.1.2. Con­cealed insulation shall be separated from the building interior by a thermal barrier consisting of at least 1/2-inch (12.7 mm) thick gypsum wallboard or approved equivalent. Exception: Cellulosic fiber loose-fill insulation complying with the requirements of Section 720.6 shall only be required to meet a smoke-development index of not more than 450, when tested in accordance with CAN/ULC S102.2, provided such insulation has a smoke-development index that complies with the requirements of Section 720.2 or 720.3, as applicable, and Section 720.6 of this code. | 720.2 Concealed installation. | Insulating materials, where concealed as installed in buildings of any type of construction, shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450. Exception: Cellulosic fiber loose-fill insulation complying with the requirements of Section 720.6 shall not be re-quired to meet a flame spread index requirement but shall be required to meet a smoke-developed index of not more than 450 when tested in accordance with CAN/ULC S102.2.
720.2.1 Facings. | Where such materials are installed in concealed spaces in buildings of Type III, IV or V construction, the flame spread and smoke-development limits do not apply to facings, coverings, and layers of reflective foil insulation that are installed behind and in substantial contact with the unexposed surface of the ceiling, wall or floor finish. Exception: All layers of single and multilayer reflective plastic core insulation shall comply with Section 2614. | 720.2.1 Facings. | Where such materials are installed in concealed spaces in buildings of Type III, IV or V construction, the flame spread and smoke-developed limitations do not apply to facings, coverings, and layers of reflective foil insulation that are installed behind and in substantial contact with the unexposed surface of the ceiling, wall or floor finish. Exception: All layers of single and multilayer reflective plastic core insulation shall comply with Section 2614.
720.3 Exposed installation. | Insulation materials, where exposed as installed in buildings of any type of construction, shall have a flame spread index of not more than 25 and a smoke-development index of not more than 50. Exception: Cellulosic fiber loose-fill insulation complying with the requirements of Section 720.6 shall not be required to meet a flame spread index requirement but shall be required to meet a smoke-development index of not more than 50 when tested in accordance with CAN/ULC S102.2. | 720.3 Exposed installation. | Insulating materials, where exposed as installed in buildings of any type of construction, shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450. Exception: Cellulosic fiber loose-fill insulation complying with the requirements of Section 720.6 shall not be re-quired to meet a flame spread index requirement but shall be required to meet a smoke-developed index of not more than 450 when tested in accordance with CAN/ULC S102.2.
720.3.1 Attic floors. | Exposed insulation materials installed on attic floors shall have a critical radiant flux of not less than 0.12 watt per square centimeter when tested in accordance with ASTM E 970. | 720.3.1 Attic floors. | Exposed insulation materials installed on attic floors shall have a critical radiant flux of not less than 0.12 watt per square centimeter when tested in accordance with ASTM E970.
720.4 Loose-fill insulation. | Loose-fill insulation materials that cannot be mounted in the ASTM E 84 apparatus without a screen or artificial supports shall comply with the flame spread and smoke-developed limits of Sections 720.2 and 720.3 when tested in accordance with CAN/ULC S102.2. Exception: Cellulosic fiber loose-fill insulation shall not be required to meet a flame spread index requirement when tested in accordance with CAN/ULC S102.2, provided such insulation has a smoke-development index that complies with the requirements of Section 720.2 or 720.3, as applicable, and Section 720.6. | 720.4 Loose-fill insulation. | Loose-fill insulation materials that cannot be mounted in the ASTM E84 or UL 723 apparatus without a screen or artificial supports shall comply with the flame spread and smoke-developed limits of Sections 720.2 and 720.3 when tested in accordance with CAN/ULC S102.2. Exception: Cellulosic fiber loose-fill insulation shall not be required to meet a flame spread index requirement when tested in accordance with CAN/ULC S102.2, provided that such insulation has a smoke-developed index of not more than 450 and complies with the requirements of Section 720.6.
720.5 Roof insulation. | The use of combustible roof insulation not complying with Sections 720.2 and 720.3 shall be permitted in any type of construction provided it is applied on top of roof decking or slab and that such insulation is covered with approved roof coverings directly applied thereto. | 720.5 Roof insulation. | The use of combustible roof insulation not complying with Sections 720.2 and 720.3 shall be permitted in any type of construction provided that insulation is covered with approved roof coverings directly applied thereto.
720.6 Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation. | Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation shall comply with CPSC 16 CFR Parts 1209 and 1404. Each package of such insulating material shall be clearly labeled in accordance with CPSC 16 CFR Parts 1209 and 1404. | 720.6 Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation. | Cellulosic fiber loose-fill insulation and self-supported spray-applied cellulosic insulation shall comply with CPSC 16 CFR Parts 1209 and 1404. Each package of such insulating material shall be clearly labeled in accordance with CPSC 16 CFR Parts 1209 and 1404.
720.7 Insulation and covering on pipe and tubing. | Insulation and covering on pipe and tubing shall comply with the requirements of the New York City Mechanical Code, the New York City Plumbing Code, and the New York City Energy Conservation Code. | 720.7 Insulation and covering on pipe and tubing. | Insulation and covering on pipe and tubing shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450. Exception: Insulation and covering on pipe and tubing installed in plenums shall comply with the International Me-chanical Code.
721.1 General. | The provisions of this section contain prescriptive details of fire-resistance-rated building elements, components or assemblies. The materials of construction listed in Tables 721.1(1), 721.1(2), and 721.1(3) shall be assumed to have the fire-resistance ratings prescribed therein. Where materials that change the capacity for heat dissipation are incorporated into a fire-resistance-rated assembly, fire test results or other substantiating data shall be made available to the commissioner to show that the required fire-resistance rating time period is not reduced. | 721.1 General. | The provisions of this section contain prescriptive details of fire-resistance-rated building elements, components or assemblies. The materials of construction specified in Tables 721.1(1), 721.1(2) and 721.1(3) shall be assumed to have the fire-resistance ratings prescribed therein. Where materials that change the capacity for heat dissipation are incorporated into a fire-resistance-rated assembly, fire test results or other substantiating data shall be made available to the building official to show that the required fire-resistance-rating time period is not reduced.
721.1.1 Thickness of protective coverings. | The thickness of fire-resistant materials required for protection of structural members shall be not less than set forth in Table 721.1(1), except as modified in this section. The figures shown shall be the net thickness of the protecting materials and shall not include any hollow space in back of the protection. | 721.1.1 Thickness of protective coverings. | The thickness of fire-resistant materials required for protection of structural members shall be not less than set forth in Table 721.1(1), except as modified in this section. The figures shown shall be the net thickness of the protecting materials and shall not include any hollow space in back of the protection. |  | See BC07 Tables&Figures
721.1.2 Unit masonry protection. | Where required, metal ties shall be embedded in bed joints of unit masonry for protection of steel columns. Such ties shall be as set forth in Table 721.1(1) or be equivalent thereto. | 721.1.2 Unit masonry protection. | Where required, metal ties shall be embedded in bed joints of unit masonry for protection of steel columns. Such ties shall be as set forth in Table 721.1(1) or be equivalent thereto. |  | See BC07 Tables&Figures
721.1.3 Reinforcement for cast-in-place concrete column protection. | Cast-in-place concrete protection for steel columns shall be reinforced at the edges of such members with wire ties of not less than 0.18 inch (4.6 mm) in diameter wound spirally around the columns on a pitch of not more than 8 inches (203.2 mm) or by equivalent reinforcement. | 721.1.3 Reinforcement for cast-in-place concrete column protection. | Cast-in-place concrete protection for steel columns shall be reinforced at the edges of such members with wire ties of not less than 0.18 inch (4.6 mm) in diameter wound spirally around the columns on a pitch of not more than 8 inches (203 mm) or by equivalent reinforcement.
721.1.4 Plaster application. | The finish coat is not required for plaster protective coatings where such coatings comply with the design mix and thickness requirements of Tables 721.1(1), 721.1(2), and 721.1(3). | 721.1.4 Plaster application. | The finish coat is not required for plaster protective coatings where those coatings comply with the design mix and thickness requirements of Tables 721.1(1), 721.1(2) and 721.1(3).
721.1.5 Bonded prestressed concrete tendons. | For members having a single tendon or more than one tendon installed with equal concrete cover measured from the nearest surface, the cover shall be not less than that set forth in Table 721.1(1). For members having multiple tendons installed with variable concrete cover, the average tendon cover shall be not less than that set forth in Table 721.1(1), provided: | 721.1.5 Bonded prestressed concrete tendons. | For members having a single tendon or more than one tendon installed with equal concrete cover measured from the nearest surface, the cover shall be not less than that set forth in Table 721.1(1). For members having multiple tendons installed with variable concrete cover, the average tendon cover shall be not less than that set forth in Table 721.1(1), provided that: |  | See BC07 Tables&Figures
722.1 General. | The provisions of this section contain procedures by which the fire resistance of specific materials or combinations of materials is established by calculations. These procedures apply only to the information contained in this section and shall not be otherwise used. The calculated fire resistance of concrete, concrete masonry and clay masonry assemblies shall be permitted in accordance with ACI 216.1/TMS 216. The calculated fire resistance of steel assemblies shall be permitted in accordance with Chapter 5 of ASCE 29. The calculated fire resistance of exposed wood members and wood decking shall be permitted in accordance with Chapter 16 of ANSI/AWC National Design Specification for Wood Construction (NDS). | 722.1 General. | The provisions of this section contain procedures by which the fire resistance of specific materials or combinations of materials is established by calculations. These procedures apply only to the information contained in this section and shall not be otherwise used. The calculated fire resistance of specific materials or combinations of materials shall be established by one of the following:
722.2 Concrete assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of concrete assemblies are established by calculations. | 722.2 Concrete assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of concrete assemblies are established by calculations.
722.2.1 Concrete walls. | Cast-in-place and precast concrete walls shall comply with Section 722.2.1.1. Multiwythe concrete walls shall comply with Section 722.2.1.2. Joints between precast panels shall comply with Section 722.2.1.3. Concrete walls with gypsum wallboard or plaster finish shall comply with Section 722.2.1.4. | 722.2.1 Concrete walls. | Cast-in-place and precast concrete walls shall comply with Section 722.2.1.1. Multiwythe concrete walls shall comply with Section 722.2.1.2. Joints between precast panels shall comply with Section 722.2.1.3. Concrete walls with gypsum wallboard or plaster finish shall comply with Section 722.2.1.4.
722.2.1.1 Cast-in-place or precast walls. | The minimum equivalent thicknesses of cast-in-place or precast concrete walls for fire-resistance ratings of 1 hour to 4 hours are shown in Table 722.2.1.1. For solid walls with flat vertical surfaces, the equivalent thickness is the same as the actual thickness. The values in Table 722.2.1.1 apply to plain, reinforced or prestressed concrete walls. | 722.2.1.1 Cast-in-place or precast walls. | The minimum equivalent thicknesses of cast-in-place or precast concrete walls for fire-resistance ratings of 1 hour to 4 hours are shown in Table 722.2.1.1. For solid walls with flat vertical surfaces, the equivalent thickness is the same as the actual thickness. The values in Table 722.2.1.1 apply to plain, reinforced or prestressed concrete walls. |  | See BC07 Tables&Figures
722.2.1.1.1 Hollow-core precast wall panels. | For hollow-core precast concrete wall panels in which the cores are of constant cross section throughout the length, calculation of the equivalent thickness by dividing the net cross-sectional area (the gross cross section minus the area of the cores) of the panel by its width shall be permitted. | 722.2.1.1.1 Hollow-core precast wall panels. | For hollow-core precast concrete wall panels in which the cores are of constant cross section throughout the length, calculation of the equivalent thickness by dividing the net cross-sectional area (the gross cross section minus the area of the cores) of the panel by its width shall be permitted
722.2.1.1.2 Core spaces filled. | Where all of the core spaces of hollow-core wall panels are filled with loose-fill material, such as expanded shale, clay or slag, or vermiculite or perlite, the fire-resistance rating of the wall is the same as that of a solid wall of the same concrete type and of the same overall thickness. | 722.2.1.1.2 Core spaces filled. | Where all of the core spaces of hollow-core wall panels are filled with loose-fill material, such as expanded shale, clay or slag, or vermiculite or perlite, the fire-resistance rating of the wall is the same as that of a solid wall of the same concrete type and of the same overall thickness.
722.2.1.1.3 Tapered cross sections. | The thickness of panels with tapered cross sections shall be that determined at a distance 2t or 6 inches (152.4 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness. | 722.2.1.1.3 Tapered cross sections. | The thickness of panels with tapered cross sections shall be that determined at a distance 2t or 6 inches (152 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness.
722.2.1.1.4 Ribbed or undulating surfaces. | The equivalent thickness of panels with ribbed or undulating surfaces shall be determined by one of the following expressions: | 722.2.1.1.4 Ribbed or undulating surfaces. | The equivalent thickness of panels with ribbed or undulating surfaces shall be determined by one of the following expressions:
722.2.1.2.1 Two or more wythes. | The fire-resistance rating for wall panels consisting of two or more wythes shall be permitted to be determined by the formula: | 722.2.1.2.1 Two or more wythes. | The fire-resistance rating for wall panels consisting of two or more wythes shall be permitted to be determined by the formula:
722.2.1.2.2 Foam plastic insulation. | The fire-resistance ratings of precast concrete wall panels consisting of a layer of foam plastic insulation sandwiched between two wythes of concrete shall be permitted to be determined by use of Equation 7-4. Foam plastic insulation with a total thickness of less than 1 inch (25.4 mm) shall be disregarded. The Rn value for thickness of foam plastic insulation of 1 inch (25.4 mm) or greater, for use in the calculation, is 5 minutes; therefore Rn0.59 = 2.5. | 722.2.1.2.2 Foam plastic insulation. | The fire-resistance ratings of precast concrete wall panels consisting of a layer of foam plastic insulation sandwiched between two wythes of concrete shall be permitted to be determined by use of Equation 7-4. Foam plastic insulation with a total thickness of less than 1 inch (25 mm) shall be disregarded. The Rn value for thickness of foam plastic insulation of 1 inch (25 mm) or greater, for use in the calculation, is 5 minutes; therefore Rn0.59 = 2.5.
722.2.1.3 Joints between precast wall panels. | Joints between precast concrete wall panels that are not insulated as required by this section shall be considered as openings in walls. Uninsulated joints shall be included in determining the percentage of openings permitted by Table 705.8. Where openings are not permitted or are required by this code to be protected, the provisions of this section shall be used to determine the amount of joint insulation required. Insulated joints shall not be considered openings for purposes of determining compliance with the allowable percentage of openings in Table 705.8. | 722.2.1.3 Joints between precast wall panels. | Joints between precast concrete wall panels that are not insulated as required by this section shall be considered as openings in walls. Uninsulated joints shall be included in determining the percentage of openings permitted by Table 705.8. Where openings are not permitted or are required by this code to be protected, the provisions of this section shall be used to determine the amount of joint insulation required. Insulated joints shall not be considered openings for purposes of determining compliance with the allowable percentage of openings in Table 705.8. |  | See BC07 Tables&Figures
722.2.1.3.1 Ceramic fiber joint protection. | Figure 722.2.1.3.1 shows thicknesses of ceramic fiber blankets to be used to insulate joints between precast concrete wall panels for various panel thicknesses and for joint widths of 3/8 inch (9.5 mm) and 1 inch (25.4 mm) for fire-resistance ratings of 1 hour to 4 hours. For joint widths between 3/8 inch (9.5 mm) and 1 inch (25.4 mm), the thickness of ceramic fiber blanket is allowed to be determined by direct interpolation. Other tested and labeled materials are acceptable in place of ceramic fiber blankets. | 722.2.1.3.1 Ceramic fiber joint protection. | Figure 722.2.1.3.1 shows thicknesses of ceramic fiber blankets to be used to insulate joints between precast concrete wall panels for various panel thicknesses and for joint widths of 3/8 inch (9.5 mm) and 1 inch (25 mm) for fire-resistance ratings of 1 hour to 4 hours. For joint widths between 3/8 inch (9.5 mm) and 1 inch (25 mm), the thickness of ceramic fiber blanket is allowed to be determined by direct interpolation. Other tested and labeled materials are acceptable in place of ceramic fiber blankets. |  | See BC07 Tables&Figures
722.2.1.4 Walls with gypsum wallboard or plaster finishes. | The fire-resistance rating of cast-in-place or precast concrete walls with finishes of gypsum wallboard or plaster applied to one or both sides shall be permitted to be calculated in accordance with the provisions of this section. | 722.2.1.4 Walls with gypsum wallboard or plaster finishes. | The fire-resistance rating of cast-in-place or precast concrete walls with finishes of gypsum wallboard or plaster applied to one or both sides shall be permitted to be calculated in accordance with the provisions of this section.
722.2.1.4.1 Nonfire-exposed side. | Where the finish of gypsum wallboard or plaster is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of the finish shall first be corrected by multiplying the actual thickness of the finish by the applicable factor determined from Table 722.2.1.4(1) based on the type of aggregate in the concrete. The corrected thickness of finish shall then be added to the actual or equivalent thickness of concrete and fire-resistance rating of the concrete and finish determined from Tables 722.2.1.1 and 722.2.1.2(1), and Figure 722.2.1.2. | 722.2.1.4.1 Nonfire-exposed side. | Where the finish of gypsum wallboard or plaster is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of the finish shall first be corrected by multiplying the actual thickness of the finish by the applicable factor determined from Table 722.2.1.4(1) based on the type of aggregate in the concrete. The corrected thickness of finish shall then be added to the actual or equivalent thickness of concrete and fire-resistance rating of the concrete and finish determined from Tables 722.2.1.1 and 722.2.1.2(1) and Figure 722.2.1.2. |  | See BC07 Tables&Figures
|  | 722.2.1.2 Multiwythe walls. | For walls that consist of two wythes of different types of concrete, the fire-resistance ratings shall be permitted to be determined from Figure 722.2.1.2.
722.2.1.4.2 Fire-exposed side. | Where gypsum wallboard or plaster is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table 722.2.1.4(2) shall be added to the fire-resistance rating determined from Tables 722.2.1.1 and 722.2.1.2(1) and Figure 722.2.1.2 for the concrete alone, or to the rating determined in Section 722.2.1.4.1 for the concrete and finish on the nonfire-exposed side. | 722.2.1.4.2 Fire-exposed side. | Where gypsum wallboard or plaster is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table 722.2.1.4(2) shall be added to the fire-resistance rating determined from Tables 722.2.1.1 and 722.2.1.2(1) and Figure 722.2.1.2 for the concrete alone, or to the rating determined in Section 722.2.1.4.1 for the concrete and finish on the nonfire-exposed side. |  | See BC07 Tables&Figures
722.2.1.4.3 Nonsymmetrical assemblies. | For a wall having no finish on one side or different types or thicknesses of finish on each side, the calculation procedures of Sections 722.2.1.4.1 and 722.2.1.4.2 shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values. Exception: For an exterior wall with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only. | 722.2.1.4.3 Nonsymmetrical assemblies. | For a wall without finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of Sections 722.2.1.4.1 and 722.2.1.4.2 shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values. Exception: For an exterior wall with a fire separation distance greater than 5 feet (1524 mm) the fire shall be assumed to occur on the interior side only.
722.2.1.4.4 Minimum concrete fire-resistance rating. | Where finishes applied to one or both sides of a concrete wall contribute to the fire-resistance rating, the concrete alone shall provide not less than one-half of the total required fire-resistance rating. Additionally, the contribution to the fire resistance of the finish on the nonfire-exposed side of a load-bearing wall shall not exceed one-half the contribution of the concrete alone. | 722.2.1.4.4 Minimum concrete fire-resistance rating. | Where finishes applied to one or both sides of a concrete wall contribute to the fire-resistance rating, the concrete alone shall provide not less than one-half of the total required fire-resistance rating. Additionally, the contribution to the fire resistance of the finish on the nonfire-exposed side of a load-bearing wall shall not exceed one-half the contribution of the concrete alone.
722.2.1.4.5 Concrete finishes. | Finishes on concrete walls that are assumed to contribute to the total fire-resistance rating of the wall shall comply with the installation requirements of Section 722.3.2.5. | 722.2.1.4.5 Concrete finishes. | Finishes on concrete walls that are assumed to contribute to the total fire-resistance rating of the wall shall comply with the installation requirements of Section 722.3.2.5.
722.2.2 Concrete floor and roof slabs. | Reinforced and prestressed floors and roofs shall comply with Section 722.2.2.1. Multicourse floors and roofs shall comply with Sections 722.2.2.2 and 722.2.2.3, respectively. | 722.2.2 Concrete floor and roof slabs. | Reinforced and prestressed floors and roofs shall comply with Section 722.2.2.1. Multicourse floors and roofs shall comply with Sections 722.2.2.2 and 722.2.2.3, respectively.
722.2.2.1 Reinforced and prestressed floors and roofs. | The minimum thicknesses of reinforced and prestressed concrete floor or roof slabs for fire-resistance ratings of 1 hour to 4 hours are shown in Table 722.2.2.1. Exception: Minimum thickness shall not be required for floors and ramps within open and enclosed parking garages constructed in accordance with Section 406. | 722.2.2.1 Reinforced and prestressed floors and roofs. | The minimum thicknesses of reinforced and prestressed concrete floor or roof slabs for fire-resistance ratings of 1 hour to 4 hours are shown in Table 722.2.2.1. Exception: Minimum thickness shall not be required for floors and ramps within parking garages constructed in accordance with Sections 406.5 and 406.6. |  | See BC07 Tables&Figures
722.2.2.1.1 Hollow-core prestressed slabs. | For hollow-core prestressed concrete slabs in which the cores are of constant cross section throughout the length, the equivalent thickness shall be permitted to be obtained by dividing the net cross-sectional area of the slab including grout in the joints, by its width. | 722.2.2.1.1 Hollow-core prestressed slabs. | For hollow-core prestressed concrete slabs in which the cores are of constant cross section throughout the length, the equivalent thickness shall be permitted to be obtained by dividing the net cross-sectional area of the slab including grout in the joints, by its width.
722.2.2.1.2 Slabs with sloping soffits. | The thickness of slabs with sloping soffits (see Figure 722.2.2.1.2) shall be determined at a distance 2t or 6 inches (152.4 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness. | 722.2.2.1.2 Slabs with sloping soffits. | The thickness of slabs with sloping soffits (see Figure 722.2.2.1.2) shall be determined at a distance 2t or 6 inches (152 mm), whichever is less, from the point of minimum thickness, where t is the minimum thickness.
722.2.2.1.3 Slabs with ribbed soffits. | The thickness of slabs with ribbed or undulating soffits (see Figure 722.2.2.1.3) shall be determined by one of the following expressions, whichever is applicable: | 722.2.2.1.3 Slabs with ribbed soffits. | The thickness of slabs with ribbed or undulating soffits (see Figure 722.2.2.1.3) shall be determined by one of the following expressions, whichever is applicable:
722.2.2.2 Multicourse floors. | The fire-resistance ratings of floors that consist of a base slab of concrete with a topping (overlay) of a different type of concrete shall comply with Figure 722.2.2.2. | 722.2.2.2 Multicourse floors. | The fire-resistance ratings of floors that consist of a base slab of concrete with a topping (overlay) of a different type of concrete shall comply with Figure 722.2.2.2.
722.2.2.3 Multicourse roofs. | The fire-resistance ratings of roofs that consist of a base slab of concrete with a topping (overlay) of an insulating concrete or with an insulating board and built-up roofing shall comply with Figures 722.2.2.3(1) and 722.2.2.3(2). | 722.2.2.3 Multicourse roofs. | The fire-resistance ratings of roofs that consist of a base slab of concrete with a topping (overlay) of an insulating concrete or with an insulating board and built-up roofing shall comply with Figures 722.2.2.3(1) and 722.2.2.3(2).
722.2.2.3.1 Heat transfer. | For the transfer of heat, three-ply built-up roofing contributes 10 minutes to the fire-resistance rating. The fire-resistance rating for concrete assemblies such as those shown in Figure 722.2.2.3(1) shall be increased by 10 minutes. This increase is not applicable to those shown in Figure 722.2.2.3(2). | 722.2.2.3.1 Heat transfer. | For the transfer of heat, three-ply built-up roofing contributes 10 minutes to the fire-resistance rating. The fire-resistance rating for concrete assemblies such as those shown in Figure 722.2.2.3(1) shall be increased by 10 minutes. This increase is not applicable to those shown in Figure 722.2.2.3(2).
722.2.2.4 Joints in precast slabs. | Joints between adjacent precast concrete slabs need not be considered in calculating the slab thickness provided that a concrete topping not less than 1 inch (25.4 mm) thick is used. Where no concrete topping is used, joints must be grouted to a depth of not less than one-third the slab thickness at the joint, but not less than 1 inch (25.4 mm), or the joints must be made fire resistant by other approved methods. | 722.2.2.4 Joints in precast slabs. | Joints between adjacent precast concrete slabs need not be considered in calculating the slab thickness provided that a concrete topping not less than 1 inch (25 mm) thick is used. Where concrete topping is not used, joints must be grouted to a depth of not less than one-third the slab thickness at the joint, but not less than 1 inch (25 mm), or the joints must be made fire resistant by other approved methods.
722.2.3 Concrete cover over reinforcement. | The minimum thickness of concrete cover over reinforcement in concrete slabs, reinforced beams and prestressed beams shall comply with this section. | 722.2.3 Concrete cover over reinforcement. | The minimum thickness of concrete cover over reinforcement in concrete slabs, reinforced beams and prestressed beams shall comply with this section.
|  | 722.2.2.1.4 Flat plate concrete slabs with uniformly spaced hollow voids. | Table 722.2.2.1 shall be used to determine the 1- and 2-hour fire-resistance ratings for flat plate concrete slabs with uniformly spaced hollow voids. The equivalent thickness of the slab shall be determined by dividing the net concrete volume of the slab by the floor area. The net concrete volume of the slab shall be equal to the volume of concrete of a solid slab minus the average concrete volume displaced by the hollow voids. |  | See BC07 Tables&Figures
722.2.3.1 Slab cover. | The minimum thickness of concrete cover to the positive moment reinforcement shall comply with Table 722.2.3(1) for reinforced concrete and Table 722.2.3(2) for prestressed concrete. These tables are applicable for solid or hollow-core one-way or two-way slabs with flat undersurfaces. These tables are applicable to slabs that are either cast in place or precast. For precast prestressed concrete not covered elsewhere, the procedures contained in PCI MNL 124 shall be acceptable. | 722.2.3.1 Slab cover. | The minimum thickness of concrete cover to the positive moment reinforcement shall comply with Table 722.2.3(1) for reinforced concrete and Table 722.2.3(2) for prestressed concrete. These tables are applicable for solid or hollow-core one-way or two-way slabs with flat undersurfaces. These tables are applicable to slabs that are either cast in place or precast. For precast prestressed concrete not covered elsewhere, the procedures contained in PCI 124 shall be acceptable. |  | See BC07 Tables&Figures
722.2.3.2 Reinforced beam cover. | The minimum thickness of concrete cover to the positive moment reinforcement (bottom steel) for reinforced concrete beams is shown in Table 722.2.3(3) for fire-resistance ratings of 1 hour to 4 hours. | 722.2.3.2 Reinforced beam cover. | The minimum thickness of concrete cover to the positive moment reinforcement (bottom steel) for reinforced concrete beams is shown in Table 722.2.3(3) for fire-resistance ratings of 1 hour to 4 hours. |  | See BC07 Tables&Figures
722.2.3.3 Prestressed beam cover. | The minimum thickness of concrete cover to the positive moment prestressing tendons (bottom steel) for restrained and unrestrained prestressed concrete beams and stemmed units shall comply with the values shown in Tables 722.2.3(4) and 722.2.3(5) for fire-resistance ratings of 1 hour to 4 hours. Values in Table 722.2.3(4) apply to beams 8 inches (203.2 mm) or greater in width. Values in Table 722.2.3(5) apply to beams or stems of any width, provided the cross-section area is not less than 40 square inches (25 806.4 mm2). In case of differences between the values determined from Table 722.2.3(4) or 722.2.3(5), it is permitted to use the smaller value. The concrete cover shall be calculated in accordance with Section 722.2.3.3.1. The minimum concrete cover for nonprestressed reinforcement in prestressed concrete beams shall comply with Section 722.2.3.2. | 722.2.3.3 Prestressed beam cover. | The minimum thickness of concrete cover to the positive moment prestressing tendons (bottom steel) for restrained and unrestrained prestressed concrete beams and stemmed units shall comply with the values shown in Tables 722.2.3(4) and 722.2.3(5) for fire-resistance ratings of 1 hour to 4 hours. Values in Table 722.2.3(4) apply to beams 8 inches (203 mm) or greater in width. Values in Table 722.2.3(5) apply to beams or stems of any width, provided that the cross-section area is not less than 40 square inches (25 806 mm2). In case of differences between the values determined from Table 722.2.3(4) or 722.2.3(5), it is permitted to use the smaller value. The concrete cover shall be calculated in accordance with Section 722.2.3.3.1. The minimum concrete cover for nonprestressed reinforcement in prestressed concrete beams shall comply with Section 722.2.3.2. |  | See BC07 Tables&Figures
722.2.3.3.1 Calculating concrete cover. | The concrete cover for an individual tendon is the minimum thickness of concrete between the surface of the tendon and the fire-exposed surface of the beam, except that for ungrouted ducts, the assumed cover thickness is the minimum thickness of concrete between the surface of the duct and the fire-exposed surface of the beam. For beams in which two or more tendons are used, the cover is assumed to be the average of the minimum cover of the individual tendons. For corner tendons (tendons equal distance from the bottom and side), the minimum cover used in the calculation shall be one-half the actual value. For stemmed members with two or more prestressing tendons located along the vertical centerline of the stem, the average cover shall be the distance from the bottom of the member to the centroid of the tendons. The actual cover for any individual tendon shall be not less than one-half the smaller value shown in Tables 722.2.3(4) and 722.2.3(5), or 1 inch (25.4 mm), whichever is greater. | 722.2.3.3.1 Calculating concrete cover. | The concrete cover for an individual tendon is the minimum thickness of concrete between the surface of the tendon and the fire-exposed surface of the beam, except that for ungrouted ducts, the assumed cover thickness is the minimum thickness of concrete between the surface of the duct and the fire-exposed surface of the beam. For beams in which two or more tendons are used, the cover is assumed to be the average of the minimum cover of the individual tendons. For corner tendons (tendons equal distance from the bottom and side), the minimum cover used in the calculation shall be one-half the actual value. For stemmed members with two or more prestressing tendons located along the vertical centerline of the stem, the average cover shall be the distance from the bottom of the member to the centroid of the tendons. The actual cover for any individual tendon shall be not less than one-half the smaller value shown in Tables 722.2.3(4) and 722.2.3(5), or 1 inch (25 mm), whichever is greater.
722.2.4 Concrete columns. | Concrete columns shall comply with this section. | 722.2.4 Concrete columns. | Concrete columns shall comply with this section.
722.2.4.1 Minimum size. | The minimum overall dimensions of reinforced concrete columns for fire-resistance ratings of 1 hour to 4 hours for exposure to fire on all sides shall comply with this section. | 722.2.4.1 Minimum size. | The minimum overall dimensions of reinforced concrete columns for fire-resistance ratings of 1 hour to 4 hours for exposure to fire on all sides shall comply with this section.
722.2.4.1.1 Concrete strength less than or equal to 12,000 psi. | For columns made with concrete having a specified compressive strength, f’c, of less than or equal to 12,000 psi (82.7 MPa), the minimum dimension shall comply with Table 722.2.4. | 722.2.4.1.1 Concrete strength less than or equal to 12,000 psi. | For columns made with concrete having a specified compressive strength, f′c, of less than or equal to 12,000 psi (82.7 MPa), the minimum dimension shall comply with Table 722.2.4. |  | See BC07 Tables&Figures
722.2.4.1.2 Concrete strength greater than 12,000 psi. | For columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), for fire-resistance ratings of 1 hour to 4 hours the minimum dimension shall be 24 inches (609.6 mm). | 722.2.4.1.2 Concrete strength greater than 12,000 psi. | For columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), for fire-resistance ratings of 1 hour to 4 hours the minimum dimension shall be 24 inches (610 mm).
722.2.4.2 Minimum cover for R/C columns. | The minimum thickness of concrete cover to the main longitudinal reinforcement in columns, regardless of the type of aggregate used in the concrete and the specified compressive strength of concrete, f’c, shall be not less than 1 inch (25.4 mm) times the number of hours of required fire resistance or 2 inches (50.8 mm), whichever is less. | 722.2.4.2 Minimum cover for R/C columns. | The minimum thickness of concrete cover to the main longitudinal reinforcement in columns, regardless of the type of aggregate used in the concrete and the specified compressive strength of concrete, f’c, shall be not less than 1 inch (25 mm) times the number of hours of required fire resistance or 2 inches (51 mm), whichever is less.
722.2.4.3 Tie and spiral reinforcement. | For concrete columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), tie and spiral reinforcement shall comply with the following: | 722.2.4.3 Tie and spiral reinforcement. | For concrete columns made with concrete having a specified compressive strength, f’c, greater than 12,000 psi (82.7 MPa), tie and spiral reinforcement shall comply with the following:
722.2.4.4 Columns built into walls. | The minimum dimensions of Table 722.2.4 do not apply to a reinforced concrete column that is built into a concrete or masonry wall provided all of the following are met: | 722.2.4.4 Columns built into walls. | The minimum dimensions of Table 722.2.4 do not apply to a reinforced concrete column that is built into a concrete or masonry wall provided that all of the following are met: |  | See BC07 Tables&Figures
722.2.4.5 Precast cover units for steel columns. | See Section 722.5.1.4. | 722.2.4.5 Precast cover units for steel columns. | See Section 722.5.1.4.
722.3 Concrete masonry. | The provisions of this section contain procedures by which the fire-resistance ratings of concrete masonry are established by calculations. | 722.3 Concrete masonry. | The provisions of this section contain procedures by which the fire-resistance ratings of concrete masonry are established by calculations.
722.3.1 Equivalent thickness. | The equivalent thickness of concrete masonry construction shall be determined in accordance with the provisions of this section. | 722.3.1 Equivalent thickness. | The equivalent thickness of concrete masonry construction shall be determined in accordance with the provisions of this section.
722.3.1.1 Concrete masonry unit plus finishes. | The equivalent thickness of concrete masonry assemblies, Tea, shall be computed as the sum of the equivalent thickness of the concrete masonry unit, Te, as determined by Section 722.3.1.2, 722.3.1.3 or 722.3.1.4, plus the equivalent thickness of finishes, Tef, determined in accordance with Section 722.3.2: | 722.3.1.1 Concrete masonry unit plus finishes. | The equivalent thickness of concrete masonry assemblies, Tea, shall be computed as the sum of the equivalent thickness of the concrete masonry unit, Te, as determined by Section 722.3.1.2, 722.3.1.3 or 722.3.1.4, plus the equivalent thickness of finishes, Tef, determined in accordance with Section 722.3.2:
722.3.1.2 Ungrouted or partially grouted construction. | Te shall be the value obtained for the concrete masonry unit determined in accordance with ASTM C 140. | 722.3.1.2 Ungrouted or partially grouted construction. | Te shall be the value obtained for the concrete masonry unit determined in accordance with ASTM C140.
722.3.1.3 Solid grouted construction. | The equivalent thickness, Te, of solid grouted concrete masonry units is the actual thickness of the unit. | 722.3.1.3 Solid grouted construction. | The equivalent thickness, Te, of solid grouted concrete masonry units is the actual thickness of the unit.
722.3.1.4 Airspaces and cells filled with loose-fill material. | The equivalent thickness of completely filled hollow concrete masonry is the actual thickness of the unit where loose-fill materials are: sand, pea gravel, crushed stone, or slag that meet ASTM C 33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders that comply with ASTM C 331; or perlite or vermiculite meeting the requirements of ASTM C 549 and ASTM C 516, respectively. | 722.3.1.4 Airspaces and cells filled with loose-fill material. | The equivalent thickness of completely filled hollow concrete masonry is the actual thickness of the unit where loose-fill materials are: sand, pea gravel, crushed stone, or slag that meet ASTM C33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders that comply with ASTM C331; or perlite or vermiculite meeting the requirements of ASTM C549 and ASTM C516, respectively.
722.3.2 Concrete masonry walls. | The fire-resistance rating of walls and partitions constructed of concrete masonry units shall be determined from Table 722.3.2. The rating shall be based on the equivalent thickness of the masonry and type of aggregate used. | 722.3.2 Concrete masonry walls. | The fire-resistance rating of walls and partitions constructed of concrete masonry units shall be determined from Table 722.3.2. The rating shall be based on the equivalent thickness of the masonry and type of aggregate used. |  | See BC07 Tables&Figures
722.3.2.1 Finish on nonfire-exposed side. | Where plaster or gypsum wallboard is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of gypsum wallboard or plaster shall be corrected by multiplying the actual thickness of the finish by applicable factor determined from Table 722.2.1.4(1). This corrected thickness of finish shall be added to the equivalent thickness of masonry and the fire-resistance rating of the masonry and finish determined from Table 722.3.2. | 722.3.2.1 Finish on nonfire-exposed side. | Where plaster or gypsum wallboard is applied to the side of the wall not exposed to fire, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The thickness of gypsum wallboard or plaster shall be corrected by multiplying the actual thickness of the finish by applicable factor determined from Table 722.2.1.4(1). This corrected thickness of finish shall be added to the equivalent thickness of masonry and the fire-resistance rating of the masonry and finish determined from Table 722.3.2. |  | See BC07 Tables&Figures
722.3.2.2 Finish on fire-exposed side. | Where plaster or gypsum wallboard is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table 722.2.1.4(2) shall be added to the fire-resistance rating determined in Section 722.3.2 for the masonry alone, or in Section 722.3.2.1 for the masonry and finish on the nonfire-exposed side. | 722.3.2.2 Finish on fire-exposed side. | Where plaster or gypsum wallboard is applied to the fire-exposed side of the wall, the contribution of the finish to the total fire-resistance rating shall be determined as follows: The time assigned to the finish as established by Table 722.2.1.4(2) shall be added to the fire-resistance rating determined in Section 722.3.2 for the masonry alone, or in Section 722.3.2.1 for the masonry and finish on the nonfire-exposed side. |  | See BC07 Tables&Figures
722.3.2.3 Nonsymmetrical assemblies. | For a wall having no finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values calculated. Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only. | 722.3.2.3 Nonsymmetrical assemblies. | For a wall without finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side of the wall to be the fire-exposed side. The fire-resistance rating of the wall shall not exceed the lower of the two values calculated. Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be as-sumed to occur on the interior side only.
722.3.2.4 Minimum concrete masonry fire-resistance rating. | Where the finish applied to a concrete masonry wall contributes to its fire-resistance rating, the masonry alone shall provide not less than one-half the total required fire-resistance rating. | 722.3.2.4 Minimum concrete masonry fire-resistance rating. | Where the finish applied to a concrete masonry wall contributes to its fire-resistance rating, the masonry alone shall provide not less than one-half the total required fire-resistance rating.
722.3.2.5 Attachment of finishes. | Installation of finishes shall be as follows: | 722.3.2.5 Attachment of finishes. | Installation of finishes shall be as follows:
722.3.4 Concrete masonry lintels. | Fire-resistance ratings for concrete masonry lintels shall be determined based upon the nominal thickness of the lintel and the minimum thickness of concrete masonry or concrete, or any combination thereof, covering the main reinforcing bars, as determined in accordance with Table 722.3.4, or by approved alternate methods. | 722.3.4 Concrete masonry lintels. | Fire-resistance ratings for concrete masonry lintels shall be determined based on the nominal thickness of the lintel and the minimum thickness of concrete masonry or concrete, or any combination thereof, covering the main reinforcing bars, as determined in accordance with Table 722.3.4, or by approved alternate methods. |  | See BC07 Tables&Figures
722.3.5 Concrete masonry columns. | The fire-resistance rating of concrete masonry columns shall be determined based upon the least plan dimension of the column in accordance with Table 722.3.5 or by approved alternate methods. | 722.3.5 Concrete masonry columns. | The fire-resistance rating of concrete masonry columns shall be determined based on the least plan dimension of the column in accordance with Table 722.3.5 or by approved alternate methods. |  | See BC07 Tables&Figures
722.4 Clay brick and tile masonry. | The provisions of this section contain procedures by which the fire-resistance ratings of clay brick and tile masonry are established by calculations. | 722.4 Clay brick and tile masonry. | The provisions of this section contain procedures by which the fire-resistance ratings of clay brick and tile masonry are established by calculations.
722.4.1 Masonry walls. | The fire-resistance rating of masonry walls shall be based upon the equivalent thickness as calculated in accordance with this section. The calculation shall take into account finishes applied to the wall and airspaces between wythes in multiwythe construction. | 722.4.1 Masonry walls. | The fire-resistance rating of masonry walls shall be based on the equivalent thickness as calculated in accordance with this section. The calculation shall take into account finishes applied to the wall and airspaces between wythes in multiwythe construction.
722.4.1.1 Equivalent thickness. | The fire-resistance ratings of walls or partitions constructed of solid or hollow clay masonry units shall be determined from Table 722.4.1(1) or 722.4.1(2). The equivalent thickness of the clay masonry unit shall be determined by Equation 7-8 where using Table 722.4.1(1). The fire-resistance rating determined from Table 722.4.1(1) shall be permitted to be used in the calculated fire-resistance rating procedure in Section 722.4.2. | 722.4.1.1 Equivalent thickness. | The fire-resistance ratings of walls or partitions constructed of solid or hollow clay masonry units shall be determined from Table 722.4.1(1) or Table 722.4.1(2). The equivalent thickness of the clay masonry unit shall be determined by Equation 7-8 where using Table 722.4.1(1). The fire-resistance rating determined from Table 722.4.1(1) shall be permitted to be used in the calculated fire-resistance rating procedure in Section 722.4.2. |  | See BC07 Tables&Figures
|  | 722.3.3 Multiwythe masonry walls. | The fire-resistance rating of wall assemblies constructed of multiple wythes of masonry materials shall be permitted to be based on the fire-resistance rating period of each wythe and the continuous airspace between each wythe in accordance with the following formula:
722.4.1.1.1 Hollow clay units. | The equivalent thickness, Te, shall be the value obtained for hollow clay units as determined in accordance with Equation 7-8. The net volume, Vn, of the units shall be determined using the gross volume and percentage of void area determined in accordance with ASTM C 67. | 722.4.1.1.1 Hollow clay units. | The equivalent thickness, Te, shall be the value obtained for hollow clay units as determined in accordance with Equation 7-8. The net volume, Vn, of the units shall be determined using the gross volume and percentage of void area determined in accordance with ASTM C67.
722.4.1.1.2 Solid grouted clay units. | The equivalent thickness of solid grouted clay masonry units shall be taken as the actual thickness of the units. | 722.4.1.1.2 Solid grouted clay units. | The equivalent thickness of solid grouted clay masonry units shall be taken as the actual thickness of the units.
722.4.1.1.3 Units with filled cores. | The equivalent thickness of the hollow clay masonry units is the actual thickness of the unit where completely filled with loose-fill materials of: sand, pea gravel, crushed stone, or slag that meet ASTM C 33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders in compliance with ASTM C 331; or perlite or vermiculite meeting the requirements of ASTM C 549 and ASTM C 516, respectively. | 722.4.1.1.3 Units with filled cores. | The equivalent thickness of the hollow clay masonry units is the actual thickness of the unit where completely filled with loose-fill materials of: sand, pea gravel, crushed stone, or slag that meet ASTM C33 requirements; pumice, scoria, expanded shale, expanded clay, expanded slate, expanded slag, expanded fly ash, or cinders in compliance with ASTM C331; or perlite or vermiculite meeting the requirements of ASTM C549 and ASTM C516, respectively.
722.4.1.2 Plaster finishes. | Where plaster is applied to the wall, the total fire-resistance rating shall be determined by the formula: | 722.4.1.2 Plaster finishes. | Where plaster is applied to the wall, the total fire-resistance rating shall be determined by the formula:
722.4.1.4 Nonsymmetrical assemblies. | For a wall having no finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side to be the fire-exposed side of the wall. The fire resistance of the wall shall not exceed the lower of the two values determined. Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be assumed to occur on the interior side only. | 722.4.1.4 Nonsymmetrical assemblies. | For a wall without finish on one side or having different types or thicknesses of finish on each side, the calculation procedures of this section shall be performed twice, assuming either side to be the fire-exposed side of the wall. The fire resistance of the wall shall not exceed the lower of the two values determined. Exception: For exterior walls with a fire separation distance greater than 5 feet (1524 mm), the fire shall be as-sumed to occur on the interior side only.
722.4.3 Reinforced clay masonry lintels. | Fire-resistance ratings for clay masonry lintels shall be determined based on the nominal width of the lintel and the minimum covering for the longitudinal reinforcement in accordance with Table 722.4.1(5). | 722.4.3 Reinforced clay masonry lintels. | Fire-resistance ratings for clay masonry lintels shall be determined based on the nominal width of the lintel and the minimum covering for the longitudinal reinforcement in accordance with Table 722.4.1(5). |  | See BC07 Tables&Figures
722.4.4 Reinforced clay masonry columns. | The fire-resistance ratings shall be determined based on the last plan dimension of the column in accordance with Table 722.4.1(6). The minimum cover for longitudinal reinforcement shall be 2 inches (50.8 mm). | 722.4.4 Reinforced clay masonry columns. | The fire-resistance ratings shall be determined based on the last plan dimension of the column in accordance with Table 722.4.1(6). The minimum cover for longitudinal reinforcement shall be 2 inches (51 mm). |  | See BC07 Tables&Figures
|  | 722.4.1.3 Multiwythe walls with airspace. | Where a continuous airspace separates multiple wythes of the wall or partition, the total fire-resistance rating shall be determined by the formula:
722.5 Steel assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of steel assemblies are established by calculations. | 722.5 Steel assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of steel assemblies are established by calculations.
722.5.1 Structural steel columns. | The fire-resistance ratings of structural steel columns shall be based on the size of the element and the type of protection provided in accordance with this section. | 722.5.1 Structural steel columns. | The fire-resistance ratings of structural steel columns shall be based on the size of the element and the type of protection provided in accordance with this section.
|  | 722.4.2 Multiwythe walls. | The fire-resistance rating for walls or partitions consisting of two or more dissimilar wythes shall be permitted to be determined by the formula:
|  | 722.4.2.1 Multiwythe walls of different material. | For walls that consist of two or more wythes of different materials (concrete or concrete masonry units) in combination with clay masonry units, the fire-resistance rating of the different materials shall be permitted to be determined from Table 722.2.1.1 for concrete; Table 722.3.2 for concrete masonry units or Table 722.4.1(1) or Table 722.4.1(2) for clay and tile masonry units. |  | See BC07 Tables&Figures
722.5.1.1 General. | These procedures establish a basis for determining the fire resistance of column assemblies as a function of the thickness of fire-resistant material and, the weight, W, and heated perimeter, D, of structural steel columns. As used in these sections, W is the average weight of a structural steel column in pounds per linear foot. The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure 722.5.1(1). | 722.5.1.1 General. | These procedures establish a basis for determining the fire resistance of column assemblies as a function of the thickness of fire-resistant material and, the weight, W, and heated perimeter, D, of structural steel columns. As used in these sections, W is the average weight of a structural steel column in pounds per linear foot. The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure 722.5.1(1).
722.5.1.1.1 Nonload-bearing protection. | The application of these procedures shall be limited to column assemblies in which the fire-resistant material is not designed to carry any of the load acting on the column. | 722.5.1.1.1 Nonload-bearing protection. | The application of these procedures shall be limited to column assemblies in which the fire-resistant material is not designed to carry any of the load acting on the column.
722.5.1.1.2 Embedments. | In the absence of substantiating fire-endurance test results, ducts, conduit, piping, and similar mechanical, electrical, and plumbing installations shall not be embedded in any required fire-resistant materials. | 722.5.1.1.2 Embedments. | In the absence of substantiating fire-endurance test results, ducts, conduit, piping, and similar mechanical, electrical, and plumbing installations shall not be embedded in any required fire-resistant materials.
722.5.1.1.3 Weight-to-perimeter ratio. | Table 722.5.1(1) contains weight-to-heated-perimeter ratios (W/D) for both contour and box fire-resistant profiles, for the wide flange shapes most often used as columns. For different fire-resistant protection profiles or column cross sections, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section. | 722.5.1.1.3 Weight-to-perimeter ratio. | Table 722.5.1(1) contains weight-to-heated-perimeter ratios (W/D) for both contour and box fire-resistant profiles, for the wide flange shapes most often used as columns. For different fire-resistant protection profiles or column cross sections, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section. |  | See BC07 Tables&Figures
722.5.1.2 Gypsum wallboard protection. | The fire resistance of structural steel columns with weight-to-heated-perimeter ratios (W/D) less than or equal to 3.65 and that are protected with Type X gypsum wallboard shall be permitted to be determined from the following expression: | 722.5.1.2 Gypsum wallboard protection. | The fire resistance of structural steel columns with weight-to-heated-perimeter ratios (W/D) less than or equal to 3.65 and that are protected with Type X gypsum wallboard shall be permitted to be determined from the following expression:
722.5.1.2.1 Attachment. | The gypsum board or gypsum panel products shall be supported as illustrated in either Figure 722.5.1(2) for fire-resistance ratings of 4 hours or less, or Figure 722.5.1(3) for fire-resistance ratings of 3 hours or less. | 722.5.1.2.1 Attachment. | The gypsum board or gypsum panel products shall be supported as illustrated in either Figure 722.5.1(2) for fire-resistance ratings of 4 hours or less, or Figure 722.5.1(3) for fire-resistance ratings of 3 hours or less.
722.5.1.2.2 Gypsum wallboard equivalent to concrete. | The determination of the fire resistance of structural steel columns from Figure 722.5.1(4) is permitted for various thicknesses of gypsum wallboard as a function of the weight-to-heated-perimeter ratio (W/D) of the column. For structural steel columns with weight-to-heated-perimeter ratios (W/D) greater than 3.65, the thickness of gypsum wallboard required for specified fire-resistance ratings shall be the same as the thickness determined for a W14 x 233 wide flange shape. | 722.5.1.2.2 Gypsum wallboard equivalent to concrete. | The determination of the fire resistance of structural steel columns from Figure 722.5.1(4) is permitted for various thicknesses of gypsum wallboard as a function of the weight-to-heated-perimeter ratio (W/D) of the column. For structural steel columns with weight-to-heated-perimeter ratios (W/D) greater than 3.65, the thickness of gypsum wallboard required for specified fire-resistance ratings shall be the same as the thickness determined for a W14 × 233 wide flange shape.
722.5.1.3.1 Material-dependent constants. | The material-dependent constants, C1and C2, shall be determined for specific fire-resistant materials on the basis of standard fire-resistance tests in accordance with Section 703.2. Unless evidence is submitted to the commissioner substantiating a broader application, this expression shall be limited to determining the fire resistance of structural steel columns with weight-to-heated-perimeter ratios (W/D) between the largest and smallest columns for which standard fire-resistance test results are available. | 722.5.1.3.1 Material-dependent constants. | The material-dependent constants, C1 and C2, shall be determined for specific fire-resistant materials on the basis of standard fire endurance tests in accordance with Section 703.2. Unless evidence is submitted to the building official substantiating a broader application, this expression shall be limited to determining the fire resistance of structural steel columns with weight-to-heated-perimeter ratios (W/D) between the largest and smallest columns for which standard fire-resistance test results are available.
722.5.1.3.2 Identification. | Spray-applied fire-resistant materials shall be identified by density and thickness required for a given fire-resistance rating. | 722.5.1.3.2 Identification. | Sprayed fire-resistant materials shall be identified by density and thickness required for a given fire-resistance rating.
722.5.1.4 Concrete-protected columns. | The fire resistance of structural steel columns protected with concrete, as illustrated in Figure 722.5.1(6)(a) and (b), shall be permitted to be determined from the following expression: | 722.5.1.4 Concrete-protected columns. | The fire resistance of structural steel columns protected with concrete, as illustrated in Figure 722.5.1(6) illustrations (a) and (b), shall be permitted to be determined from the following expression:
722.5.1.4.1 Reentrant space filled. | For wide-flange structural steel columns completely encased in concrete with all reentrant spaces filled (Figure 722.5.1(6)(c)), the thermal capacity of the concrete within the reentrant spaces shall be permitted to be added to the thermal capacity of the steel column, as follows: | 722.5.1.4.1 Reentrant space filled. | For wide-flange structural steel columns completely encased in concrete with all reentrant spaces filled Figure 722.5.1(6), illustration (c), the thermal capacity of the concrete within the reentrant spaces shall be permitted to be added to the thermal capacity of the steel column, as follows:
|  | 722.5.1.3 Sprayed fire-resistant materials. | The fire resistance of wide-flange structural steel columns protected with sprayed fire-resistant materials, as illustrated in Figure 722.5.1(5), shall be permitted to be determined from the following expression:
722.5.1.4.2 Concrete properties unknown. | If specific data on the properties of concrete are not available, the values given in Table 722.5.1(2) are permitted. | 722.5.1.4.2 Concrete properties unknown. | If specific data on the properties of concrete are not available, the values given in Table 722.5.1(2) are permitted. |  | See BC07 Tables&Figures
722.5.1.4.3 Minimum concrete cover. | For structural steel column encased in concrete with all reentrant spaces filled, Figure 722.5.1(6)(c) and Tables 722.5.1(7) and 722.5.1(8) indicate the thickness of concrete cover required for various fire-resistance ratings for typical wide-flange sections. The thicknesses of concrete indicated in these tables apply to structural steel columns larger than those listed. | 722.5.1.4.3 Minimum concrete cover. | For structural steel column encased in concrete with all reentrant spaces filled, Figure 722.5.1(6), illustration (c) and Tables 722.5.1(7) and 722.5.1(8) indicate the thickness of concrete cover required for various fire-resistance ratings for typical wide-flange sections. The thicknesses of concrete indicated in these tables apply to structural steel columns larger than those specified.
722.5.1.4.4 Minimum precast concrete cover. | For structural steel columns protected with precast concrete column covers as shown in Figure 722.5.1(6)(a), Tables 722.5.1(9) and 722.5.1(10) indicate the thickness of the column covers required for various fire-resistance ratings for typical wide-flange shapes. The thicknesses of concrete given in these tables apply to structural steel columns larger than those listed. | 722.5.1.4.4 Minimum precast concrete cover. | For structural steel columns protected with precast concrete column covers as shown in Figure 722.5.1(6), illustration (a), Tables 722.5.1(9) and 722.5.1(10) indicate the thickness of the column covers required for various fire-resistance ratings for typical wide-flange shapes. The thicknesses of concrete given in these tables apply to structural steel columns larger than those specified.
722.5.1.4.5 Masonry protection. | The fire resistance of structural steel columns protected with concrete masonry units or clay masonry units as illustrated in Figure 722.5.1(7), shall be permitted to be determined from the following expression: | 722.5.1.4.5 Masonry protection. | The fire resistance of structural steel columns protected with concrete masonry units or clay masonry units as illustrated in Figure 722.5.1(7) shall be permitted to be determined from the following expression:
722.5.1.4.6 Equivalent concrete masonry thickness. | For structural steel columns protected with concrete masonry, Table 722.5.1(5) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes. For structural steel columns protected with clay masonry, Table 722.5.1(6) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes. | 722.5.1.4.6 Equivalent concrete masonry thickness. | For structural steel columns protected with concrete masonry, Table 722.5.1(5) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes. For structural steel columns protected with clay masonry, Table 722.5.1(6) gives the equivalent thickness of concrete masonry required for various fire-resistance ratings for typical column shapes. |  | See BC07 Tables&Figures
722.5.2 Structural steel beams and girders. | The fire-resistance ratings of structural steel beams and girders shall be based upon the size of the element and the type of protection provided in accordance with this section. | 722.5.2 Structural steel beams and girders. | The fire-resistance ratings of structural steel beams and girders shall be based on the size of the element and the type of protection provided in accordance with this section.
722.5.2.1 Determination of fire resistance. | These procedures establish a basis for determining resistance of structural steel beams and girders that differ in size from that specified in approved fire-resistance-rated assemblies as a function of the thickness of fire-resistant material and the weight (W) and heated perimeter (D) of the beam or girder. As used in these sections, W is the average weight of a structural steel element in pounds per linear foot (plf). The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure 722.5.2. | 722.5.2.1 Determination of fire resistance. | These procedures establish a basis for determining resistance of structural steel beams and girders that differ in size from that specified in approved fire-resistance-rated assemblies as a function of the thickness of fire-resistant material and the weight (W) and heated perimeter (D) of the beam or girder. As used in these sections, W is the average weight of a structural steel element in pounds per linear foot (plf). The heated perimeter, D, is the inside perimeter of the fire-resistant material in inches as illustrated in Figure 722.5.2. |  | See BC07 Tables&Figures
722.5.2.1.1 Weight-to-heated perimeter. | The weight-to-heated-perimeter ratios (W/D), for both contour and box fire-resistant protection profiles, for the wide flange shapes most often used as beams or girders are given in Table 722.5.1(4). For different shapes, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section. | 722.5.2.1.1 Weight-to-heated perimeter. | The weight-to-heated-perimeter ratios (W/D), for both contour and box fire-resistant protection profiles, for the wide flange shapes most often used as beams or girders are given in Table 722.5.1(4). For different shapes, the weight-to-heated-perimeter ratios (W/D) shall be determined in accordance with the definitions given in this section. |  | See BC07 Tables&Figures
722.5.2.1.2 Beam and girder substitutions. | Except as provided for in Section 722.5.2.2, structural steel beams in approved fire-resistance-rated assemblies shall be considered the minimum permissible size. Other beam or girder shapes shall be permitted to be substituted provided that the weight-to-heated-perimeter ratio (W/D) of the substitute beam is equal to or greater than that of the beam specified in the approved assembly. | 722.5.2.1.2 Beam and girder substitutions. | Except as provided for in Section 722.5.2.2, structural steel beams in approved fire-resistance-rated assemblies shall be considered to be the minimum permissible size. Other beam or girder shapes shall be permitted to be substituted provided that the weight-to-heated-perimeter ratio (W/D) of the substitute beam is equal to or greater than that of the beam specified in the approved assembly.
722.5.2.2.1 Minimum thickness. | The use of Equation 7-17 is subject to the following conditions: | 722.5.2.2.1 Minimum thickness. | The use of Equation 7-17 is subject to the following conditions:
722.5.2.3 Structural steel trusses. | The fire resistance of structural steel trusses protected with fire-resistant mate­rials spray applied to each of the individual truss elements shall be permitted to be determined in accordance with this section. The thickness of the fire-resistant material shall be determined in accordance with Section 722.5.1.3. The weight-to-heated-perimeter ratio (W/D) of truss elements which can be simultaneously exposed to fire on all sides shall be determined on the same basis as columns, as specified in Section 722.5.1.1. The weight-to-heated-perimeter ratio (W/D) of truss ele­ments which directly support floor or roof assembly shall be determined on the same basis as beams and girders, as specified in Section 722.5.2.1. Exception: The fire resistance of structural steel trusses protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire-resistance tests in accordance with Section 703.2. | 722.5.2.3 Structural steel trusses.
722.6 Wood assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of wood assemblies are established by calculations. | 722.6 Wood assemblies. | The provisions of this section contain procedures by which the fire-resistance ratings of wood assemblies are established by calculations.
722.6.1 General. | This section contains procedures for calculating the fire-resistance ratings of walls, floor/ceiling and roof/ceiling assemblies based in part on the standard method of testing referenced in Section 703.2. | 722.6.1 General. | This section contains procedures for calculating the fire-resistance ratings of walls, floor/ceiling and roof/ceiling assemblies based in part on the standard method of testing referenced in Section 703.2.
|  | 722.5.2.2 Sprayed fire-resistant materials. | The provisions in this section apply to structural steel beams and girders protected with sprayed fire-resistant materials. Larger or smaller beam and girder shapes shall be permitted to be substituted for beams specified in approved unrestrained or restrained fire-resistance-rated assemblies, provided that the thickness of the fire-resistant material is adjusted in accordance with the following expression:
722.6.1.1 Maximum fire-resistance rating. | Fire-resistance ratings calculated for assemblies using the methods in Section 722.6 shall be limited to a maximum of 1 hour. | 722.6.1.1 Maximum fire-resistance rating. | Fire-resistance ratings calculated for assemblies using the methods in Section 722.6 shall be limited to not more than 1 hour.
722.6.1.2 Dissimilar membranes. | Where dissimilar membranes are used on a wall assembly that requires consideration of fire exposure from both sides, the calculation shall be made from the least fire-resistant (weaker) side. | 722.6.1.2 Dissimilar membranes. | Where dissimilar membranes are used on a wall assembly that requires consideration of fire exposure from both sides, the calculation shall be made from the least fire-resistant (weaker) side.
722.6.2 Walls, floors and roofs. | These procedures apply to both load-bearing and nonload-bearing assemblies. | 722.6.2 Walls, floors and roofs. | These procedures apply to both load-bearing and nonload-bearing assemblies.
722.6.2.1 Fire-resistance rating of wood frame assemblies. | The fire-resistance rating of a wood frame assembly is equal to the sum of the time assigned to the membrane on the fire-exposed side, the time assigned to the framing members and the time assigned for additional contribution by other protective measures such as insulation. The membrane on the unexposed side shall not be included in determining the fire resistance of the assembly. | 722.6.2.1 Fire-resistance rating of wood frame assemblies. | The fire-resistance rating of a wood frame assembly is equal to the sum of the time assigned to the membrane on the fire-exposed side, the time assigned to the framing members and the time assigned for additional contribution by other protective measures such as insulation. The membrane on the unexposed side shall not be included in determining the fire resistance of the assembly.
722.6.2.2 Time assigned to membranes. | Table 722.6.2(1) indicates the time assigned to membranes on the fire-exposed side. | 722.6.2.2 Time assigned to membranes. | Table 722.6.2(1) indicates the time assigned to membranes on the fire-exposed side. |  | See BC07 Tables&Figures
722.6.2.3 Exterior walls. | For an exterior wall with a fire separation distance greater than 5 feet (1524 mm), the wall is assigned a rating dependent on the interior membrane and the framing as described in Tables 722.6.2(1) and 722.6.2(2). The membrane on the outside of the nonfire-exposed side of exterior walls with a fire separation distance greater than 5 feet (1524 mm) shall consist of sheathing, sheathing paper and siding as described in Table 722.6.2(3). | 722.6.2.3 Exterior walls. | For an exterior wall with a fire separation distance greater than 10 feet (3048 mm), the wall is assigned a rating dependent on the interior membrane and the framing as described in Table 722.6.2(1) and Table 722.6.2(2). The membrane on the outside of the nonfire-exposed side of exterior walls with a fire separation distance greater than 10 feet (3048 mm) shall consist of sheathing, sheathing paper and siding as described in Table 722.6.2(3). |  | See BC07 Tables&Figures
722.6.2.4 Floors and roofs. | In the case of a floor or roof, the standard test provides only for testing for fire exposure from below. Except as noted in Section 703.3, Item 5, floor or roof assemblies of wood framing shall have an upper membrane consisting of a subfloor and finished floor conforming to Table 722.6.2(4) or any other membrane that has a contribution to fire resistance of not less than 15 minutes in Table 722.6.2(1). | 722.6.2.4 Floors and roofs. | In the case of a floor or roof, the standard test provides only for testing for fire exposure from below. Except as noted in Section 703.2.3, floor or roof assemblies of wood framing shall have an upper membrane consisting of a subfloor and finished floor conforming to Table 722.6.2(4) or any other membrane that has a contribution to fire resistance of not less than 15 minutes in Table 722.6.2(1). |  | See BC07 Tables&Figures
722.6.2.5 Additional protection. | Table 722.6.2(5) indicates the time increments to be added to the fire resistance where glass fiber, rock wool, slag mineral wool or cellulose insulation is incorporated in the assembly. | 722.6.2.5 Additional protection. | Table 722.6.2(5) indicates the time increments to be added to the fire resistance where glass fiber, rockwool, slag mineral wool or cellulose insulation is incorporated in the assembly. |  | See BC07 Tables&Figures
722.6.2.6 Fastening. | Fastening of wood frame assemblies and the fastening of membranes to the wood framing members shall be done in accordance with Chapter 23. | 722.6.2.6 Fastening. | Fastening of wood frame assemblies and the fastening of membranes to the wood framing members shall be done in accordance with Chapter 23.
|  | 722.7 Fire-resistance rating for mass timber. | The required fire resistance of mass timber elements in Section 602.4 shall be determined in accordance with Section 703.2. The fire-resistance rating of building elements shall be as required in Tables 601 and 705.5 and as specified elsewhere in this code. The fire-resistance rating of the mass timber elements shall consist of the fire resistance of the unprotected element added to the protection time of the noncombustible protection.
|  | 722.7.1 Minimum required protection. | Where required by Sections 602.4.1 through 602.4.3, noncombustible protection shall be provided for mass timber building elements in accordance with Table 722.7.1(1). The rating, in minutes, contributed by the noncombustible protection of mass timber building elements, components or assemblies, shall be established in accordance with Section 703.6. The protection contributions indicated in Table 722.7.1(2) shall be deemed to comply with this requirement where installed and fastened in accordance with Section 722.7.2. |  | See BC07 Tables&Figures
|  | 722.7.2 Installation of gypsum board noncombustible protection. | Gypsum board complying with Table 722.7.1(2) shall be installed in accordance with this section. |  | See BC07 Tables&Figures
|  | 722.7.2.1 Interior surfaces. | Layers of Type X gypsum board serving as noncombustible protection for interior surfaces of wall and ceiling assemblies determined in accordance with Table 722.7.1(1) shall be installed in accordance with the following: 1. Each layer shall be attached with Type S drywall screws of sufficient length to penetrate the mass timber at least 1 inch (25 mm) when driven flush with the paper surface of the gypsum board. Exception: The third layer, where determined necessary by Section 722.7, shall be permitted to be at-tached with 1-inch (25 mm) No. 6 Type S drywall screws to furring channels in accordance with AISI S220. 2. Screws for attaching the base layer shall be 12 inches (305 mm) on center in both directions. 3. Screws for each layer after the base layer shall be 12 inches (305 mm) on center in both directions and off-set from the screws of the previous layers by 4 inches (102 mm) in both directions. 4. All panel edges of any layer shall be offset 18 inches (457 mm) from those of the previous layer. 5. All panel edges shall be attached with screws sized and offset as in Items 1 through 4 and placed at least 1 inch (25 mm) but not more than 2 inches (51 mm) from the panel edge. 6. All panels installed at wall-to-ceiling intersections shall be installed such that ceiling panels are installed first and the wall panels are installed after the ceiling panel has been installed and is fitted tight to the ceil-ing panel. Where multiple layers are required, each layer shall repeat this process. 7. All panels installed at a wall-to-wall intersection shall be installed such that the panels covering an exterior wall or a wall with a greater fire-resistance rating shall be installed first and the panels covering the other wall shall be fitted tight to the panel covering the first wall. Where multiple layers are required, each layer shall repeat this process. 8. Panel edges of the face layer shall be taped and finished with joint compound. Fastener heads shall be cov-ered with joint compound. 9. Panel edges protecting mass timber elements adjacent to unprotected mass timber elements in accordance with Section 602.4.2.2 shall be covered with 11/4-inch (32 mm) metal corner bead and finished with joint compound. |  | See BC07 Tables&Figures
|  | 722.7.2.2 Exterior surfaces. | Layers of Type X gypsum board serving as noncombustible protection for the outside of the exterior mass timber walls determined in accordance with Table 722.7.1(1) shall be fastened 12 inches (305 mm) on center each way and 6 inches (152 mm) on center at all joints or ends. All panel edges shall be attached with fasteners located at least 1 inch (25 mm) but not more than 2 inches (51 mm) from the panel edge. Fasteners shall comply with one of the following: |  | See BC07 Tables&Figures
701.2 Multiple use fire assemblies. | Fire assemblies that serve multiple purposes in a building shall comply with all of the requirements that are applicable for each of the individual fire assemblies.
702.1 Definitions. | The following terms are defined in Chapter 2:
703.2 Fire-resistance ratings. | The fire-resistance rating of building elements, components or assemblies shall be determined in accordance with the test procedures set forth in ASTM E 119 or UL 263 or in accordance with Section 703.3. The fire-resistance rating of penetrations and fire-resistant joint systems shall be determined in accordance with Sections 714 and 715, respectively.
703.2.1 Nonsymmetrical wall construction. | Interior walls and partitions of nonsymmetrical construction shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests conducted in compliance with ASTM E 119 or UL 263. Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the commissioner, the wall need not be subjected to tests from the opposite side (see Section 705.5 of this code for exterior walls).
703.2.2 Combustible components. | Combustible aggre­gates may be integrated with other materials to form a noncombustible material provided that the entire mixture, in the form in which it is to be used in construction, meets the requirement of this code for noncombustible construction.
703.2.3 Restrained classification. | Fire-resistance-rated assemblies tested under ASTM E 119 or UL 263 shall not be considered to be restrained unless evidence satisfactory to the commissioner is furnished by the registered design professional showing that the construction qualifies for a restrained classification in accordance with ASTM E 119 or UL 263. Restrained construction shall be identified on the construction documents.
703.2.4 Supplemental features. | Where materials, systems or devices that have not been tested as part of a fire-resistance-rated assembly are incorporated into the building element component or assembly, sufficient data shall be made available to the commissioner to show that the required fire-resistance rating is not reduced. Materials and methods of construction used to protect joints and penetrations in fire-resistance-rated building elements, components or assemblies shall not reduce the required fire-resistance rating.
703.2.5 Exterior bearing walls. | In determining the fire-resistance rating of exterior bearing walls, compliance with the ASTM E 119 or UL 263 criteria for unexposed surface temperature rise and ignition of cotton waste due to passage of flame or gases is required only for a period of time corresponding to the required fire-resistance rating of an exterior nonbearing wall with the same fire separation distance, and in a building of the same group. Where the fire-resistance rating, determined in accordance with this section, exceeds the fire-resistance rating determined in accordance with ASTM E 119 or UL 263, the fire exposure time period, water pressure and application duration criteria for the hose stream test of ASTM E 119 or UL 263 shall be based on the fire-resistance rating determined in accordance with this section.
703.3 Methods for determining fire resistance. | The application of any of the methods listed in this section shall be based on the fire exposure and acceptance criteria specified in ASTM E 119 or UL 263. The required fire resistance of a building element, component or assembly shall be permitted to be established by any of the following methods or procedures:
703.4 Automatic sprinklers. | Under the prescriptive fire-resistance requirements of this code, the fire-resistance rating of a building element, component or assembly shall be established without the use of automatic sprinklers or any other fire suppression system being incorporated as part of the assembly tested in accordance with the fire exposure, procedures and acceptance criteria specified in ASTM E 119 or UL 263. However, this section shall not prohibit or limit the duties and powers of the commissioner as allowed by Sections 28-103.1.3 and 28-103.3 of Administrative Code.
703.5 Noncombustibility tests. | The tests indicated in Sections 703.5.1 and 703.5.2 shall serve as criteria for acceptance of building materials as set forth in Sections 602.2, 602.3 and 602.4 in Type I, II, III and IV construction. The term “noncombustible” does not apply to the flame spread characteristics of interior finish or trim materials. A material shall not be classified as a noncombustible building construction material if it is subject to an increase in combustibility or flame spread beyond the limitations herein established through the effects of age, fabrication or erection techniques, moisture or other atmospheric conditions.
703.5.1 Elementary materials. | Materials required to be noncombustible shall be tested in accordance with ASTM E 136.
703.5.2 Composite materials. | Materials having a structural base of noncombustible material as determined in accordance with Section 703.5.1 of this code with a surfacing not more than 0.125 inch (3.18 mm) thick that has a flame spread index not greater than 50 when tested in accordance with ASTM E 84 or UL 723 shall be acceptable as noncombustible materials.
703.6 Fire-resistance-rated glazing. | Fire-resistance-rated glazing, when tested in accordance with ASTM E 119 or UL 263 and complying with the requirements of Section 707 of this code, shall be permitted. Fire-resistance-rated glazing shall bear a label marked in accordance with Table 716.3 of this code and issued by an approved agency that shall be permanently identified on the glazing. |  |  |  | See BC07 Tables&Figures
703.7 Marking and identification. | Where there is a concealed floor, floor-ceiling or attic space, fire walls, fire barriers, fire partitions, smoke barriers and smoke partitions or any other wall required to have protected openings or penetrations shall be effectively and permanently identified with signs or stenciling in the concealed space. Such identification shall:
704.4 Protection of secondary members. | Secondary members that are required to have protection to achieve a fire-resistance rating shall be protected by individual encasement protection.
704.14 Fire retardant or intumescent coatings on mass timber. | Fire retardant or intumescent coatings shall not be used to achieve the required fire-resistance rating on structural elements composed of heavy timber members including, but not limited to, glued-laminated members, cross laminated timber (CLT) or structural composite lumber (SCL).
705.2.1 Type I and II construction. | Projections from walls, including balconies on the exterior of buildings of Type I or II construction shall be of noncombustible materials.
705.2.2.1 Exterior balconies and similar projections. | Exterior balconies and similar projections shall be permitted to be constructed of combustible materials provided that the exterior balcony or similar projection affords the fire-resistance rating required by Table 601 for floor construction. Exceptions: Balconies or similar projections serving as a required exit shall not be constructed of combustible materials. |  |  |  | See BC07 Tables&Figures
705.3 Buildings on the same tax lot. | For the purposes of determining the required wall and opening protection, projections and roof-covering requirements, buildings on the same tax lot shall be assumed to have an imaginary line between them. Exceptions: 1. Two or more buildings on the same tax lot shall be either regulated as separate buildings or shall be considered as portions of one building if the aggregate area of such buildings is within the limits specified in Chapter 5 for a single building. Where the buildings contain different occupancy groups or are of different types of construction, the area shall be that allowed for the most restrictive occupancy or construction. 2. Where an S-2 parking garage of Construction Type I or IIA is erected on the same lot as a Group R-2 building, and there is no fire separation distance between these buildings, then the adjoining exterior walls between the buildings are permitted to have occupant use openings in accordance with Section 706.8. However, opening protectives in such openings shall only be required in the exterior wall of the S-2 parking garage, not in the exterior wall openings in the R-2 building, and these opening protectives in the exterior wall of the S-2 parking garage shall be not less than 11/2-hour fire protection rating.
705.12 Portions of a building cantilevered over existing buildings. | Where a portion of a building is cantilevered over an adjacent building or tax lot by a horizontal distance greater than 1 foot (304.8 mm), the cantilevered portions shall be protected with construction that conforms to a fire engineering analysis acceptable to the commissioner that conforms to Section 705.12.1. In no case shall the protection for structural elements and horizontal assemblies be less than that required by the building type of construction. In no case shall the fire-resistance rating of exterior walls or any other cantilevered exterior surfaces be less than that required by the building type of construction, and in no case shall the limitations for openings on such exterior surfaces be less than that required for a lot line condition pursuant to Table 705.8, including footnote “m.” |  |  |  | See BC07 Tables&Figures
705.12.1 Analysis. | The analysis shall demonstrate that all portions of the building that cantilever will withstand the anticipated effects of a design fire in accordance with generally accepted fire engineering principles with respect to at least all of the following building elements:
705.12.1.1 Criteria. | With respect to the design fire within the existing building over which the proposed building is cantilevered, the analysis shall include a scenario to burn-out, where any active fire suppression systems do not operate, the fire department does not intervene, all interior vertical compartmentation, including at the entrances to the stairways, has been removed, and the fuel loading exceeds what is normally expected for the current occupancy by a factor of safety acceptable to the commissioner. Where there is no existing building below the cantilever, or where the existing building below the cantilever is significantly underbuilt, the commissioner may require additional data and analysis.
705.12.2 Fire Department access to buildings and roofs. | The applicant shall submit to the department an approval from the Fire Department that the proposed cantilever complies with applicable provisions of the New York City Fire Code with respect to access to buildings and roofs.
705.12.3 Fire protection peer review. | A fire protection peer review of the analysis required by Sections 705.12.1 and 705.12.1.1 shall be submitted to the department for each such analysis.
705.12.3.1. Fire protection peer reviewer. | The fire protection peer review shall be performed by a qualified independent fire protection engineer who has been retained by or on behalf of the owner. A fire protection peer reviewer shall meet the requirements of the rules of the department.
705.12.3.2 Extent of fire protection peer review. | The fire protection peer reviewer shall review the fire engineering analysis and construction documents relevant to the analysis for general compliance with the applicable provisions of this code.
705.12.3.3 Fire protection peer review report. | The fire protection peer reviewer shall submit a report to the department stating that the fire engineering analysis conforms to the requirements of this code without exception.
705.12.3.4 Responsibility. | The responsibility for the fire engineering analysis shall comply with Sections 705.12.3.4.1 and 705.12.3.4.2.
705.12.3.4.1 Applicant of record. | The architect or engineer submitting the fire engineering analysis shall retain responsibility for the fire engineering analysis. The activities and reports of the fire protection peer reviewer shall not relieve the applicant of record of this responsibility.
705.12.3.4.2 Fire protection peer reviewer. | The fire protection peer reviewer’s report shall state his or her opinion regarding the fire engineering analysis by the applicant of record.
706.1.2 Walls separating attached one- and two-family dwellings. | Attached one- and two-family dwellings shall be separated by walls constructed in accordance with Section 706 or Appendix M.
707.3.11 Public corridors. | The fire-resistance rating of public corridor walls shall comply with Table 1020.1.2. |  |  |  | See BC07 Tables&Figures
707.10.1 Prohibited ducts and air transfer openings. | Penetrations by ducts and air transfer openings into an enclosure for exit access stairways and ramps shall only be allowed when permitted by Sections 1023.4 and 1023.6.
709.4.1 Smoke-barrier walls separating smoke compartments. | Smoke-barrier walls used to separate smoke compartments shall form an effective membrane continuous from outside wall to outside wall.
709.8 Duct and air transfer openings. | Penetrations by duct and air transfer openings shall comply with Section 717.
710.5.2.2 Smoke and draft-control doors. | Where required elsewhere in the code, doors in smoke partitions shall meet the requirements for a smoke and draft control door assembly tested in accordance with UL 1784. The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot (0.015424 m3/s m2) of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature test and the elevated temperature exposure test. Installation of smoke doors shall be in accordance with NFPA 105.
710.5.2.3 Self-closing or automatic-closing doors. | Where required elsewhere in the code, doors in smoke partitions shall be self- or automatic-closing by smoke detection in accordance with Section 716.5.9.3.
711.2.1.1 Noncombustible materials. | Horizontal floor or roof assemblies shall be of noncombustible materials when such assemblies serve as horizontal offsets to fire walls or fire barriers required to be noncombustible.
711.2.6 Crawl spaces. | In 1-hour fire-resistance-rated floor/ceiling assemblies, the ceiling membrane is not required to be installed over crawl spaces that are not intended for occupancy or storage and that are less than 24 inches (609.6 mm) in height. Where the ceiling membrane is not provided, occupancy or storage is not permitted in the crawl space.
711.2.7 Attic spaces. | In 1-hour fire-resistance-rated roof assemblies, the floor membrane is not required to be installed where the attic space above the floor membrane is not intended for occupancy or storage. Where the floor membrane is not provided, occupancy or storage is not permitted in the attic space.
713.12 Enclosure at the top. | Shafts that do not extend to the top of the building or structure shall comply with one of the following:
713.12.1 Smoke venting of stair and other closed shafts. | All closed shafts, including vertical exit enclosures, having a floor area exceeding 4 square feet (0.37 m2) shall be provided with a smoke vent in accordance with Sections 713.12.1.1 through 713.12.1.3. Interior vertical exit shaft enclosures shall also comply with Chapter 10. Exceptions: 1. Elevator and dumbwaiter shafts in accordance with Chapter 30. 2. Interior exit stairways and ramps constructed as smokeproof enclosures in accordance with Section 1023.11.
713.12.1.1 Smoke vent construction. | Smoke vents may be constructed as windows, louvers, skylights, vent ducts, or similar devices, and shall be approved for such use. Where a vent duct is installed, such vent duct shall be enclosed by construction having the same fire-resistance rating as required for the shaft enclosure.
713.12.1.2 Smoke vent dimensions. | The effective venting area shall be not less than 3½ percent of the maximum shaft area at any floor, but in no event less than 72 square inches (46 451.5 mm2).
713.12.1.3 Smoke vent location. | Smoke vents shall be located in accordance with Section 713.12.1.3.1 or 713.12.1.3.2, as applicable.
713.12.1.3.1 Smoke vents located above the roof line. | Where a closed shaft or smoke vent duct penetrates through the roof of the building, the vent shall be approved for such use and located as follows:
713.12.1.3.2 Smoke vents located in an exterior wall. | Where a smoke vent is located in an exterior wall, openings in the wall are prohibited within an area 30 feet (9144 mm) vertically above the vent opening and 5 feet (1524 mm) horizontally on either side of the vent opening.
713.13 Waste and linen chutes, including discharge rooms, and incinerator rooms. | Waste and linen chutes, and discharge rooms for such chutes, shall comply with the provisions of NFPA 82, Chapter 6 of this code and shall meet the requirements of Sections 713.13.1 through 713.13.6 of this code. Incinerator rooms shall meet the provisions of Sections 713.13.4 through 713.13.5 of this code. Exception: Chutes serving and contained within a single dwelling unit.
713.13.1 Waste and linen. | A shaft enclosure containing a recycling, or waste or linen chute, and any associated discharge room, shall not be used for any other purpose and shall have a fire-resistance rating of 2 hours. Openings into the shaft, including those from access rooms and discharge rooms, shall be protected in accordance with this section and Section 716. Openings into chutes shall not be located in corridors. Doors into chutes shall be self-closing. Discharge doors shall be self- or automatic-closing upon the actuation of a smoke detector in accordance with Section 716.5.9.3, except that heat-activated closing devices shall be permitted between the shaft and the discharge room.
713.13.3 Waste and linen chute access rooms. | Access openings for waste and linen chutes shall be located in dedicated rooms or compartments enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711 or both. Openings into the access rooms shall be protected by opening protectives having a fire protection rating of not less than 11/2 hours. Doors to access rooms shall be self-closing, except where the storage of waste, including recyclables, or linen and other laundry, is not permitted in such access room, doors may be automatic-closing upon the detection of smoke in accordance with Section 716.5.9.3. Exception: Access openings for waste or linen chutes located within a dwelling unit need not be located within a separate room or compartment.
714.1.2 Special inspection. | All through-penetration and membrane-penetration firestop systems shall comply with the special inspection requirements of Chapter 17.
714.2 Installation details. | Where sleeves are used, they shall be securely fastened to the assembly penetrated. The space between the item contained in the sleeve and the sleeve itself and any space between the sleeve and the assembly penetrated shall be protected in accordance with this section. Insulation and coverings on or in the penetrating item shall not penetrate the assembly unless the specific material used has been tested as part of the assembly in accordance with this section.
714.3 Fire-resistance-rated walls. | Penetrations into or through fire walls, fire barriers, smoke barrier walls and fire partitions shall comply with Sections 714.3.1 through 714.3.3. Penetrations in smoke barrier walls shall also comply with Section 714.4.3.
714.3.1 Through-penetrations. | Through-penetrations of fire-resistance-rated walls shall comply with Section 714.3.1.1 or 714.3.1.2. Exception: Where the penetrating items are steel, ferrous or copper pipes, tubes or conduits, the annular space between the penetrating item and the fire-resistance-rated wall is permitted to be protected by either of the following measures:
714.3.1.1 Fire-resistance-rated assemblies. | Penetrations shall be installed as tested in an approved fire-resistance-rated assembly.
714.3.1.2 Through-penetration firestop system. | Through-penetrations shall be protected by an approved penetration firestop system installed as tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water and shall have an F rating of not less than the required fire-resistance rating of the wall penetrated.
714.3.2 Membrane penetrations. | Membrane penetrations shall be protected by a membrane penetration firestop installed in accordance with Section 714.3.1. Where walls or partitions are required to have a fire-resistance rating, recessed fixtures shall be installed such that the required fire resistance will not be reduced. Exceptions: 1. Membrane penetrations of maximum 2-hour fire-resistance-rated walls and partitions by steel electrical boxes that do not exceed 16 square inches (0.0103 m²) in area, provided the aggregate area of the openings does not exceed 100 square inches (0.0645 m²) for any 100 square feet (9.29 m²) of wall area. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.2 mm). Such boxes on opposite sides of the wall or partition shall be separated by one of the following: 1.1. By a horizontal distance of not less than 24 inches (609.6 mm) where the wall or partition is constructed with individual noncommunicating stud cavities; 1.2. By a horizontal distance of not less than the depth of the wall cavity where the wall cavity is filled with cellulose loose-fill, rock wool or slag mineral wool insulation; 1.3. By solid fireblocking in accordance with Section 718.2.1; 1.4. By protecting both outlet boxes with listed putty pads; or 1.5. By other listed materials and methods. 2. Membrane penetrations by listed electrical boxes of any material, provided such boxes have been tested for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. The annular space between the wall membrane and the box shall not exceed 1/8 inch (3.2 mm) unless listed otherwise. Such boxes on opposite sides of the wall or partition shall be separated by one of the following: 2.1. By the horizontal distance specified in the listing of the electrical boxes; 2.2. By solid fireblocking in accordance with Section 718.2.1; 2.3. By protecting both boxes with listed putty pads; or 2.4. By other listed materials and methods. 3. Membrane penetrations by electrical boxes of any size or type that have been listed as part of a wall opening protective material system for use in fire-resistance-rated assemblies and are installed in accordance with the instructions included in the listing. 4. Membrane penetrations by boxes other than electrical boxes, provided such penetrating items and the annular space between the wall membrane and the box, are protected by an approved membrane-penetration firestop system installed as tested in accordance with ASTM E 814 or UL 1479, with a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water, and shall have an F and T rating of not less than the required fire-resistance rating of the wall penetrated and be installed in accordance with their listing. 5. The annular space created by the penetration of an automatic sprinkler, provided it is covered by a metal escutcheon plate. 6. Membrane penetrations of maximum 2-hour fire resistance-rated walls and partitions by steel electrical boxes that exceed 16 square inches (0.0103 m²) in area, or steel electrical boxes of any size having an aggregate area through the membrane exceeding 100 square inches (0.0645 m²) in any 100 square feet (9.29 m²) of wall area, provided such penetrating items are protected by listed putty pads or other listed materials and methods, and installed in accordance with the listing.
714.3.3 Dissimilar materials. | Noncombustible penetrating items shall not connect to combustible items beyond the point of fire stopping unless it can be demonstrated to the commissioner that the fire-resistance integrity of the wall is maintained.
714.4 Horizontal assemblies. | Penetrations of a fire-resistance-rated floor, floor/ceiling assembly or the ceiling membrane of a roof/ceiling assembly not required to be enclosed in a shaft by Section 711.1 shall be protected in accordance with Sections 714.4.1 through 714.4.2.2.
714.4.1 Through-penetrations. | Through-penetrations of horizontal assemblies shall comply with Section 714.4.1.1 or 714.4.1.2. Exceptions: 1. Penetrations by steel, ferrous or copper conduits, pipes, tubes or vents or concrete or masonry items through a single fire-resistance-rated floor assembly where the annular space is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 or UL 263 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. Penetrating items with a maximum 6-inch (152.4 mm) nominal diameter shall not be limited to the penetration of a single fire-resistance-rated floor assembly, provided the aggregate area of the penetrations does not exceed 144 square inches (92 903 mm²) in any 100 square feet (9.3 m²) of floor area. 2. Penetrations in a single concrete floor by steel, ferrous or copper conduits, pipes, tubes or vents with a maximum 6-inch (152.4 mm) nominal diameter, provided that the concrete, grout or mortar is installed the full thickness of the floor or the thickness required to maintain the fire-resistance rating. The penetrating items shall not be limited to the penetration of a single concrete floor, provided the area of the opening through each floor does not exceed 144 square inches (92 903 mm²). 3. Penetrations by listed electrical boxes of any material, provided that such boxes have been tested for use in fire-resistance-rated assemblies and installed in accordance with the instructions included in the listing.
714.4.1.1 Installation. | Through-penetrations shall be installed as tested in the approved fire-resistance-rated assembly.
714.4.3 Penetrations in smoke barriers. | Penetrations in smoke barriers shall be protected by an approved through-penetration firestop system installed and tested in accordance with the requirements of UL 1479 for air leakage. The L rating of the system measured at 0.30 inch (7.47 Pa) of water in both the ambient temperature and elevated temperature tests shall not exceed:
714.5 Nonfire-resistance-rated assemblies. | Penetrations of nonfire-resistance-rated floor or floor/ceiling assemblies or the ceiling membrane of a nonfire-resistance-rated roof/ceiling assembly shall meet the requirements of Section 713 or shall comply with Section 714.5.1 or 714.5.2.
714.5.1 Noncombustible penetrating items. | Noncombustible penetrating items that connect not more than three stories are permitted, provided that the annular space is filled with an approved noncombustible material or with a fill, void or cavity material that is tested and classified for use in through-penetration firestop systems.
714.5.2 Penetrating items. | Penetrating items that connect not more than two stories are permitted, provided that the annular space is filled with an approved material to resist the free passage of flame and the products of combustion.
715.1.1 Curtain wall assembly. | The void created at the intersection of a floor/ceiling assembly and an exterior curtain wall assembly shall be protected in accordance with Section 715.4.
715.3 Fire test criteria. | Fire-resistant joint systems shall be tested in accordance with the requirements of either ASTM E 1966 or UL 2079. Nonsymmetrical wall joint systems shall be tested with both faces exposed to the furnace, and the assigned fire-resistance rating shall be the shortest duration obtained from the two tests. Where evidence is furnished to show that the wall was tested with the least fire-resistant side exposed to the furnace, subject to acceptance of the commissioner, the wall need not be subjected to tests from the opposite side. Exception: For exterior walls with a horizontal fire separation distance greater than 5 feet (1524 mm), the joint system shall be required to be tested for interior fire exposure only.
715.4 Exterior curtain wall/floor intersection. | Where fire resistance-rated floor or floor/ceiling assemblies are required, voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies shall be sealed with an approved system to prevent the interior spread of fire. Such systems shall be securely installed and tested in accordance with ASTM E 2307 to provide an F rating for a time period not less than the fire-resistance rating of the floor assembly. Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 705.8.5. Exception: Voids created at the intersection of the exterior curtain wall assemblies and such floor assemblies where the vision glass extends to the finished floor level shall be permitted to be sealed with an approved material to prevent the interior spread of fire. Such material shall be securely installed and capable of preventing the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 time-temperature fire conditions under a minimum positive pressure differential of 0.01 inch (0.254 mm) of water column (2.5 Pa) for the time period not less than the fire-resistance rating of the floor assembly.
715.4.1 Exterior curtain wall/nonfire-resistance-rated floor assembly intersections. | Voids created at the intersection of exterior curtain wall assemblies and nonfire-resistance-rated floor or floor/ceiling assemblies shall be sealed with an approved material or system to retard the interior spread of fire and hot gases between stories.
715.4.2 Exterior curtain wall/vertical fire barrier intersections. | Voids created at the intersection of nonfire-resistance-rated exterior curtain wall assemblies and fire barriers shall be filled. An approved material or system shall be used to fill the void and shall be securely installed in or on the intersection for its entire length so as not to dislodge, loosen or otherwise impair its ability to accommodate expected building movements and to retard the passage of fire and hot gases.
715.5 Spandrel wall. | Height and fire-resistance requirements for curtain wall spandrels shall comply with Section 705.8.5. Where Section 705.8.5 does not require a fire-resistance-rated spandrel wall, the requirements of Section 715.4 shall still apply to the intersection between the spandrel wall and the floor.
715.6 Fire-resistant joint systems in smoke barriers. | Fire-resistant joint systems in smoke barriers, and joints at the intersection of a horizontal smoke barrier and an exterior curtain wall, shall be tested in accordance with the requirements of UL 2079 for air leakage. The L rating of the joint system shall not exceed 5 cfm per linear foot (0.00775 m3/s m) of joint at 0.30 inch (7.47 Pa) of water for both the ambient temperature and elevated temperature tests.
716.2 Fire-resistance-rated glazing. | Fire-resistance-rated glazing tested as part of a fire-resistance-rated wall or floor/ceiling assembly in accordance with ASTM E 119 or UL 263 and labeled in accordance with Section 703.6 shall not otherwise be required to comply with this section where used as part of a wall or floor/ceiling assembly. Fire-resistance-rated glazing shall be permitted in fire door and fire window assemblies where tested and installed in accordance with their listings and where in compliance with the requirements of this section.
716.3 Marking fire-rated glazing assemblies. | Fire-rated glazing assemblies shall be marked in accordance with Tables 716.3, 716.5 and 716.6.
716.3.1 Fire-rated glazing identification. | For fire-rated glazing, the label shall bear the identification required in Tables 716.3 and 716.5. “D” indicates that the glazing is permitted to be used in fire door assemblies and that the glazing meets the fire protection requirements of NFPA 252. “H” shall indicate that the glazing meets the hose stream requirements of NFPA 252. “T” shall indicate that the glazing meets the temperature requirements of Section 716.5.5.1. The placeholder “XXX” represents the fire-rating period, in minutes.
716.3.2 Fire-protection-rated glazing identification. | For fire-protection-rated glazing, the label shall bear the following identification required in Tables 716.3 and 716.6: “OH – XXX.” “OH” indicates that the glazing meets both the fire protection and the hose-stream requirements of NFPA 257 or UL 9 and is permitted to be used in fire window openings. The placeholder “XXX” represents the fire-rating period, in minutes.
716.3.3 Fire-rated glazing that exceeds the code requirements. | Fire-rated glazing assemblies marked as complying with hose stream requirements (H) shall be permitted in applications that do not require compliance with hose stream requirements. Fire-rated glazing assemblies marked as complying with temperature rise requirements (T) shall be permitted in applications that do not require compliance with temperature rise requirements. Fire-rated glazing assemblies marked with ratings (XXX) that exceed the ratings required by this code shall be permitted.
716.4 Alternative methods for determining fire protection ratings. | The application of any of the alternative methods listed in this section shall be based on the fire exposure and acceptance criteria specified in NFPA 252, NFPA 257 or UL 9. The required fire resistance of an opening protective shall be permitted to be established by any of the following methods or procedures:
716.5 Fire door and shutter assemblies. | Approved fire door and fire shutter assemblies shall be constructed of any material or assembly of component materials that conforms to the test requirements of Section 716.5.1, 716.5.2 or 716.5.3 and the fire protection rating indicated in Table 716.5. Fire door frames with transom lights, sidelights or both shall be permitted in accordance with Section 716.5.6. Fire door assemblies and shutters shall be installed in accordance with the provisions of this section and NFPA 80. Exceptions: 1. Labeled protective assemblies that conform to the requirements of this section or UL 10A, UL 14B and UL 14C for tin-clad fire door assemblies. 2. Floor fire door assemblies in accordance with Section 712.1.13.1. |  |  |  | See BC07 Tables&Figures
716.5.1 Side-hinged or pivoted swinging doors. | Fire door assemblies with side-hinged and pivoted swinging doors shall be tested in accordance with NFPA 252 or UL 10C. After 5 minutes into the NFPA 252 test, the neutral pressure level in the furnace shall be established at 40 inches (1016 mm) or less above the sill.
716.5.2 Other types of assemblies. | Fire door assemblies with other types of doors, including swinging elevator doors, horizontal sliding fire door assemblies, and fire shutter assemblies, bottom and side-hinged chute intake doors, and top-hinged chute discharge doors, shall be tested in accordance with NFPA 252 or UL 10B. The pressure in the furnace shall be maintained as nearly equal to the atmospheric pressure as possible. Once established, the pressure shall be maintained during the entire test period.
716.5.3 Door assemblies in corridors and smoke barriers. | Fire door assemblies located in corridor walls or smoke barrier walls having a fire-resistance rating in accordance with Table 716.5 shall be tested in accordance with NFPA 252 or UL 10C. Exceptions: 1. Viewports that require a hole not larger than 1 inch (25.4 mm) in diameter through the door, have not less than a 0.25-inch (6.4 mm) thick glass disc and the holder is of metal that will not melt out where subject to temperatures of 1,700°F (926.7°C). 2. Corridor door assemblies in occupancies of Group I-2 shall be in accordance with Section 407.3.1. 3. Horizontal sliding doors in smoke barriers that comply with Sections 408.6 and 408.8.4 in occupancies in Group I-3. |  |  |  | See BC07 Tables&Figures
716.5.3.1 Smoke and draft control. | Fire door assemblies shall meet the requirements for a smoke and draft control door assembly tested in accordance with UL 1784. The air leakage rate of the door assembly shall not exceed 3.0 cubic feet per minute per square foot (0.01524 m3/s • m2) of door opening at 0.10 inch (24.9 Pa) of water for both the ambient temperature and elevated temperature tests. Louvers shall be prohibited. Installation of smoke doors shall be in accordance with NFPA 105.
716.5.3.2 Glazing in door assemblies. | Glazing material in any other part of the door assembly, including transom lights and sidelights, shall be tested in accordance with NFPA 257 or UL 9, including the hose stream test, in accordance with Section 716.6 of this code.
716.5.4 Reserved.
716.5.5 Doors in interior exit stairways and ramps and exit passageways. | Fire door assemblies in interior exit stairways and ramps and exit passageways shall have a maximum transmitted temperature rise of not more than 450°F (232.2°C) above ambient at the end of 30 minutes of standard fire test exposure. Exception: The maximum transmitted temperature is not required in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2.
716.5.5.1 Glazing in doors. | Fire-protection-rated glazing in excess of 100 square inches (0.065 m2) is not permitted. Fire-resistance-rated glazing in excess of 100 square inches (64 516 mm2) shall be permitted in fire doors. Listed fire-resistance-rated glazing in a fire door shall have a maximum transmitted temperature rise in accordance with Section 716.5.5 of this code when the fire door is tested in accordance with NFPA 252, UL 10B or UL 10C.
716.5.6 Fire door frames with transom lights and sidelights. | Door frames with transom lights, sidelights or both, shall be permitted where a 3/4-hour fire protection rating or less is required in accordance with Table 716.5. Fire door frames with transom lights, sidelights, or both, installed with fire-resistance-rated glazing tested as an assembly in accordance with ASTM E 119 or UL 263 shall be permitted where a fire protection rating exceeding 3/4 hour is required in accordance with Table 716.5 of this code. |  |  |  | See BC07 Tables&Figures
716.5.7 Labeled protective assemblies. | Fire door assemblies shall be labeled by an approved agency. The labels shall comply with NFPA 80, and shall be permanently affixed to the door or frame.
716.5.7.1 Fire door labeling requirements. | Fire doors shall be labeled showing the name of the manufacturer or other identification readily traceable back to the manufacturer, the name or trademark of the third-party inspection agency, the fire protection rating and, where required for fire doors in interior exit stairways and ramps and exit passageways by Section 716.5.5, the maximum transmitted temperature end point. Smoke and draft control doors complying with UL 1784 shall be labeled as such and shall comply with Section 716.5.7. Labels shall be approved and permanently affixed. The label shall be applied at the factory or location where fabrication and assembly are performed.
716.5.7.1.1 Vision light kits, louvers and components. | Listed vision light kits and louvers and their required preparations shall be considered as part of the labeled door where such installations are listed and where quality assurance testing is done under the listing program of the third-party testing agency. Fire doors and door assemblies shall be permitted to consist of components, including glazing, vision light kits and hardware that are listed or classified and labeled for such use by different third-party agencies.
716.5.7.2 Oversized doors. | Oversized fire doors shall bear an oversized fire door label by an approved agency or shall be provided with a certificate of inspection furnished by an approved testing agency. Where a certificate of inspection is furnished by an approved testing agency, the certificate shall state that the door conforms to the requirements of design, materials and construction, but has not been subjected to the fire test.
716.5.7.3 Smoke and draft control door labeling requirements. | Smoke and draft control doors complying with UL 1784 shall be labeled in accordance with Section 716.5.7.1 and shall show the letter “S” on the fire rating label of the door. This marking shall indicate that the door and frame assembly are in compliance where listed or labeled gasketing is installed.
716.5.7.4 Fire door frame labeling requirements. | Fire door frames shall be labeled showing the names of the manufacturer and the third-party inspection agency.
716.5.7.5 Fire door operator labeling requirements. | Fire door operators for horizontal sliding doors shall be labeled and listed for use with the assembly.
716.5.8 Glazing material. | Fire-rated glazing and fire-resistance-rated glazing conforming to the opening protection requirements in Section 716.5 shall be permitted in fire door assemblies.
716.5.8.1 Size limitations. | Fire-resistance-rated glazing shall comply with the size limitations in Section 716.5.8.1.1. Fire-protection-rated glazing shall comply with the size limitations of NFPA 80, and as provided in Section 716.5.8.1.2.
716.5.8.1.1 Fire-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. | Fire-rated glazing tested to ASTM E 119 or UL 263 and NFPA 252, UL 10B or UL 10C shall be permitted in fire door assemblies located in fire walls and in fire barriers in accordance with Table 716.5 of this code to the maximum size tested and in accordance with their listings. |  |  |  | See BC07 Tables&Figures
716.5.8.1.2 Fire-protection-rated glazing in door assemblies in fire walls and fire barriers rated greater than 1 hour. | Fire-rated glazing shall be prohibited in fire walls and fire barriers except as provided in Sections 716.5.8.1.2.1 and 716.5.8.1.2.2.
716.5.8.1.2.1 Horizontal exits. | Fire-protection-rated glazing shall be permitted as vision panels in self-closing swinging fire door assemblies serving as horizontal exits in fire walls where limited to 100 square inches (64 516 mm2) with no dimension exceed­ing 10 inches (254 mm).
716.5.8.1.2.2 Fire barriers. | Fire-rated glazing shall be permitted in fire doors having a 11/2-hour fire protection rating intended for installation in fire barriers, where limited to 100 square inches (64 516 mm2).
716.5.8.2 Elevator, stairway and ramp protectives. | Approved fire-rated glazing used in fire door assemblies in elevator, stairway and ramp enclosures shall be so located as to furnish clear vision of the passageway or approach to the elevator, stairway or ramp.
716.5.8.3 Labeling. | Fire-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard and information required in Table 716.3 that shall be issued by an approved agency and shall be permanently identified on the glazing. |  |  |  | See BC07 Tables&Figures
716.5.8.4 Safety glazing. | Fire-rated glazing installed in fire door assemblies shall comply with the safety glazing requirements of Chapter 24 where applicable.
716.5.9 Door closing. | Fire doors shall be latching and self- or automatic-closing in accordance with this section. Exceptions: 1. Fire doors located in common walls separating sleeping units in Group R-1 shall be permitted without or self- or automatic-closing devices. 2. The elevator car doors and the associated hoistway enclosure doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I emergency recall operation.
716.5.9.1 Latch required. | Unless otherwise specifically permitted, single fire doors and both leaves of pairs of side-hinged swinging fire doors shall be provided with an active latch bolt that will secure the door when it is closed.
716.5.9.1.1 Chute intake door latching. | Chute intake doors shall be positive latching, remaining latched and closed in the event of latch spring failure during a fire emergency.
716.5.9.2 Automatic-closing fire door assemblies. | Automatic-closing fire door assemblies shall be self-closing in accordance with NFPA 80.
716.5.9.3 Smoke-activated doors. | Automatic-closing fire doors installed in the following locations shall be automatic-closing by the actuation of smoke detectors installed in accordance with Section 907.3 or by loss of power to the smoke detector where such detector is powered by the building’s normal electrical service or by loss of power to the hold-open device. Doors that are automatic-closing by smoke detection shall not have more than a 10-second delay before the door starts to close after the smoke detector is actuated.
716.5.9.4 Doors in pedestrian ways. | Vertical sliding or vertical rolling steel fire doors in openings through which pedestrian’s travel shall be heat activated or activated by smoke detectors with alarm verification.
716.5.10 Swinging fire shutters. | Where fire shutters of the swinging type are installed in exterior openings, not less than one row in every three vertical rows shall be arranged to be readily opened from the outside, and shall be identified by distinguishing marks or letters not less than 6 inches (152.4 mm) high.
716.5.11 Rolling fire shutters. | Where fire shutters of the rolling type are installed, such shutters shall include approved automatic-closing devices.
716.6 Fire-protection-rated glazing. | Glazing in fire window assemblies shall be fire protection rated in accordance with this section and Table 716.6. Glazing in fire door assemblies shall comply with Section 716.5.8. Fire-protection-rated glazing in fire window assemblies shall be tested in accordance with and shall meet the acceptance criteria of NFPA 257 or UL 9. Fire-protection-rated glazing shall comply with NFPA 80. Openings in nonfire-resistance-rated exterior wall assemblies that require protection in accordance with Section 705.3, 705.8, 705.8.5 or 705.8.6 shall have a fire protection rating of not less than ¾ hour. |  |  |  | See BC07 Tables&Figures
716.6.1 Testing under positive pressure. | NFPA 257 or UL 9 shall evaluate fire-protection-rated glazing under positive pressure. Within the first 10 minutes of a test, the pressure in the furnace shall be adjusted so not less than two-thirds of the test specimen is above the neutral pressure plane, and the neutral pressure plane shall be maintained at that height for the balance of the test.
716.6.2 Nonsymmetrical glazing systems. | Nonsymmetrical fire-protection-rated glazing systems in fire partitions, fire barriers or in exterior walls with a fire separation distance of 5 feet (1524 mm) or less pursuant to Section 705 shall be tested with both faces exposed to the furnace, and the assigned fire protection rating shall be the shortest duration obtained from the two tests conducted in compliance with NFPA 257 or UL 9.
716.6.3 Safety glazing. | Fire-protection-rated glazing and fire-resistance-rated glazing installed in fire window assemblies shall comply with the safety glazing requirements of Chapter 24 where applicable.
716.6.4 Glass and glazing. | Glazing in fire window assemblies shall be fire-protection-rated glazing installed in accordance with and complying with the size limitations set forth in NFPA 80.
716.6.5 Installation. | Fire-protection-rated glazing shall be in the fixed position or be automatic-closing and shall be installed in approved frames.
716.6.6 Window mullions. | Metal mullions that exceed a nominal height of 12 feet (3658 mm) shall be protected with materials to afford the same fire-resistance rating as required for the wall construction in which the protective is located.
716.6.7 Interior fire window assemblies. | Fire-protection-rated glazing used in fire window assemblies located in fire partitions and fire barriers shall be limited to use in assemblies with a maximum fire-resistance rating of 1 hour in accordance with this section.
716.6.7.1 Where 3/4-hour fire protection window assemblies permitted. | Fire-protection-rated glazing requiring 45-minute opening protection in accordance with Table 716.6 shall be limited to fire partitions designed in accordance with Section 708 and fire barriers utilized in the applications set forth in Sections 707.3.6, 707.3.7 and 707.3.9 where the fire-resistance rating does not exceed 1 hour. Fire-resistance-rated glazing assemblies tested in accordance with ASTM E 119 or UL 263 shall not be subject to the limitations of this section. |  |  |  | See BC07 Tables&Figures
716.6.7.2 Area limitations. | The total area of the glazing in fire-protection-rated window assemblies shall not exceed 25 percent of the area of a common wall with any room.
716.6.8 Labeling requirements. | Fire-protection-rated glazing shall bear a label or other identification showing the name of the manufacturer, the test standard and information required in Section 716.3.2 and Table 716.6 that shall be issued by an approved agency and permanently identified on the glazing. |  |  |  | See BC07 Tables&Figures
717.2.1.1 Remote control. | Provisions for operation by remote control of combination fire/smoke dampers shall be in accordance with Section 607.2.1.1 of the New York City Mechanical Code.
717.2.3 Supply air systems. | Smoke dampers in supply airhandling systems having a capacity equal to or greater than 15,000 cfm (7.1 m3/s) shall be installed in accordance with Section 607.2.3 of the New York City Mechanical Code.
717.3.3.1 Fire damper actuation device. | The fire damper actuation device shall meet one of the following requirements:
717.5.2.2 Public corridors. | A listed smoke damper designed to resist the passage of smoke shall be provided at each point a duct or air transfer opening penetrates a public corridor wall or floor constructed as a fire barrier. Exceptions: 1. Smoke dampers are not required where the building is equipped throughout with an engineered smoke control system in accordance with Section 909, and smoke dampers are not necessary for the operation and control of the system. 2. Smoke dampers are not required in corridor penetrations where the duct is constructed of steel not less than 0.019-inch (0.48 mm) in thickness and there are no openings serving the corridor. 3. Smoke dampers are not required in corridor penetrations in Group R-2 buildings and Public Corridors serving R-2 spaces in mixed use buildings. 4. Smoke dampers shall not be required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air under fire emergency conditions. The air-handling system shall be continuously monitored to ensure continuous airflow at a constantly attended location and be inspected and maintained in accordance with the system manufacturer’s instructions.
717.5.3.1 Limitations. | Shafts that constitute air ducts shall be limited in accordance with Section 607.5.5.2 of the New York City Mechanical Code. Exceptions: 1. Fire dampers are not required at penetrations of shafts where any of the following criteria are met: 1.1. In buildings equipped throughout with an automatic sprinkler system in accordance with Chapter 9, steel exhaust subducts having minimum thickness of 0.0187 inch (0.4712 mm) (No. 26 gage) extend not less than 22 inches (558.8 mm) vertically in exhaust shafts provided that there is a continuous airflow upward to the outdoors whenever the building is occupied. 1.2. Penetrations are tested in accordance with ASTM E 119 or UL 263 as part of the fire-resistance-rated assembly. 1.3. Ducts are used as part of an approved smoke control system designed and installed in accordance with Section 909 and where the fire damper will interfere with the operation of the smoke control system. 1.4. The penetrations are in parking garage exhaust or supply shafts that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction. 2. Smoke dampers are not required in exhaust ducts or shafts where the exhaust fan is maintained in operation whenever the building is occupied, in bathrooms and toilet room exhausts. 3. Smoke dampers are not required at penetrations of exhaust or supply shafts in parking garages that are separated from other building shafts by not less than 2-hour fire-resistance-rated construction. 4. Smoke dampers are not required at penetrations of shafts where ducts are used as part of an engineered mechanical smoke control system designed in accordance with Section 909 and where the smoke damper will interfere with the operation of the smoke control system. 5. Fire dampers and/or smoke dampers are not required at a shaft where the shaft is acting as an extension of the mechanical equipment room that it serves and the shaft and mechanical equipment room maintain fire and smoke sepa¬ration required by the greater of the two spaces from the occupied portions of the building and meet the requirements of Sections 713.11 and 713.12. 6. Smoke dampers are not required to be located within a prescribed distance of a fire-rated enclosure within which the air handling equipment is located and where isolation smoke dampers are used in air-handling equipment in accordance with Section 607.2.3 of the New York City Mechanical Code. 7. Smoke dampers are not required in ducts where the air continues to move and the air-handling system installed is arranged to prevent recirculation of exhaust or return air during a fire emergency condition. Such fans shall be provided with standby power in accordance with Chapter 27.
717.6.1 Through-penetrations. | In occupancies other than Groups I-2 and I-3, a duct and air transfer opening system constructed of approved materials in accordance with the New York City Mechanical Code that penetrates a fire-resistance-rated floor/ceiling assembly that connects not more than two stories is permitted without shaft enclosure protection, provided a listed fire damper is installed at the floor line or the duct is protected in accordance with Section 714.4. For air transfer openings, see Section 712.1.9. Exception: A duct serving a dwelling unit is permitted to penetrate three floors or less without a fire damper at each floor, provided such duct meets all of the following requirements: 1. The duct shall be contained and located within the cavity of a wall and shall be constructed of steel having a minimum wall thickness of 0.0187 inches (0.4749 mm) (No. 26 gage). 2. The duct shall open into only one dwelling or sleeping unit and the duct system shall be continuous from the unit to the exterior of the building. 3. The duct shall not exceed 5-inch (127 mm) nominal diameter and the total area of such ducts shall not exceed 100 square inches (0.065 m2) in any 100 square feet (9.3 m2) of floor area. 4. The annular space around the duct is protected with materials that prevent the passage of flame and hot gases sufficient to ignite cotton waste where subjected to ASTM E 119 or UL 263 time-temperature conditions under a minimum positive pressure differential of 0.01 inch (2.49 Pa) of water at the location of the penetration for the time period equivalent to the fire-resistance rating of the construction penetrated. 5. Grille openings located in a ceiling of a fire-resistance-rated floor/ceiling or roof/ceiling assembly shall be protected with a listed ceiling radiation damper installed in accordance with Section 717.6.2.1 of this code.
717.6.2.1 Ceiling radiation dampers. | Ceiling radiation dampers shall be tested in accordance with Section 717.3.1. Ceiling radiation dampers shall be installed in accordance with the details listed in the fire-resistance-rated assembly and the manufacturer’s instructions and the listing. Ceiling radiation dampers are not required where one of the following applies:
718.2.6 Architectural trim. | Fireblocking shall be installed within concealed spaces of exterior wall coverings and other exterior architectural elements where permitted to be of combustible construction as specified in Section 1406 or where erected with combustible frames, at maximum intervals of 20 feet (6096 mm) so that there will be no open space exceeding 100 square feet (9.3 m2). Where wood furring strips are used, they shall be of approved wood of natural decay resistance or preservative-treated wood. If non-continuous, such elements shall have closed ends, with at least 4 inches (101.6 mm) of separation between sections. For the purposes of this section, fenestration products, and flashing of fenestration products and water-resistive barrier flashing and accessories at other locations, including through wall flashings and attachment accessories, shall not be considered combustible construction. Exceptions: 1. Fireblocking of cornices is not required in single-family dwellings. Fireblocking of cornices of a two-family dwelling is required only at the line of dwelling unit separation. 2. Fireblocking shall not be required where the exterior wall covering does not contain plastic or foam plastic insulation, is installed on noncombustible framing and the exterior wall covering is one of the following materials: 2.1. Aluminum siding having a minimum thickness of 0.019 inch (0.5 mm). 2.2. Corrosion‐resistant steel siding not less than 0.016 inch (0.4 mm) at any point. 2.3.‡ Walls in which the water-resistive barrier is the only combustible component and the exterior wall has a wall covering of brick, concrete, stone, terra cotta, stucco or steel with minimum thicknesses in accordance with Table 1405.2. 3. Exterior wall coverings containing plastics, metal composite materials (MCM) or high-pressure decorative exterior-grade compact laminates (HPL) panels shall comply with Section 718.2.6.1. |  |  |  | See BC07 Tables&Figures
718.2.6.1 Exterior wall coverings containing plastics, metal composite materials (MCM) or high-pressure decorative exterior-grade compact laminates (HPL) panels. | Exterior wall coverings containing plastics complying with Chapter 26, metal composite materials (MCM) or high-pressure decorative exterior-grade compact laminates (HPL), shall be fireblocked.
718.2.6.1.1 Locations. | Noncombustible fireblocking materials shall be required at all of the following locations to cut off concealed spaces within the exterior wall covering:
718.2.6.1.2 Foam plastic insulation. | Foam plastic insulation in the exterior wall covering shall be interrupted with noncombustible materials approved for fireblocking at locations specified in Section 718.2.6.1.1. Exceptions: 1. One-story buildings complying with Section 2603.4.1.4. 2. Fireblocking shall not be required at each floor level and interrupt the foam plastic insulation provided the foam plastic insulation has a flame spread index of not more than 25 as determined in accordance with ASTM E 84 or UL 723 and comply with the following conditions: 2.1. Concrete and masonry veneer. Fireblocking material shall not be required at each floor level for concrete or masonry veneer installed less than 75 feet (22 860 mm) above grade as part of an exterior wall covering containing foam plastic insulation, with or without air space, and installed on masonry or concrete backup walls. 2.2. Exterior insulation and finish systems (EIFS). Fireblocking material shall not be required at each floor level for EIFS containing foam plastic insulation installed less than 75 feet (22 860 mm) above grade, and installed on masonry or concrete backup walls. 3. Detached one- and two-family dwellings. Fireblocking of foam plastic insulation shall not be required at each floor level in detached one- and two-family dwellings of Type V construction that do not exceed three stories or 40 feet (12 192 mm) in height above grade plane.
718.3.2 Group R. | Draftstopping shall be provided in floor/ceiling spaces in Group R buildings. Draftstopping shall be located above and in line with the dwelling unit separations. Exceptions: 1. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are installed in the combustible concealed spaces where the draftstopping is being omitted. 3. Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2). 4. Draftstopping shall not be required where the structural members within the concealed ceiling space are individually protected on all sides for their full length with materials having the required fire-resistance rating.
718.3.3 Other groups. | In occupancies other than Group R, draftstopping shall be installed so that horizontal floor areas do not exceed 3,000 square feet (278.7 m2). Exceptions: 1. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Draftstopping shall not be required where the structural members within the concealed ceiling space are individually protected on all sides for their full length with materials having the required fire-resistance rating.
718.4.2 Groups R-1 and R-2. | Draftstopping shall be provided in attics, mansards, overhangs or other concealed roof spaces of Group R-2 buildings with three or more dwelling units and in all Group R-1 buildings. Draftstopping shall be installed above, and in line with dwelling unit separation walls that do not extend to the underside of the roof sheathing above. Exceptions: 1. Draftstopping shall not be required where the structural members within the concealed attic space are individually protected on all sides for their full length with materials having the required fire-resistance rating. 2. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. In occupancies in Group R-2 that do not exceed four stories above grade plane, the attic space shall be subdivided by draftstops into areas not exceeding 3,000 square feet (278.7 m2) or above every two dwelling units, whichever is smaller. 4. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.2, provided that automatic sprinklers are installed in the combustible concealed space where the draftstopping is being omitted. 5. Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2).
718.4.3 Other groups. | Draftstopping shall be installed in attics and concealed roof spaces, such that any horizontal area does not exceed 3,000 square feet (278.7 m2). Exceptions: 1. Draftstopping is not required in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Draftstopping shall not be required where the structural members within the concealed attic space are individually protected on all sides for their full length with materials having the required fire-resistance rating. 3. Where laminated wood I-joist assemblies are used, the space between the ceiling and the floor or roof above shall be divided into approximately equal areas not greater than 500 square feet (46.5 m2).
720.1.1 Noncombustible construction. | Insulating materials used in noncombustible construction must either:
720.1.2 Combustible construction. | Insulating materials used in combustible construction shall have a flame spread index not greater than 25, a smoke-development index not greater than 450, and be without evidence of continuous progressive combustion when tested in accordance with ASTM E 84.
722.1.1 Definitions. | The following terms are defined in Chapter 2 of this code:
722.2.1.2 Multi-wythe walls. | For walls that consist of two wythes of different types of concrete, the fire-resistance ratings shall be permitted to be determined from Figure 722.2.1.2.
7/8 inch.
7/8 inch.
722.3.3 Multi-wythe masonry walls. | The fire-resistance rating of wall assemblies constructed of multiple wythes of masonry materials shall be permitted to be based on the fire-resistance rating period of each wythe and the continuous airspace between each wythe in accordance with the following formula:
722.4.1.3 Multi-wythe walls with airspace. | Where a continuous airspace separates multiple wythes of the wall or partition, the total fire-resistance rating shall be determined by the formula:
722.4.2 Multi-wythe walls. | The fire-resistance rating for walls or partitions consisting of two or more dissimilar wythes shall be permitted to be determined by the formula:
722.4.2.1 Multi-wythe walls of different material. | For walls that consist of two or more wythes of different materials (concrete or concrete masonry units) in combination with clay masonry units, the fire-resistance rating of the different materials shall be permitted to be determined from Table 722.2.1.1 for concrete; Table 722.3.2 for concrete masonry units or Table 722.4.1(1) or 722.4.1(2) for clay and tile masonry units. |  |  |  | See BC07 Tables&Figures
7. Type S screws, 1 inch long, shall be used for attaching the first layer of gypsum board or gypsum panel product to the steel studs and the third layer to the sheet metal angles at 24 inches on center. | Type S screws 13/4-inch long shall be used for attaching the second layer of gypsum board or gypsum panel product to the steel studs and the fourth layer to the sheet metal angles at 12 inches on center. Type S screws 21/4 inches long shall be used for attaching the third layer of gypsum board or gypsum panel product to the steel studs at 12 inches on center.
722.5.1.3 Spray-applied fire-resistant materials. | The fire resistance of wide-flange structural steel columns protected with spray-applied fire-resistant materials, as illustrated in Figure 722.5.1(5), shall be permitted to be determined from the following expression: R= [C_(1 ) (W⁄D)+ C_2 ]h (Equation 7-13) where: R = Fire resistance (minutes). h = Thickness of spray-applied fire-resistant material (inches). D = Heated perimeter of the structural steel column (inches). C_1 and C_2 = Material-dependent constants. W = Weight of structural steel column (pounds per linear foot). Exception: The fire resistance of structural steel columns protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire resistance tests in accordance with Section 703.2.
722.5.2.2 Spray-applied fire-resistant materials. | The provisions in this section apply to structural steel beams and girders protected with spray-applied fire-resistant materials. Larger or smaller beam and girder shapes shall be permitted to be substituted for beams specified in approved unrestrained or restrained fire-resistance-rated assemblies, provided that the thickness of the fire-resistant material is adjusted in accordance with the following expression: h_2= [{(W_1⁄D_1 )+0.60} /{(W_2⁄D_2 )+0.60}] h_1 (Equation 7-17) where: h =Thickness of spray-applied fire-resistant material in inches. W =Weight of the structural steel beam or girder in pounds per linear foot. D =Heated perimeter of the structural steel beam or girder in inches. Subscript 1 refers to the beam and fire-resistant material thickness in the approved assembly. Subscript 2 refers to the substitute beam or girder and the required thickness of fire-resistant material. Exception: The fire-resistance of structural steel beams and girders protected with intumescent or mastic fire-resistant coatings shall be determined on the basis of fire-resistance tests in accordance with Section 703.2.

## BC8
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
801.1 Scope. | The provisions of this chapter shall govern the use of materials used as interior finishes, trim and decorative materials. | 801.1 Scope. | The provisions of this chapter shall govern the use of materials used as interior finishes, trim and decorative materials.
|  | 802.1 Interior wall and ceiling finish. | The provisions of Section 803 shall limit the allowable fire performance and smoke development of interior wall and ceiling finish materials based on occupancy classification.
|  | 802.2 Interior floor finish. | The provisions of Section 804 shall limit the allowable fire performance of interior floor finish materials based on occupancy classification.
|  | 802.3 Decorative materials and trim. | Decorative materials and trim shall be restricted by combustibility, fire performance or flame propagation performance criteria in accordance with Section 806.
|  | 802.4 Applicability. | For buildings in flood hazard areas as established in Section 1612.3, interior finishes, trim and decorative materials below the elevation required by Section 1612 shall be flood-damage-resistant materials.
|  | 802.5 Application. | Combustible materials shall be permitted to be used as finish for walls, ceilings, floors and other interior surfaces of buildings.
|  | 802.6 Windows. | Show windows in the exterior walls of the first story above grade plane shall be permitted to be of wood or of unprotected metal framing.
|  | 802.7 Foam plastics. | Foam plastics shall not be used as interior finish except as provided in Section 803.4. Foam plastics shall not be used as interior trim except as provided in Section 806.5 or 2604.2. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.
803.1 General. | Interior wall and ceiling finish materials shall be accepted as compliant for fire performance and smoke development in accordance with Section 803.1.1 or Section 803.1.2, and installed in accordance with the criteria therein. | 803.1 General. | Interior wall and ceiling finish materials shall be classified for fire performance and smoke development in accordance with Section 803.1.1 or 803.1.2, except as shown in Sections 803.1.3 through 803.15. Materials tested in accordance with Section 803.1.1 shall not be required to be tested in accordance with Section 803.1.2.
|  | 803.1.1 Interior wall and ceiling finish materials tested in accordance with NFPA 286. | Interior wall and ceiling finish materials shall be classified in accordance with NFPA 286 and comply with Section 803.1.1.1. Materials complying with Section 803.1.1.1 shall be considered to also comply with the requirements of Class A.
|  | 803.1.1.1 Acceptance criteria for NFPA 286. | The interior finish shall comply with the following:
|  | 803.1.2 Interior wall and ceiling finish materials tested in accordance with ASTM E84 or UL 723. | Interior wall and ceiling finish materials shall be classified in accordance with ASTM E84 or UL 723. Such interior finish materials shall be grouped in the following classes in accordance with their flame spread and smoke-developed indices. Class A = Flame spread index 0–25; smoke-developed index 0–450. Class B = Flame spread index 26–75; smoke developed index 0–450. Class C = Flame spread index 76–200; smoke-developed index 0–450. Exception: Materials tested in accordance with Section 803.1.1 and as indicated in Sections 803.1.3 through 803.13.
|  | 803.1.3 Interior wall and ceiling finish materials with different requirements. | The materials indicated in Sections 803.2 through 803.13 shall be tested as indicated in the corresponding sections.
803.2 Thickness exemption. | Materials having a thickness less than 0.036 inch (0.9 mm) applied directly to the surface of walls or ceilings shall not be required to be tested. | 803.2 Thickness exemption. | Materials having a thickness less than 0.036 inch (0.9 mm) applied directly to the surface of walls or ceilings shall not be required to be tested.
803.3 Heavy timber exemption. | Exposed portions of building elements complying with the requirements for buildings of Type IV construction in Section 602.4 shall not be subject to interior finish requirements. | 803.3 Heavy timber exemption. | Exposed portions of building elements complying with the requirements for buildings of heavy timber construction in Section 602.4 or Section 2304.11 shall not be subject to interior finish requirements except in interior exit stairways, interior exit ramps, and exit passageways.
803.4 Foam plastics. | Foam plastics shall not be used as interior finish except as provided in Section 2603.9. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover. | 803.4 Foam plastics. | Foam plastics shall not be used as interior finish except as provided in Section 2603.9. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.
803.5 Textile wall coverings. | Where used as interior wall finish materials, textile wall coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2, 803.1.3 or 803.1.4.1. | 803.5 Textile wall coverings. | Where used as interior wall finish materials, textile wall coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product-mounting system, including adhesive, and shall comply with the requirements of one of the following: Section 803.1.1, 803.5.1 or 803.5.2.
|  | 803.5.1 Room corner test for textile wall coverings and expanded vinyl wall coverings. | Textile wall coverings and expanded vinyl wall coverings shall meet the criteria of Section 803.5.1.1 when tested in the manner intended for use in accordance with the Method B protocol of NFPA 265 using the product-mounting system, including adhesive.
|  | 803.5.1.1 Acceptance criteria for NFPA 265. | The interior finish shall comply with the following:
|  | 803.5.2 Acceptance criteria for textile and expanded vinyl wall or ceiling coverings tested to ASTM E84 or UL 723. | Textile wall and ceiling coverings and expanded vinyl wall and ceiling coverings shall have a Class A flame spread index in accordance with ASTM E84 or UL 723 and be protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. Test specimen preparation and mounting shall be in accordance with ASTM E2404.
803.6 Textile ceiling coverings. | Where used as interior ceiling finish materials, textile ceiling coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2 or 803.1.4.1. | 803.6 Textile ceiling coverings. | Where used as interior ceiling finish materials, textile ceiling coverings, including materials having woven or nonwoven, napped, tufted, looped or similar surface and carpet and similar textile materials, shall be tested in the manner intended for use, using the product-mounting system, including adhesive, and shall comply with the requirements of Section 803.1.1 or 803.5.2.
803.7 Expanded vinyl wall coverings. | Where used as interior wall finish materials, expanded vinyl wall coverings shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2, 803.1.3 or 803.1.4.1. | 803.7 Expanded vinyl wall coverings. | Where used as interior wall finish materials, expanded vinyl wall coverings shall be tested in the manner intended for use, using the product-mounting system, including adhesive, and shall comply with the requirements of one of the following: Section 803.1.1, 803.5.1 or 803.5.2.
803.8 Expanded vinyl ceiling coverings. | Where used as interior ceiling finish materials, expanded vinyl ceiling coverings shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.2 or 803.1.4.1. | 803.8 Expanded vinyl ceiling coverings. | Where used as interior ceiling finish materials, expanded vinyl ceiling coverings shall be tested in the manner intended for use, using the product mounting system, including adhesive, and shall comply with the requirements of Section 803.1.1 or 803.5.2.
803.9 High-density polyethylene (HDPE) and polypropylene (PP). | Where high-density polyethylene or polypropylene is used as an interior finish it shall comply with Section 803.1.2. | 803.9 High-density polyethylene (HDPE) and polypropylene (PP). | Where high-density polyethylene or polypropylene is used as an interior finish, it shall comply with Section 803.1.1.
803.10 Site-fabricated stretch systems. | Where used as interior wall or interior ceiling finish materials, site-fabricated stretch systems containing all three components described in the definition in Chapter 2 of this code shall be tested in the manner intended for use, and shall comply with the requirements of Section 803.1.1 or 803.1.2 of this code. If the materials are tested in accordance with ASTM E 84 or UL 723, specimen preparation and mounting shall be in accordance with ASTM E 2573. | 803.10 Site-fabricated stretch systems. | Where used as interior wall or interior ceiling finish materials, site-fabricated stretch systems containing all three components described in the definition in Chapter 2 shall be tested in the manner intended for use, and shall comply with the requirements of Section 803.1.1 or with the requirements of Class A in accordance with Section 803.1.2. If the materials are tested in accordance with ASTM E84 or UL 723, specimen preparation and mounting shall be in accordance with ASTM E2573.
|  | 803.11 Laminated products factory produced with a wood substrate. | Laminated products factory produced with a wood substrate shall comply with one of the following:
|  | 803.12 Facings or wood veneers intended to be applied on site over a wood substrate. | Facings or veneers intended to be applied on site over a wood substrate shall comply with one of the following:
|  | 803.13 Interior finish requirements based on occupancy. | Interior wall and ceiling finish shall have a flame spread index not greater than that specified in Table 803.13 for the group and location designated. Interior wall and ceiling finish materials tested in accordance with NFPA 286 and meeting the acceptance criteria of Section 803.1.1.1, shall be permitted to be used where a Class A classification in accordance with ASTM E84 or UL 723 is required. |  | See BC08 Tables &Figures
|  | 803.14 Stability. | Interior finish materials regulated by this chapter shall be applied or otherwise fastened in such a manner that such materials will not readily become detached where subjected to room temperatures of 200°F (93°C) for not less than 30 minutes.
|  | 803.15 Application of interior finish materials to fire-resistance-rated or noncombustible building elements. | Where interior finish materials are applied on walls, ceilings or structural elements required to have a fire-resistance rating or to be of noncombustible construction, these finish materials shall comply with the provisions of this section.
|  | 803.15.1 Direct attachment and furred construction. | Where walls, ceilings or structural elements are required by any provision in this code to be of fire-resistance-rated or noncombustible construction, the interior finish material shall be applied directly against such construction or to furring strips not exceeding 13/4 inches (44 mm), applied directly against such surfaces.
|  | 803.15.1.1 Furred construction. | If the interior finish material is applied to furring strips, the intervening spaces between such furring strips shall comply with one of the following: 1. Be filled with material that is inorganic or noncombustible. 2. Be filled with material that meets the requirements of a Class A material in accordance with Section 803.1.1 or 803.1.2. 3. Be fireblocked at not greater than 8 feet (2438 mm) in every direction in accordance with Section 718. Exception: Compliance with Item 1, 2 or 3 is not required where the materials used to create the concealed space are noncombustible.
|  | 803.15.2 Set-out construction. | Where walls and ceilings are required to be of fire-resistance-rated or noncombustible construction and walls are set out or ceilings are dropped distances greater than specified in Section 803.15.1, Class A finish materials, in accordance with Section 803.1.1 or 803.1.2, shall be used. Exceptions: 1. Where interior finish materials are protected on both sides by an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. Where interior finish materials are attached to noncombustible backing or furring strips installed as specified in Section 803.15.1.1. 3. Where the combustible void is filled with a noncombustible material.
|  | 803.15.2.1 Hangers and assembly members. | The hangers and assembly members of such dropped ceilings that are below the horizontal fire-resistance-rated floor or roof assemblies shall be of noncombustible materials. The construction of each set-out wall and horizontal fire-resistance-rated floor or roof assembly shall be of fire-resistance-rated construction as required elsewhere in this code. Exception: In Types III and V construction, fire-retardant-treated wood shall be permitted for use as hangers and assembly members of dropped ceilings.
|  | 803.15.3 Heavy timber construction. | Wall and ceiling finishes of all classes as permitted in this chapter that are installed directly against the wood decking or planking of heavy timber construction in Section 602.4.4.2 or 2304.11 or to wood furring strips applied directly to the wood decking or planking shall be fireblocked as specified in Section 803.15.1.1.
804.1 General. | Interior floor finish and floor covering materials shall comply with this section. | 804.1 General. | Interior floor finish and floor covering materials shall comply with Sections 804.2 through 804.4.2. Exception: Floor finishes and coverings of a traditional type, such as wood, vinyl, linoleum or terrazzo, and resilient floor covering materials that are not composed of fibers.
|  | 803.15.4 Materials. | An interior wall or ceiling finish material that is not more than 1/4 inch (6.4 mm) thick shall be applied directly onto the wall, ceiling or structural element without the use of furring strips and shall not be suspended away from the building element to which that finish material it is applied. Exceptions: 1. Noncombustible interior finish materials. 2. Materials that meet the requirements of Class A materials in accordance with Section 803.1.1 or 803.1.2 where the qualifying tests were made with the material furred out from the noncombustible backing shall be permitted to be used with furring strips. 3. Materials that meet the requirements of Class A materials in accordance with Section 803.1.1 or 803.1.2 where the qualifying tests were made with the material suspended away from the noncombustible backing shall be permitted to be used suspended away from the building element.
804.2 Classification. | Interior floor finish and floor covering materials required by Section 804.4.1 of this code to be of Class I or II materials shall be classified in accordance with NFPA 253 or ASTM E 648. The classification referred to herein corresponds to the classifications determined by NFPA 253 or ASTM E 648 as follows: Class I, 0.45 watts/cm2 or greater; Class II, 0.22 watts/cm2 or greater. | 804.2 Classification. | Interior floor finish and floor covering materials required by Section 804.4.2 to be of Class I or II materials shall be classified in accordance with ASTM E648 or NFPA 253. The classification referred to herein corresponds to the classifications determined by ASTM E648 or NFPA 253 as follows: Class I, 0.45 watts/cm2 or greater; Class II, 0.22 watts/cm2 or greater.
804.3 Testing and identification. | Interior floor finish and floor covering materials shall be tested by an approved agency in accordance with NFPA 253 or ASTM E 648 and identified by a hang tag or other suitable method so as to identify the manufacturer or supplier and style, and shall indicate the interior floor finish or floor covering classification in accordance with Section 804.2 of this code. Carpet-type floor coverings shall be tested as proposed for use, including underlayment. Test reports confirming the information provided in the manufacturer’s product identification shall be furnished to the department upon request. | 804.3 Testing and identification. | Interior floor finish and floor covering materials shall be tested by an agency in accordance with ASTM E648 or NFPA 253 and identified by a hang tag or other suitable method so as to identify the manufacturer or supplier and style, and shall indicate the interior floor finish or floor covering classification in accordance with Section 804.2. Carpet-type floor coverings shall be tested as proposed for use, including underlayment. Test reports confirming the information provided in the manufacturer’s product identification shall be furnished to the building official on request.
|  | 804.4 Interior floor finish requirements. | Interior floor covering materials shall comply with Sections 804.4.1 and 804.4.2 and interior floor finish materials shall comply with Section 804.4.2.
|  | 804.4.1 Test requirement. | In all occupancies, interior floor covering materials shall comply with the requirements of the DOC FF-1 “pill test” (CPSC 16 CFR Part 1630) or with ASTM D2859.
805.1 Application. | Combustible materials installed on or embedded in floors of buildings of Type I or II construction shall comply with Sections 805.1.1 through 805.1.4. | 805.1 Application. | Combustible materials installed on or embedded in floors of buildings of Type I or II construction shall comply with Sections 805.1.1 through 805.1.3. Exception: Stages and platforms constructed in accordance with Sections 410.2 and 410.3, respectively.
|  | 804.4.2 Minimum critical radiant flux. | In all occupancies, interior floor finish and floor covering materials in enclosures for stairways and ramps, exit passageways, corridors and rooms or spaces not separated from corridors by partitions extending from the floor to the underside of the ceiling shall withstand a minimum critical radiant flux. The minimum critical radiant flux shall be not less than Class I in Groups I-1, I-2 and I-3 and not less than Class II in Groups A, B, E, H, I-4, M, R-1, R-2 and S. Exception: Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, Class II materials are permitted in any area where Class I materials are required, and materials complying with DOC FF-1 “pill test” (CPSC 16 CFR Part 1630) or with ASTM D2859 are permitted in any area where Class II materials are required.
805.1.1 Subfloor construction. | Floor sleepers, bucks and nailing blocks shall not be constructed of combustible materials, unless the space between the fire-resistance-rated floor assembly and the flooring is either solidly filled with noncombustible materials or fireblocked in accordance with Section 718, and provided that such open spaces shall not extend under or through permanent partitions or walls. | 805.1.1 Subfloor construction. | Floor sleepers, bucks and nailing blocks shall not be constructed of combustible materials, unless the space between the fire-resistance-rated floor assembly and the flooring is either solidly filled with noncombustible materials or fireblocked in accordance with Section 718, and provided that such open spaces shall not extend under or through permanent partitions or walls.
805.1.2 Wood finish flooring. | Wood finish flooring is permitted to be attached directly to the embedded or fireblocked wood sleepers and shall be permitted where cemented directly to the top surface of approved fire-resistance-rated floor assemblies or directly to a wood subfloor attached to sleepers as provided for in Section 805.1.1. | 805.1.2 Wood finish flooring. | Wood finish flooring is permitted to be attached directly to the embedded or fireblocked wood sleepers and shall be permitted where cemented directly to the top surface of fire-resistance-rated floor assemblies or directly to a wood subfloor attached to sleepers as provided for in Section 805.1.1.
805.1.3 Insulating boards. | Combustible insulating boards not more than ½-inch (12.7 mm) thick and covered with finish flooring are permitted where attached directly to a noncombustible floor assembly or to wood subflooring attached to sleepers as provided for in Section 805.1.1. | 805.1.3 Insulating boards. | Combustible insulating boards not more than 1/2 inch (12.7 mm) thick and covered with finish flooring are permitted where attached directly to a noncombustible floor assembly or to wood subflooring attached to sleepers as provided for in Section 805.1.1.
|  | 806.1 General. | The following requirements shall apply to all occupancies:
|  | 806.2 Combustible decorative materials. | In Groups A, B, E, I, M and R-1 and in dormitories in Group R-2, curtains, draperies, fabric hangings and similar combustible decorative materials suspended from walls or ceilings shall comply with Section 806.4 and shall not exceed 10 percent of the specific wall or ceiling area to which such materials are attached. Exceptions: 1. In auditoriums in Group A, the permissible amount of curtains, draperies, fabric hangings and similar combustible decorative materials suspended from walls or ceilings shall not exceed 75 percent of the aggregate wall area where the building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1, and where the material is installed in accordance with Section 803.15 of this code. 2. In Group R-2 dormitories, within sleeping units and dwelling units, the permissible amount of curtains, draperies, fabric hangings and similar decorative materials suspended from walls or ceiling shall not exceed 50 percent of the aggregate wall areas where the building is equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1. 3. In Group B and M occupancies, the amount of combustible fabric partitions suspended from the ceiling and not supported by the floor shall comply with Section 806.4 and shall not be limited. 4. The 10-percent limit shall not apply to curtains, draperies, fabric hangings and similar combustible decorative materials used as window coverings.
|  | 806.3 Occupancy-based requirements. | Occupancy-based requirements for combustible decorative materials, other than decorative vegetation, not complying with Section 806.4 shall comply with Sections 807.5.1 through 807.5.6 of the International Fire Code.
|  | 806.4 Acceptance criteria and reports. | Where required to exhibit improved fire performance, curtains, draperies, fabric hangings and similar combustible decorative materials suspended from walls or ceilings shall be tested by an approved agency and meet the flame propagation performance criteria of Test 1 or 2, as appropriate, of NFPA 701, or exhibit a maximum heat release rate of 100 kW when tested in accordance with NFPA 289, using the 20 kW ignition source. Reports of test results shall be prepared in accordance with the test method used and furnished to the building official on request.
|  | 806.5 Foam plastic. | Foam plastic used as trim in any occupancy shall comply with Section 2604.2.
806.6 Pyroxylin plastic. | Imitation leather or other material consisting of or coated with a pyroxylin or similarly hazardous base shall not be used in Group A occupancies. | 806.6 Pyroxylin plastic. | Imitation leather or other material consisting of or coated with a pyroxylin or similarly hazardous base shall not be used in Group A occupancies.
806.7 Interior trim. | Material, other than foam plastic used as interior trim, shall have a minimum Class C flame spread index and maximum smoke-developed index when tested in accordance with ASTM E 84 or UL 723 as described in Section 803.1.1. Combustible trim, excluding handrails and guardrails, shall not exceed 10 percent of the specific wall or ceiling area in which it is attached. | 806.7 Interior trim. | Material, other than foam plastic used as interior trim, shall have a minimum Class C flame spread and smoke-developed index when tested in accordance with ASTM E84 or UL 723, as described in Section 803.1.2. Combustible trim, excluding handrails and guardrails, shall not exceed 10 percent of the specific wall or ceiling area to which it is attached.
806.8 Interior floor-wall base. | Interior floor-wall base that is 6 inches (152.4 mm) or less in height shall be tested in accordance with Section 804.2 and shall be not less than Class II. Where a Class I floor finish is required, the floor-wall base shall be Class I. | 806.8 Interior floor-wall base. | Interior floor-wall base that is 6 inches (152 mm) or less in height shall be tested in accordance with Section 804.2 and shall be not less than Class II. Where a Class I floor finish is required, the floor-wall base shall be Class I. Exception: Interior trim materials that comply with Section 806.7.
807.1 Insulation. | Thermal and acoustical insulation shall comply with Section 720. | 807.1 Insulation. | Thermal and acoustical insulation shall comply with Section 720.
|  | 806.9 Combustible lockers. | Where lockers constructed of combustible materials are used, the lockers shall be considered to be interior finish and shall comply with Section 803. Exception: Lockers constructed entirely of wood and noncombustible materials shall be permitted to be used wherever interior finish materials are required to meet a Class C classification in accordance with Section 803.1.2.
808.1 Acoustical ceiling systems. | The quality, design, fabrication and erection of metal suspension systems for acoustical tile and lay-in panel ceilings in buildings or structures shall conform to generally accepted engineering practice, the provisions of this chapter and other applicable requirements of this code. | 808.1 Acoustical ceiling systems. | The quality, design, fabrication and erection of metal suspension systems for acoustical tile and lay-in panel ceilings in buildings or structures shall conform to generally accepted engineering practice, the provisions of this chapter and other applicable requirements of this code.
808.1.1 Materials and installation. | Acoustical materials complying with the interior finish requirements of Section 803 shall be installed in accordance with the manufacturer’s recommendations and applicable provisions for applying interior finish. | 808.1.1 Materials and installation. | Acoustical materials complying with the interior finish requirements of Section 803 shall be installed in accordance with the manufacturer’s recommendations and applicable provisions for applying interior finish.
808.1.1.1 Suspended acoustical ceilings. | Acoustical ceilings that are to be suspended below floor or roof construction by means of a framing system shall consist of supporting hangers of minimum ¼-inch diameter (6.4 mm) steel rods, carrying channels of minimum 1½-inch deep (38.1 mm) cold-rolled steel weighing 0.440 pounds per linear foot (0.681 kg/m), and a supporting grid complying with Appendix R. Use of wire hangers shall not be permitted. Direct hung suspension systems shall not be permitted. | 808.1.1.1 Suspended acoustical ceilings. | Suspended acoustical ceiling systems shall be installed in accordance with the provisions of ASTM C635 and ASTM C636.
808.1.1.2 Fire-resistance-rated construction. | Acoustical ceiling systems that are part of fire-resistance-rated construction shall be installed in the same manner used in the assembly tested and shall comply with the provisions of Chapter 7. | 808.1.1.2 Fire-resistance-rated construction. | Acoustical ceiling systems that are part of fire-resistance-rated construction shall be installed in the same manner used in the assembly tested and shall comply with the provisions of Chapter 7.
801.2 Interior wall and ceiling finish. | The provisions of Section 803 shall limit the allowable fire performance and smoke development of interior wall and ceiling finish materials based on occupancy classification.
801.3 Interior floor finish. | The provisions of Section 804 shall limit the allowable fire performance of interior floor finish materials based on occupancy classification.
801.4 Decorative materials and trim. | Decorative materials and trim shall be restricted by combustibility, fire performance or flame propagation performance criteria in accordance with Section 806.
801.5 Applicability in flood hazard areas. | For buildings in flood hazard areas as established in Appendix G, interior finishes, trim and decorative materials below the design flood elevation shall be flood-damage-resistant materials.
801.6 Application. | Combustible materials complying with the requirements of this chapter shall be permitted to be used as finish for walls, ceilings, floors and other interior surfaces of buildings.
801.7 Windows. | Show windows in the exterior walls of the first story above grade plane shall be permitted to be of wood or of unprotected metal framing.
801.8 Foam plastics. | Foam plastics shall not be used as interior finish except as provided in Section 803.4. Foam plastics shall not be used as interior trim except as provided in Section 806.5 or 2604.2. This section shall apply both to exposed foam plastics and to foam plastics used in conjunction with a textile or vinyl facing or cover.
802.1 Definitions. | The following terms are defined in Chapter 2:
803.1.1 Interior wall and ceiling finish materials. | Interior wall and ceiling finish materials shall be tested and classified in accordance with ASTM E 84 or UL 723. Such interior finish materials shall be grouped in the following classes in accordance with their flame spread and smoke-developed indexes.
803.1.2 Room corner test for interior wall or ceiling finish materials. | As an alternative to Section 803.1.1, interior wall or ceiling finish materials shall be permitted to be tested in accordance with NFPA 286. Interior wall or ceiling finish materials tested in accordance with NFPA 286 shall comply with Section 803.1.2.1 of this code.
803.1.2.1 Acceptance criteria for NFPA 286. | The interior finish shall comply with the following:
803.1.3 Room corner test for textile wall coverings and expanded vinyl wall coverings. | Textile wall coverings and expanded vinyl wall coverings shall meet the criteria of Section 803.1.3.1 of this code when tested in the manner intended for use in accordance with the Method B protocol of NFPA 265 using the product-mounting system, including adhesive.
803.1.3.1 Acceptance criteria for NFPA 265. | The interior finish shall comply with the following:
803.1.4 Flame-spread and smoke-developed tests for textile wall or ceiling coverings. | Specimens shall be tested and indexed per ASTM E 84 or UL 723, and classified for flame spread per Section 803.1.4.1 of this code.
803.1.4.1 Acceptance criteria for textile and expanded vinyl wall or ceiling coverings tested to ASTM E 84 or UL 723. | Textile wall and ceiling coverings and expanded vinyl wall and ceiling coverings shall have a Class A flame spread index per Section 803.1.1 of this code; shall meet the smoke developed index requirements of Section 803.1.1; and shall be protected by an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2 of this code. Test specimen preparation and mounting shall be in accordance with ASTM E 2404.
803.11 Interior finish requirements based on group. | Interior wall and ceiling finish shall have a flame spread index and smoke-developed index not greater than that specified in Table 803.11 of this code for the group and location designated. Interior wall and ceiling finish materials tested in accordance with NFPA 286 and meeting the acceptance criteria of Section 803.1.2.1 of this code, shall be permitted to be used where a Class A classification, in accordance with ASTM E 84 or UL 723, is required. |  |  |  | See BC08 Tables &Figures
803.12 Stability. | Interior finish materials regulated by this chapter shall be applied or otherwise fastened in such a manner that such materials will not readily become detached where subjected to room temperatures of 200°F (93.3°C) for not less than 30 minutes.
803.13 Application of interior finish materials to fire-resistance-rated or noncombustible building elements. | Where interior finish materials are applied on walls, ceilings or structural elements required to have a fire-resistance rating or to be of noncombustible construction, these finish materials shall comply with the provisions of this section.
803.13.1 Direct attachment and furred construction. | Where walls and ceilings are required by any provision in this code to be of fire-resistance-rated or noncombustible construction, the interior finish material shall be applied directly against such construction or to furring strips not exceeding 13/4 inches (44.5 mm), applied directly against such surfaces.
803.13.1.1 Furred construction. | If the interior finish material is applied to furring strips, the intervening spaces between such furring strips shall comply with one of the following:
803.13.2 Set-out construction. | Where walls and ceilings are required to be of fire-resistance-rated or noncombustible construction and walls are set out or ceilings are dropped distances greater than specified in Section 803.13.1, Class A finish materials, in accordance with Section 803.1.1 or 803.1.2, shall be used.
803.13.2.1 Hangers and assembly members. | The hangers and assembly members of such dropped ceilings that are below the horizontal-fire-resistance-rated floor or roof assemblies shall be of noncombustible materials. The construction of each set out wall and horizontal fire-resistance-rated floor or roof assembly shall be of fire-resistance-rated construction as required elsewhere in this code.
803.13.3 Heavy timber construction. | Wall and ceiling finishes of all classes as permitted in this chapter that are installed directly against the wood decking or planking of Type IV construction or to wood furring strips applied directly to the wood decking or planking shall be fireblocked as specified in Section 803.13.1.1.
803.13.4 Materials. | An interior wall or ceiling finish material that is not more than ¼ inch (6.4 mm) thick shall be applied directly onto the wall, ceiling or building element without the use of furring strips and shall not be suspended away from the building element to which that finish material is applied.
804.4 Interior floor finish limitations. | In buildings and spaces classified in Occupancy Group H and in all exits and exit passageways of any occupancy group, floor finishes shall be of noncombustible materials.
804.4.1 Minimum critical radiant flux. | Interior floor fin­ishes shall not be less than Class I in Occupancy Groups I-2 and I-3 and not less than Class II in Occupancy Groups A, B, E, H, I-4, M, R-1, R-2 and S. In all other occupancy groups, the interior floor finish shall comply with the DOC FF-1 “pill test” (CPSC 16 CFR, Part 1630).
804.5 Volatile organic compounds emissions in carpet and carpet cushion. | Carpet and carpet cushion as defined in Section 17-1401 of the Administrative Code shall comply with the limits on volatile organic compound emissions set forth in Chapter 14 of Title 17 of such code.
805.1.4 Carpet-type floor coverings. | Carpet-type floor coverings are permitted where cemented directly to the top surface of approved fire-resistance-rated construction or directly to a wood subfloor attached to sleepers as provided for in Section 805.1.1.
806.1 Decorations. | All decorations shall comply with the requirements of the New York City Fire Code.
806.2 Reserved.
806.3 Reserved.
806.4 Reserved.
806.5 Foam plastic as trim. | Foam plastic used as trim shall comply with Section 2604.2 and shall not be permitted in occupancies other than Group R-3, within individual dwelling units of Group R-1 and R-2 occupancies, or unless approved in accordance with Section 2603.9.

## BC9
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
901.1 Scope. | The provisions of this chapter shall specify where fire protection systems are required and shall apply to the design, installation and operation of fire protection systems. | 901.1 Scope. | The provisions of this chapter shall specify where fire protection and life safety systems are required and shall apply to the design, installation and operation of fire protection and life safety systems.
901.1.1 Referenced standards. | Where this code makes reference to the nationally recognized standards NFPA 13, NFPA 13D, NFPA 13R, NFPA 14, NFPA 20, NFPA 72, or NFPA 92, such standard shall be as modified for New York City in accordance with Appendix Q of this code.
901.2 Fire protection systems. | Fire protection systems shall be installed, repaired, operated and maintained in accordance with this code and the New York City Fire Code. Any fire protection system for which an exception or reduction to the provisions of this code has been granted shall be considered to be a required system. Exception: Any fire protection system or portion thereof not required by this code shall be permitted to be installed provided that such system meets the requirements of this code. | 901.2 Fire protection systems. | Fire protection and life safety systems shall be installed, repaired, operated and maintained in accordance with this code and the International Fire Code. Exception: Any fire protection or life safety system or portion thereof not required by this code shall be permitted to be installed for partial or complete protection provided that such system meets the requirements of this code.
901.3 Modifications. | No person shall remove or modify any fire protection system installed or maintained under the provisions of this code or the New York City Fire Code without approval by the commissioner. | 901.3 Modifications. | Persons shall not remove or modify any fire protection system installed or maintained under the provisions of this code or the International Fire Code without approval by the building official.
901.2.1 Fire protection systems within a building. | Fire protection systems shall be dedicated to one building only. Exception: Upon review and approval by the commissioner and the Fire Department, multiple buildings may be served by one fire protection system.
901.4 Threads. | Threads provided for Fire Department connections to sprinkler systems, standpipes, yard hydrants or any other fire hose connection shall be compatible with the connections used by the Fire Department. | 901.4 Threads. | Threads provided for fire department connections to sprinkler systems, standpipes, yard hydrants or any other fire hose connection shall be compatible with the connections used by the local fire department.
901.5 Acceptance tests. | Fire protection systems shall be tested in accordance with the requirements of this code and the New York City Fire Code. When required by this chapter, the tests shall be conducted in the presence of the department or an approved agency. Tests required by this code, the New York City Fire Code and the standards listed in this code shall be conducted at the expense of the owner or the owner’s representative. It shall be unlawful to occupy portions of a structure until the required fire protection systems within that portion of the structure have been tested and approved. | 901.5 Acceptance tests. | Fire protection systems shall be tested in accordance with the requirements of this code and the International Fire Code. Where required, the tests shall be conducted in the presence of the building official. Tests required by this code, the International Fire Code and the standards listed in this code shall be conducted at the expense of the owner or the owner’s authorized agent. It shall be unlawful to occupy portions of a structure until the required fire protection systems within that portion of the structure have been tested and approved.
901.6 Supervisory service. | Where required, fire protection systems shall be monitored by a central supervising station in accordance with NFPA 72. | 901.6 Supervisory service. | Where required, fire protection systems shall be monitored by an approved supervising station in accordance with NFPA 72.
901.6.1 Automatic sprinkler systems. | Automatic sprinkler systems shall be monitored by a central supervising station. Exceptions: 1. A central supervising station is not required for automatic sprinkler systems protecting one- and two-family dwellings. 2. Limited area sprinkler systems serving no more than 6 sprinkler heads. | 901.6.1 Automatic sprinkler systems. | Automatic sprinkler systems shall be monitored by an approved supervising station. Exceptions: 1. A supervising station is not required for automatic sprinkler systems protecting one- and two-family dwellings. 2. Limited area systems in accordance with Section 903.3.8.
901.6.2 Fire alarm systems. | Fire alarm systems required by the provisions of Section 907.2 of this code and the New York City Fire Code shall be monitored by a central supervising station in accordance with Section 907.6.5. Exceptions: 1. Single- and multiple-station smoke alarms and carbon monoxide alarms required by Section 907.2.11. 2. Smoke detectors in Group I-3 occupancies. 3. Supervisory service is not required for automatic sprinkler systems in one- and two-family dwellings.
901.6.3 Group H. | Manual fire alarm, automatic fire-extinguishing and emergency alarm systems in Group H occupancies shall be monitored by an approved supervising station. Exception: When approved by the Fire Department, on-site monitoring at a constantly attended location shall be permitted provided that notifications to the Fire Department will be equal to those provided by a central supervising station.
901.7 Fire areas. | Where buildings, or portions thereof, are divided into fire areas so as not to exceed the limits established for requiring a fire protection system in accordance with this chapter, such fire areas shall be separated by fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, having a fire-resistance rating of not less than that determined in accordance with Section 707.3.10. | 901.7 Fire areas. | Where buildings, or portions thereof, are divided into fire areas so as not to exceed the limits established for requiring a fire protection system in accordance with this chapter, such fire areas shall be separated by fire walls constructed in accordance with Section 706, fire barriers constructed in accordance with Section 707, or horizontal assemblies constructed in accordance with Section 711, or a combination therof having a fire-resistance rating of not less than that determined in accordance with Section 707.3.10.
901.8 Construction documents. | Construction documents shall comply with Chapter 1 of Title 28 of the Administrative Code, Section 107 and other applicable provisions of this code and its referenced standards.
901.9 Special provisions for prior code buildings. | The provisions of this chapter shall apply to alterations and changes of use or occupancy to prior code buildings in accordance with Sections 901.9.1 through 901.9.6.
901.9.1 Additions, alterations or repairs. | Additions, alterations, renovations or repairs to existing systems shall conform to that required for new systems without requiring the existing system to comply with all of the requirements of this code, except as otherwise required in Sections 901.9.2 through 901.9.6. Additions, alterations or repairs shall not cause an existing installation to become unsafe, hazardous or overloaded.
901.9.1.1 Minor additions, alterations, renovations and repairs. | Minor additions, alterations, renovations and repairs to existing systems shall meet the provisions for new construction, unless such work is done in the same manner and arrangement as was in the existing system, is not hazardous and is approved.
901.9.2 Additional requirements based on change of occupancy or use. | Fire protection systems governed by this chapter shall be provided:
901.9.3 Additional requirements for enlargements. | Fire protection systems shall be provided in enlarged portions of a building and where this chapter would require such systems in new construction for a space or building. Exception: Section 901.9.3 shall not require sprinklers to be installed in enlarged portions of unsprinklered buildings to be occupied exclusively as one- or two-family dwellings. This exception shall not apply where sprinklers are otherwise required by the provisions of Sections 901.9.2 or 901.9.4.
901.9.4 Additional requirements based on value of alterations. | Fire protection systems shall be provided to buildings and spaces in accordance with the provisions of Sections 901.9.4.1 through 901.9.4.3.
903.1 General. | Automatic sprinkler systems shall comply with this section. Installation of automatic sprinkler systems shall comply with the special inspection requirements of Chapter 17. | 903.1 General. | Automatic sprinkler systems shall comply with this section.
901.9.4.1 Alterations requiring fire protection systems throughout a building. | If the value of alterations to the building equals or exceeds 60 percent of the value of the existing building, or, in the case of a building containing 4 or more dwelling units, 50 percent of the value of the existing building, the entire building shall be made to comply with the fire protection requirements of this chapter as if it were hereafter erected.
903.1.1 Alternative protection. | Where permitted by the New York City Fire Code, the Fire Department may approve the installation of alternative automatic fire-extinguishing systems complying with this code and the New York City Fire Code in lieu of automatic sprinkler protection. | 903.1.1 Alternative protection. | Alternative automatic fire-extinguishing systems complying with Section 904 shall be permitted instead of automatic sprinkler protection where recognized by the applicable standard and approved by the fire code official.
901.9.4.2 Alterations requiring fire protection systems in the space being altered. | If the value of alterations of a space is between 30 percent and 60 percent of the value of the existing building, or, in the case of a building containing 4 or more dwelling units, if the value of alterations of a space is between 30 percent and 50 percent of the value of the existing building, those portions of the building being altered shall be made to comply with the fire protection requirements of this chapter.
903.2 Where required. | Approved automatic sprinkler systems in new buildings and structures shall be provided in the locations described in Sections 903.2.1 through 903.2.13. Exceptions: 1. Sprinklers shall not be required in electrical equipment rooms where all of the following conditions are met: 1.1 The room is dedicated to electrical equipment only. 1.2 Only dry-type electrical equipment is used. 1.3 Equipment is installed in a 2-hour fire-rated enclosure including protection for penetrations. 1.4 No combustible storage is permitted to be stored in the room. 2. Sprinklers shall not be permitted in elevator machine rooms and elevator machinery spaces. 3. Sprinklers shall not be required in rooms and spaces protected by an alternative fire suppression system in accordance with the New York City Fire Code and Section 904 of this code. | 903.2 Where required. | Approved automatic sprinkler systems in new buildings and structures shall be provided in the locations described in Sections 903.2.1 through 903.2.12. Exception: Spaces or areas in telecommunications buildings used exclusively for telecommunications equipment, associated electrical power distribution equipment, batteries and standby engines, provided that those spaces or ar-eas are equipped throughout with an automatic smoke detection system in accordance with Section 907.2 and are separated from the remainder of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or not less than 2-hour horizontal assemblies constructed in accordance with Section 711, or both.
901.9.4.3 Additional requirements for buildings containing 4 or more dwelling units. | For buildings containing 4 or more dwelling units, if the value of alterations to an existing space classified in Occupancy Group R-1 or R-2 exceeds 50 percent of the value of the space, such space shall be made to comply with the fire protection requirements of this chapter.
903.2.1 Group A. | An automatic sprinkler system shall be provided throughout buildings and portions thereof used as Group A occupancies as provided in this section. For Group A-1, A-2, A-3 and A-4 occupancies, the automatic sprinkler system shall be provided throughout the story where the fire area containing the Group A-1, A-2, A-3 or A-4 occupancy is located, and throughout all stories from the Group A occupancy to, and including, the levels of exit discharge serving the Group A occupancy. For Group A-5 occupancies, the automatic sprinkler system shall be provided in the spaces indicated in Section 903.2.1.5. In all Group A occupancies providing live entertainment, dressing rooms and property rooms used in conjunction with such assembly occupancy shall be pro­vided with an automatic sprinkler system. Stages shall comply with Section 410.7. | 903.2.1 Group A. | An automatic sprinkler system shall be provided throughout buildings and portions thereof used as Group A occupancies as provided in this section.
901.9.5 Additional provisions. | In buildings or spaces not otherwise required to provide fire protection systems in accordance with this chapter, fire protection systems shall be provided for the types of alterations described in Sections 901.9.5.1 through 901.9.5.4.
903.2.1.1 Group A-1. | An automatic sprinkler system shall be provided for fire areas containing Group A-1 occupancies and intervening floors of the building where one of the following conditions exists: | 903.2.1.1 Group A-1. | An automatic sprinkler system shall be provided throughout stories containing Group A-1 occupancies and throughout all stories from the Group A-1 occupancy to and including the levels of exit discharge serving that occupancy where one of the following conditions exists:
901.9.5.1 Additional requirements for providing smoke and carbon monoxide alarms in dwelling units during alterations involving removal of existing interior finishes. | Smoke and/or carbon monoxide alarms complying with the location, interconnection and power source requirements of this chapter shall be provided throughout a dwelling unit when alteration work results in the removal of existing and/or installation of new interior wall or ceiling finishes permitting the installation of concealed wiring for all the required alarms throughout the dwelling unit.
903.2.1.2 Group A-2. | An automatic sprinkler system shall be provided for Group A-2 occupancies where any one of the following conditions exists: | 903.2.1.2 Group A-2. | An automatic sprinkler system shall be provided throughout stories containing Group A-2 occupancies and throughout all stories from the Group A-2 occupancy to and including the levels of exit discharge serving that occupancy where one of the following conditions exists:
901.9.5.2 Additional requirements for providing standpipes in newly constructed stair shafts. | Where an alteration includes the addition or replacement of an entire exit stair shaft that is a required means of egress, the entire shaft shall be equipped with a standpipe in accordance with Section 905.
903.2.1.3 Group A-3. | An automatic sprinkler system shall be provided for fire areas containing Group A-3 occupancies and intervening floors of the building where one of the following conditions exists: 1. The fire area exceeds 12,000 square feet (1114.8 m2). 2. The fire area has an occupant load of 300 or more. 3. The aggregate occupant load of all fire areas occupied by Group A, located on any given floor other than the level of exit discharge, is 300 or more. Exception: Areas used exclusively as participant sports areas where the main floor area is located at the same level as the level of exit discharge of the main entrance and exit. | 903.2.1.3 Group A-3. | An automatic sprinkler system shall be provided throughout stories containing Group A-3 occupancies and throughout all stories from the Group A-3 occupancy to and including the levels of exit discharge serving that occupancy where one of the following conditions exists:
901.9.5.3 Additional requirements for enlargements of buildings with existing standpipe systems. | Where the alteration involves the addition of stories to a building with an existing standpipe system, and one or more stair shafts are not currently equipped with standpipes, standpipes shall be provided to all stair shafts in accordance with this chapter. Exception: Additional standpipes are not required where: 1. The alteration involves the addition of only one story; 2. Existing standpipes in existing stair shafts are extended in accordance with this chapter; 3. Standpipe hose connections are provided in compliance with Section 905.4, Item 6; and 4. The demand on the standpipe system, including any additional demand, with respect to flow and pressure does not exceed the capacity of the existing approved system.
903.2.1.4 Group A-4. | An automatic sprinkler system shall be provided for fire areas containing Group A-4 occupancies and intervening floors of the building where one of the following conditions exists: 1. The fire area exceeds 12,000 square feet (1114.8 m2). 2. The fire area has an occupant load of 300 or more. 3. The aggregate occupant load of all fire areas occupied by Group A, located on any given floor other than the level of exit discharge, is 300 or more. Exception: Areas used exclusively as participant sports areas where the main floor area is located at the same level as the level of exit discharge of the main entrance and exit. | 903.2.1.4 Group A-4. | An automatic sprinkler system shall be provided throughout stories containing Group A-4 occupancies and throughout all stories from the Group A-4 occupancy to and including the levels of exit discharge serving that occupancy where one of the following conditions exists:
901.9.5.4 Additional requirements for enlargements of buildings with no existing standpipe systems. | Where the alteration involves the addition of stories to a building with no existing standpipe system, standpipes shall be provided to all stair shafts in accordance with this chapter. Exception: Standpipes are not required where: 1. the alteration involves the addition of only one story; 2. the completed building does not exceed 7 stories; and 3. the completed building does not exceed 85 feet (25.9 m) in height.
903.2.1.5 Group A-5. | An automatic sprinkler system shall be provided in all enclosed areas of the structure, including but not limited to the concession concourse, concession stands, retail areas, press boxes and other accessory occupancies, in excess of 1,000 square feet (92.9 m2). | 903.2.1.5 Group A-5. | An automatic sprinkler system shall be provided for all enclosed Group A-5 accessory use areas in excess of 1,000 square feet (93 m2).
901.9.6 Seismic supports. | The determination as to whether seismic requirements apply to an alteration shall be made in accordance with the 1968 Building Code and interpretations by the department relating to such determinations. Any applicable seismic loads and requirements shall be permitted to be determined in accordance with Chapter 16 of this code or the 1968 Building Code and Reference Standard RS 9-6 of such code.
902.1 Definitions. | The following terms are defined in Chapter 2:
903.2.1.6 Assembly occupancies on roofs. | Where an occupied roof has an assembly occupancy with an occupant load exceeding 100 for Group A-2 and 300 for other Group A occupancies, all floors between the occupied roof and the level of exit discharge shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. Exception: Open parking garages of Type I or Type II construction. | 903.2.1.6 Assembly occupancies on roofs. | Where an occupied roof has an assembly occupancy with an occupant load exceeding 100 for Group A-2 and 300 for other Group A occupancies, all floors between the occupied roof and the level of exit discharge shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. Exception: Open parking garages of Type I or Type II construction.
903.2.1.7 Multiple fire areas. | An automatic sprinkler system shall be provided where multiple fire areas of Group A-1, A-2, A-3 or A-4 occupancies share exit or exit access components and the combined occupant load of theses fire areas is 300 or more. | 903.2.1.7 Multiple fire areas. | An automatic sprinkler system shall be provided where multiple fire areas of Group A-1, A-2, A-3 or A-4 occupancies share exit or exit access components and the combined occupant load of theses fire areas is 300 or more.
903.1.2 Construction documents. | Construction documents for automatic sprinkler systems shall contain plans that include the following data and information:
903.2.3 Group E. | An automatic sprinkler system shall be provided for Group E occupancies as follows: 1. Throughout all Group E fire areas greater than 12,000 square feet (1114.8 m2) in area. 2. Throughout every portion of educational buildings below the level of exit discharge. Exception: An automatic sprinkler system is not required in any fire area or area below the level of exit discharge where every classroom throughout the building has not fewer than one exterior exit door at ground level without intervening corridors, passageways, interior exit stairways or ramps or exit passageways. | 903.2.3 Group E. | An automatic sprinkler system shall be provided for Group E occupancies as follows: 1. Throughout all Group E fire areas greater than 12,000 square feet (1115 m2) in area. 2. The Group E fire area is located on a floor other than a level of exit discharge serving such occupancies. Exception: In buildings where every classroom has not fewer than one exterior exit door at ground level, an automatic sprinkler system is not required in any area below the lowest level of exit discharge serving that area. 3. The Group E fire area has an occupant load of 300 or more.
903.2.4.1 Woodworking operations. | An automatic sprinkler system shall be provided throughout all Group F-1 occupancy fire areas that contain woodworking operations in excess of 2,500 square feet (232.3 m2) in area that generate finely divided combustible waste or use finely divided combustible materials. | 903.2.4.1 Woodworking operations. | An automatic sprinkler system shall be provided throughout all Group F-1 occupancy fire areas that contain woodworking operations in excess of 2,500 square feet (232 m2) in area that generate finely divided combustible waste or use finely divided combustible materials.
903.2.5 Group H. | Automatic sprinkler systems shall be provided in high-hazard occupancies as required in the New York City Fire Code and Sections 903.2.5.1 through 903.2.5.3 of this code. | 903.2.5 Group H. | Automatic sprinkler systems shall be provided in high-hazard occupancies as required in Sections 903.2.5.1 through 903.2.5.3.
903.2.5.1 General. | An automatic sprinkler system shall be installed in Group H occupancies. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group H. | 903.2.5.1 General. | An automatic sprinkler system shall be installed in Group H occupancies.
903.2.5.2 Group H-5 occupancies. | An automatic sprinkler system shall be installed throughout buildings containing Group H-5 occupancies. The design of the sprinkler system shall be not less than that required by this code for the occupancy hazard classifications in accordance with Table 903.2.5.2. Where the design area of the sprinkler system consists of a corridor protected by one row of sprinklers, the maximum number of sprinklers required to be calculated is 13. | 903.2.5.2 Group H-5 occupancies. | An automatic sprinkler system shall be installed throughout buildings containing Group H-5 occupancies. The design of the sprinkler system shall be not less than that required by this code for the occupancy hazard classifications in accordance with Table 903.2.5.2. |  | See BC09 Tables&Figures
903.2.5.3 Pyroxylin plastics. | An automatic sprinkler system shall be provided in buildings, or portions thereof, where cellulose nitrate film or pyroxylin plastics are manufactured, stored or handled in quantities exceeding 100 pounds (45.4 kg). | 903.2.5.3 Pyroxylin plastics. | An automatic sprinkler system shall be provided in buildings, or portions thereof, where cellulose nitrate film or pyroxylin plastics are manufactured, stored or handled in quantities exceeding 100 pounds (45 kg).
903.2.6 Group I. | An automatic sprinkler system shall be provided in Group I occupancies. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group I. Exceptions: 1. An automatic sprinkler system installed in accordance with Section 903.3.1.2 or 903.3.1.3 shall be allowed in Group I-1 facilities if located in an I-1 occupancy building or a residential building, provided such building is six stories or less in height. 2. An automatic sprinkler system is not required where Group I-4 day care facilities are at the level of exit discharge and where every room where care is provided has not fewer than one exterior exit door. 3. In buildings where Group I-4 day care is provided on levels other than the level of exit discharge, an automatic sprinkler system in accordance with Section 903.3.1.1 shall be installed on the entire floor where care is provided, all floors between the level of care and the level of exit discharge, and all floors below the level of exit discharge other than areas classified as an open parking garage. | 903.2.6 Group I. | An automatic sprinkler system shall be provided throughout buildings with a Group I fire area. Exceptions: 1. An automatic sprinkler system installed in accordance with Section 903.3.1.2 shall be permitted in Group I-1, Condition 1 facilities. 2. An automatic sprinkler system is not required where Group I-4 day care facilities are at the level of exit discharge and where every room where care is provided has not fewer than one exterior exit door. 3. In buildings where Group I-4 day care is provided on levels other than the level of exit discharge, an au-tomatic sprinkler system in accordance with Section 903.3.1.1 shall be installed on the entire floor where care is provided, all floors between the level of care and the level of exit discharge, and all floors below the level of exit discharge other than areas classified as an open parking garage.
903.2.2 Group B. | An automatic sprinkler system shall be installed for Group B occupancies as provided in Sections 903.2.2.1 and 903.2.2.2.
903.2.7 Group M. | An automatic sprinkler system shall be provided throughout buildings containing a Group M occupancy where one of the following conditions exists: | 903.2.7 Group M. | An automatic sprinkler system shall be provided throughout buildings containing a Group M occupancy where one of the following conditions exists:
903.2.2.1 Ambulatory health care facilities. | An automatic sprinkler system shall be installed throughout all fire areas containing a Group B ambulatory health care facility occupancy. In buildings where ambulatory care is provided on levels other than the level of exit discharge, an automatic sprinkler system shall be installed throughout the entire floor where such care is provided as well as all floors below, and all floors between the level of ambulatory care and the nearest level of exit discharge, including the level of exit discharge.
903.2.7.1 High-piled storage. | An automatic sprinkler system shall be provided in accordance with the New York City Fire Code in all buildings of Group M where storage of merchandise is in high-piled or rack storage arrays. | 903.2.7.1 High-piled storage. | An automatic sprinkler system shall be provided in accordance with the International Fire Code in all buildings of Group M where storage of merchandise is in high-piled or rack storage arrays.
903.2.2.2 Animal service facilities. | An automatic sprinkler system shall be provided for animal service facilities. Exceptions: 1. Animal service facilities that provide 24 hour in-person supervision of animals sheltered therein and are equipped with smoke alarms. 2. Animal service facilities that were in operation on or before December 31, 2016, and are equipped with an automatic smoke detection system.
903.2.8 Group R. | An automatic sprinkler system shall be installed in Group R fire areas. An automatic sprinkler system shall be installed throughout buildings with a main use or dominant occupancy of Group R. Exception: An automatic sprinkler system shall not be required in detached one- and two-family dwellings and multiple single-family dwellings (townhouses), provided that such structures are not more than three stories above grade plane in height and have separate means of egress. | 903.2.8 Group R. | An automatic sprinkler system installed in accordance with Section 903.3 shall be provided throughout all buildings with a Group R fire area.
903.2.4 Group F. | An automatic sprinkler system shall be provided throughout all buildings containing a Group F occupancy where any one of the following conditions exists:
903.2.4.2 Repair garages. | An automatic sprinkler system shall be provided throughout all buildings used as repair garages in accordance with Section 406, as follows:
903.2.4.3 Group F-1 fire areas. | An automatic sprinkler system shall be provided throughout any Group F-1 occupancy fire area where any one of the following conditions exists:
903.2.9 Group S-1. | An automatic sprinkler system shall be provided throughout all buildings containing a Group S-1 occupancy where any one of the following conditions exists: | 903.2.9 Group S-1. | An automatic sprinkler system shall be provided throughout all buildings containing a Group S-1 occupancy where one of the following conditions exists:
903.2.9.2 Bulk storage of tires. | Buildings and structures where the area for the storage of tires exceeds 500 square feet (46.5 m2) or 7,500 cubic feet (212.3 m3) shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 903.2.9.2 Bulk storage of tires. | Buildings and structures where the area for the storage of tires exceeds 20,000 cubic feet (566 m3) shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
903.2.10.1 Commercial parking garages. | An automatic sprinkler system shall be provided throughout buildings used for storage of commercial trucks, buses or other commercial motor vehicles where the fire area exceeds 5,000 square feet (464.5 m2). | 903.2.10.1 Commercial parking garages. | An automatic sprinkler system shall be provided throughout buildings used for storage of commercial motor vehicles where the fire area exceeds 5,000 square feet (464 m2).
903.2.7.2 Group M fire areas. | An automatic sprinkler system shall be provided throughout any Group M occupancy fire area where any one of the following conditions exists:
903.2.11 Specific building areas and hazards. | An automatic sprinkler system shall be installed for building design or hazards in the locations set forth in Sections 903.2.11.1 through 903.2.11.13. | 903.2.11 Specific building areas and hazards. | In all occupancies other than Group U, an automatic sprinkler system shall be installed for building design or hazards in the locations set forth in Sections 903.2.11.1 through 903.2.11.6.
903.2.9.1 Group S-1 fire areas. | An automatic sprinkler system shall be provided throughout any Group S-1 occupancy fire area where the fire area exceeds 500 square feet (46.5 m2).
903.2.11.1.1 Opening dimensions and access. | Such openings shall have a minimum dimension of not less than 30 inches (762 mm). Such openings shall be accessible to the Fire Department from the exterior and shall not be obstructed in a manner that firefighting or rescue cannot be accomplished from the exterior. | 903.2.11.1.1 Opening dimensions and access. | Openings shall have a minimum dimension of not less than 30 inches (762 mm). Access to such openings shall be provided for the fire department from the exterior and shall not be obstructed in a manner such that fire fighting or rescue cannot be accomplished from the exterior.
903.2.11.1.2 Openings on one side only. | Where such openings in a story are provided on only one side and the opposite wall of such story is more than 100 feet (30 480 mm) from such openings, the story shall be equipped throughout with an approved automatic sprinkler system, or openings as specified above shall be provided on not fewer than two sides of the story. | 903.2.11.1.2 Openings on one side only. | Where openings in a story are provided on only one side and the opposite wall of such story is more than 75 feet (22 860 mm) from such openings, the story shall be equipped throughout with an approved automatic sprinkler system, or openings shall be provided on not fewer than two sides of the story.
903.2.9.3 High-piled storage. | An automatic sprinkler system shall be provided in accordance with the New York City Fire Code in all buildings or portions thereof in Group S-1 occupancies where the storage of merchandise is in high-piled or rack storage arrays.
903.2.10 Group S-2. | An automatic sprinkler system shall be installed throughout buildings greater than 5,000 square feet (464.5 m2) in area where the main use or dominant occupancy is Group S-2.
903.2.10.2 Group S-2 fire areas. | An automatic sprinkler system shall be provided throughout any Group S-2 occupancy fire area greater than 5,000 square feet (464.5 m2).
903.2.10.3 Parking garages. | An automatic sprinkler system shall be provided throughout buildings classified as enclosed parking garages in accordance with Section 406.4 or where an open or enclosed parking garage is located beneath other occupancy groups.
903.2.10.4 High-piled storage. | An automatic sprinkler system shall be provided in all buildings or portions thereof of Group S-2 occupancies in accordance with the New York City Fire Code.
903.2.12 During construction. | Automatic sprinkler systems required during construction, alteration and demolition operations shall be provided in accordance with the New York City Fire Code and Chapter 33 of this code. | 903.2.12 During construction. | Automatic sprinkler systems required during construction, alteration and demolition operations shall be provided in accordance with Chapter 33 of the International Fire Code.
903.2.11.1 Above- or below-grade stories. | An automatic sprinkler system shall be installed throughout every above- or below-grade story of all buildings where the floor area exceeds 1,500 square feet (139.4 m2) and where not fewer than one of the following types of exterior wall openings is provided:
903.3 Installation requirements. | Automatic sprinkler systems shall be designed and installed in accordance with Sections 903.3.1 through 903.3.8. | 903.3 Installation requirements. | Automatic sprinkler systems shall be designed and installed in accordance with Sections 903.3.1 through 903.3.8.
903.3.1 Standards. | Sprinkler systems shall be designed and installed in accordance with Section 903.3.1.1, 903.3.1.2 or 903.3.1.3. | 903.3.1 Standards. | Sprinkler systems shall be designed and installed in accordance with Section 903.3.1.1 unless otherwise permitted by Sections 903.3.1.2 and 903.3.1.3 and other chapters of this code, as applicable.
903.3.1.1 NFPA 13 sprinkler systems. | Where the provisions of this code require that a building or portion thereof be equipped throughout with an automatic sprinkler system in accordance with this section, sprinklers shall be installed throughout in accordance with NFPA 13 except as provided in Sectionsǂ 903.3.1.1.1 and 903.2 of this code. | 903.3.1.1 NFPA 13 sprinkler systems. | Where the provisions of this code require that a building or portion thereof be equipped throughout with an automatic sprinkler system in accordance with this section, sprinklers shall be installed throughout in accordance with NFPA 13 except as provided in Sections 903.3.1.1.1 and 903.3.1.1.2.
903.2.11.1.3 Below-grade stories. | Where any portion of a below-grade story is located more than 75 feet (22 860 mm) from openings required by Section 903.2.11.1, or where walls, partitions, or other obstructions are installed that restrict the application of water from hose streams, the below-grade story shall be equipped throughout with an approved automatic sprinkler system.
903.2.11.2 Other above-grade stories. | An automatic sprinkler system shall be installed throughout every above-grade story of buildings below a height of 100 feet (30 480 mm), other than the first story or ground floor, on which access is not provided directly from the outdoors by at least one window or readily identifiable access panel within each 50 feet (15 240 mm) or fraction thereof of horizontal length of every wall that fronts on a street or frontage space required pursuant to Section 501.3.1.
903.2.11.2.1 Opening dimensions and access. | Such windows shall be openable from the inside or breakable from both the inside and the outside, and shall have a size when open of at least 24 inches by 36 inches (609.6 mm by 914.4 mm). Such panels shall be openable from both the inside and outside and shall have a height when open of 48 inches (1220 mm) and a width of at least 32 inches (812.8 mm). The sill of the window or panel shall not be higher than 36 inches (914.4 mm) above the inside floor. Where not all of the windows are openable or breakable, the windows intended to satisfy the requirements of this section shall be readily identifiable.
903.3.1.2 NFPA 13R sprinkler systems. | Where allowed in buildings of Group R, up to and including six stories in height, automatic sprinkler systems shall be installed throughout in accordance with NFPA 13R. | 903.3.1.2 NFPA 13R sprinkler systems. | Automatic sprinkler systems in Group R occupancies shall be permitted to be installed throughout in accordance with NFPA 13R where the Group R occupancy meets all of the following conditions:
903.2.11.3 Other below-grade stories. | An automatic sprinkler system shall be installed throughout every first basement or cellar story below grade of buildings on which access is not provided directly from the outdoors within each 100 feet (30 480 mm) or fraction thereof of horizontal length of every wall that fronts on a street or frontage space required pursuant to Section 501.3.1. Exceptions: 1. One- and two-family dwellings need not provide direct access. 2. Any building classified in Occupancy Group R-2 not more than three stories in height and with not more than two dwelling units on any story need not provide direct access when such first basement or cellar story is used for dwelling units or for uses accessory to the residential use in the building. 3. Except as provided in Exception 2, above, for Group R-1 and R-2 occupancies, only one direct access from the outdoors to the first basement or cellar story consisting of a stair or door shall be required when such story is used for dwelling units or for uses accessory to the residential use in the building.
903.3.1.2.1 Balconies and decks. | Sprinkler protection shall be provided for exterior balconies, decks and ground-floor patios of dwelling units where the building is of Type V construction and automatic sprinkler protection is required for the Group R occupancy. Side wall sprinklers that are used to protect such areas shall be permitted to be located such that their deflectors are within 1 inch (25.4 mm) to 6 inches (152.4 mm) below the structural members, and a maximum distance of 14 inches (355.6 mm) below the deck of the exterior balconies and decks that are constructed of open wood joist construction. | 903.3.1.2.1 Balconies and decks. | Sprinkler protection shall be provided for exterior balconies, decks and ground floor patios of dwelling units and sleeping units where either of the following conditions exists: 1. The building is of Type V construction, provided that there is a roof or deck above. 2. Exterior balconies, decks and ground floor patios of dwelling units and sleeping units are constructed in accordance with Section 705.2.3.1, Exception 3.
903.2.11.3.1 Opening dimensions and access. | Such access shall be by stairs, doors, windows or other means that provide an opening 48 inches (1220 mm) high and 32 inches (812.8 mm) wide, the sill of which shall not be higher than 36 inches (914.4 mm) above the inside floor. If an areaway is used to provide below grade access, the minimum horizontal dimension shall be at least one-third the depth of the areaway or 6 feet (1828.8 mm), whichever is less.
903.2.11.4 Signs obstructing openings. | Where wall signs are erected to cover doors or windows of existing buildings, access panels shall be provided as necessary to comply with the requirements of Section 903.2.11.
903.2.11.5 Compliance with the New York State Multiple Dwelling Law. | Nothing in Section 903.2.11 shall be construed so as to supersede any applicable provisions of Section 54 of the New York State Multiple Dwelling Law relating to access to cellars or basements in multiple dwellings.
903.3.1.3 NFPA 13D sprinkler systems. | Where allowed, automatic sprinkler systems in one- and two-family dwellings and townhouses, up to and including six stories in height, shall be installed throughout in accordance with NFPA 13D. | 903.3.1.3 NFPA 13D sprinkler systems. | Automatic sprinkler systems installed in one- and two-family dwellings; Group R-3; Group R-4, Condition 1; and townhouses shall be permitted to be installed throughout in accordance with NFPA 13D.
903.2.11.6 Rubbish and linen chutes. | An automatic sprinkler system shall be installed at the top of rubbish and linen chutes, in chute access rooms, and in their terminal rooms. Chutes shall have additional sprinkler heads installed at alternate floors and at the lowest intake. Where a rubbish chute extends through a building more than one floor below the lowest intake, or through areas with no openings, such an extension shall have sprinklers installed that are recessed from the drop area of the chute and protected from freezing in accordance with Section 903.3.1.1. Such sprinklers shall be installed at alternate floors, beginning with the second level below the last intake and ending with the floor above the discharge. All chute sprinklers shall be accessible for servicing and shall not obstruct the vertical path for rubbish or linens.
903.3.2 Quick-response and residential sprinklers. | Where automatic sprinkler systems are required by this code, quick-response or residential automatic sprinklers shall be installed in all of the following areas in accordance with Section 903.3.1 and their listings: | 903.3.2 Quick-response and residential sprinklers. | Where automatic sprinkler systems are required by this code, quick-response or residential automatic sprinklers shall be installed in all of the following areas in accordance with Section 903.3.1 and their listings:
903.2.11.7 Buildings 55 feet (16 764 mm) or more in height. | An automatic sprinkler system shall be installed throughout buildings that have one or more stories with an occupant load of 30 or more located 55 feet (16 764 mm) or more above the lowest level of Fire Department vehicle access, measured to the finished floor. Exceptions: 1. Open parking structures without any other occupancy groups, unless otherwise required. 2. Occupancies in Group F-2, unless required by the New York State Department of Labor.
903.3.3 Obstructed locations. | Automatic sprinklers shall be installed with due regard to obstructions that will delay activation or obstruct the water distribution pattern. Automatic sprinklers shall be installed in or under covered kiosks, displays, booths, concession stands, or equipment that exceeds 4 feet (1220 mm) in width. Not less than a 3-foot (914.4 mm) clearance shall be maintained between automatic sprinklers and the top of piles of combustible fibers. Exception: Kitchen equipment under exhaust hoods protected with a fire-extinguishing system in accordance with this code and the New York City Fire Code. | 903.3.3 Obstructed locations. | Automatic sprinklers shall be installed with regard to obstructions that will delay activation or obstruct the water distribution pattern and shall be in accordance with the applicable automatic sprinkler system standard that is being used. Automatic sprinklers shall be installed in or under covered kiosks, displays, booths, concession stands, or equipment that exceeds 4 feet (1219 mm) in width. Not less than a 3-foot (914 mm) clearance shall be maintained between automatic sprinklers and the top of piles of combustible fibers. Exception: Kitchen equipment under exhaust hoods protected with a fire-extinguishing system in accordance with Section 904.
903.2.11.8 Ducts conveying hazardous exhausts. | Where required by the New York City Mechanical Code, automatic sprinklers shall be provided in ducts conveying hazardous exhaust or flammable or combustible materials. Exception: Ducts where the largest cross-sectional diameter of the duct is less than 10 inches (254 mm).
903.3.4 Actuation. | Automatic sprinkler systems shall be automatically actuated unless specifically provided for in this code. | 903.3.4 Actuation. | Automatic sprinkler systems shall be automatically actuated unless specifically provided for in this code.
903.2.11.9 Commercial cooking operations. | An automatic sprinkler system shall not be installed in a commercial kitchen exhaust hood and duct system. Fire-extinguishing systems shall be installed in commercial cooking systems in accordance with this code and the New York City Fire Code.
903.3.5 Water supplies. | Water supplies for automatic sprinkler systems shall comply with this section and the standards referenced in Section 903.3.1. The potable water supply shall be protected against back flow in accordance with the requirements of this section, the New York City Plumbing Code, and Rules of the New York City Department of Environmental Protection. | 903.3.5 Water supplies. | Water supplies for automatic sprinkler systems shall comply with this section and the standards referenced in Section 903.3.1. The potable water supply shall be protected against backflow in accordance with the requirements of this section and the International Plumbing Code. For connections to public waterworks systems, the water supply test used for design of fire protection systems shall be adjusted to account for seasonal and daily pressure fluctuations based on information from the water supply authority and as approved by the fire code official.
903.2.11.10 Other buildings, occupancies and areas. | In addition to the requirements of Section 903.2, the provisions indicated in Table 903.2.11.10 also require the installation of a suppression system for certain buildings and areas. Suppression systems shall also be required as provided for in other sections of this code, the New York City Fuel Gas Code, and the New York City Mechanical Code. |  |  |  | See BC09 Tables&Figures
903.3.5.1 Domestic services. | Where the domestic service provides the water supply for the automatic sprinkler system, the supply shall be in accordance with NFPA 13, 13R and 13D. | 903.3.5.1 Domestic services. | Where the domestic service provides the water supply for the automatic sprinkler system, the supply shall be in accordance with this section.
903.2.11.11 Steel-plated and vault-like occupancies. | An automatic sprinkler system shall be installed throughout all steel-plated or similarly reinforced or secured vault-like occupancies regardless of area.
903.2.11.12 Refuse collection and disposal areas. | An automatic sprinkler system shall be installed throughout all areas used for the storage and sorting of refuse and recyclables.
903.3.6 Hose threads. | Fire hose threads and fittings used in connection with automatic sprinkler systems shall be approved and compatible with Fire Department hose threads. | 903.3.6 Hose threads. | Fire hose threads and fittings used in connection with automatic sprinkler systems shall be as prescribed by the fire code official.
903.2.11.13 Laundry drying areas. | An automatic sprinkler system shall be installed in spaces in which two or more clothes drying machines are installed. Sprinkler heads shall be spaced to cover the areas 5 feet (1524 mm) on all sides of the drying machines.
903.3.8 Limited area sprinkler systems. | Limited area sprinkler systems shall be in accordance with the standards listed in Section 903.3.1 except as provided in Sections 903.3.8.1 through 903.3.8.5. | 903.3.8 Limited area sprinkler systems. | Limited area sprinkler systems shall be in accordance with the standards listed in Section 903.3.1 except as provided in Sections 903.3.8.1 through 903.3.8.5.
903.2.13 Type IV construction with cross-laminated timber (CLT) or structural composite lumber (SCL). | Automatic sprinkler systems in accordance with NFPA 13 shall be required throughout buildings utilizing Type IV construction with CLT or SCL as follows:
903.3.8.1 Number of sprinklers. | Limited area sprinkler systems shall not exceed six sprinklers in any single fire area. | 903.3.8.1 Number of sprinklers. | Limited area sprinkler systems shall not exceed six sprinklers in any single fire area.
903.3.8.2 Occupancy hazard classification. | Only areas classified by NFPA 13 as Light Hazard or Ordinary Hazard Group 1 shall be permitted to be protected by limited area sprinkler systems. | 903.3.8.2 Occupancy hazard classification. | Only areas classified by NFPA 13 as Light Hazard or Ordinary Hazard Group 1 shall be permitted to be protected by limited area sprinkler systems.
903.3.8.3 Piping arrangement. | Where a limited area sprinkler system is installed in a building with an automatic wet standpipe system, sprinklers shall be supplied by the standpipe system. Where a limited area sprinkler system is installed in a building without an automatic wet standpipe system, water shall be permitted to be supplied by the plumbing system provided that the plumbing system is capable of simultaneously supplying domestic and sprinkler demands. | 903.3.8.3 Piping arrangement. | Where a limited area sprinkler system is installed in a building with an automatic wet standpipe system, sprinklers shall be supplied by the standpipe system. Where a limited area sprinkler system is installed in a building without an automatic wet standpipe system, water shall be permitted to be supplied by the plumbing system provided that the plumbing system is capable of simultaneously supplying domestic and sprinkler demands.
903.3.8.4 Supervision. | Control valves shall not be installed between the water supply and sprinklers unless the valves are of an approved indicating type that are supervised or secured in the open position. | 903.3.8.4 Supervision. | Control valves shall not be installed between the water supply and sprinklers unless the valves are of an approved indicating type that are supervised or secured in the open position.
903.3.1.1.1 Exempt locations protected by other means. | When approved by the Fire Department, automatic sprinklers shall not be required in the following:
903.3.8.5 Calculations. | Hydraulic calculations in accordance with NFPA 13 shall be provided to demonstrate that the available water flow and pressure are adequate to supply all sprinklers installed in any single fire area with discharge densities corresponding to the hazard classification. | 903.3.8.5 Calculations. | Hydraulic calculations in accordance with NFPA 13 shall be provided to demonstrate that the available water flow and pressure are adequate to supply all sprinklers installed in any single fire area with discharge densities corresponding to the hazard classification.
903.4 Sprinkler system supervision and alarms. | Valves controlling the water supply for automatic sprinkler systems, pumps, tanks, water levels and temperatures, critical air pressures and water-flow switches on all sprinkler systems shall be electrically supervised by the fire alarm system where such fire alarm system is required by Section 907. Exceptions: 1. Automatic sprinkler systems protecting one- and two-family dwellings. 2. Limited area sprinkler systems in accordance with Section 903.3.8. 3. Automatic sprinkler systems installed in accordance with NFPA 13R where a common supply main is used to supply both domestic water and the automatic sprinkler system, and a separate shutoff valve for the automatic sprinkler system is not provided. 4. Jockey pump control valves that are sealed or locked in the open position. 5. Control valves to commercial kitchen hoods, paint spray booths or dip tanks that are sealed or locked in the open position. 6. Valves controlling the fuel supply to fire pump engines that are sealed or locked in the open position. 7. Trim valves to pressure switches in dry, preaction and deluge sprinkler systems that are sealed or locked in the open position. | 903.4 Sprinkler system supervision and alarms. | Valves controlling the water supply for automatic sprinkler systems, pumps, tanks, water levels and temperatures, critical air pressures and waterflow switches on all sprinkler systems shall be electrically supervised by a listed fire alarm control unit. Exceptions: 1. Automatic sprinkler systems protecting one- and two-family dwellings. 2. Limited area sprinkler systems in accordance with Section 903.3.8. 3. Automatic sprinkler systems installed in accordance with NFPA 13R where a common supply main is used to supply both domestic water and the automatic sprinkler system, and a separate shutoff valve for the automat-ic sprinkler system is not provided. 4. Jockey pump control valves that are sealed or locked in the open position. 5. Control valves to commercial kitchen hoods, paint spray booths or dip tanks that are sealed or locked in the open position. 6. Valves controlling the fuel supply to fire pump engines that are sealed or locked in the open position. 7. Trim valves to pressure switches in dry, preaction and deluge sprinkler systems that are sealed or locked in the open position. 8. Underground key or hub gate valves in roadway boxes.
903.3.1.2.2 Open-ended corridors. | Sprinkler protection and freeze protection shall be provided in open-ended corridors and associated exterior stairways and ramps as specified in Section 1027.6, Exception 3.
903.4.2 Alarms. | An approved audible device, located on the exterior of the building in an approved location, shall be connected to each automatic sprinkler system. Such sprinkler water-flow alarm devices shall be activated by water flow equivalent to the flow of a single sprinkler of the smallest orifice size installed in the system. Alarm devices shall be provided on the exterior of the building in an approved location or in a location approved by the Fire Department, except in buildings equipped with a fire alarm system. Where a fire alarm system is installed, actuation of the automatic sprinkler system shall actuate the building fire alarm system. | 903.4.2 Alarms. | An approved audible device, located on the exterior of the building in an approved location, shall be connected to each automatic sprinkler system. Such sprinkler waterflow alarm devices shall be activated by water flow equivalent to the flow of a single sprinkler of the smallest orifice size installed in the system. Where a fire alarm system is installed, actuation of the automatic sprinkler system shall actuate the building fire alarm system.
903.4.3 Floor control valves. | Approved supervised indicating control valves shall be provided at the point of connection to the riser on each floor in high-rise buildings. | 903.4.3 Floor control valves. | Approved supervised indicating control valves shall be provided at the point of connection to the riser on each floor in high-rise buildings.
903.5 Testing and maintenance. | Sprinkler systems shall be tested and maintained in accordance with the New York City Fire Code. | 903.5 Testing and maintenance. | Sprinkler systems shall be tested and maintained in accordance with the International Fire Code.
904.1 General. | Automatic fire-extinguishing systems, other than automatic sprinkler systems, shall be designed, installed, inspected, tested and maintained in accordance with the provisions of this section, the New York City Fire Code, and the applicable referenced standards. | 904.1 General. | Automatic fire-extinguishing systems, other than automatic sprinkler systems, shall be designed, installed, inspected, tested and maintained in accordance with the provisions of this section and the applicable referenced standards.
903.3.5.1.1 Residential combination services. | A single combination water supply shall be permitted in accordance with NFPA 13R.
904.3 Installation. | Automatic fire-extinguishing systems shall be installed in accordance with this section. | 904.3 Installation. | Automatic fire-extinguishing systems shall be installed in accordance with this section.
903.3.5.2 Secondary on-site water supply. | A secondary on-site water supply for high-rise buildings shall be provided in accordance with Section 403.3.3.
904.3.1 Electrical wiring. | Electrical wiring shall be in accordance with the New York City Electrical Code. | 904.3.1 Electrical wiring. | Electrical wiring shall be in accordance with NFPA 70.
904.3.2 Actuation. | Automatic fire-extinguishing systems shall be automatically actuated and provided with a manual means of actuation in accordance with Section 904.12.1. Where more than one hazard could be simultaneously involved in fire due to their proximity, all hazards shall be protected by a single system designed to protect all hazards that could become involved. Exception: Multiple systems shall be permitted to be installed if they are designed to operate simultaneously. | 904.3.2 Actuation. | Automatic fire-extinguishing systems shall be automatically actuated and provided with a manual means of actuation in accordance with Section 904.11.1. Where more than one hazard could be simultaneously involved in fire due to their proximity, all hazards shall be protected by a single system designed to protect all hazards that could become involved. Exception: Multiple systems shall be permitted to be installed if they are designed to operate simultaneously.
903.3.7 Fire Department connections. | The location of Fire Department connections for automatic sprinkler systems shall be installed in accordance with Sections 905 and 912.
904.3.3 System interlocking. | Automatic equipment interlocks with fuel shutoffs, ventilation controls, door closers, window shutters, conveyor openings, smoke and heat vents and other features necessary for proper operation of the fire-extinguishing system shall be provided as required by the design and installation standard utilized for the hazard. | 904.3.3 System interlocking. | Automatic equipment interlocks with fuel shutoffs, ventilation controls, door closers, window shutters, conveyor openings, smoke and heat vents and other features necessary for proper operation of the fire-extinguishing system shall be provided as required by the design and installation standard utilized for the hazard.
904.3.4 Alarms and warning signs. | Where alarms are required to indicate the operation of automatic fire-extinguishing systems, distinctive audible and visible alarms and warning signs shall be provided to warn of pending agent discharge. Where exposure to automatic-extinguishing agents poses a hazard to persons and a delay is required to ensure the evacuation of occupants before agent discharge, a separate warning signal shall be provided to alert occupants once agent discharge has begun. Audible signals shall be in accordance with Section 907.5.2. | 904.3.4 Alarms and warning signs. | Where alarms are required to indicate the operation of automatic fire-extinguishing systems, distinctive audible and visible alarms and warning signs shall be provided to warn of pending agent discharge. Where exposure to automatic-extinguishing agents poses a hazard to persons and a delay is required to ensure the evacuation of occupants before agent discharge, a separate warning signal shall be provided to alert occupants once agent discharge has begun. Audible signals shall be in accordance with Section 907.5.2.
904.3.5 Monitoring. | Where a fire alarm system is installed, automatic fire-extinguishing systems shall be monitored by the fire alarm system in accordance with NFPA 72. | 904.3.5 Monitoring. | Where a building fire alarm system is installed, automatic fire-extinguishing systems shall be monitored by the building fire alarm system in accordance with NFPA 72.
904.4 Inspection and testing. | Automatic fire-extinguishing systems shall be inspected and tested in accordance with the provisions of this section and the New York City Fire Code prior to acceptance. | 904.4 Inspection and testing. | Automatic fire-extinguishing systems shall be inspected and tested in accordance with the provisions of this section prior to acceptance.
904.4.1 Inspection. | Prior to conducting final acceptance tests, all of the following items shall be inspected: | 904.4.1 Inspection. | Prior to conducting final acceptance tests, all of the following items shall be inspected:
904.4.2 Alarm testing. | Notification appliances, connections to fire alarm systems and connections to central supervising stations shall be tested in accordance with this section and Section 907 to verify proper operation. | 904.4.2 Alarm testing. | Notification appliances, connections to fire alarm systems and connections to approved supervising stations shall be tested in accordance with this section and Section 907 to verify proper operation.
904.4.2.1 Audible and visible signals. | The audibility and visibility of notification appliances signaling agent discharge or system operation, where required, shall be verified. | 904.4.2.1 Audible and visible signals. | The audibility and visibility of notification appliances signaling agent discharge or system operation, where required, shall be verified.
904.4.3 Monitor testing. | Connections to protected premises and supervising station fire alarm systems shall be tested to verify proper identification and retransmission of alarms from automatic fire-extinguishing systems. | 904.4.3 Monitor testing. | Connections to protected premises and supervising station fire alarm systems shall be tested to verify proper identification and retransmission of alarms from automatic fire-extinguishing systems.
903.4.1 Signals and monitoring. | Alarm, supervisory and trouble signals shall be distinctly different and shall be automatically transmitted to a central supervising station or when approved by the Fire Department, shall sound an audible signal at a constantly attended location. Exceptions: 1. Underground key or hub valves in roadway boxes provided by the city or a public utility are not required to be monitored. 2. Backflow prevention device test valves, located in limited area sprinkler system supply piping, shall be locked in the open position. In occupancies required to be equipped with a fire alarm system, the backflow preventer valves shall be electrically supervised by a tamper switch installed in accordance with NFPA 72 and separately annunciated.
904.5 Wet-chemical systems. | Wet-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code. | 904.5 Wet-chemical systems. | Wet-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 17A and their listing. Records of inspections and testing shall be maintained.
904.6 Dry-chemical systems. | Dry-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with New York City Fire Code. New dry-chemical extinguishing systems are not permitted for the protection of kitchen equipment. | 904.6 Dry-chemical systems. | Dry-chemical extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 17 and their listing. Records of inspections and testing shall be maintained.
904.7 Foam systems. | Foam-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code. | 904.7 Foam systems. | Foam-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 11 and NFPA 16 and their listing. Records of inspections and testing shall be maintained.
904.8 Carbon dioxide systems. | Carbon dioxide extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code. | 904.8 Carbon dioxide systems. | Carbon dioxide extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 12 and their listing. Records of inspections and testing shall be maintained.
903.6 Painting of dedicated sprinkler piping and valve handles. | Dedicated sprinkler piping shall be painted and such painting certified in accordance with Sections 903.6.1 through 903.6.5 of this code. In addition to painting, sprinkler piping may also be identified by lettered legend in accordance with ANSI A13.1. Where the piping is required to be listed and labeled, such painting shall not obscure such labeling. Exceptions: 1. Attachments, gauges, valves and operable parts of sprinkler systems other than valve handles. 2. Horizontal branch lines. 3. Where different color coding may be required by Section 3406 of the New York City Fire Code for facilities storing, handling, and using flammable and combustible liquids in connection with special operations.
904.9 Halon systems. | Halogenated extinguishing systems shall not be permitted. However, existing systems shall be maintained, periodically inspected and tested in accordance with the New York City Fire Code. | 904.9 Halon systems. | Halogenated extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 12A and their listing. Records of inspections and testing shall be maintained.
903.6.1 New buildings. | Cross connections and risers in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red and the handles of valves serving dedicated sprinklers shall be painted green prior to the hydrostatic pressure test regardless of whether they will be enclosed at a later point in time. Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.
904.10 Clean-agent systems. | Clean-agent fire-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with the New York City Fire Code. | 904.10 Clean-agent systems. | Clean-agent fire-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 2001 and their listing. Records of inspections and testing shall be maintained.
903.6.2 Alterations. | Cross connections and risers for independent (stand-alone) existing sprinkler systems that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red and the handles of valves serving such existing sprinkler systems shall be painted green. Where the alteration requires a hydrostatic pressure test such painting shall be completed prior to such test. Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.
904.11 Automatic water mist systems. | Automatic water mist systems shall be permitted in applications that are consistent with the applicable listing or approvals and shall comply with Sections 904.11.1 through 904.11.3. | 904.11 Automatic water mist systems. | Automatic water mist systems shall be permitted in applications that are consistent with the applicable listing or approvals and shall comply with Sections 904.11.1 through 904.11.3.
903.6.3 Retroactive requirement for completed buildings. | Notwithstanding any other provision of law, all exposed risers and cross connections of completed buildings in existence on March 2, 2010, shall be painted red and all handles of valves serving such sprinkler system shall be painted green. Exception: Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow.
904.11.1 Design and installation requirements. | Automatic water mist systems shall be designed and installed in accordance with Sections 904.11.1.1 through 904.11.1.4. | 904.11.1 Design and installation requirements. | Automatic water mist systems shall be designed and installed in accordance with Sections 904.11.1.1 through 904.11.1.4.
903.6.4 Buildings under construction on March 2, 2010. | Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of a new building or alteration of an existing building prior to March 2, 2010, and the work is not signed off by the department prior to such date, all exposed cross connections and risers in any such building shall be painted red prior to the hydrostatic pressure test, including cross connections and risers that will be enclosed at a later point in time, and handles of valves serving such sprinkler system shall be painted green. Exceptions: 1. Where a standpipe system is used as a combination standpipe and sprinkler system, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red and the handles of valves serving such combination system shall be painted yellow. 2. Cross connections and risers enclosed prior to March 2, 2010, need not be painted.
904.11.1.1 General. | Automatic water mist systems shall be designed and installed in accordance with the manufacturer’s instructions and the New York City Fire Code. | 904.11.1.1 General. | Automatic water mist systems shall be designed and installed in accordance with NFPA 750 and the manufacturer’s instructions.
903.6.5 Certification of completion of system painting. | For all buildings where sprinkler and combination sprinkler and standpipe systems are not subject to a special inspection pursuant to Section 1705.2.9 of this code, a licensed master plumber, licensed master fire suppression piping contractor, registered design professional or an individual holding an appropriate certificate of fitness from the Fire Department for the operation and/or maintenance of such system shall certify on forms provided by the department that all required painting has been completed in accordance with Section 903.6. Such certification shall be maintained on the premises and made available for inspection by the department and the Fire Department.
904.11.1.2 Actuation. | Automatic water mist systems shall be automatically actuated. | 904.11.1.2 Actuation. | Automatic water mist systems shall be automatically actuated.
904.11.1.3 Water supply protection. | Connections to a potable water supply shall be protected against backflow in accordance with the New York City Plumbing Code. | 904.11.1.3 Water supply protection. | Connections to a potable water supply shall be protected against backflow in accordance with the International Plumbing Code.
904.1.1 Construction documents. | Construction documents for alternative automatic fire-extinguishing systems shall be approved by the Fire Department and shall contain plans that include at least the following data and information: 1. Commercial kitchen suppression systems: 1.1. Location of all surface, plenum and duct nozzles; surface dimensions and location of all cooking appliances; the location of automatic fuel shutoff and statement as to type (gas or electric); location and distance of the remote control or manual pull station; 1.2. Identification of the grease filters to be used in any kitchen hood; the dimensions of all hoods and all related ducts, including termination of duct at the exterior of the building; 1.3. Identification of the fire suppression piping system; the make and model of the system; the type of extinguishing agent and number and size of agent containers; size, length, and type of all piping that will be used; the number and location of all fusible links or detectors and the temperature setting; any surface, plenum and duct nozzles. 2. For extinguishing agent systems, the plan should also include type and concentration of the extinguishing agent, the method of providing power supply to smoke or heat detectors, fire rating of partitions, location of all audible/visible alarms within and outside the location involved and the details of construction of the room to contain the extinguishing agent. If the area is not sprinklered, the following information is required: 2.1. The size and location of the reserve supply, and 2.2 Information as to why it has been determined that water is not effective as an extinguishing agent for the fire hazard in such location. 3. The plans must note whether the proposed system is connected to the building’s fire alarm system. Exception: For that portion of a fire suppression piping system within an approved preengineered system, a schematic isometric diagram shall be acceptable in lieu of full plans, provided that the location and method of pressure relief must be indicated with areas and volumes to where said relief is taken.
904.11.1.4 Secondary water supply. | Where a secondary water supply is required for an automatic sprinkler system, an automatic water mist system shall be provided with an approved secondary water supply in accordance with the New York City Fire Code. | 904.11.1.4 Secondary water supply. | Where a secondary water supply is required for an automatic sprinkler system, an automatic water mist system shall be provided with an approved secondary water supply.
904.2 Where required. | Automatic fire-extinguishing systems installed as an alternative to the required automatic sprinkler systems of Section 903 shall be approved by the Fire Department. Automatic fire-extinguishing systems shall not be considered alternatives for the purposes of exceptions or reductions allowed by other requirements of this code.
904.11.2 Water mist system supervision and alarms. | Supervision and alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4. | 904.11.2 Water mist system supervision and alarms. | Supervision and alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.
904.2.1 Hood system suppression. | Each required commercial kitchen exhaust hood and duct system required by Chapter 5 of the New York City Mechanical Code to have a Type I hood shall be protected with an automatic fire-extinguishing system installed in accordance with this code and the New York City Fire Code.
904.11.2.1 Monitoring. | Monitoring shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.1. | 904.11.2.1 Monitoring. | Monitoring shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.1.
904.11.2.2 Alarms. | Alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.2. | 904.11.2.2 Alarms. | Alarms shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.2.
904.11.2.3 Floor control valves. | Floor control valves shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.3. | 904.11.2.3 Floor control valves. | Floor control valves shall be provided as required for automatic sprinkler systems in accordance with Section 903.4.3.
905.1 General. | Standpipe systems shall be provided in buildings and structures in accordance with this section. Fire hose threads used in connection with standpipe systems shall be approved by the Fire Commissioner. Standpipe systems in buildings used for high-piled combustible storage shall be in accordance with the New York City Fire Code. Installation of standpipe systems shall comply with the special inspection requirements of Chapter 17 of this code. | 905.1 General. | Standpipe systems shall be provided in new buildings and structures in accordance with Sections 905.2 through 905.11. In buildings used for high-piled combustible storage, fire protection shall be in accordance with the International Fire Code.
905.3 Required installations. | Standpipe systems shall be installed where required by Sections 905.3.1 through 905.3.9 and in the locations indicated in Sections 905.4, 905.5 and 905.6. Standpipe systems are allowed to be combined with automatic sprinkler systems. Exception: Standpipe systems are not required in buildings occupied entirely by Group R-3. | 905.3 Required installations. | Standpipe systems shall be installed where required by Sections 905.3.1 through 905.3.8. Standpipe systems are allowed to be combined with automatic sprinkler systems. Exception: Standpipe systems are not required in Group R-3 occupancies.
905.3.2 Group A. | Class I automatic wet standpipes shall be provided in nonsprinklered Group A buildings having an occupant load exceeding 1,000 persons. Exceptions: 1. Open-air-seating spaces without enclosed spaces. 2. Class I automatic dry and semiautomatic dry standpipes or manual wet standpipes are allowed in buildings where the highest floor surface used for human occupancy is not more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access. Dry standpipes are permitted only where subject to freezing temperatures. | 905.3.2 Group A. | Class I automatic wet standpipes shall be provided in nonsprinklered Group A buildings having an occupant load exceeding 1,000 persons. Exceptions: 1. Open-air-seating spaces without enclosed spaces. 2. Class I automatic dry and semiautomatic dry standpipes or manual wet standpipes are allowed in build-ings that are not high-rise buildings. Exception: Where the building or area is equipped throughout with an automatic sprinkler system, a 11/2-inch (38 mm) hose connection shall be installed in accordance with NFPA 13 or in accordance with NFPA 14 for Class II or III standpipes.
905.3.4 Stages. | Stages greater than 1,000 square feet in area (92.9 m2), or any assembly occupancy having an occupant load of 1,000 or more with a stage of any size, shall be equipped with a Class III wet standpipe system with a hose station on each side of the stage. Such hose stations shall comply with Section 905.6 and shall have sufficient hose to provide protection for the entire stage area from either standpipe location. The exceptions allowed under Section 905.3.1 shall not apply to these hose stations. | 905.3.4 Stages. | Stages greater than 1,000 square feet in area (93 m2) shall be equipped with a Class III wet standpipe system with 11/2-inch and 21/2-inch (38 mm and 64 mm) hose connections on each side of the stage. Exception: Where the building or area is equipped throughout with an automatic sprinkler system, a 11/2-inch (38 mm) hose connection shall be installed in accordance with NFPA 13 or in accordance with NFPA 14 for Class II or III standpipes.
905.3.5 Underground buildings. | Underground buildings shall be equipped throughout with a Class I automatic wet or manual wet standpipe system. | 905.3.5 Underground buildings. | Underground buildings shall be equipped throughout with a Class I automatic wet or manual wet standpipe system.
905.3.6 Helistops and heliports. | Buildings with a helistop or heliport that are equipped with a standpipe shall extend the standpipe to the roof level on which the helistop or heliport is located in accordance with the New York City Fire Code. All portions of the helistop and heliport area shall be within 150 feet (45 720 mm) of a 2½-inch (63.5 mm) outlet on a Class I or III standpipe, in accordance with the New York City Fire Code. | 905.3.6 Helistops and heliports. | Buildings with a rooftop helistop or heliport shall be equipped with a Class I or III standpipe system extended to the roof level on which the helistop or heliport is located in accordance with Section 2007.5 of the International Fire Code.
905.3.7 Marinas and boatyards. | Standpipes in marine terminals, piers, wharves, marinas and boatyards shall comply with the New York City Fire Code or other requirements of the Fire Department. | 905.3.7 Marinas and boatyards. | Standpipes in marinas and boatyards shall comply with Chapter 36 of the International Fire Code.
904.11.3 Testing, operation and maintenance. | Automatic water mist systems shall be tested, operated and maintained in accordance with the New York City Fire Code.
905.4 Location of Class I standpipe hose connections. | Class I standpipe hose connections shall be provided in all of the following locations: 1. In every required stairway, a hose connection shall be provided for each floor level above or below grade. Hose connections shall be readily accessible and located at the riser on each floor-level landing and on the entrance floor above the standpipe riser control valve. Nonrequired enclosed stairways that do not serve as a means of egress are not required to have hose connections. Stairways without hose connections shall have a sign on the door to the stairway stating, “No standpipe connections in stairway”. 2. On each side of the wall adjacent to the exit opening of a horizontal exit. Exception: Where floor areas adjacent to a horizontal exit are reachable from exit stairway hose connections by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the horizontal exit. 3. In every exit passageway at the entrance from the exit passageway to the other areas of a building. Exception: Where floor areas adjacent to an exit passageway are reachable from exit stairway hose connections by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the entrance from the exit passageway to other areas of the building. 4. In covered mall buildings, in accordance with Section 905.3.3.2. 5. Where the roof has a slope of less than four units vertical in 12 units horizontal (33.3-percent slope), each standpipe shall be provided with a hose connection located either on the roof or at the highest landing of stairways with stair access to the roof. An additional hose connection shall be provided at the top of the most hydraulically remote standpipe for testing purposes. This additional hose connection shall not be required when a roof manifold is installed in accordance with NFPA 14. 6. Where the most remote portion of a floor or story is more than 150 feet (45 720 mm) from a hose connection, additional hose connections shall be provided in approved locations. For the purposes of this section, a penthouse with an occupant load greater than 10 shall be considered a story. 7. In any staircase where the change in elevation between floor landings is more than 25 feet (7620 mm), in addition to the hose connections required by Item 1, a hose connection shall be installed at the first intermediate stair landing below the higher floor level. | 905.4 Location of Class I standpipe hose connections. | Class I standpipe hose connections shall be provided in all of the following locations: 1. In every required interior exit stairway, a hose connection shall be provided for each story above and below grade plane. Hose connections shall be located at the main floor landing unless otherwise approved by the fire code official. Exception: A single hose connection shall be permitted to be installed in the open corridor or open breezeway between open stairs that are not greater than 75 feet (22 860 mm) apart. 2. On each side of the wall adjacent to the exit opening of a horizontal exit. Exception: Where floor areas adjacent to a horizontal exit are reachable from an interior exit stairway hose connection by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the horizontal exit. 3. In every exit passageway, at the entrance from the exit passageway to other areas of a building. Exception: Where floor areas adjacent to an exit passageway are reachable from an interior exit stairway hose connection by a 30-foot (9144 mm) hose stream from a nozzle attached to 100 feet (30 480 mm) of hose, a hose connection shall not be required at the entrance from the exit passageway to other areas of the building. 4. In covered mall buildings, adjacent to each exterior public entrance to the mall and adjacent to each entrance from an exit passageway or exit corridor to the mall. In open mall buildings, adjacent to each public entrance to the mall at the perimeter line and adjacent to each entrance from an exit passageway or exit corridor to the mall. 5. Where the roof has a slope less than 4 units vertical in 12 units horizontal (33.3-percent slope), a hose connec-tion shall be located to serve the roof or at the highest landing of an interior exit stairway with access to the roof provided in accordance with Section 1011.12. 6. Where the most remote portion of a nonsprinklered floor or story is more than 150 feet (45 720 mm) from a hose connection or the most remote portion of a sprinklered floor or story is more than 200 feet (60 960 mm) from a hose connection, the fire code official is authorized to require that additional hose connections be pro-vided in approved locations.
904.12 Commercial cooking systems. | The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Preengineered automatic wet-chemical extinguishing systems shall be approved by the Fire Commissioner, tested in accordance with UL 300, and listed and labeled for the intended application. The protected area shall include the area under the hood and over the cooking equip­ment, the area above or behind the filters and the opening of the hood into the branch duct. Where a preengineered system is installed and the size of the protected area exceeds that allowed for a single preengineered system, additional preengineered systems arranged for simultaneous operation shall be pro­vided. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed in accordance with this code, its listing and the manufacturer’s instructions. Only automatic fire-extinguishing systems of the following types shall be installed in accordance with the New York City Fire Code:
905.4.1 Protection. | Risers and laterals of Class I standpipe systems not located within an enclosed stairway or pressurized enclosure shall be protected by a degree of fire resistance equal to that required for vertical enclosures in the building in which they are located. No standpipe riser shall be placed in any shaft containing a gas or fuel pipeline. Exception: In buildings equipped throughout with an approved automatic sprinkler system, laterals that are not located within an enclosed stairway or pressurized enclosure are not required to be enclosed in fire resistance rated construction. | 905.4.1 Protection. | Risers and laterals of Class I standpipe systems not located within an interior exit stairway shall be protected by a degree of fire resistance equal to that required for vertical enclosures in the building in which they are located. Exception: In buildings equipped throughout with an approved automatic sprinkler system, laterals that are not located within an interior exit stairway are not required to be enclosed within fire-resistance-rated construction.
904.12.1 Manual system operation. | A manual actuation device shall be located at or near a means of egress from the cooking area not less than 10 feet (3048 mm) and not more than 20 feet (6096 mm), from the kitchen exhaust system. The manual actuation device shall be installed not more than 48 inches (1220 mm) or less than 42 inches (1066.8 mm) above the finished floor and shall clearly identify the hazard protected. The manual actuation device shall require a maximum force of 40 pounds (177.9 N) and a maximum movement of 14 inches (355.6 mm) to actuate the fire suppression system. Exception: Automatic sprinkler systems shall not be required to be equipped with manual actuation means.
905.4.2 Interconnection. | In buildings where more than one standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14. | 905.4.2 Interconnection. | In buildings where more than one standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14.
904.12.2 System interconnection. | The actuation of the fire suppression system shall automatically shut down the fuel or electrical power supply to the cooking equipment. The fuel and electrical supply reset shall be manual.
905.5 Location of Class II standpipe hose connections. | Class II standpipe hose connections shall be prohibited. | 905.5 Location of Class II standpipe hose connections. | Class II standpipe hose connections located so that all portions of the building are within 30 feet (9144 mm) of a nozzle attached to 100 feet (30 480 mm) of hose. Class II standpipe hose connections shall be located where they will have ready access.
904.13 Domestic cooking systems in Group I-2. | In Group I-2 occupancies where cooking facilities are installed in accordance with Section 407.2.6 of this code, the domestic cooking hood provided over the cooktop or range shall be equipped with an automatic fire-extinguishing system of a type recognized for protection of domestic cooking equipment. Preengineered automatic extinguishing systems shall be tested in accordance with UL 300A and listed and labeled for the intended application. The system shall be installed in accordance with this code, its listing and the manufacturer’s instructions.
904.13.1 Manual system operation and interconnection. | Manual actuation and system interconnection for the hood suppression system shall be installed in accordance with Sections 904.12.1 and 904.12.2, respectively.
904.13.2 Portable fire extinguishers for domestic cooking equipment in Group I-2. | A portable fire extinguisher complying with Section 906 shall be installed within a 30-foot (9144 mm) distance of travel from domestic cooking appliances.
905.6 Location of Class III standpipe hose connections. | Class III standpipe systems shall have 2½-inch (63.5 mm) hose connections located as required for Class I standpipes in Section 905.4. At each hose connection, there shall be a hose station. The hose stations shall be equipped with a minimum of 125 feet (38 100 mm) but not more than a maximum of 150 feet (45 720 mm) of 1½-inch (38.1 mm) fire hose connected to an adjustable fog nozzle. The hose shall be attached to the 2½-inch (63.5 mm) hose connection by a 2½-inch (63.5 mm) by 1½-inch (38.1 mm) non-swivel reducing coupling. The hose shall be mounted on a rack and may be located in a cabinet, in accordance with Section 905.7. A pressure restricting device shall be installed when required by NFPA 14. Such pressure restricting device and reducing coupling shall be installed in such a manner that they are readily removable by the Fire Department. | 905.6 Location of Class III standpipe hose connections. | Class III standpipe systems shall have hose connections located as required for Class I standpipes in Section 905.4 and shall have Class II hose connections as required in Section 905.5. |  | See BC09 Tables&Figures
905.1.1 Construction documents. | Construction documents for standpipe systems shall contain plans that include, at a minimum, the following data and information:
905.6.1 Protection. | Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems in accordance with Section 905.4.1. | 905.6.1 Protection. | Risers and laterals of Class III standpipe systems shall be protected as required for Class I systems in accordance with Section 905.4.1.
905.2 Installation standards. | Standpipe systems shall be installed in accordance with this section and NFPA 14.
905.6.2 Interconnection. | In buildings where more than one standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14. | 905.6.2 Interconnection. | In buildings where more than one Class III standpipe is provided, the standpipes shall be interconnected in accordance with NFPA 14.
905.7 Cabinets. | Cabinets containing firefighting equipment such as standpipes, fire hoses, fire extinguishers or Fire Department valves shall not be blocked from use or obscured from view. | 905.7 Cabinets. | Cabinets containing fire-fighting equipment such as standpipes, fire hoses, fire extinguishers or fire department valves shall not be blocked from use or obscured from view.
905.3.1 Applicability. | Class III standpipe systems shall be installed throughout the following buildings: 1. In buildings two stories or more in height with floor area of 10,000 square feet (929 m2) or greater on any story; 2. In buildings three stories or more in height with floor area of 7,500 square feet (696.8 m2) or greater on any story; 3. In buildings of any area with a floor level having an occupant load of 30 or more that is located 55 feet (16 764 mm) or more above the lowest level of Fire Department vehicle access; and 4. In buildings of any area, constructed in accordance with Section 403, with occupied floors located 75 feet (22 860 mm) or more above the lowest level of Fire Department vehicle access. Exceptions: The following exceptions are allowed as an alternative to the requirement of a Class III standpipe system: 1. Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2 provided that the following additional requirements are met: 1.1. A locked noncombustible storage cabinet shall be provided on the main entrance floor. One additional locked storage cabinet shall be provided on every tenth floor above the main entrance floor, such that no occupant on any floor would have to travel more than five floors to reach a cabinet in a location within 15 feet (4572 mm) of each standpipe riser. Where one standpipe riser is installed in the building, such cabinet shall contain at least one fog nozzle, one 11/2-inch (38.1 mm) spanner wrench, one 21/2-inch (63.5 mm) spanner wrench, one 21/2-inch (63.5 mm) by 11/2 inch (38.1 mm) nonswivel reducing coupling, and 125 feet (38.1 m) of inch (38.1 mm) hose. 1.1.1. The cabinet shall be kept locked, openable by a Fire Department citywide standard key. 1.1.2. The cabinet shall be labeled, “FOR FIRE DEPARTMENT ONLY.” 1.1.3. A metal sign stating clearly where the storage cabinet is located shall be placed in each stair enclosure on the main entrance floor and on each floor where the cabinet is located. 1.2. Hose valves are capped with a hose valve cap fastened to the valve with a chain. 2. Class I manual standpipes are allowed in open parking garages where the highest floor is located not more than 150 feet (45 720 mm) above the lowest level of Fire Department vehicle access. 3. Class I manual dry standpipes are allowed in open parking garages that are subject to freezing temperatures, provided that the hose connections are located as required for Class III standpipes in accordance with Section 905.6. 4. Class I standpipes are allowed in below-grade stories equipped throughout with an automatic sprinkler system. 5. Standpipe outlets may be omitted in portions of first floors or basements that are completely separated from the entrance hall or enclosed stairways leading to the upper floors, provided that portable fire extinguishers are installed, subject to the approval of the Fire Commissioner. |  |  |  | See BC09 Tables&Figures
905.7.1 Cabinet equipment identification. | Cabinets shall be identified in an approved manner by a permanently attached sign with white letters not less than 2 inches (50.8 mm) high and a red background color, indicating the equipment contained therein. Exceptions: 1. Doors not large enough to accommodate a written sign with 2-inch lettering shall be marked with a permanently attached pictogram indicating the equipment contained therein, in addition to corresponding smaller white lettering on a red background adjacent to such pictogram. 2. Doors that have either an approved visual identification clear glass panel or a complete glass door panel are not required to be marked. | 905.7.1 Cabinet equipment identification. | Cabinets shall be identified in an approved manner by a permanently attached sign with letters not less than 2 inches (51 mm) high in a color that contrasts with the background color, indicating the equipment contained therein. Exceptions: 1. Doors not large enough to accommodate a written sign shall be marked with a permanently attached pic-togram of the equipment contained therein. 2. Doors that have either an approved visual identification clear glass panel or a complete glass door panel are not required to be marked.
905.7.2 Locking cabinet doors. | Cabinets shall be unlocked. Exceptions: 1. Visual identification panels of glass or other approved transparent frangible material that is easily broken and allows access. 2. Approved locking arrangements. 3. Locking of cabinets shall be permitted in Group I-3. | 905.7.2 Locking cabinet doors. | Cabinets shall be unlocked. Exceptions: 1. Visual identification panels of glass or other approved transparent frangible material that is easily broken and allows access. 2. Approved locking arrangements. 3. Group I-3 occupancies.
905.3.3 Covered mall buildings. | Covered mall buildings and buildings connected thereto shall be equipped throughout with a Class I automatic wet standpipe system, except as permitted by Sections 905.3.3.1 through 905.3.3.3.
905.8 Dry standpipes. | Dry standpipes shall not be installed. Exception: Where subject to freezing and in accordance with NFPA 14. | 905.8 Dry standpipes. | Dry standpipes shall not be installed. Exception: Where subject to freezing and in accordance with NFPA 14.
905.3.3.1 Covered-mall building height. | Covered-mall buildings where the highest occupied floor level is located not more than 30 feet (9144 mm) above the lowest level of the Fire Department vehicle access shall be permitted to be provided with Class I hose connections connected to the mall sprinkler system in accordance with Section 8.17.5.2 of NFPA 13 regarding hose con­nections for Fire Department use and under the following conditions:
905.9 Valve supervision. | Valves controlling water supplies shall be supervised in the open position so that a change in the normal position of the valve will generate a supervisory signal at the central supervising station required by Section 903.4. Where a fire alarm system is provided, a signal shall also be transmitted to the fire alarm system. Exceptions: 1. Valves to underground key or hub valves in roadway boxes provided by the city or a public utility do not require supervision. 2. Valves locked in the normal position and inspected as provided in this code in buildings not equipped with a fire alarm system. | 905.9 Valve supervision. | Valves controlling water supplies shall be supervised in the open position so that a change in the normal position of the valve will generate a supervisory signal at the supervising station required by Section 903.4. Where a fire alarm system is provided, a signal shall be transmitted to the control unit. Exceptions: 1. Valves to underground key or hub valves in roadway boxes do not require supervision. 2. Valves locked in the normal position and inspected as provided in this code in buildings not equipped with a fire alarm system.
905.3.3.2 Location of hose connections. | Hose connections shall be provided in accordance with Section 905.4 and at each of the following locations:
905.10 During construction. | Standpipe systems required during construction, alteration and demolition operations shall be provided in accordance with Section 3303.8. | 905.10 During construction. | Standpipe systems required during construction and demolition operations shall be provided in accordance with Section 3311.
905.3.3.3 Installation standard. | Except as provided in Sections 905.3.3.1 and 905.3.3.2, the Class I hose connections and Fire Department connections shall be designed in conformance with NFPA 14.
905.3.8 Rooftop gardens, landscaped roofs and green roofs. | Buildings with a rooftop garden, landscaped roof, green roof, or roof used for any purpose other than weather protection or maintenance that are equipped with a standpipe system shall extend the standpipe system to the roof level on which the rooftop garden, landscaped roof, green roof, or roof used for any purpose other than weather protection or maintenance is located.
905.3.9 High-piled stock or rack storage. | Where exit passageways are required in accordance with Chapter 10 of this code, a standpipe system shall be provided in accordance with the New York City Fire Code in all buildings containing high-piled stock or rack storage.
905.5.1 Reserved.
907.1 General. | This section covers the application, installation, performance and maintenance of fire alarm systems and their components. Systems shall be designed and installed in accordance with NFPA 72 and the New York City Electrical Code. Systems shall be tested and maintained in accordance with this code and the New York City Fire Code. | 907.1 General. | This section covers the application, installation, performance and maintenance of fire alarm systems and their components.
907.1.1 Construction documents. | Construction documents for fire alarm systems shall be submitted for review and approval to the Fire Department prior to system installation. Construction documents shall include, but not be limited to, all of the following: | 907.1.1 Construction documents. | Construction documents for fire alarm systems shall be of sufficient clarity to indicate the location, nature and extent of the work proposed and show in detail that it will conform to the provisions of this code, the International Fire Code; and relevant laws, ordinances, rules and regulations, as determined by the fire code official.
905.11 Painting of dedicated standpipes. | Dedicated standpipes and the handles of valves serving standpipes shall be painted and such painting certified in accordance with Sections 905.11.1 through 905.11.6. In addition to painting, standpipe piping may also be identified by lettered legend in accordance with ANSI A13.1. Where the piping is required to be listed and labeled such painting shall not obscure such labeling. Exceptions: 1. Attachments, gauges, valves and operable parts of standpipes other than valve handles. 2. Where different color coding may be required by Section 3406 of the New York City Fire Code for facilities storing, handling, and using flammable and combustible liquids in connection with special operations.
905.11.1 New buildings. | All portions of a standpipe system and the handles of valves serving the standpipe system in new buildings, including buildings constructed pursuant to Section 28-101.4.2 of the Administrative Code, shall be painted red prior to the hydrostatic pressure test whether or not they are intended to be enclosed at the end of construction.
905.11.2 Alterations. | Existing handles of valves serving existing standpipe systems and existing unpainted standpipe risers that are exposed during alterations, including alterations pursuant to Section 28-101.4.2 of the Administrative Code shall be painted red. Where the alteration requires a hydrostatic pressure test such painting shall be completed prior to such test.
907.2.1 Group A. | A manual and automatic fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group A occupancies where the occupant load due to the assembly occupancy is 300 or more. Group A occupancies not separated from one another in accordance with Section 707.3.10 shall be considered as a single occupancy for the purposes of applying this section. Portions of Group E occupancies occupied for assembly purposes shall be provided with a fire alarm system as required for the Group E occupancy. Exceptions: 1. Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system and the notification appliances will activate upon sprinkler water flow. This exception shall not apply to Group A-2 occupancies used as a cabaret. 2. A Group A-2 occupancy used as a cabaret with an occupant load of 75 or more, including associated stages, dressing rooms, and property rooms, shall be equipped with a manual fire alarm system. Such a Group A-2 occupancy with an occupant load of 300 or more shall also be equipped with an automatic fire alarm system. 3. Group A occupancies with a stage in accordance with Section 410, and having an occupant load of 75 or more, shall be provided with a voice/alarm communication system as required by Sections 410.9 and 907.2.1.1. | 907.2.1 Group A. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group A occupancies where the occupant load due to the assembly occupancy is 300 or more, or where the Group A occupant load is more than 100 persons above or below the lowest level of exit discharge. Group A occupancies not separated from one another in accordance with Section 707.3.10 shall be considered as a single occupancy for the purposes of applying this section. Portions of Group E occupancies occupied for assembly purposes shall be provided with a fire alarm system as required for the Group E occupancy. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automat-ic sprinkler system installed in accordance with Section 903.3.1.1 and the occupant notification appliances will activate throughout the notification zones upon sprinkler water flow.
905.11.3 Retroactive requirement for completed buildings. | Notwithstanding any other provision of law, all portions of exposed standpipe systems and handles of valves serving the standpipe system of completed buildings in existence March 2, 2010 shall be painted red.
905.11.4 Buildings under construction on March 2, 2010. | Notwithstanding any other provision of law, where construction documents were approved and permits issued for the construction of a new building or alteration of an existing building prior to March 2, 2010, and the work is not signed off by the department prior to such date, all exposed portions of the standpipe system and handles of valves serving the standpipe system shall be painted red prior to the hydrostatic pressure test, including portions that will be enclosed at a later point in time. Exception: Portions of the standpipe system enclosed prior to March 2, 2010, need not be painted.
907.2.1.2 Emergency voice/alarm communication captions. | Stadiums, arenas and grandstands required to caption audible public announcements shall be in accordance with Section 907.5.2.2.4. | 907.2.1.2 Emergency voice/alarm communication captions. | Stadiums, arenas and grandstands required to caption audible public announcements shall be in accordance with Section 907.5.2.2.4.
905.11.5 Combination standpipe and sprinkler systems. | Where a standpipe system that is used as a combination standpipe and sprinkler system is required to be painted pursuant to Section 905.11.1, 905.11.2, 905.11.3 or 905.11.4, the sprinkler risers and cross connections that are also used for the standpipe system shall be painted red, and the handles of valves serving such combination standpipe and sprinkler system shall be painted yellow.
907.2.2 Group B. | A manual and automatic fire alarm system shall be installed in Group B occupancies where one of the following conditions exists: | 907.2.2 Group B. | A manual fire alarm system, which activates the occupant notification system in accordance with Section 907.5, shall be installed in Group B occupancies where one of the following conditions exists: 1. The combined Group B occupant load of all floors is 500 or more. 2. The Group B occupant load is more than 100 persons above or below the lowest level of exit discharge. 3. The fire area contains an ambulatory care facility. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automat-ic sprinkler system installed in accordance with Section 903.3.1.1 and the occupant notification appliances will activate throughout the notification zones upon sprinkler water flow.
905.11.6 Certification of completion of system painting. | For all buildings where standpipe and combination sprinkler and standpipe systems are not subject to a special inspection pursuant to Section 1705.30 of this code, a licensed master plumber, licensed master fire suppression piping contractor, registered design professional or an individual holding an appropriate certificate of fitness from the Fire Department for the operation and/or maintenance of such system shall certify on forms provided by the department that all required painting has been completed in accordance with Section 905.11. Such certification shall be maintained on the premises and made available for inspection by the department and the Fire Department.
907.2.2.1 Ambulatory care facilities. | Fire areas containing ambulatory care facilities shall be provided with an electronically supervised automatic partial-coverage smoke detection system installed within the ambulatory care facility and in public use areas outside of tenant spaces and along the path of egress, including public corridors and elevator lobbies. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, provided the occupant notification appliances will activate throughout the notification zones upon sprinkler waterflow. | 907.2.2.1 Ambulatory care facilities. | Fire areas containing ambulatory care facilities shall be provided with an electronically supervised automatic smoke detection system installed within the ambulatory care facility and in public use areas outside of tenant spaces, including public corridors and elevator lobbies. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, provided that the occupant notification appliances will activate throughout the notification zones upon sprinkler waterflow.
906.1 General. | Portable fire extinguishers shall be provided in occupancies and locations as required by the New York City Fire Code.
907.2.3 Group E. | A manual and automatic fire alarm system shall be installed in Group E occupancies. An emergency voice/alarm communication system meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall be installed in Group E occupancies. Automatic sprinkler systems, smoke detectors and/or other initiating devices, shall be installed in accordance with other sections of this code. When such systems, initiating devices, and/or detectors are installed, they shall be connected to the building fire alarm system. Exception: Emergency voice/alarm communication systems meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall not be required in Group E occupancies with occupant loads of 100 or less, provided that activation of the manual and automatic fire alarm system initiates an approved occupant notification signal in accordance with Section 907.5. | 907.2.3 Group E. | A manual fire alarm system that initiates the occupant notification signal utilizing an emergency voice/alarm communication system meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall be installed in Group E occupancies. Where automatic sprinkler systems or smoke detectors are installed, such systems or detectors shall be connected to the building fire alarm system. Exceptions: 1. A manual fire alarm system shall not be required in Group E occupancies with an occupant load of 50 or less. 2. Emergency voice/alarm communication systems meeting the requirements of Section 907.5.2.2 and in-stalled in accordance with Section 907.6 shall not be required in Group E occupancies with occupant loads of 100 or less, provided that activation of the manual fire alarm system initiates an approved occu-pant notification signal in accordance with Section 907.5. 3. Manual fire alarm boxes shall not be required in Group E occupancies where all of the following apply: 3.1. Interior corridors are protected by smoke detectors. 3.2. Auditoriums, cafeterias, gymnasiums and similar areas are protected by heat detectors or other approved detection devices. 3.3. Shops and laboratories involving dusts or vapors are protected by heat detectors or other ap-proved detection devices. 3.4 Manual activation is provided from a normally occupied location. 4. Manual fire alarm boxes shall not be required in Group E occupancies where all of the following apply: 4.1. The building is equipped throughout with an approved automatic sprinkler system installed in ac-cordance with Section 903.3.1.1. 4.2. The emergency voice/alarm communication system will activate on sprinkler waterflow. 4.3. Manual activation is provided from a normally occupied location.
907.2.4 Group F. | A manual and automatic fire alarm system shall be installed in Group F occupancies that are two or more stories in height and have an occupant load of 100 or more, or when 25 persons or more are above or below the lowest level of exit discharge. | 907.2.4 Group F. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group F occupancies where both of the following conditions exist: 1. The Group F occupancy is two or more stories in height. 2. The Group F occupancy has a combined occupant load of 500 or more above or below the lowest level of ex-it discharge. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automat-ic sprinkler system installed in accordance with Section 903.3.1.1 and the occupant notification appliances will activate throughout the notification zones upon sprinkler water flow.
907.2.5 Group H. | A manual and automatic fire alarm system shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. In addition to the automatic fire alarm system requirements of Section 907.2, an automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with the New York City Fire Code. Exception: Where exempt under the New York City Fire Code. | 907.2.5 Group H. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group H-5 occupancies and in occupancies used for the manufacture of organic coatings. An automatic smoke detection system shall be installed for highly toxic gases, organic peroxides and oxidizers in accordance with Chapters 60, 62 and 63, respectively, of the International Fire Code.
907.1.1.1 Amended construction documents. | Amendments to approved construction documents shall be submitted and approved by the Fire Department before the final inspection of the work or equipment is completed, and such amendments when approved shall be deemed part of the original construction documents. The Fire Department may allow minor revisions of construction documents to be made and submitted to the Fire Department after the completion of work but prior to sign-off of the work in accordance with rules promulgated by the Fire Department regarding such amendments.
907.2.6 Group I. | A manual and automatic fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group I occupancies. An automatic smoke detection system that activates the occupant notification system shall be provided in accordance with Sections 907.2.6.1. 907.2.6.2 and 907.2.6.3.3. | 907.2.6 Group I. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group I occupancies. An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be provided in accordance with Sections 907.2.6.1, 907.2.6.2 and 907.2.6.3.3. Exceptions: 1. Manual fire alarm boxes in sleeping units of Group I-1 and I-2 occupancies shall not be required at exits if located at all care providers’ control stations or other constantly attended staff locations, provided that such manual fire alarm boxes are visible and provided with ready access, and the distances of travel re-quired in Section 907.4.2.1 are not exceeded. 2. Occupant notification systems are not required to be activated where private mode signaling installed in accordance with NFPA 72 is approved by the fire code official and staff evacuation responsibilities are included in the fire safety and evacuation plan required by Section 404 of the International Fire Code.
907.1.2 Equipment. | Systems and their components shall be listed for the purpose for which they are installed. The fire alarm control unit shall meet the requirements of the Fire Department.
907.2.6.1 Group I-1. | An automatic smoke detection system shall be installed in corridors, waiting areas open to corridors and habitable spaces other than sleeping units and kitchens. The system shall be activated in accordance with Section 907.5. Exception: Smoke detection is not required for exterior balconies. | 907.2.6.1 Group I-1. | In Group I-1 occupancies, an automatic smoke detection system shall be installed in corridors, waiting areas open to corridors and habitable spaces other than sleeping units and kitchens. The system shall be activated in accordance with Section 907.5. Exceptions: 1. For Group I-1, Condition 1 occupancies, smoke detection in habitable spaces is not required where the facility is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1. 2. Smoke detection is not required for exterior balconies.
907.2 Where required. | An approved fire alarm system installed in accordance with the provisions of this code and NFPA 72 shall be provided in accordance with Sections 907.2.1 through 907.2.23 and provide occupant notification in accordance with Section 907.5, unless other requirements are provided by another section of this code. A minimum of one manual fire alarm box shall be provided in an approved location to initiate a fire alarm signal for fire alarm systems employing automatic fire detectors or waterflow detection devices. Where other sections of this code allow elimination of fire alarm boxes due to sprinklers, a single fire alarm box shall be installed. Exceptions: 1. The manual fire alarm box is not required for fire alarm systems dedicated to elevator recall control and supervisory service. 2. The manual fire alarm box is not required for Group R-2 occupancies unless required by the Fire Department to provide a means for fire watch personnel to initiate an alarm during a sprinkler system impairment event. Where provided, the manual fire alarm box shall not be located in an area that is accessible to the public. In all occupancies where an automatic fire alarm system is required by this section, selective coverage smoke detectors shall be located as follows, unless partial or total coverage automatic detection is specified. 1. In each mechanical equipment, electrical, transformer, telephone equipment or similar room, in elevator machine rooms, and in elevator lobbies. 2. In air distribution systems in accordance with Section 606 of the New York City Mechanical Code.
907.2.6.2 Group I-2. | An automatic smoke detection system shall be installed in corridors in nursing homes (both intermediate-care and skilled nursing facilities), corridors in detoxi­fication facilities and spaces permitted to be open to the corridors by Section 407.2. The system shall be activated in accordance with Section 907.5. Hospitals shall be equipped with smoke detection as required in Section 407. A one-way voice communication system activated in accordance with Section 907.5.2.2 shall be provided at the fire command center for use by Fire Department personnel. A two-way voice communication system in accordance with Section 907.2.13.3 shall be provided for Group I-2 buildings. | 907.2.6.2 Group I-2. | An automatic smoke detection system shall be installed in corridors in Group I-2, Condition 1 facilities and spaces permitted to be open to the corridors by Section 407.2. The system shall be activated in accordance with Section 907.4. Group I-2, Condition 2 occupancies shall be equipped with an automatic smoke detection system as required in Section 407. Exceptions: 1. Corridor smoke detection is not required in smoke compartments that contain sleeping units where such units are provided with smoke detectors that comply with UL 268. Such detectors shall provide a visual display on the corridor side of each sleeping unit and shall provide an audible and visual alarm at the care providers’ station attending each unit. 2. Corridor smoke detection is not required in smoke compartments that contain sleeping units where sleeping unit doors are equipped with automatic door-closing devices with integral smoke detectors on the unit sides installed in accordance with their listing, provided that the integral detectors per-form the required alerting function.
907.2.1.1 System initiation in Group A occupancies. | Activation of the fire alarm in Group A-1 occupancies with an occupant load of 300 or more, and in all other Group A occupancies with an occupant load of 1,000 or more, shall initiate a presignal system in accordance with NFPA 72 at a constantly attended location from which the Fire Department shall be notified and live voice evacuation instructions shall be initiated using an emergency voice/alarm communications system in accordance with Section 907.5.2.2.
907.2.6.3.1 System initiation. | Actuation of an automatic fire-extinguishing system, automatic sprinkler system, a manual fire alarm box, a fire detector, or a smoke detector shall initiate an approved alarm signal that automatically notifies staff. | 907.2.6.3.1 System initiation. | Actuation of an automatic fire-extinguishing system, automatic sprinkler system, a manual fire alarm box or a fire detector shall initiate an approved fire alarm signal that automatically notifies staff.
907.2.6.3.2 Manual fire alarm boxes. | Manual fire alarm boxes are not required to be located in accordance with Section 907.4.2 where the fire alarm boxes are provided at staff-attended locations having direct supervision over areas where manual fire alarm boxes have been omitted. | 907.2.6.3.2 Manual fire alarm boxes. | Manual fire alarm boxes are not required to be located in accordance with Section 907.4.2 where the fire alarm boxes are provided at staff-attended locations having direct supervision over areas where manual fire alarm boxes have been omitted.
907.2.6.3.2.1 Manual fire alarm boxes in detainee areas. | Manual fire alarm boxes are allowed to be locked in areas occupied by detainees, provided that staff members are present within the subject area and have keys readily available to operate the manual fire alarm boxes. | 907.2.6.3.2.1 Manual fire alarm boxes in detainee areas. | Manual fire alarm boxes are allowed to be locked in areas occupied by detainees, provided that staff members are present within the subject area and have keys readily available to operate the manual fire alarm boxes.
907.2.2.2 Large-area buildings. | Group B occupancies having a total gross area exceeding 100,000 square feet (9290.3 m2) located in buildings where the highest occupied floor is 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.
907.2.6.3.3 Automatic smoke detection system. | An automatic smoke detection system shall be installed throughout resident housing areas, including sleeping units and contiguous day rooms, group activity spaces and other common spaces normally accessible to residents. Exceptions: 1. Other approved smoke detection arrangements providing equivalent protection, including, but not limited to, placing detec¬tors in exhaust ducts from cells or behind protective guards listed for the purpose, are allowed when necessary to prevent damage or tampering. 2. Sleeping units in Use Conditions 2 and 3 as described in Section 308. 3. Smoke detectors are not required in sleeping units with four or fewer occupants in smoke compartments that are equipped throughout with an approved automatic sprinkler system installed in accordance with Section 903.3.1.1. | 907.2.6.3.3 Automatic smoke detection system. | An automatic smoke detection system shall be installed throughout resident housing areas, including sleeping units and contiguous day rooms, group activity spaces and other common spaces normally open to residents. Exceptions: 1. Other approved smoke detection arrangements providing equivalent protection, including, but not limited to, placing detectors in exhaust ducts from cells or behind protective guards listed for the purpose, are allowed where necessary to prevent damage or tampering. 2. Sleeping units in Use Conditions 2 and 3 as described in Section 308. 3. Smoke detectors are not required in sleeping units with four or fewer occupants in smoke compart-ments that are equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1.
907.2.7 Group M. | A manual and automatic fire alarm system shall be installed in Group M occupancies where any one of the following conditions exists: | 907.2.7 Group M. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group M occupancies where one of the following conditions exists: 1. The combined Group M occupant load of all floors is 500 or more persons. 2. The Group M occupant load is more than 100 persons above or below the lowest level of exit discharge. Exceptions: 1. A manual fire alarm system is not required in covered or open mall buildings complying with Section 402. 2. Manual fire alarm boxes are not required where the building is equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 and the occupant notification appliances will automatically activate throughout the notification zones upon sprinkler water flow.
907.2.8 Group R-1. | Fire alarm systems shall be installed in Group R-1 occupancies as required in Sections 907.2.8.1 through 907.2.8.5. | 907.2.8 Group R-1. | Fire alarm systems and smoke alarms shall be installed in Group R-1 occupancies as required in Sections 907.2.8.1 through 907.2.8.3.
907.2.8.1 Manual fire alarm system. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R-1 occupancies. Exception: A manual fire alarm system is not required in buildings not over two stories in height where all individual sleeping units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each individual dwelling unit has an exit directly to a public way, exit court or yard. | 907.2.8.1 Manual fire alarm system. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R- 1 occupancies. Exceptions: 1. A manual fire alarm system is not required in buildings not more than two stories in height where all individual sleeping units and contiguous attic and crawl spaces to those units are separated from each other and public or common areas by not less than 1-hour fire partitions and each individual sleeping unit has an exit directly to a public way, egress court or yard. 2. Manual fire alarm boxes are not required throughout the building where all of the following condi-tions are met: 2.1. The building is equipped throughout with an automatic sprinkler system installed in accord-ance with Section 903.3.1.1 or 903.3.1.2. 2.2. The notification appliances will activate upon sprinkler water flow. 2.3. Not fewer than one manual fire alarm box is installed at an approved location.
907.2.8.2 Automatic smoke detection system. | An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be installed in all public corridors serving dwelling units or sleeping units in accordance with Section 907.2.8.3. Exception: An automatic fire detection system is not required in buildings that do not have public corridors serving sleeping units and each sleeping unit has a means of egress door opening directly to an exterior exit access that leads directly to an exit. | 907.2.8.2 Automatic smoke detection system. | An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be installed throughout all interior corridors serving sleeping units. Exception: An automatic smoke detection system is not required in buildings that do not have interior corri-dors serving sleeping units and where each sleeping unit has a means of egress door opening directly to an ex-it or to an exterior exit access that leads directly to an exit.
907.2.6.1.1 Smoke detectors within dwelling and sleeping units. | Smoke detectors and notification appliances shall be installed in dwelling units and such notification appliances shall activate only in the unit in which the alarm originates. Such detectors and appliances shall be annunciated by dwelling unit at a constantly attended location from which the fire alarm system is capable of being manually activated. Smoke detectors are required in the following areas:
907.2.9 Group R-2. | A fire alarm system without alarm notification appliances and smoke alarms shall be installed in accordance with this section in Group R-2 occupancies, other than student apartments, where such occupancy satisfies any one of the following conditions: | 907.2.9 Group R-2. | Fire alarm systems and smoke alarms shall be installed in Group R-2 occupancies as required in Sections 907.2.9.1 through 907.2.9.3.
907.2.6.3 Group I-3. | Group I-3 occupancies shall be equipped with a manual and automatic fire alarm system and automatic smoke detection system installed for alerting staff.
907.2.9.2 Smoke alarms. | Single- and multiple-station smoke alarms shall be installed in accordance with Section 907.2.11. | 907.2.9.2 Smoke alarms. | Single- and multiple-station smoke alarms shall be installed in accordance with Section 907.2.11.
907.2.10 Group S. | A manual and automatic fire alarm system shall be installed in Group S occupancies where any one of the following conditions exists: | 907.2.10 Group S. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group S public- and self-storage occupancies three stories or greater in height for interior corridors and interior common areas. Visible notification appliances are not required within storage units. Exception: Manual fire alarm boxes are not required where the building is equipped throughout with an automat-ic sprinkler system installed in accordance with Section 903.3.1.1, and the occupant notification appliances will activate throughout the notification zones upon sprinkler water flow.
907.2.11 Single- and multiple-station smoke alarms. | Listed single- and multiple-station smoke alarms complying with UL 217 shall be installed in accordance with Sections 907.2.11.1 through 907.2.11.7 and NFPA 72. | 907.2.11 Single- and multiple-station smoke alarms. | Listed single- and multiple-station smoke alarms complying with UL 217 shall be installed in accordance with Sections 907.2.11.1 through 907.2.11.7 and NFPA 72.
907.2.7.1 Large-area buildings. | Group M occupancies having a total gross area exceeding 100,000 square feet (9290.3 m2) located in buildings where the highest occupied floor is 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access and covered mall buildings having a total gross area exceeding 50,000 square feet (4645.2 m2) shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 initiating a total evacuation signal.
907.2.11.3 Installation near cooking appliances. | Smoke alarms shall not be installed in the following locations unless this would prevent placement of a smoke alarm in a location required by Section 907.2.11.1: | 907.2.11.3 Installation near cooking appliances. | Smoke alarms shall not be installed in the following locations unless this would prevent placement of a smoke alarm in a location required by Section 907.2.11.1 or 907.2.11.2:
907.2.11.4 Installation near bathrooms. | Smoke alarms shall be installed not less than 3 feet (914.4 mm) horizontally from the door or opening of a bathroom that contains a bathtub or shower unless this would prevent placement of a smoke alarm required by Section 907.2.11.1. | 907.2.11.4 Installation near bathrooms. | Smoke alarms shall be installed not less than 3 feet (914 mm) horizontally from the door or opening of a bathroom that contains a bathtub or shower unless this would prevent placement of a smoke alarm required by Section 907.2.11.1 or 907.2.11.2.
907.2.11.5 Interconnection. | Where more than one smoke alarm is required to be installed within an individual dwelling unit or sleeping unit in Group R-2 and R-3 occupancies, the smoke alarms shall be intercon­nected in such a manner that the activation of one alarm will activate all of the alarms in the individual unit. Physical interconnection of smoke alarms shall not be required where listed wireless alarms are installed and all alarms sound upon activation of one alarm. The alarm shall be clearly audible in all bedrooms over background noise levels with all intervening doors closed. | 907.2.11.5 Interconnection. | Where more than one smoke alarm is required to be installed within an individual dwelling unit or sleeping unit in Group R or I-1 occupancies, the smoke alarms shall be interconnected in such a manner that the activation of one alarm will activate all of the alarms in the individual unit. Physical interconnection of smoke alarms shall not be required where listed wireless alarms are installed and all alarms sound upon activation of one alarm. The alarm shall be clearly audible in all bedrooms over background noise levels with all intervening doors closed.
907.2.8.3 Smoke detectors within dwelling units and sleeping units. | Smoke detectors and audible notification appliances shall be installed in dwelling units and sleeping units and shall be annunci­ated by dwelling unit and sleeping unit at a constantly attended location from which the fire alarm system is capable of being manually activated. Smoke detectors are required in the following areas:
907.2.8.4 Group R-1 student dormitories. | A manual and automatic smoke detection system shall be installed in occupancies for student or school staff dormitory housing in all of the following locations: 1. Common spaces outside of sleeping units. 2. Laundry rooms, mechanical equipment rooms and storage rooms. 3. Interior corridors serving sleeping units. Exception: An automatic smoke detection system is not required in buildings that do not have interior corridors serving sleeping units or dwelling units and where each sleeping unit or dwelling unit either has a means of egress door opening directly to an exterior exit access that leads directly to an exit or a means of egress door opening directly to an exit.
907.2.11.7 Smoke detection system. | Smoke detectors listed in accordance with UL 268 and provided as part of the building fire alarm system shall be an acceptable alternative to single and multiple station smoke alarms and shall comply with the following: | 907.2.11.7 Smoke detection system. | Smoke detectors listed in accordance with UL 268 and provided as part of the building fire alarm system shall be an acceptable alternative to single- and multiple-station smoke alarms and shall comply with the following:
907.2.8.5 Large Group R-1 occupancies. | Group R-1 occupancies with a total of more than 50 sleeping rooms above street level located in buildings where the highest occupied floor is 75 feet (22 860 mm) or less above the lowest level of Fire Department vehicle access, or communal sleeping facilities above street level occupied or designed to be occupied by more than 50 lodgers, shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.
907.2.12 Special amusement buildings. | An automatic smoke detection system shall be provided in special amusement buildings in accordance with Sections 907.2.12.1 through 907.2.12.3. Exception: In areas where ambient conditions will cause a smoke detection system to alarm, an approved alternative type of automatic detector shall be installed. | 907.2.12 Special amusement buildings. | An automatic smoke detection system shall be provided in special amusement buildings in accordance with Sections 907.2.12.1 through 907.2.12.3.
907.2.12.1 Alarm. | Actuation of a single smoke detector, automatic sprinkler system or other automatic fire detection system shall initiate a pre-signal system in accordance with NFPA 72 at a constantly attended location from which the Fire Department shall be notified and live voice evacuation instructions shall be initiated using an emergency voice/alarm communications system in accordance with Section 907.5.2.2. | 907.2.12.1 Alarm. | Activation of any single smoke detector, the automatic sprinkler system or any other automatic fire detection device shall immediately activate an audible and visible alarm at the building at a constantly attended location from which emergency action can be initiated, including the capability of manual initiation of requirements in Section 907.2.12.2.
907.2.9.1 Group R-2 student apartments. | Where the main use or dominant occupancy of a building is classified as R-2 student apartments, as defined in Section 310.2, fire alarm systems shall be installed in accordance with Section 907.2.8. Where the main use or dominant occupancy of a building is not classified as R-2 student apartments and the building is occupied partially by Group R-2 student apartments, fire alarm systems shall be installed in accordance with Sections 907.2.9.1.1 through 907.2.9.2.
907.2.12.2 System response. | The following minimum system actuations and responses shall be required upon approval by the department and the Fire Department. The activation of two or more smoke detectors, a single smoke detector equipped with an alarm verification feature, the automatic sprinkler system or other approved fire detection device shall automatically do all of the following: | 907.2.12.2 System response. | The activation of two or more smoke detectors, a single smoke detector equipped with an alarm verification feature, the automatic sprinkler system or other approved fire detection device shall automatically do all of the following:
907.2.9.1.1 Manual fire alarm system. | A manual fire alarm system shall be installed throughout all public corridors serving student apartments and student-related uses. Student-related uses shall include common spaces such as recreation rooms, lounges, dining rooms, laundry rooms and storage rooms. Exceptions: 1. A manual fire alarm system is not required in buildings not over two stories in height where all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire partitions and each individual dwelling unit has an exit directly to a public way, exit court or yard. 2. A manual fire alarm system is not required in buildings containing fewer than 15 student apartments.
907.2.12.3 Emergency voice/alarm communication system. | An emergency voice/alarm communication system, which is also allowed to serve as a public address system, shall be installed in accordance with Section 907.5.2.2 and be audible throughout the entire special amusement building. | 907.2.12.3 Emergency voice/alarm communication system. | An emergency voice/alarm communication system, which is allowed to serve as a public address system, shall be installed in accordance with Section 907.5.2.2 and be audible throughout the entire special amusement building.
907.2.9.1.2 Automatic fire alarm system. | An automatic fire alarm system without alarm notification appliances shall be installed in accordance with this section in Group R-2 student apartments and student-related uses. The activation of any smoke detector required by this section shall initiate a signal at a central station or a constantly attended location. Smoke detectors shall be located as follows: 1. In each mechanical equipment, electrical, transformer, telephone equipment or similar room, in elevator machine rooms, and in eleva¬tor lobbies. 2. In air distribution systems in accordance with Section 606 of the New York City Mechanical Code. 3. Throughout all public corridors serving student apartments and student-related uses. Student-related uses shall include common spaces such as recreation rooms, lounges, dining rooms, laundry rooms and storage rooms. However, smoke detectors shall not be required in such public corridors in buildings containing fewer than 15 student apartments. Exception: An automatic fire alarm system is not required in buildings not over two stories in height where all individual dwelling units and contiguous attic and crawl spaces are separated from each other and public or common areas by at least 1-hour fire barriers and each individual dwelling unit has an exit directly to a public way, exit court or yard.
907.2.13 High-rise buildings. | In addition to the requirements of Sections 907.2.1 through 907.2.12, buildings constructed in accordance with Section 403 and having floors used for human occupancy located more than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access shall be provided with an automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1, a Fire Department communication system in accordance with Section 907.2.13.2, a two-way communication system in accordance with Section 907.2.13.3, and an emergency voice/alarm communication system in accordance with Section 907.5.2.2. Exceptions: 1. Open parking garages in accordance with Section 406.5. 2. Buildings with an occupancy in Group A-5 in accordance with Section 303.6. 3. Low-hazard special occupancies in accordance with Section 503.1.1. 4. Buildings with an occupancy in Group H-1, H-2 or H-3 in accordance with Section 415. | 907.2.13 High-rise buildings. | High-rise buildings shall be provided with an automatic smoke detection system in accordance with Section 907.2.13.1, a fire department communication system in accordance with Section 907.2.13.2 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2. Exceptions: 1. Airport traffic control towers in accordance with Sections 412 and 907.2.22. 2. Open parking garages in accordance with Section 406.5. 3. Buildings with an occupancy in Group A-5 in accordance with Section 303.1. 4. Low-hazard special occupancies in accordance with Section 503.1.1. 5. Buildings with an occupancy in Group H-1, H-2 or H-3 in accordance with Section 415. 6. In Group I-1 and I-2 occupancies, the alarm shall sound at a constantly attended location and occupant notification shall be broadcast by the emergency voice/alarm communication system.
907.2.13.1 Automatic smoke detection. | In addition to smoke detection otherwise required by this code, automatic smoke detection in high-rise buildings shall be in accordance with Sections 907.2.13.1.1 and 907.2.13.1.2. Exception for Group R-2 occupancies: In R-2 occupancies, the activation of smoke detectors shall initiate a signal at a central supervising station or a constantly attended location and shall not initiate a signal to alarm notification appliances. | 907.2.13.1 Automatic smoke detection. | Automatic smoke detection in high-rise buildings shall be in accordance with Sections 907.2.13.1.1 and 907.2.13.1.2.
907.2.10.1 Large-area buildings. | Group S occupancies having a total gross area exceeding 500,000 square feet (46 451.5 m2) located in buildings, where the highest occupied floor is 75 feet (22 860) or less above the lowest level of Fire Department vehicle access, shall be provided with automatic smoke detection connected to an automatic fire alarm system in accordance with Section 907.2.13.1 and an emergency voice/alarm communication system in accordance with Section 907.5.2.2 that initiates a total evacuation signal.
907.2.13.1.2 Duct smoke detection. | Duct smoke detectors complying with Section 907.3.1 shall be located in air distribution systems in accordance with Section 606 of the New York City Mechanical Code. | 907.2.13.1.2 Duct smoke detection. | Duct smoke detectors complying with Section 907.3.1 shall be located as follows:
907.2.11.1 Smoke alarms in Groups R-2 and R-3. | Single- or multiple-station smoke alarms shall be installed and maintained in Groups R-2 and R-3, regardless of occupant load at all of the following locations within all dwelling units:
907.2.11.1.1 Group R-2 occupancy. | Smoke alarms shall be provided with the capability to support visible alarm notification appliances in accordance with ICC/ANSI A117.1.
907.2.14 Atriums connecting more than two stories. | A fire alarm system shall be installed in occupancies with an atrium that connects more than two stories, with smoke detection installed in locations as required by a rational analysis in Section 909.4 and in accordance with the system operation requirements in Section 909.17. The system shall be activated in accordance with Section 907.5. Such occupancies in Group A, E or M shall be provided with an emergency voice/alarm communication system complying with the requirements of Section 907.5.2.2. | 907.2.14 Atriums connecting more than two stories. | A fire alarm system shall be installed in occupancies with an atrium that connects more than two stories, with smoke detection installed in locations required by a rational analysis in Section 909.4 and in accordance with the system operation requirements in Section 909.17. The system shall be activated in accordance with Section 907.5. Such occupancies in Group A, E or M shall be provided with an emergency voice/alarm communication system complying with the requirements of Section 907.5.2.2.
907.2.11.2 Power source. | Required smoke alarms shall receive their primary power from a dedicated branch circuit or the unswitched portion of a branch circuit also used for power or lighting, or both, and shall be equipped with a battery backup. Smoke alarms shall emit a signal when the batteries are low. Wiring shall be permanent and without a disconnecting switch other than as required for over-current protection. Exception: Smoke alarms with integral strobes shall not require battery backup provided that the smoke alarms are connected to an emergency or standby power electrical source.
907.2.15 High-piled combustible storage areas. | An automatic fire detection system shall be installed throughout high-piled combustible storage areas where required by the New York City Fire Code. | 907.2.15 High-piled combustible storage areas. | An automatic smoke detection system shall be installed throughout high-piled combustible storage areas where required by Section 3206.5 of the International Fire Code.
907.2.16 Aerosol storage uses. | Aerosol storage rooms and general-purpose warehouses containing aerosols shall be provided with an approved manual fire alarm system where required by the New York City Fire Code. | 907.2.16 Aerosol storage uses. | Aerosol product rooms and general-purpose warehouses containing aerosol products shall be provided with an approved manual fire alarm system where required by the International Fire Code.
907.2.17 Lumber, wood structural panel and veneer mills. | Lumber, wood structural panel and veneer mills shall be provided with a manual fire alarm system. | 907.2.17 Lumber, wood structural panel and veneer mills. | Lumber, wood structural panel and veneer mills shall be provided with a manual fire alarm system.
907.2.11.6 Smoke alarms and smoke detectors in group R occupancies. | On and after January 1, 2021, smoke alarms and smoke detectors shall not be installed or replaced in an individual dwelling or sleeping unit, including dwellings or units in prior code buildings, within an area of exclusion determined by a 20 foot (6096 mm) radial distance along a horizontal flow path from a stationary or fixed cooking appliance, unless listed in accordance with the 8th edition of UL 217 for smoke alarms or the 7th edition of UL 268 for smoke detectors.
907.2.18.1 Smoke detectors. | Not fewer than one smoke detector listed for the intended purpose shall be installed in all of the following areas: | 907.2.18.1 Smoke detectors. | Not fewer than one smoke detector listed for the intended purpose shall be installed in all of the following areas:
907.2.18.2 Alarm required. | Activation of the smoke exhaust system shall activate an audible alarm at a constantly attended location. | 907.2.18.2 Alarm required. | Activation of the smoke control system shall activate an audible alarm at a constantly attended location.
907.2.20 Covered and open mall buildings. | Where the total floor area exceeds 50,000 square feet (4645.2 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided. Emergency voice/alarm communication systems serving a mall, required or otherwise, shall be accessible to the Fire Department. The system shall be provided in accordance with Section 907.5.2.2. | 907.2.20 Covered and open mall buildings. | Where the total floor area exceeds 50,000 square feet (4645 m2) within either a covered mall building or within the perimeter line of an open mall building, an emergency voice/alarm communication system shall be provided. Access to emergency voice/alarm communication systems serving a mall, required or otherwise, shall be provided for the fire department. The system shall be provided in accordance with Section 907.5.2.2.
907.2.22 Airport traffic control towers. | An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be provided in airport control towers in accordance with Sections 907.2.22.1 and 907.2.22.2. Exception: Audible appliances shall not be installed within the control tower cab. | 907.2.22 Airport traffic control towers. | An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be provided in airport control towers in accordance with Sections 907.2.22.1 and 907.2.22.2. Exception: Audible appliances shall not be installed within the control tower cab.
907.2.22.1 Airport traffic control towers with multiple exits and automatic sprinklers. | Airport traffic control towers with multiple exits and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be provided with smoke detectors in all of the following locations: | 907.2.22.1 Airport traffic control towers with multiple exits and automatic sprinklers. | Airport traffic control towers with multiple exits and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be provided with smoke detectors in all of the following locations:
907.2.22.2 Other airport traffic control towers. | Airport traffic control towers with a single exit or where sprinklers are not installed throughout shall be provided with smoke detectors in all of the following locations: | 907.2.22.2 Other airport traffic control towers. | Airport traffic control towers with a single exit or where sprinklers are not installed throughout shall be provided with smoke detectors in all of the following locations:
907.2.13.1.1 Automatic smoke detection. | Automatic smoke detectors shall be provided in accordance with this section. Smoke detectors shall be connected to an automatic fire alarm system. The activation of any detector required by this section shall activate the emergency voice/alarm communication system. Smoke detectors shall be located as follows:
907.3 Fire safety functions. | Automatic fire detectors utilized for the purpose of performing fire safety functions shall be connected to the building’s fire alarm control unit where a fire alarm system is required by Section 907.2. Detectors shall, upon actuation, perform the intended function and activate the alarm notification appliances or activate a visible and audible supervisory signal at a constantly attended location. Exception: In buildings not equipped with a fire alarm system, the automatic fire detector shall be powered by normal electrical service and, upon actuation, perform the intended function. The detectors shall be located in accordance with NFPA 72. | 907.3 Fire safety functions. | Automatic fire detectors utilized for the purpose of performing fire safety functions shall be connected to the building’s fire alarm control unit where a fire alarm system is required by Section 907.2. Detectors shall, upon actuation, perform the intended function and activate the alarm notification appliances or activate a visible and audible supervisory signal at a constantly attended location. In buildings not equipped with a fire alarm system, the automatic fire detector shall be powered by normal electrical service and, upon actuation, perform the intended function. The detectors shall be located in accordance with NFPA 72.
907.2.13.2 Fire Department communication system. | The Fire Department Auxiliary Radio Communication System (ARCS) shall be in accordance with Section 916.
907.3.1 Duct smoke detectors. | Smoke detectors installed in ducts shall be listed for the air velocity, temperature and humidity present in the duct. Duct smoke detectors shall be connected to the building’s fire alarm control unit when a fire alarm system is required by Section 907.2. Activation of a duct smoke detector shall initiate a visible and audible alarm signal at a constantly attended location and shall perform the intended fire safety function in accordance with this code and the New York City Mechanical Code. Duct smoke detectors shall not be used as a substitute for required open area detection. Exceptions: 1. The alarm signal at a constantly attended location is not required where duct smoke detectors activate the building’s alarm notification appliances. 2. In occupancies not required to be equipped with a fire alarm system, actuation of a smoke detector shall activate a visible and an audible signal in an approved location. Smoke detector trouble conditions shall activate a visible or audible signal in an approved location and shall be identified as air duct detector trouble. | 907.3.1 Duct smoke detectors. | Smoke detectors installed in ducts shall be listed for the air velocity, temperature and humidity present in the duct. Duct smoke detectors shall be connected to the building’s fire alarm control unit where a fire alarm system is required by Section 907.2. Activation of a duct smoke detector shall initiate a visible and audible supervisory signal at a constantly attended location and shall perform the intended fire safety function in accordance with this code and the International Mechanical Code. In facilities that are required to be monitored by a supervising station, duct smoke detectors shall report only as a supervisory signal and not as a fire alarm. They shall not be used as a substitute for required open area detection. Exceptions: 1. The supervisory signal at a constantly attended location is not required where duct smoke detectors acti-vate the building’s alarm notification appliances. 2. In occupancies not required to be equipped with a fire alarm system, actuation of a smoke detector shall activate a visible and an audible signal in an approved location. Smoke detector trouble conditions shall activate a visible or audible signal in an approved location and shall be identified as air duct detector trouble.
907.2.13.3 Two-Way Communication System. | A two-way voice communication system (warden) phone that complies with the requirements of NFPA 72 shall be provided in the following locations and shall comply with the following requirements. Such phones shall communicate with the fire command center. 1. In Group B high-rise office buildings and large area office buildings, there shall be a minimum of two phones located on every floor accessible to all occupants, with each phone located within 5 feet (1524 mm) of a different exit stair. 2. Where elevator lobbies are permitted to be locked, the phones provided are permitted to be connected to the fire alarm system. 3. If phones are provided in areas of rescue assistance and refuge areas, the phones are permitted to be connected to the fire alarm system. 4. Where phones are provided to meet the requirements for stairway communication systems in Section 403.5.3.1, the phones are permitted to be connected to the fire alarm system. 5. In all Group I-2 buildings, there shall be a phone located at staff attended locations, such as nurses’ stations or similar locations accessible to all staff members, on every patient floor per fire/smoke zone. Phones shall also be located in areas of the building where the fire alarm does not sound. Exception: Group R-2 occupancies.
907.3.3 Elevator emergency operation. | Automatic fire detectors installed for elevator emergency operation shall be installed in accordance with the provisions of Chapter 30 of this code, ASME A17.1 and NFPA 72. | 907.3.3 Elevator emergency operation. | Automatic fire detectors installed for elevator emergency operation shall be installed in accordance with the provisions of ASME A17.1/CSA B44 and NFPA 72.
907.3.4 Wiring. | The wiring to the auxiliary devices and equipment used to accomplish fire safety functions shall be monitored for integrity in accordance with NFPA 72 and the New York City Electrical Code. | 907.3.4 Wiring. | The wiring to the auxiliary devices and equipment used to accomplish the fire safety functions shall be monitored for integrity in accordance with NFPA 72.
907.4 Initiating devices. | Where manual or automatic alarm initiation is required as part of a fire alarm system, the initiating devices shall be installed in accordance with Sections 907.4.1 through 907.4.4. | 907.4 Initiating devices. | Where a fire alarm system is required by another section of this code, occupant notification in accordance with Section 907.5 shall be initiated by one or more of the following. Initiating devices shall be installed in accordance with Sections 907.4.1 through 907.4.3.1.
907.4.1 Protection of fire alarm control unit. | In areas that are not continuously occupied, a single smoke detector shall be provided at the location of each fire alarm control unit, notification appliance circuit power extenders, and supervising station transmitting equipment. Exceptions: 1. Where ambient conditions prohibit installation of a smoke detector, a heat detector shall be permitted. 2. In prior code buildings, where a fire alarm control unit is installed in an interior exit stairway or ramp or exit passageway, a smoke detector is not required at the location of such fire alarm control unit. | 907.4.1 Protection of fire alarm control unit. | In areas that are not continuously occupied, a single smoke detector shall be provided at the location of each fire alarm control unit, notification appliance circuit power extenders, and supervising station transmitting equipment. Exception: Where ambient conditions prohibit installation of a smoke detector, a heat detector shall be permit-ted.
907.2.18 Underground buildings with compartment smoke control system. | Where a compartment smoke control system is installed in an underground building as required by Section 405, automatic smoke detectors shall be provided in accordance with Section 907.2.18.1.
907.4.2 Manual fire alarm boxes. | Where a manual fire alarm system is required by another section of this code, it shall be activated by fire alarm boxes installed in accordance with Sections 907.4.2.1 through 907.4.2.6. | 907.4.2 Manual fire alarm boxes. | Where a manual fire alarm system is required by another section of this code, it shall be activated by fire alarm boxes installed in accordance with Sections 907.4.2.1 through 907.4.2.6.
907.4.2.1 Location. | Manual fire alarm boxes shall be located not more than 5 feet (1524 mm) from the entrance to each exit. Additional manual fire alarm boxes shall be located so that travel distance to the nearest box does not exceed 200 feet (60 960 mm). | 907.4.2.1 Location. | Manual fire alarm boxes shall be located not more than 5 feet (1524 mm) from the entrance to each exit. In buildings not protected by an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, additional manual fire alarm boxes shall be located so that the distance of travel to the nearest box does not exceed 200 feet (60 960 mm).
907.4.2.2 Height. | The height of the manual fire alarm boxes shall be not less than 42 inches (1066.8 mm) and not more than 48 inches (1220 mm) measured vertically, from the floor level to the activating handle or lever of the box. | 907.4.2.2 Height. | The height of the manual fire alarm boxes shall be not less than 42 inches (1067 mm) and not more than 48 inches (1372 mm) measured vertically, from the floor level to the activating handle or lever of the box.
907.2.19 Underground buildings. | In underground buildings complying with Section 405 where the lowest level of a structure is more than 30 feet (9144 mm) below the lowest level of exit discharge, the structure shall be equipped throughout with a manual and automatic fire alarm system, including an emergency voice/alarm communication system installed in accordance with Section 907.5.2.2.
907.4.2.3 Color. | Manual fire alarm boxes shall be red in color. | 907.4.2.3 Color. | Manual fire alarm boxes shall be red in color.
907.4.2.4 Signs. | Where fire alarm systems are not required to be monitored by a supervising station, an approved permanent sign that reads: WHEN ALARM SOUNDS—CALL 911 shall be installed adjacent to each manual fire alarm box. Exception: Where the manufacturer has permanently provided this information on the manual fire alarm box. | 907.4.2.4 Signs. | Where fire alarm systems are not monitored by an approved supervising station in accordance with ​Section 907.6.6​, an approved permanent sign shall be installed adjacent to each manual fire alarm box that reads: WHEN ALARM SOUNDS CALL FIRE DEPARTMENT. Exception: Where the manufacturer has permanently provided this information on the manual fire alarm box.
907.2.21 Reserved.
907.4.2.5 Protective covers. | The Fire Department is authorized to require the installation of listed manual fire alarm box protective covers to prevent malicious false alarms or provide the manual fire alarm box with protection from physical damage. The protective cover shall be transparent or red in color with a transparent face to permit visibility of the manual fire alarm box. Each cover shall include proper operating instructions. A protective cover that emits a local alarm signal shall not be installed unless approved. Protective covers shall not project more than that permitted by Section 1003.3.3. | 907.4.2.5 Protective covers. | The fire code official is authorized to require the installation of listed manual fire alarm box protective covers to prevent malicious false alarms or to provide the manual fire alarm box with protection from physical damage. The protective cover shall be transparent or red in color with a transparent face to permit visibility of the manual fire alarm box. Each cover shall include proper operating instructions. A protective cover that emits a local alarm signal shall not be installed unless approved. Protective covers shall not project more than that permitted by Section 1003.3.3.
907.4.2.6 Unobstructed and unobscured. | Manual fire alarm boxes shall be readily accessible, unobstructed, unobscured and visible at all times. | 907.4.2.6 Unobstructed and unobscured. | Manual fire alarm boxes shall be provided with ready access, unobstructed, unobscured and visible at all times.
907.4.3 Automatic smoke detection. | Where an automatic smoke detection system is required, it shall utilize smoke detectors unless ambient conditions prohibit such an installation. In spaces where smoke detectors cannot be utilized due to ambient conditions, approved automatic heat detectors shall be permitted. | 907.4.3 Automatic smoke detection. | Where an automatic smoke detection system is required, it shall utilize smoke detectors unless ambient conditions prohibit such an installation. In spaces where smoke detectors cannot be utilized due to ambient conditions, approved automatic heat detectors shall be permitted.
907.4.3.1 Automatic sprinkler system. | For conditions other than specific fire safety functions noted in Section 907.3, in areas where ambient conditions prohibit the installation of smoke detectors, an automatic sprinkler system installed in such areas in accordance with Section 903.3.1.1 or 903.3.1.2 and that is connected to the fire alarm system shall be approved as automatic heat detection. | 907.4.3.1 Automatic sprinkler system. | For conditions other than specific fire safety functions noted in Section 907.3, in areas where ambient conditions prohibit the installation of smoke detectors, an automatic sprinkler system installed in such areas in accordance with Section 903.3.1.1 or 903.3.1.2 and that is connected to the fire alarm system shall be approved as automatic heat detection.
907.2.23 Battery rooms. | An approved automatic smoke detection system shall be installed in areas containing any battery systems. Where the battery room is located in a building or space that is provided with a fire alarm system or subsystem, the smoke detectors shall be connected to such building fire alarm system or subsystem. The detection system shall be supervised by a central supervising station, or a local alarm that will sound an audible signal at a constantly attended location. Battery rooms shall also comply with the requirements of the New York City Fire Code.
907.3.2 Delayed egress locks. | Where delayed egress locks are installed on means of egress doors in accordance with Section 1010.1.9.7, an automatic smoke or heat detection system shall be installed as required by that section.
907.5.2 Alarm notification appliances. | Alarm notification appliances shall be provided and shall be listed for their purpose. | 907.5.2 Alarm notification appliances. | Alarm notification appliances shall be provided and shall be listed for their purpose.
907.5.2.1 Audible alarms. | Audible alarm notification appliances shall be provided and emit a distinctive sound that is not to be used for any purpose other than that of a fire alarm. Exceptions: 1. Visible alarm notification appliances shall be allowed in lieu of audible alarm notification appliances in critical care areas of Group I-2 occupancies. 2. Where provided, audible notification appliances located in each occupant evacuation elevator lobby in accordance with Section 3008.10.1 shall be connected to a separate notification zone for manual paging only. | 907.5.2.1 Audible alarms. | Audible alarm notification appliances shall be provided and emit a distinctive sound that is not to be used for any purpose other than that of a fire alarm. Exceptions: 1. Audible alarm notification appliances are not required in critical care areas of Group I-2, Condition 2 occupancies that are in compliance with Section 907.2.6, Exception 2. 2. A visible alarm notification appliance installed in a nurses’ control station or other continuously at-tended staff location in a Group I-2, Condition 2 suite shall be an acceptable alternative to the instal-lation of audible alarm notification appliances throughout a suite or unit in Group I-2, Condition 2 occupancies that are in compliance with Section 907.2.6, Exception 2. 3. Where provided, audible notification appliances located in each enclosed occupant evacuation eleva-tor lobby in accordance with Section 3008.9.1 shall be connected to a separate notification zone for manual paging only.
907.5.2.1.1 Average sound pressure. | The audible alarm notification appliances shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level or 5 dBA above the maximum sound level having a duration of not less than 60 seconds, whichever is greater, in every occupiable space within the building. The minimum sound pressure levels shall be: 75 dBA in occupancies in Groups R and I-1; 90 dBA in mechanical equipment rooms and 60 dBA in other occupancies. For one-way voice communication system in Group R-2 occupancies, the minimum sound pressure level of the alert tone shall be 75 dBA throughout the dwelling unit. | 907.5.2.1.1 Average sound pressure. | The audible alarm notification appliances shall provide a sound pressure level of 15 decibels (dBA) above the average ambient sound level or 5 dBA above the maximum sound level having a duration of not less than 60 seconds, whichever is greater, in every occupiable space within the building.
907.3.5 Monitoring of hold-open devices and closers. | All hold-open devices used in automatic-closing doors pursuant to the exception to Section 713.7 shall be electrically supervised to monitor the integrity of the wiring connections among the fire alarm system, the smoke detection system, and the hold-open devices.
907.5.2.1.2 Maximum sound pressure. | The maximum sound pressure level for audible alarm notification appliances shall be 110 dBA at the minimum hearing distance from the audible appliance. Where the average ambient noise is greater than 95 dBA, visible alarm notification appliances shall be provided in accordance with NFPA 72 and audible alarm notification appliances shall not be required. | 907.5.2.1.2 Maximum sound pressure. | The total sound pressure level produced by combining the ambient sound pressure level with all audible notification appliances operating shall not exceed 110 dBA at the minimum hearing distance from the audible appliance. Where the average ambient noise is greater than 105 dBA, visible alarm notification appliances shall be provided in accordance with NFPA 72 and audible alarm notification appliances shall not be required.
907.5.2.2 Emergency voice/alarm communication systems. | Emergency voice/alarm communication systems required by this code shall be designed and installed in accordance with NFPA 72. The operation of any automatic fire detector, sprinkler waterflow device or manual fire alarm box shall automatically sound an alert tone followed by voice instructions giving approved information and directions for a general or staged evacuation in accordance with the building’s fire safety and evacuation plans required by the New York City Fire Code. In high-rise buildings, the system shall operate on at least the alarming floor, the floor above and the floor below. Speakers shall be provided throughout the building by paging zones. At a minimum, paging zones shall be provided as follows: 1. Each exit stairway. 2. Each floor. 3. Refuge areas as defined in Chapter 2 of this code. Exceptions: 1. Group I-1 and I-2 occupancies. In Group I-1 and I-2 occupancies, the alarm shall sound in a constantly attended area and a general occupant notification shall be broadcast over the overhead page. 2. Group R-2 occupancies greater than 75 feet (22 860 mm) in height. In Group R-2 occupied buildings greater than 75 feet (22 860 mm) in height above the lowest level of Fire Department vehicle access, activation of any smoke detector or sprinkler water flow device shall initiate a signal at a central supervising station or constantly attended location and shall not initiate a signal to an alarm notification appliance. An emergency voice/alarm communication system shall not be required. However, a one-way voice communication shall be provided between the fire command center for use by Fire Department personnel and the following terminal areas: 2.1. Within dwelling units. An intercom system may be utilized when provided with an override feature for use by Fire Department personnel. Such intercom system shall comply with rules promulgated by the commissioner establishing installation requirements. 2.2. Within required exit stairs. Annunciation devices shall be located at least on every other story units. Such annunciation devices shall comply with rules promulgated by the commissioner establishing installation requirements. | 907.5.2.2 Emergency voice/alarm communication systems. | Emergency voice/alarm communication systems required by this code shall be designed and installed in accordance with NFPA 72. The operation of any automatic fire detector, sprinkler waterflow device or manual fire alarm box shall automatically sound an alert tone followed by voice instructions giving approved information and directions for a general or staged evacuation in accordance with the building’s fire safety and evacuation plans required by Section 404 of the International Fire Code. In high-rise buildings, the system shall operate on at least the alarming floor, the floor above and the floor below. Speakers shall be provided throughout the building by paging zones. At a minimum, paging zones shall be provided as follows: 1. Elevator groups. 2. Interior exit stairways. 3. Each floor. 4. Areas of refuge as defined in Chapter 2. Exception: In Group I-1 and I-2 occupancies, the alarm shall sound in a constantly attended area and a gen-eral occupant notification shall be broadcast over the overhead page.
907.5.2.2.1 Manual override. | A manual override for emergency voice communication shall be provided on a selective and all-call basis for all paging zones. | 907.5.2.2.1 Manual override. | A manual override for emergency voice communication shall be provided on a selective and all-call basis for all paging zones.
907.5.2.2.2 Live voice messages. | The emergency voice/alarm communication system shall have multi-channel capability to broadcast live voice messages by paging zones on a selective and all-call basis without automatic interruption of the alarm tones on the floor of incidence, floor above or floor below. | 907.5.2.2.2 Live voice messages. | The emergency voice/alarm communication system shall have the capability to broadcast live voice messages by paging zones on a selective and all-call basis.
907.5.2.2.4 Emergency voice/alarm communication captions. | Where stadiums, arenas and grandstands provide audible public announcements, the emergency/voice alarm communication system shall be captioned. Emergency captions shall be approved by the Fire Department. | 907.5.2.2.4 Emergency voice/alarm communication captions. | Where stadiums, arenas and grandstands have 15,000 fixed seats or more and provide audible public announcements, the emergency/voice alarm communication system shall provide prerecorded or real-time captions. Prerecorded or live emergency captions shall be from an approved location constantly attended by personnel trained to respond to an emergency.
907.5.2.3 Visible alarms. | Visible alarm notification appliances shall be provided in accordance with Sections 907.5.2.3.1 through 907.5.2.3.2. Exceptions: 1. Visible alarm notification appliances shall not be required in exits as defined in Chapter 2. 2. Visible alarm notification appliances shall not be required in elevator cars. | 907.5.2.3 Visible alarms. | Visible alarm notification appliances shall be provided in accordance with Sections 907.5.2.3.1 through 907.5.2.3.3. Exceptions: 1. Visible alarm notification appliances are not required in alterations, except where an existing fire alarm system is upgraded or replaced, or a new fire alarm system is installed. 2. Visible alarm notification appliances shall not be required in exits as defined in Chapter 2. 3. Visible alarm notification appliances shall not be required in elevator cars. 4. Visual alarm notification appliances are not required in critical care areas of Group I-2, Condition 2 occupancies that are in compliance with Section 907.2.6, Exception 2. 5. A visible alarm notification appliance installed in a nurses’ control station or other continuously at-tended staff location in a Group I-2, Condition 2 suite shall be an acceptable alternative to the instal-lation of visible alarm notification appliances throughout the suite or unit in Group I-2, Condition 2 occupancies that are in compliance with Section 907.2.6, Exception 2.
907.4.4 Fire-extinguishing systems. | Where a fire alarm system is required by another section of this code or is otherwise installed, automatic fire-extinguishing systems installed in accordance with Section 904 shall be monitored by the fire alarm system.
907.5.2.3.2 Groups I-1 and R-1. | Group I-1 and R-1 dwelling units or sleeping units in accordance with Table 907.5.2.3.2 shall be provided with a visible alarm notification appliance, activated by both the in-room smoke detector and the building fire alarm system. | 907.5.2.3.2 Groups I-1 and R-1. | Habitable spaces in dwelling units and sleeping units in Group I-1 and R-1 occupancies in accordance with Table 907.5.2.3.2 shall be provided with visible alarm notification. Visible alarms shall be activated by the in-room smoke alarm and the building fire alarm system. |  | See BC09 Tables&Figures
907.5 Occupant notification systems. | A fire alarm system shall annunciate at the fire alarm control unit and shall initiate occupant notification upon activation, in accordance with Sections 907.5.1 through 907.5.2.3.2. Where a fire alarm system is required by another section of this code, it shall be activated by: 1. Automatic fire detectors. 2. Automatic sprinkler system waterflow devices. 3. Manual fire alarm boxes. 4. Automatic fire-extinguishing systems. Exception: Where notification systems are allowed elsewhere in Section 907 to annunciate at a constantly attended location or to a central supervising station.
907.5.1 Presignal feature. | A presignal feature shall not be installed unless approved by the Fire Department. Where a presignal feature is provided, a signal shall be annunciated at a constantly attended location approved by the Fire Department, in order that occupant notification can be activated in the event of fire or other emergency.
907.6 Installation and monitoring. | A fire alarm system shall be installed and monitored in accordance with Sections 907.6.1 through 907.6.5.2 of this code and NFPA 72. | 907.6 Installation and monitoring. | A fire alarm system shall be installed and monitored in accordance with Sections 907.6.1 through 907.6.6.3 and NFPA 72.
907.6.1 Wiring. | Wiring shall comply with the requirements of the New York City Electrical Code and NFPA 72. Wireless protection systems utilizing radio-frequency transmitting devices shall comply with the special requirements for supervision of low-power wireless systems in NFPA 72. | 907.6.1 Wiring. | Wiring shall comply with the requirements of NFPA 70 and NFPA 72. Wireless protection systems utilizing radio-frequency transmitting devices shall comply with the special requirements for supervision of low-power wireless systems in NFPA 72.
907.6.2 Power supply. | The primary and secondary power supply for the fire alarm system shall be provided in accordance with the New York City Electrical Code. Exception: Secondary power for single-station and multiple-station smoke alarms as required in Section 907.2.11.2. | 907.6.2 Power supply. | The primary and secondary power supply for the fire alarm system shall be provided in accordance with NFPA 72. Exception: Back-up power for single-station and multiple-station smoke alarms as required in Section 907.2.11.6.
907.5.2.2.3 Alternate uses. | When approved by the Fire Commissioner, the emergency voice/alarm communication system may be allowed to be used for other announcements.
907.5.2.2.5 Emergency power. | Emergency voice/alarm communications systems shall be provided with an approved emergency power source in accordance with Section 2702 of this code and the New York City Electrical Code.
907.5.2.3.1 Public and common areas. | Visible alarm notification appliances shall be provided in public use areas and common use areas, as defined in Chapter 2. Exception: Where employee work areas have audible alarm coverage, the notification appliance circuits serving the employee work areas shall be initially designed with not less than 20-percent spare capacity to account for the potential of adding visible notification appliances in the future to accommodate hearing impaired employee(s).
907.7 Acceptance tests and completion. | Upon completion of the installation, the fire alarm system and all fire alarm components shall be tested in accordance with NFPA 72. | 907.7 Acceptance tests and completion. | Upon completion of the installation, the fire alarm system and all fire alarm components shall be tested in accordance with NFPA 72.
907.7.1 Single- and multiple-station alarm devices. | When the installation of the alarm devices is complete, each device and interconnecting wiring for multiple-station alarm devices shall be tested in accordance with the smoke alarm provisions of NFPA 72. | 907.7.1 Single- and multiple-station alarm devices. | When the installation of the alarm devices is complete, each device and interconnecting wiring for multiple-station alarm devices shall be tested in accordance with the smoke alarm provisions of NFPA 72.
907.7.2 Record of completion. | A record of completion in accordance with NFPA 72 verifying that the system has been installed and tested in accordance with the approved construction documents and specifications shall be provided. | 907.7.2 Record of completion. | A record of completion in accordance with NFPA 72 verifying that the system has been installed and tested in accordance with the approved plans and specifications shall be provided.
907.6.3 Zones. | Each floor shall be zoned separately. For non-addressable systems, a zone shall not exceed 22,500 square feet (2090.3 m2). The length of any zone shall not exceed 300 feet (91 440 mm) in any direction. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13.
907.7.3 Instructions. | Operating, testing and maintenance instructions, and record drawings (“as builts”) and equipment specifications shall be provided at an approved location. | 907.7.3 Instructions. | Operating, testing and maintenance instructions and record drawings (“as-builts”) and equipment specifications shall be provided at an approved location.
907.6.3.1 Zoning indicator panel. | A zoning indicator panel and the associated controls shall be provided at the main building entrance accessible to responding Fire Department personnel and in other locations approved by the commissioner and the Fire Department. The visual zone indication shall lock in until the system is reset and shall not be canceled by the operation of an audible-alarm silencing switch.
907.8 Inspection, testing and maintenance. | The maintenance and testing schedules and procedures for fire alarm and fire detection systems shall be in accordance with the New York City Fire Code. | 907.8 Inspection, testing and maintenance. | The maintenance and testing schedules and procedures for fire alarm and fire detection systems shall be in accordance with Section 907.8 of the International Fire Code.
907.6.3.2 High-rise buildings. | In high-rise buildings constructed in accordance with Section 403, a separate zone by floor shall be provided for each of the following types of alarm-initiating devices where provided:
908.1 Group H occupancies. | Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided in accordance with Section 415.5 of this code and the New York City Fire Code. | 908.1 Group H occupancies. | Emergency alarms for the detection and notification of an emergency condition in Group H occupancies shall be provided in accordance with Section 415.5.
907.6.4 Access. | Access shall be provided to each fire alarm device and notification appliance for periodic inspection, maintenance and testing.
908.2 Group H-5 occupancy. | Emergency alarms for notification of an emergency condition in a Hazardous Production Material (HPM) facility shall be provided as required in Section 415.11.3.5. A continuous gas detection system shall be provided for HPM gases in accordance with Section 415.11.7 of this code and the New York City Fire Code. | 908.2 Group H-5 occupancy. | Emergency alarms for notification of an emergency condition in an HPM facility shall be provided as required in Section 415.11.4.
907.6.5 Monitoring. | Fire alarm systems required by this chapter or by the New York City Fire Code shall be monitored by a central supervising station in accordance with NFPA 72 and approved by the Fire Commissioner. Exception: Monitoring by a central supervising station is not required for: 1. Single- and multiple-station smoke alarms required by Section 907.2.11. 2. Smoke detectors in Group I-3 occupancies. 3. Automatic sprinkler systems in one- and two-family dwellings.
907.6.5.1 Automatic telephone-dialing devices. | Automatic telephone-dialing devices used to transmit an emergency alarm shall not be connected to any Fire Department telephone number unless approved by the Fire Commissioner.
909.1 Scope and purpose. | This section applies to mechanical or passive smoke control systems where they are required by other provisions of this code. A smoke control system, where required, facilitates the evacuation of the occupants. The purpose of this section is to establish minimum requirements for the design, installation and acceptance testing of smoke control systems that are intended to provide a tenable environment for the evacuation or relocation of occupants. These provisions are not intended for the preservation of contents, the timely restoration of operations or for assistance in fire suppression or post-fire smoke purge. Smoke control systems regulated by this section serve a different purpose than the smoke- and heat-venting provisions found in Section 910. Mechanical smoke control systems shall not be considered exhaust systems under Chapter 5 of the New York City Mechanical Code. | 909.1 Scope and purpose. | This section applies to mechanical or passive smoke control systems where they are required by other provisions of this code. The purpose of this section is to establish minimum requirements for the design, installation and acceptance testing of smoke control systems that are intended to provide a tenable environment for the evacuation or relocation of occupants. These provisions are not intended for the preservation of contents, the timely restoration of operations or for assistance in fire suppression or overhaul activities. Smoke control systems regulated by this section serve a different purpose than the smoke- and heat-removal provisions found in Section 910. Mechanical smoke control systems shall not be considered exhaust systems under Chapter 5 of the International Mechanical Code.
907.6.5.2 Termination of monitoring service. | Termination of fire alarm monitoring services shall be in accordance with the New York City Fire Code.
909.2 General design requirements. | Buildings, structures or parts thereof required by this code to have a smoke control system or systems shall have such systems designed in accordance with the applicable requirements of Section 909 and the generally accepted and well-established principles of engineering relevant to the design. The construction documents shall include sufficient information and detail to adequately describe the elements of the design necessary for the proper implementation of the smoke control systems. These documents shall be accompanied by sufficient information and analysis to demonstrate compliance with these provisions. | 909.2 General design requirements. | Buildings, structures or parts thereof required by this code to have a smoke control system or systems shall have such systems designed in accordance with the applicable requirements of Section 909 and the generally accepted and well-established principles of engineering relevant to the design. The construction documents shall include sufficient information and detail to adequately describe the elements of the design necessary for the proper implementation of the smoke control systems. These documents shall be accompanied by sufficient information and analysis to demonstrate compliance with these provisions.
909.3 Special inspection and test requirements. | In addition to the ordinary inspection and test requirements that buildings, structures and parts thereof are required to undergo, smoke control systems subject to the provisions of Section 909 shall undergo special inspections and tests sufficient to verify the proper commissioning of the smoke control design in its final installed condition. The design submission accompanying the construction documents shall clearly detail procedures and methods to be used and the devices, flow measurement, and other items subject to such inspections and tests. Such commissioning shall be in accordance with generally accepted engineering practice and, where possible, based on published standards for the particular testing involved. The special inspections and tests required by this section shall be conducted under the same terms in Section 1705. Records of the special inspection, including device locations, duct air leakage, pressure differentials, air/smoke flow measurements, smoke detection and control verification shall be maintained on the premises as a baseline against which future tests can be compared. | 909.3 Special inspection and test requirements. | In addition to the ordinary inspection and test requirements that buildings, structures and parts thereof are required to undergo, smoke control systems subject to the provisions of Section 909 shall undergo special inspections and tests sufficient to verify the proper commissioning of the smoke control design in its final installed condition. The design submission accompanying the construction documents shall clearly detail procedures and methods to be used and the items subject to such inspections and tests. Such commissioning shall be in accordance with generally accepted engineering practice and, where possible, based on published standards for the particular testing involved. The special inspections and tests required by this section shall be conducted under the same terms in Section 1704.
909.4 Analysis. | A rational analysis supporting the types of smoke control systems to be employed, their methods of operation, the systems supporting them and the methods of construction to be utilized shall accompany the submitted construction documents and shall include, but not be limited to, the items indicated in Sections 909.4.1 through 909.4.7. The basis of design and design analysis of the smoke control system shall be submitted to the department and the Fire Department. | 909.4 Analysis. | A rational analysis supporting the types of smoke control systems to be employed, their methods of operation, the systems supporting them and the methods of construction to be utilized shall accompany the submitted construction documents and shall include, but not be limited to, the items indicated in Sections 909.4.1 through 909.4.7.
909.4.1 Stack effect. | The system shall be designed such that the maximum probable normal or reverse stack effect will not adversely interfere with the system’s capabilities. In determining the maximum probable stack effect, altitude, elevation, weather history and interior temperatures shall be used. | 909.4.1 Stack effect. | The system shall be designed such that the maximum probable normal or reverse stack effect will not adversely interfere with the system’s capabilities. In determining the maximum probable stack effect, altitude, elevation, weather history and interior temperatures shall be used.
909.4.2 Temperature effect of fire. | Buoyancy and expansion caused by the design fire in accordance with Section 909.9 shall be analyzed. The system shall be designed such that these effects do not adversely interfere with the system’s capabilities. | 909.4.2 Temperature effect of fire. | Buoyancy and expansion caused by the design fire in accordance with Section 909.9 shall be analyzed. The system shall be designed such that these effects do not adversely interfere with the system’s capabilities.
909.4.3 Wind effect. | The design shall consider the adverse effects of wind. Such consideration shall be consistent with the wind-loading provisions of Chapter 16. | 909.4.3 Wind effect. | The design shall consider the adverse effects of wind. Such consideration shall be consistent with the wind-loading provisions of Chapter 16.
909.4.4 HVAC systems. | The design shall consider the effects of the heating, ventilating and air-conditioning (HVAC) systems on both smoke and fire transport. The analysis shall include all permutations of systems’ status. The design shall consider the effects of the fire on the HVAC systems. | 909.4.4 HVAC systems. | The design shall consider the effects of the heating, ventilating and air-conditioning (HVAC) systems on both smoke and fire transport. The analysis shall include all permutations of systems status. The design shall consider the effects of the fire on the HVAC systems.
909.4.5 Climate. | The design shall consider the effects of low temperatures on systems, property and occupants. Air inlets and exhausts shall be located so as to prevent snow or ice blockage. | 909.4.5 Climate. | The design shall consider the effects of low temperatures on systems, property and occupants. Air inlets and exhausts shall be located so as to prevent snow or ice blockage.
908.3 Highly toxic and toxic materials. | A gas detection system shall be provided to detect the presence of highly toxic or toxic gas at or below the permissible exposure limit (PEL) or ceiling limit of the gas for which detection is provided. The system shall be capable of monitoring the discharge from the treatment system at or below one-half the immediately dangerous to life and health (IDLH) limit and shall comply with the New York City Fire Code. Exception: A gas detection system is not required for toxic gases when the physiological warning threshold level for the gas is at a level below the accepted PEL for the gas.
909.4.6 Duration of operation. | All portions of active or passive smoke control systems shall be capable of continued operation after detection of the fire event for a period of not less than either 20 minutes or 1.5 times the required safe egress time, whichever is greater. | 909.4.6 Duration of operation. | All portions of active or engineered smoke control systems shall be capable of continued operation after detection of the fire event for a period of not less than either 20 minutes or 1.5 times the calculated egress time, whichever is greater.
908.3.1 Alarms. | The gas detection system shall initiate a local alarm and transmit a signal to a constantly attended control station when a short-term hazard condition is detected. The alarm shall be both visible and audible and shall provide warning both inside and outside the area where gas is detected. The audible alarm shall be distinct from all other alarms. Exception: Signal transmission to a constantly attended control station is not required when not more than one cylinder of highly toxic or toxic gas is stored.
909.4.7 Smoke control system interaction. | The design shall consider the interaction effects of the operation of multiple smoke control systems for all design scenarios. | 909.4.7 Smoke control system interaction. | The design shall consider the interaction effects of the operation of multiple smoke control systems for all design scenarios.
908.3.2 Shutoff of gas supply. | The gas detection system shall automatically close the shutoff valve at the source on gas supply piping and tubing related to the system being monitored for whichever gas is detected. Exception: Automatic shutdown is not required for reactors utilized for the production of highly toxic or toxic compressed gases where such reactors are: 1. Operated at pressures less than 15 pounds per square inch gauge (psig) (103.4 kPa); 2. Constantly attended; and 3. Provided with readily accessible emergency shutoff valves.
909.5 Smoke barrier construction. | Smoke barriers required for passive smoke control and a smoke control system using the pressurization method shall comply with Section 709. Smoke barriers shall be constructed and sealed to limit leakage areas exclusive of protected openings. The maximum allowable leakage area shall be the aggregate area calculated using the following leakage area ratios: | 909.5 Smoke barrier construction. | Smoke barriers required for passive smoke control and a smoke control system using the pressurization method shall comply with Section 709. The maximum allowable leakage area shall be the aggregate area calculated using the following leakage area ratios:
908.3.3 Valve closure. | The automatic closure of shutoff valves shall be in accordance with the following: 1. When the gas-detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close. 2. Where the gas-detection sampling point initiating the gas detection system alarm is within a gas room and compressed gas containers are not in gas cabinets or exhausted enclosures, the shutoff valves on all gas lines for the specific gas detected shall automatically close. 3. Where the gas-detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve for the compressed container of specific gas detected supplying the manifold shall automatically close. Exception: When the gas-detection sampling point initiating the gas detection system alarm is at a use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve in the gas valve enclosure for the branch line located in the piping distribution manifold enclosure shall automatically close.
909.5.1 Total leakage area. | Total leakage area of the barrier is the product of the smoke barrier gross area multiplied by the allowable leakage area ratio, plus the area of other openings such as gaps around doors and operable windows. | 909.5.1 Total leakage area. | Total leakage area of the barrier is the product of the smoke barrier gross area multiplied by the allowable leakage area ratio, plus the area of other openings such as gaps around doors and operable windows.
908.4 Ozone gas-generator rooms. | Ozone gas-generator rooms shall be equipped with a continuous gas detection system that will shut off the generator and sound a local alarm when concentrations above the PEL occur and shall comply with the New York City Fire Code.
909.5.2 Testing of leakage area. | Compliance with the maximum allowable leakage area shall be determined by achieving the minimum air pressure difference across the barrier with the system in the smoke control mode for mechanical smoke control systems utilizing the pressurization method. Compliance with the maximum allowable leakage area of passive smoke control systems shall be verified through methods such as door fan testing or other methods, as approved by the commissioner and the Fire Commissioner. | 909.5.2 Testing of leakage area. | Compliance with the maximum total leakage area shall be determined by achieving the minimum air pressure difference across the barrier with the system in the smoke control mode for mechanical smoke control systems utilizing the pressurization method. Compliance with the maximum total leakage area of passive smoke control systems shall be verified through methods such as door fan testing or other methods, as approved by the fire code official.
908.5 Repair garages. | A flammable-gas detection system shall be provided in repair garages for vehicles fueled by enumerated gases in accordance with Section 406.8.5 of this code and the New York City Fire Code.
909.5.3 Opening protection. | Openings in smoke barriers shall be protected by automatic-closing devices actuated by the required controls for the mechanical smoke control system. Door openings shall be protected by fire door assemblies complying with Section 716.5.3. Exceptions: 1. Passive smoke control systems with automatic-closing devices actuated by spot-type smoke detectors listed for releasing service installed in accordance with Section 907.3. 2. Fixed openings between smoke zones that are protected utilizing the airflow method. 3. In Group I-1, Group I-2, and Group B ambulatory care facilities, where a pair of opposite-swinging doors are installed across a corridor in accordance with Section 909.5.3.1, the doors shall not be required to be protected in accordance with Section 716. The doors shall be close-fitting within operational tolerances and shall not have a center mullion, louvers, grilles, or door undercuts in excess of ¾ inch (19.1 mm). The doors shall have head and jamb stops and astragals or rabbets at meeting edges. If allowed by the door manufacturer’s listing, positive-latching devices are not required. 4. In Group I-1, Group I-2 and Group B ambulatory care facilities, where such doors are special-purpose horizontal sliding, accordion or folding door assemblies installed in accordance with Section 1010.1.4.3 and are automatic closing by smoke detection in accordance with Section 716.5.9.3. 5. Group I-3. 6. Openings between smoke zones with clear ceiling heights of 14 feet (4267 mm) or greater and bank-down capacity of greater than 20 minutes as determined by the design fire size. | 909.5.3 Opening protection. | Openings in smoke barriers shall be protected by automatic-closing devices actuated by the required controls for the mechanical smoke control system. Door openings shall be protected by fire door assemblies complying with Section 716. Exceptions: 1. Passive smoke control systems with automatic-closing devices actuated by spot-type smoke detectors listed for releasing service installed in accordance with Section 907.3. 2. Fixed openings between smoke zones that are protected utilizing the airflow method. 3. In Group I-1, Condition 2; Group I-2; and ambulatory care facilities, where a pair of opposite-swinging doors are installed across a corridor in accordance with Section 909.5.3.1, the doors shall not be required to be protected in accordance with Section 716. The doors shall be close-fitting within operational toler-ances and shall not have a center mullion or undercuts in excess of 3/4 inch (19.1 mm), louvers or grilles. The doors shall have head and jamb stops and astragals or rabbets at meeting edges and, where permitted by the door manufacturer’s listing, positive-latching devices are not required. 4. In Group I-2 and ambulatory care facilities, where such doors are special-purpose horizontal sliding, ac-cordion or folding door assemblies installed in accordance with Section 1010.3.3 and are automatic clos-ing by smoke detection in accordance with Section 716.2.6.5. 5. Group I-3. 6. Openings between smoke zones with clear ceiling heights of 14 feet (4267 mm) or greater and bank-down capacity of greater than 20 minutes as determined by the design fire size.
908.6 Refrigerant detectors. | Machinery rooms shall contain refrigerant detectors with audible and visual alarms. The detectors, or sampling tubes that draw air to each detector, shall be located in all areas where refrigerant from a leak will concentrate. The alarm shall be actuated at a value not greater than the corresponding TLV-TWA values for the refrigerant classification indicated in the New York City Mechanical Code. Detectors and alarms shall be placed in approved locations. Refrigerant detectors shall initiate all functions as required by the New York City Mechanical Code and New York City Fire Code.
908.7 Carbon dioxide (CO2) systems. | The emergency alarm system for a carbon dioxide system, including detection, pre-discharge and discharge alarms, shall be provided in accordance with the New York City Fire Code.
909.5.3.2 Ducts and air transfer openings. | Ducts and air transfer openings are required to be protected with a minimum Class II, 250°F (121.1°C) smoke damper complying with Section 717. | 909.5.3.2 Ducts and air transfer openings. | Ducts and air transfer openings are required to be protected with a minimum Class II, 250°F (121°C) smoke damper complying with Section 717.
908.8 Gas detection systems. | Gas detection systems shall be provided in accordance with Section 918.
909.6 Pressurization method. | The primary mechanical means of controlling smoke shall be by pressure differences across smoke barriers. Maintenance of a tenable environment is not required in the smoke control zone of fire origin. | 909.6 Pressurization method. | The primary mechanical means of controlling smoke shall be by pressure differences across smoke barriers. Maintenance of a tenable environment is not required in the smoke control zone of fire origin.
908.9 Medical gas. | Medical gas pressure monitoring and alarm systems shall be provided in accordance with NFPA 99.
909.6.1 Minimum pressure difference. | The minimum pressure difference across a smoke barrier shall be 0.05-inch water gauge (0.0124 kPa) in fully sprinklered buildings. In buildings permitted to be other than fully sprinklered, the smoke control system shall be designed to achieve pressure differences not less than two times the maximum calculated pressure difference produced by the design fire. | 909.6.1 Minimum pressure difference. | The pressure difference across a smoke barrier used to separate smoke zones shall be not less than 0.05-inch water gage (0.0124 kPa) in fully sprinklered buildings.
908.10 Flammable gas. | Rooms and spaces containing flammable gas distribution piping operating at levels above 15 pounds per square inch gauge (psig) (103.4 kPa) shall be provided with an approved flammable gas detection-alarm system and shall comply with the New York City Fire Code.
909.6.2 Maximum pressure difference. | The maximum air pressure difference across a smoke barrier shall be determined by required door-opening or closing forces. The actual force required to open exit doors when the system is in the smoke control mode shall be in accordance with Section 1010.1.3. Opening and closing forces for other doors shall be determined by standard engineering methods for the resolution of forces and reactions. The calculated force to set a side-hinged, swinging door in motion shall be determined by: | 909.6.2 Maximum pressure difference. | The maximum air pressure difference across a smoke barrier shall be determined by required door-opening or closing forces. The actual force required to open exit doors when the system is in the smoke control mode shall be in accordance with Section 1010.1.3. Opening and closing forces for other doors shall be determined by standard engineering methods for the resolution of forces and reactions. The calculated force to set a side-hinged, swinging door in motion shall be determined by:
908.11 Construction documents. | Construction documents for emergency alarm systems shall be submitted for review and approval to the Fire Department prior to system installation.
909.6.3 Pressurized stairways and elevator hoistways. | Where stairways or elevator hoistways are pressurized, such pressurization systems shall comply with Section 909 of this code as smoke control systems, in addition to the requirements of Sections 909.20 and 909.21 of this code and the New York City Fire Code. | 909.6.3 Pressurized stairways and elevator hoistways. | Where stairways or elevator hoistways are pressurized, such pressurization systems shall comply with Section 909 as smoke control systems, in addition to the requirements of Sections 909.20 of this code and 909.21 of the International Fire Code.
908.12 Acceptance testing and maintenance. | Acceptance testing and maintenance of emergency alarm systems shall be performed in accordance with the New York City Fire Code.
909.7.1 Prohibited conditions. | This method shall not be employed where either the quantity of air or the velocity of the airflow will adversely affect other portions of the smoke control system, unduly intensify the fire, disrupt plume dynamics or interfere with exiting. In no case shall airflow toward the fire exceed 200 feet per minute (1.02 m/s). Where the calculated airflow exceeds this limit, the airflow method shall not be used. | 909.7.1 Prohibited conditions. | This method shall not be employed where either the quantity of air or the velocity of the airflow will adversely affect other portions of the smoke control system, unduly intensify the fire, disrupt plume dynamics or interfere with exiting. Airflow toward the fire shall not exceed 200 feet per minute (1.02 m/s). Where the calculated airflow exceeds this limit, the airflow method shall not be used.
909.1.1 Definitions. | The following terms are defined in Chapter 2 of this code:
909.8 Exhaust method. | Where approved by the commissioner, mechanical smoke control for large enclosed volumes, such as in atriums or malls, shall be permitted to utilize the exhaust method. Smoke control systems using the exhaust method shall be designed in accordance with NFPA 92. | 909.8 Exhaust method. | Where approved by the fire code official, mechanical smoke control for large enclosed volumes, such as in atriums or malls, shall be permitted to utilize the exhaust method. Smoke control systems using the exhaust method shall be designed in accordance with NFPA 92.
909.8.1 Smoke layer. | The height of the lowest horizontal surface of the accumulating smoke layer shall be maintained not less than 6 feet (1828.8 mm) above any walking surface that forms a portion of a required egress system within the smoke zone. | 909.8.1 Smoke layer. | The height of the lowest horizontal surface of the smoke layer interface shall be maintained not less than 6 feet (1829 mm) above a walking surface that forms a portion of a required egress system within the smoke zone.
909.9 Design fire. | The design fire shall be based on a rational analysis performed by the registered design professional and approved by the commissioner. The design fire shall be based on the analysis in accordance with Section 909.4 and this section. | 909.9 Design fire. | The design fire shall be based on a rational analysis performed by the registered design professional and approved by the fire code official. The design fire shall be based on the analysis in accordance with Section 909.4 and this section.
909.3.1 Periodic testing. | Smoke control systems shall be verified weekly through the automatic control system in accordance with Section 909.12 and shall be tested annually to ensure proper operation of detection devices, dampers, fans and controls in accordance with the requirements of Sections 909.18.1, 909.18.3, 909.18.5 and 909.18.7. Full testing of smoke control systems in accordance with Sections 909.18 through 909.18.7 shall be conducted at 5-year intervals by an inspector qualified in accordance with Section 909.18.8.2. Test reports shall include all information required by Section 909.18.8.3 and shall be compared against the baseline special inspection report. Causes for any significant deviations from the baseline report shall be identified and corrected. A record of each inspection and test shall be maintained on the premises by the owner or lessee, and the records for at least the last 5 years of operation shall be made available for inspection by the department and the Fire Commissioner.
909.9.1 Factors considered. | The engineering analysis shall include the characteristics of the fuel, fuel load, effects included by the fire and whether the fire is likely to be steady or unsteady. | 909.9.1 Factors considered. | The engineering analysis shall include the characteristics of the fuel, fuel load, effects included by the fire and whether the fire is likely to be steady or unsteady.
909.9.2 Design fire fuel. | Determination of the design fire shall include consideration of the type of fuel, fuel spacing and configuration. | 909.9.2 Design fire fuel. | Determination of the design fire shall include consideration of the type of fuel, fuel spacing and configuration.
909.9.3 Heat-release assumptions. | The analysis shall make use of best available data from approved sources and shall not be based on excessively stringent limitations of combustible material. | 909.9.3 Heat-release assumptions. | The analysis shall make use of best available data from approved sources and shall not be based on excessively stringent limitations of combustible material.
909.9.4 Sprinkler effectiveness assumptions. | A documented engineering analysis shall be provided for conditions that assume fire growth is halted at the time of sprinkler activation. | 909.9.4 Sprinkler effectiveness assumptions. | A documented engineering analysis shall be provided for conditions that assume fire growth is halted at the time of sprinkler activation.
909.10 Equipment. | Equipment including, but not limited to, fans, ducts, automatic dampers and balance dampers, shall be suitable for its intended use, suitable for the probable exposure temperatures that the rational analysis indicates and as approved by the commissioner. | 909.10 Equipment. | Equipment including, but not limited to, fans, ducts, automatic dampers and balance dampers, shall be suitable for its intended use, suitable for the probable exposure temperatures that the rational analysis indicates and as approved by the fire code official.
909.10.1 Exhaust fans. | Components of exhaust fans shall be rated and certified by the manufacturer for the probable temperature rise to which the components will be exposed. This temperature rise shall be computed in accordance with NFPA 92. | 909.10.1 Exhaust fans. | Components of exhaust fans shall be rated and certified by the manufacturer for the probable temperature rise to which the components will be exposed. This temperature rise shall be computed by: Ts = (Qc/mc) + (Ta) (Equation 9-2) where: c = Specific heat of smoke at smoke layer temperature, Btu/lb°F (kJ/kg × K). m = Exhaust rate, pounds per second (kg/s). Qc = Convective heat output of fire, Btu/s (kW). Ta = Ambient temperature, °F (K). Ts = Smoke temperature, °F (K). Exception: Reduced Ts as calculated based on the assurance of adequate dilution air.
909.10.2 Ducts. | Duct materials and joints shall be capable of withstanding the probable temperatures and pressures to which they are exposed as determined in accordance with Section 909.10.1. Ducts shall be constructed and supported in accordance with the New York City Mechanical Code. Ducts shall be leak tested to 1.5 times the maximum design pressure in accordance with nationally accepted practices. Measured leakage shall not exceed 5 percent of design flow. Results of such testing shall be a part of the documentation procedure. Ducts shall be supported directly from fire-resistance-rated structural elements of the building by substantial, noncombustible supports. Exception: Flexible connections, for the purpose of vibration isolation, complying with the New York City Mechanical Code and that are constructed of approved fire-resistance-rated materials. | 909.10.2 Ducts. | Duct materials and joints shall be capable of withstanding the probable temperatures and pressures to which they are exposed as determined in accordance with Section 909.10.1. Ducts shall be constructed and supported in accordance with the International Mechanical Code. Ducts shall be leak tested to 1.5 times the maximum design pressure in accordance with nationally accepted practices. Measured leakage shall not exceed 5 percent of design flow. Results of such testing shall be a part of the documentation procedure. Ducts shall be supported directly from fire-resistance-rated structural elements of the building by substantial, noncombustible supports. Exception: Flexible connections, for the purpose of vibration isolation, complying with the International Me-chanical Code and that are constructed of approved fire-resistance-rated materials.
909.10.3 Equipment, inlets and outlets. | Equipment shall be located so as not to expose uninvolved portions of the building to an additional fire hazard. Outside air inlets shall be located so as to minimize the potential for introducing smoke or flame into the building. Exhaust outlets shall be located so as to minimize reintroduction of smoke into the building and to limit exposure of the building or adjacent buildings to an additional fire hazard. | 909.10.3 Equipment, inlets and outlets. | Equipment shall be located so as to not expose uninvolved portions of the building to an additional fire hazard. Outside air inlets shall be located so as to minimize the potential for introducing smoke or flame into the building. Exhaust outlets shall be so located as to minimize reintroduction of smoke into the building and to limit exposure of the building or adjacent buildings to an additional fire hazard.
909.10.4 Automatic dampers. | Automatic dampers, regardless of the purpose for which they are installed within the smoke control system, shall comply with Section 717.3.1. | 909.10.4 Automatic dampers. | Automatic dampers, regardless of the purpose for which they are installed within the smoke control system, shall be listed and conform to the requirements of approved, recognized standards.
909.10.5 Fans. | In addition to other requirements, belt-driven fans shall have 1.5 times the number of belts required for the design duty with the minimum number of belts being two. Fans shall be selected for stable performance based on normal temperature and, where applicable, elevated temperature. Calculations and manufacturer’s fan curves shall be part of the documentation procedures. Fans shall be supported and restrained by noncombustible devices in accordance with the requirements of Chapter 16. Motors driving fans shall not be operated beyond their nameplate horsepower (kilowatts), as determined from measurement of actual current draw, and shall have a minimum service factor of 1.15. | 909.10.5 Fans. | In addition to other requirements, belt-driven fans shall have 1.5 times the number of belts required for the design duty, with the minimum number of belts being two. Fans shall be selected for stable performance based on normal temperature and, where applicable, elevated temperature. Calculations and manufacturer’s fan curves shall be part of the documentation procedures. Fans shall be supported and restrained by noncombustible devices in accordance with the requirements of Chapter 16.
909.11 Standby power. | The smoke control system shall be supplied with two sources of power. The primary power supply shall be from the normal building power systems, while the secondary power source shall be from a standby power system complying with Section 2702. | 909.11 Standby power. | Smoke control systems shall be provided with standby power in accordance with Section 2702.
909.11.1 Equipment room. | The standby power source shall be located in a room separate from the normal power transformers and switch gears, and ventilated directly to and from the exterior. The room shall be enclosed with not less than 2-hour fire barriers constructed in accordance with Section 707, or with not less than 2-hour fire-resistance-rated horizontal assemblies constructed in accordance with Section 711, or both. | 909.11.1 Equipment room. | The standby power source and its transfer switches shall be in a room separate from the normal power transformers and switch gears and ventilated directly to and from the exterior. The room shall be enclosed with not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
909.11.2 Power sources and power surges. | Elements of the smoke control system relying on electronic volatile memories or similar systems shall be supplied with uninterruptable power sources of sufficient duration to span a 15-minute primary power interruption. Elements of the smoke control system susceptible to power surges shall be suitably protected by conditioners, suppressors or other approved means. | 909.11.2 Power sources and power surges. | Elements of the smoke control system relying on volatile memories or the like shall be supplied with uninterruptable power sources of sufficient duration to span 15-minute primary power interruption. Elements of the smoke control system susceptible to power surges shall be suitably protected by conditioners, suppressors or other approved means.
909.5.3.1 Group I-2 and Group B ambulatory care facilities. | In Group I-2 and Group B ambulatory care facilities, where doors are installed across a corridor, the doors shall be automatic closing by smoke detection in accordance with Section 716.5.9.3 and shall have a vision panel with fire protection-rated glazing materials in fire protection-rated frames, the area of which shall not exceed that tested.
909.12 Detection and control systems. | Fire detection systems providing control input or output signals to mechanical smoke control systems or elements thereof shall comply with the requirements of Section 907. Such systems shall be equipped with a control unit complying with UL 864 and listed as smoke control equipment. | 909.12 Detection and control systems. | Fire detection systems providing control input or output signals to mechanical smoke control systems or elements thereof shall comply with the requirements of Section 907. Such systems shall be equipped with a control unit complying with UL 864 and listed as smoke control equipment.
909.12.1 Verification. | Control systems for mechanical smoke control systems shall include provisions for verification. Verification shall include positive confirmation of actuation, testing, manual override and the presence of power downstream of all disconnects. A preprogrammed weekly test sequence shall report, abnormal conditions audibly, visually and by printed report. The preprogrammed weekly test shall operate all devices, equipment and components used for smoke control. Exception: Where verification of individual components tested through the preprogrammed weekly testing sequence will interfere with, and produce unwanted effects to, normal building operation, such individual components are permitted to be bypassed from the preprogrammed weekly testing, where approved by the Fire Department and in accordance with both of the following: 1. Where the operation of components is bypassed from the preprogrammed weekly test, presence of power downstream of all disconnects shall be verified weekly by a listed control unit. 2. Testing of all components bypassed from the preprogrammed weekly test shall be tested semi-annually, and be tested under standby power conditions in accordance with Section 909 of the New York City Fire Code. | 909.12.1 Verification. | Control systems for mechanical smoke control systems shall include provisions for verification. Verification shall include positive confirmation of actuation, testing, manual override and the presence of power downstream of all disconnects. A preprogrammed weekly test sequence shall report abnormal conditions audibly, visually and by printed report. The preprogrammed weekly test shall operate all devices, equipment and components used for smoke control. Exception: Where verification of individual components tested through the preprogrammed weekly testing se-quence will interfere with, and produce unwanted effects to, normal building operation, such individual compo-nents are permitted to be bypassed from the preprogrammed weekly testing, where approved by the building of-ficial and in accordance with both of the following: 1. Where the operation of components is bypassed from the preprogrammed weekly test, presence of power downstream of all disconnects shall be verified weekly by a listed control unit. 2. Testing of all components bypassed from the preprogrammed weekly test shall be in accordance with Sec-tion 909.20.6 of the International Fire Code.
909.12.2 Wiring. | In addition to meeting requirements of the New York City Electrical Code, all wiring, regardless of voltage, shall be fully enclosed within continuous raceways. | 909.12.2 Wiring. | In addition to meeting requirements of NFPA 70, all wiring, regardless of voltage, shall be fully enclosed within continuous raceways.
909.12.3 Activation. | Smoke control systems shall be activated in accordance with this section. | 909.12.3 Activation. | Smoke control systems shall be activated in accordance with this section.
909.12.3.1 Pressurization, airflow or exhaust method. | Mechanical smoke control systems using the pressurization, airflow or exhaust method shall have completely automatic control. | 909.12.3.1 Pressurization, airflow or exhaust method. | Mechanical smoke control systems using the pressurization, airflow or exhaust method shall have completely automatic control.
909.12.3.2 Passive method. | Passive smoke control systems actuated by spot-type detectors listed for releasing service shall be permitted. | 909.12.3.2 Passive method. | Passive smoke control systems actuated by approved spot-type detectors listed for releasing service shall be permitted.
909.7 Air flow design method. | Where approved by the commissioner, smoke migration through openings fixed in a permanently open position, which are located between smoke control zones by the use of the airflow method, shall be permitted. The design air flow shall be in accordance with this section. Air flow shall be directed to limit smoke migration from the fire zone. The geometry of openings shall be considered to prevent flow reversal from turbulent effects. Smoke control systems using the airflow method shall be designed in accordance with NFPA 92.
909.12.4 Automatic control. | Where completely automatic control is required or used, the automatic-control sequences shall be initiated from an appropriately zoned automatic sprinkler system complying with Section 903.3.1.1, manual controls that are readily accessible to the Fire Department and any smoke detectors required by engineering analysis. See Section 909.16 for manual control requirements. | 909.12.4 Automatic control. | Where completely automatic control is required or used, the automatic-control sequences shall be initiated from an appropriately zoned automatic sprinkler system complying with Section 903.3.1.1, manual controls provided with ready access for the fire department and any smoke detectors required by engineering analysis.
909.13 Control air tubing. | Control air tubing shall be of sufficient size to meet the required response times. Tubing shall be flushed clean and dry prior to final connections and shall be adequately supported and protected from damage. Tubing passing through concrete or masonry shall be sleeved and protected from abrasion and electrolytic action. | 909.13 Control air tubing. | Control air tubing shall be of sufficient size to meet the required response times. Tubing shall be flushed clean and dry prior to final connections and shall be adequately supported and protected from damage. Tubing passing through concrete or masonry shall be sleeved and protected from abrasion and electrolytic action.
909.13.1 Materials. | Control air tubing shall be hard drawn copper, Type L, ACR in accordance with ASTM B 42, ASTM B 43, ASTM B 68, ASTM B 88, ASTM B 251 and ASTM B 280. Fittings shall be wrought copper or brass, solder type, in accordance with ASME B 16.18 or ASME B16.22. Changes in direction shall be made with appropriate tool bends. Brass compression-type fittings shall be used at final connection to devices; other joints shall be brazed using a BCuP-5 brazing alloy with solidus above 1,100°F (593.3°C) and liquids below 1,500°F (815.6°C). Brazing flux shall be used on copper-to-brass joints only. Exception: Nonmetallic tubing used within control panels and at the final connection to devices provided all of the following conditions are met: | 909.13.1 Materials. | Control-air tubing shall be hard-drawn copper, Type L, ACR in accordance with ASTM B42, ASTM B43, ASTM B68/B68M, ASTM B88, ASTM B251 and ASTM B280. Fittings shall be wrought copper or brass, solder type in accordance with ASME B16.18 or ASME B16.22. Changes in direction shall be made with appropriate tool bends. Brass compression-type fittings shall be used at final connection to devices; other joints shall be brazed using a BCuP-5 brazing alloy with solidus above 1,100°F (593°C) and liquids below 1,500°F (816°C). Brazing flux shall be used on copper-to-brass joints only. Exception: Nonmetallic tubing used within control panels and at the final connection to devices provided that all of the following conditions are met: 1. Tubing shall comply with the requirements of Section 602.2.1.3 of the International Mechanical Code. 2. Tubing and connected devices shall be completely enclosed within a galvanized or paint-grade steel en-closure having a minimum thickness of 0.0296 inch (0.7534 mm) (No. 22 gage). Entry to the enclosure shall be by copper tubing with a protective grommet of neoprene or Teflon or by suitable brass compres-sion to male barbed adapter. 3. Tubing shall be identified by appropriately documented coding. 4. Tubing shall be neatly tied and supported within the enclosure. Tubing bridging cabinets and doors or moveable devices shall be of sufficient length to avoid tension and excessive stress. Tubing shall be pro-tected against abrasion. Tubing connected to devices on doors shall be fastened along hinges.
909.13.2 Isolation from other functions. | Control tubing serving other than smoke control functions shall be isolated by automatic isolation valves or shall be an independent system. | 909.13.2 Isolation from other functions. | Control tubing serving other than smoke control functions shall be isolated by automatic isolation valves or shall be an independent system.
909.13.3 Testing. | Control air tubing shall be tested at three times the operating pressure for not less than 30 minutes without any noticeable loss in gauge pressure prior to final connection to devices. | 909.13.3 Testing. | Control air tubing shall be tested at three times the operating pressure for not less than 30 minutes without any noticeable loss in gauge pressure prior to final connection to devices.
909.14 Marking and identification. | The detection and control systems shall be clearly marked at all junctions, accesses and terminations. | 909.14 Marking and identification. | The detection and control systems shall be clearly marked at all junctions, accesses and terminations.
909.15 Control diagrams. | Identical control diagrams showing all devices in the system and identifying their location and function shall be maintained current and kept on file with the department, the Fire Department and in the fire command center in a format and manner approved by the Fire Commissioner. | 909.15 Control diagrams. | Identical control diagrams showing all devices in the system and identifying their location and function shall be maintained current and kept on file with the fire code official, the fire department and in the fire command center in a format and manner approved by the fire code official.
909.16.3 Control action and priorities. | The firefighter’s control panel actions shall be as follows: 1. ON-OFF and OPEN-CLOSE control actions shall have the highest priority of any control point within the building. Once issued from the firefighter’s control panel, automatic or manual control from any other control point within the building shall not contradict the control action. Where automatic means are provided to interrupt normal, nonemergency equipment operation or produce a specific result to safeguard the building or equipment including, but not limited to, duct freezestats, duct smoke detectors, high-temperature cutouts, temperature-actuated linkage and similar devices, such means shall be capable of being overridden by the firefighter’s control panel. The last control action as indicated by each firefighter’s control panel switch position shall prevail. Control actions shall not require the smoke control system to assume more than one configuration at any one time. Exception: Power disconnects required by the New York City Electrical Code. 2. Only the AUTO position of each three-position firefighter’s control panel switch shall allow automatic or manual control action from other control points within the building. The AUTO position shall be the NORMAL, nonemergency, building control position. Where a firefighter’s control panel is in the AUTO position, the actual status of the device (on, off, open, closed) shall continue to be indicated by the status indicator described in Section 909.16.1. Where directed by an automatic signal to assume an emergency condition, the NORMAL position shall become the emergency condition for that device or group of devices within the zone. Control actions shall not require the smoke control system to assume more than one configuration at any one time. | 909.16.3 Control action and priorities. | The fire-fighter’s control panel actions shall be as follows: 1. ON-OFF and OPEN-CLOSE control actions shall have the highest priority of any control point within the building. Once issued from the fire fighter’s control panel, automatic or manual control from any other con-trol point within the building shall not contradict the control action. Where automatic means are provided to interrupt normal, nonemergency equipment operation or produce a specific result to safeguard the building or equipment including, but not limited to, duct freezestats, duct smoke detectors, high-temperature cutouts, temperature-actuated linkage and similar devices, such means shall be capable of being overridden by the fire fighter’s control panel. The last control action as indicated by each fire fighter’s control panel switch po-sition shall prevail. Control actions shall not require the smoke control system to assume more than one con-figuration at any one time. Exception: Power disconnects required by NFPA 70. 2. Only the AUTO position of each three-position fire-fighter’s control panel switch shall allow automatic or manual control action from other control points within the building. The AUTO position shall be the NOR-MAL, nonemergency, building control position. Where a fire fighter’s control panel is in the AUTO position, the actual status of the device (on, off, open, closed) shall continue to be indicated by the status indicator de-scribed in Section 909.16.1. Where directed by an automatic signal to assume an emergency condition, the NORMAL position shall become the emergency condition for that device or group of devices within the zone. Control actions shall not require the smoke control system to assume more than one configuration at any one time.
909.17 System response time. | Smoke-control system activation shall be initiated immediately after receipt of an appropriate automatic or manual activation command. Smoke control systems shall activate individual components (such as dampers and fans) in the sequence necessary to prevent physical damage to the fans, dampers, ducts and other equipment. For purposes of smoke control, the firefighter’s control panel response time shall be the same for automatic or manual smoke control action initiated from any other building control point. The total response time, including that necessary for detection, shutdown of operating equipment and smoke control system startup, shall allow for full operational mode to be achieved before the conditions in the space exceed the design smoke condition. The system response time for each component and their sequential relationships shall be detailed in the required rational analysis and verification of their installed condition reported in the required final report. | 909.17 System response time. | Smoke-control system activation shall be initiated immediately after receipt of an appropriate automatic or manual activation command. Smoke control systems shall activate individual components (such as dampers and fans) in the sequence necessary to prevent physical damage to the fans, dampers, ducts and other equipment. For purposes of smoke control, the fire fighter’s control panel response time shall be the same for automatic or manual smoke control action initiated from any other building control point. The total response time, including that necessary for detection, shutdown of operating equipment and smoke control system startup, shall allow for full operational mode to be achieved before the conditions in the space exceed the design smoke condition. Upon receipt of an alarm condition at the fire alarm control panel, fans, dampers and automatic doors shall have achieved their proper operating state and the final status shall be indicated at the smoke control panel within 90 seconds. The system response time for each component and their sequential relationships shall be detailed in the required rational analysis and verification of their installed condition reported in the required final report.
909.18 Acceptance testing. | Devices, equipment, components and sequences shall be individually tested. These tests, in addition to those required by other provisions of this code, shall consist of determination of function, sequence and, where applicable, capacity of their installed condition. | 909.18 Acceptance testing. | Devices, equipment, components and sequences shall be individually tested. These tests, in addition to those required by other provisions of this code, shall consist of determination of function, sequence and, where applicable, capacity of their installed condition.
909.18.1 Detection devices. | Smoke or fire detectors that are a part of a smoke control system shall be tested in accordance with Chapter 9 in their installed condition. Where applicable, this testing shall include verification of airflow in both minimum and maximum conditions. | 909.18.1 Detection devices. | Smoke or fire detectors that are a part of a smoke control system shall be tested in accordance with Chapter 9 in their installed condition. Where applicable, this testing shall include verification of airflow in both minimum and maximum conditions.
909.18.2 Ducts. | Ducts that are part of a smoke control system shall be traversed using generally accepted practices to determine actual air quantities. | 909.18.2 Ducts. | Ducts that are part of a smoke control system shall be traversed using generally accepted practices to determine actual air quantities.
909.10.6 Seismic Requirements. | Smoke control systems covered by Section 909 are required to function after an earthquake. Such smoke control systems shall be seismically designed in accordance with Section 1613 of this code and ASCE 7. The component importance factor, Ip, shall be taken as 1.5 in accordance with ASCE 7, Section 13.1.3. The smoke control system includes all components required for its operation, including but not limited to fans, ducts, electrical power, switchboards, motor control centers, starters, and controls. Exception: Smoke control systems in structures classified in Seismic Design Categories A or B shall have a component importance factor, Ip, of 1.0.
909.18.3 Dampers. | Dampers shall be tested for function in their installed condition. | 909.18.3 Dampers. | Dampers shall be tested for function in their installed condition.
909.18.4 Inlets and outlets. | Inlets and outlets shall be read using generally accepted practices to determine air quantities. | 909.18.4 Inlets and outlets. | Inlets and outlets shall be read using generally accepted practices to determine air quantities.
909.18.5 Fans. | Fans shall be examined for correct rotation. Measurements of voltage, amperage, revolutions per minute (rpm) and belt tension shall be made. | 909.18.5 Fans. | Fans shall be examined for correct rotation. Measurements of voltage, amperage, revolutions per minute (rpm) and belt tension shall be made.
909.18.6 Smoke barriers. | Measurements using inclined manometers or other approved calibrated measuring devices shall be made of the pressure differences across smoke barriers. Such measurements shall be conducted for each possible smoke control condition. | 909.18.6 Smoke barriers. | Measurements using inclined manometers or other approved calibrated measuring devices shall be made of the pressure differences across smoke barriers. Such measurements shall be conducted for each possible smoke control condition.
909.18.7 Controls. | Each smoke zone equipped with an automatic-initiation device shall be put into operation by the actuation of one such device. Each additional device within the zone shall be verified to cause the same sequence without requiring the operation of fan motors in order to prevent damage. Control sequences shall be verified throughout the system, including verification of override from the firefighter’s control panel and simulation of standby power conditions. | 909.18.7 Controls. | Each smoke zone equipped with an automatic-initiation device shall be put into operation by the actuation of one such device. Each additional device within the zone shall be verified to cause the same sequence without requiring the operation of fan motors in order to prevent damage. Control sequences shall be verified throughout the system, including verification of override from the fire fighter’s control panel and simulation of standby power conditions.
909.18.8.1 Scope of testing. | Special inspections shall be conducted in accordance with the following: | 909.18.8.1 Scope of testing. | Testing shall be conducted in accordance with the following:
909.18.8.2 Qualifications. | Special inspectors for smoke control shall have a certification as air balancers and expertise in fire protection engineering or mechanical engineering. | 909.18.8.2 Qualifications. | Approved agencies for smoke control testing shall have expertise in fire protection engineering, mechanical engineering and certification as air balancers.
909.18.8.3 Reports. | A complete report of testing shall be prepared by the special inspector or approved agency. The report shall include identification of all devices by manufacturer, nameplate data, design values, measured values and identification tag or mark. The report shall be reviewed by the responsible engineer and, when satisfied that the design intent has been achieved, the engineer shall seal, sign and date the report. | 909.18.8.3 Reports. | A complete report of testing shall be prepared by the approved agency. The report shall include identification of all devices by manufacturer, nameplate data, design values, measured values and identification tag or mark. The report shall be reviewed by the responsible registered design professional and, when satisfied that the design intent has been achieved, the responsible registered design professional shall sign, seal and date the report.
909.18.8.3.1 Report filing. | A copy of the final report and each inspection report shall be filed with the department and Fire Commissioner, and an identical copy shall be maintained in an approved location at the building. | 909.18.8.3.1 Report filing. | A copy of the final report shall be filed with the fire code official and an identical copy shall be maintained in an approved location at the building.
909.18.9 Identification and documentation. | Charts, drawings and other documents identifying and locating each component of the smoke control system, and describing its proper function and maintenance requirements, shall be maintained on file at the building as an attachment to the report required by Section 909.18.8.3. Devices shall have an approved identifying tag or mark on them consistent with the other required documentation and shall be dated indicating the last time they were successfully tested and by whom. | 909.18.9 Identification and documentation. | Charts, drawings and other documents identifying and locating each component of the smoke control system, and describing its proper function and maintenance requirements, shall be maintained on file at the building as an attachment to the report required by Section 909.18.8.3. Devices shall have an approved identifying tag or mark on them consistent with the other required documentation and shall be dated indicating the last time they were successfully tested and by whom.
909.12.4.1 Building Management System. | Automatic and manual operation of the smoke control system may alternately be done through a Building Management System (BMS) that is approved by the Fire Department and meets the following requirements:
909.19 System acceptance. | Buildings, or portions thereof, required by this code to comply with this section shall not be issued a certificate of occupancy until such time that the department determines that the provisions of this section have been fully satisfied and a written maintenance program is approved by the New York City Fire Department. Exception: In buildings of phased construction, the department may issue a temporary certificate of occupancy provided that those portions of the building to be occupied meet the requirements of this section and that the remainder does not pose a significant hazard to the safety of the proposed occupants or adjacent buildings. | 909.19 System acceptance. | Buildings, or portions thereof, required by this code to comply with this section shall not be issued a certificate of occupancy until such time that the fire code official determines that the provisions of this section have been fully complied with and that the fire department has received satisfactory instruction on the operation, both automatic and manual, of the system and a written maintenance program complying with the requirements of Section 909.20.1 of the International Fire Code has been submitted and approved by the fire code official. Exception: In buildings of phased construction, a temporary certificate of occupancy, as approved by the fire code official, shall be allowed provided that those portions of the building to be occupied meet the requirements of this section and that the remainder does not pose a significant hazard to the safety of the proposed occupants or adja-cent buildings.
909.20 Smokeproof enclosures. | Where required by Section 1023.11, a smoke proof enclosure shall be constructed in accordance with this section. Where access to the roof is required by the New York City Fire Code, such access shall be from the smoke proof enclosure where a smoke proof enclosure is required. Smokeproof enclosures shall consist of one of the following systems: | 909.20 Smokeproof enclosures. | Where required by Section 1023.12, a smokeproof enclosure shall be constructed in accordance with this section. A smokeproof enclosure shall consist of an interior exit stairway or ramp that is enclosed in accordance with the applicable provisions of Section 1023 and an open exterior balcony, ventilated vestibule or pressurized stair and pressurized entrance vestibule meeting the requirements of this section. Where access to the roof is required by the International Fire Code, such access shall be from the smokeproof enclosure where a smokeproof enclosure is required.
909.20.1 Access. | Access to the interior exit stairway or ramp shall be by way of a vestibule or an open exterior balcony, unless such stairway is pressurized in accordance with Section 909.20.5. The minimum dimension of the vestibule or open exterior balcony shall not be less than the required width of the corridor leading to the vestibule or open exterior balcony but shall not have a width of less than 44 inches (1117.6 mm) and shall not have a length of less than 72 inches (1828.8 mm) in the direction of egress travel. | 909.20.1 Access. | Access to the stairway or ramp shall be by way of a vestibule or an open exterior balcony. The minimum dimension of the vestibule shall be not less than the required width of the corridor leading to the vestibule but shall not have a width of less than 44 inches (1118 mm) and shall not have a length of less than 72 inches (1829 mm) in the direction of egress travel.
909.20.2 Construction. | The smoke proof enclosure shall be separated from the remainder of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Openings are not permitted other than the required means of egress doors. The vestibule shall be separated from the stairway or ramp by not less than a 2-hour fire-resistance-rated fire barrier. The open exterior balcony shall be constructed in accordance with the fire-resistance-rating requirements for floor construction. | 909.20.2 Construction. | The smokeproof enclosure shall be separated from the remainder of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Openings are not permitted other than the required means of egress doors. The vestibule shall be separated from the stairway or ramp by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The open exterior balcony shall be constructed in accordance with the fire-resistance rating requirements for floor assemblies.
909.20.2.1 Door closers. | Doors in a smoke proof enclosure shall be self- or automatic-closing by actuation of a smoke detector in accordance with Section 716.5.9.3 and shall be installed at the floor-side entrance to the smoke proof enclosure. The actuation of the smoke detector on any door shall activate the closing devices on all doors in the smoke proof enclosure at all levels. Smoke detectors shall be installed in accordance with Section 907.3. | 909.20.2.1 Door closers. | Doors in a smokeproof enclosure shall be self- or automatic closing by actuation of a smoke detector in accordance with Section 716.2.6.6 and shall be installed at the floor-side entrance to the smokeproof enclosure. The actuation of the smoke detector on any door shall activate the closing devices on all doors in the smokeproof enclosure at all levels. Smoke detectors shall be installed in accordance with Section 907.3.
909.20.3 Natural ventilation alternative. | The provisions of Sections 909.20.3.1 through 909.20.3.3 shall apply to ventilation of smoke proof enclosures by natural means. | 909.20.3 Natural ventilation alternative. | The provisions of Sections 909.20.3.1 through 909.20.3.3 shall apply to ventilation of smokeproof enclosures by natural means.
909.20.3.1 Balcony doors. | Where access to the stairway or ramp is by way of an open exterior balcony, the door assembly into the enclosure shall be a fire door assembly in accordance with Section 716.5. | 909.20.3.1 Balcony doors. | Where access to the stairway or ramp is by way of an open exterior balcony, the door assembly into the enclosure shall be a fire door assembly in accordance with Section 716.
909.16 Firefighter’s smoke control panel. | A firefighter’s smoke control panel for Fire Department emergency response purposes only shall be provided and shall include manual control or override of automatic control for mechanical smoke control systems. The panel shall be located in a fire command center complying with Section 911 in high-rise buildings or buildings with smoke-protected assembly seating. In all other buildings, the firefighter’s smoke control panel shall be installed in the ground floor lobby of the building, adjacent to the fire alarm control panel or remote annunciator, or in another approved location. The firefighter’s smoke control panel shall either be a separate panel or can be integrated with a UUKL listed fire alarm control panel. The firefighter’s smoke control panel shall comply with Sections 909.16.1 through 909.16.3. Where required in Section 917, the post-fire smoke purge system shall be manually activated from the firefighter’s control panel or an adjacent panel.
909.20.3.2 Vestibule doors. | Where access to the stairway or ramp is by way of a vestibule, the door assembly into the vestibule shall be a fire door assembly complying with Section 716.5. The door assembly from the vestibule to the stairway shall have not less than a 90-minute fire protection rating complying with Section 716.5. | 909.20.3.2 Vestibule doors. | Where access to the stairway or ramp is by way of a vestibule, the door assembly into the vestibule shall be a fire door assembly complying with Section 716. The door assembly from the vestibule to the stairway shall have not less than a 20-minute fire protection rating complying with Section 716.
909.16.1 Panel indicators. | Fans within the building shall be shown on the firefighter’s control panel. A clear indication of the direction of airflow and the relationship of components shall be displayed. Status indicators shall be provided for all smoke control equipment, annunciated by fan and zone, and by pilot-lamp-type indicators as follows:
909.20.3.3 Vestibule ventilation. | Each vestibule shall have a minimum net area of 16 square feet (1.5 m2) of opening in a wall facing an outer court, yard or public way that is not less than 20 feet (6096 mm) in width. | 909.20.3.3 Vestibule ventilation. | Each vestibule shall have a minimum net area of 16 square feet (1.5 m2) of opening in a wall facing an outer court, yard or public way that is not less than 20 feet (6096 mm) in width.
909.16.2 Panel controls. | The firefighter’s control panel shall provide control capability over the complete smoke control system equipment within the building as follows: 1. ON-AUTO-OFF control over each individual piece of operating smoke control equipment that can also be controlled from other sources within the building. This includes stairway pressurization fans; smoke exhaust fans; supply, return and exhaust fans; elevator shaft fans and other operating equipment used or intended for smoke control purposes. 2. OPEN-AUTO-CLOSE control over dampers relating to smoke control and that are also controlled from other sources within the building. Dampers are permitted to be controlled by individual damper or grouped by smoke zone. 3. ON-OFF or OPEN-CLOSE control over smoke control and other critical equipment associated with a fire or smoke emergency and that can only be controlled from the firefighter’s control panel. The firefighter’s control panel shall be configured as described in Section 911. Exceptions: 1. Systems, where approved by the commissioner and the Fire Department, where the controls and indicators are combined to control and indicate all elements of a single smoke zone as a unit. 2. Systems, where approved by the commissioner and the Fire Department, where the control is accomplished by computer interface using approved, plain English commands.
909.20.4 Mechanical ventilation alternative. | The provisions of Sections 909.20.4.1 through 909.20.4.5 shall apply to ventilation of smoke proof enclosures by mechanical means. | 909.20.4 Mechanical ventilation alternative. | The provisions of Sections 909.20.4.1 through 909.20.4.4 shall apply to ventilation of smokeproof enclosures by mechanical means.
909.20.4.1 Vestibule doors. | The door assembly from the building into the vestibule shall be a fire door assembly complying with Section 716.5.3. The door assembly from the vestibule to the stairway or ramp shall not have less than a 90-minute fire protection rating and shall meet the requirements for a smoke door assembly in accordance with Section 716.5.3. The door shall be installed in accordance with NFPA 105. | 909.20.4.1 Vestibule doors. | The door assembly from the building into the vestibule shall be a fire door assembly complying with Section 716.2.2.1. The door assembly from the vestibule to the stairway or ramp shall not have less than a 20-minute fire protection rating and shall meet the requirements for a smoke door assembly in accordance with Section 716.2.2.1. The door shall be installed in accordance with NFPA 105.
909.20.4.2 Vestibule ventilation. | The vestibule shall be supplied with not less than one air change per minute and the exhaust shall not be less than 150 percent of supply. Supply air shall enter and exhaust air shall discharge from the vestibule through separate, tightly constructed ducts used only for that purpose. Supply air shall enter the vestibule within 6 inches (152.4 mm) of the floor level. The top of the exhaust register shall be located at the top of the smoke trap but not more than 6 inches (152.4 mm) down from the top of the trap, and shall be entirely within the smoke trap area. Doors in the open position shall not obstruct duct openings. Duct openings with controlling dampers are permitted where necessary to meet the design requirements, but dampers are not otherwise required. | 909.20.4.2 Vestibule ventilation. | The vestibule shall be supplied with not less than one air change per minute and the exhaust shall be not less than 150 percent of supply. Supply air shall enter and exhaust air shall discharge from the vestibule through separate, tightly constructed ducts used only for that purpose. Supply air shall enter the vestibule within 6 inches (152 mm) of the floor level. The top of the exhaust register shall be located at the top of the smoke trap but not more than 6 inches (152 mm) down from the top of the trap, and shall be entirely within the smoke trap area. Doors in the open position shall not obstruct duct openings. Duct openings with controlling dampers are permitted where necessary to meet the design requirements, but dampers are not otherwise required.
909.20.4.2.1 Engineered ventilation system. | Where a specially engineered system is used, the system shall exhaust a quantity of air equal to not less than 90 air changes per hour from any vestibule in the emergency operation mode and shall be sized to handle three vestibules simultaneously. Smoke detectors shall be located at the floor-side entrance to each vestibule and shall activate the system for the affected vestibule. Smoke detectors shall be installed in accordance with Section 907.3. | 909.20.4.2.1 Engineered ventilation system. | Where a specially engineered system is used, the system shall exhaust a quantity of air equal to not less than 90 air changes per hour from any vestibule in emergency operation mode and shall be sized to handle three vestibules simultaneously. Smoke detectors shall be located at the floor-side entrance to each vestibule and shall activate the system for the affected vestibule. Smoke detectors shall be installed in accordance with Section 907.3.
909.20.4.3 Smoke trap. | The vestibule ceiling shall not be less than 20 inches (508 mm) higher than the door opening into the vestibule to serve as a smoke and heat trap and to provide an upward-moving air column. The height shall not be decreased unless approved and justified by design and test. | 909.20.4.3 Smoke trap. | The vestibule ceiling shall be not less than 20 inches (508 mm) higher than the door opening into the vestibule to serve as a smoke and heat trap and to provide an upward-moving air column. The height shall not be decreased unless approved and justified by design and test.
909.20.4.4 Stairway or ramp shaft air movement system. | The stairway or ramp shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10 inch of water (24.9 Pa) in the shaft relative to the vestibule with all doors closed. The system shall maintain a maximum of 0.35 inch of water (87.2 Pa) in the shaft relative to the building measured with all stairway doors closed under maximum anticipated stack pressures. | 909.20.4.4 Stairway or ramp shaft air movement system. | The stairway or ramp shaft shall be provided with a dampered relief opening and supplied with sufficient air to maintain a minimum positive pressure of 0.10 inch of water (25 Pa) in the shaft relative to the vestibule with all doors closed.
909.20.5 Stairway and ramp pressurization alternative. | Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided each interior exit stairway or ramp is pressurized to not less than 0.10 inch of water (24.9 Pa) and not more than 0.35 inches of water (87.2 Pa) in the shaft relative to the building measured with all interior exit stairway and ramp doors closed under maximum anticipated conditions of stack effect and wind effect. | 909.20.5 Stairway and ramp pressurization alternative. | Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the vestibule is not required, provided that each interior exit stairway or ramp is pressurized to not less than 0.10 inch of water (25 Pa) and not more than 0.35 inches of water (87 Pa) in the shaft relative to the building measured with all interior exit stairway and ramp doors closed under maximum anticipated conditions of stack effect and wind effect.
909.18.8 Special inspections for smoke control. | Smoke control systems shall be tested by a special inspector in accordance with Chapter 17.
909.21 Elevator hoistway pressurization alternative. | Where elevator hoistway pressurization is provided in lieu of required enclosed elevator lobbies, the pressurization system shall comply with Sections 909.21.1 through 909.21.11. | 909.21 Elevator hoistway pressurization alternative. | Where elevator hoistway pressurization is provided in lieu of required enclosed elevator lobbies, the pressurization system shall comply with Sections 909.21.1 through 909.21.11.
909.21.1 Pressurization requirements. | Elevator hoistways shall be pressurized to maintain a minimum positive pressure of 0.10 inch of water (24.9 Pa) and a maximum positive pressure of 0.25 inch of water (62.2 Pa) with respect to adjacent occupied space on all floors. This pressure shall be measured at the midpoint of each hoistway door, with all elevator cars at the floor of recall and all hoistway doors on the floor of recall open and all other hoistway doors closed. The pressure differentials shall be measured between the hoistway and the adjacent elevator landing. The opening and closing of hoistway doors at each level must be demonstrated during this test. The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet. Exceptions: 1. On floors containing only Group R occupancies, the pressure differential is permitted to be measured between the hoistway and a dwelling unit or sleeping unit. 2. Where an elevator opens into a lobby enclosed in accordance with Section 3007.6 or 3008.7, the pressure differential is permitted to be measured between the hoistway and the floor space immediately outside of the door(s) to the enclosed lobby. 3. The pressure differential is permitted to be measured relative to the outdoor atmosphere on floors other than the following: 3.1. The fire floor. 3.2. The two floors immediately below the fire floor. 3.3. The floor immediately above the fire floor. 4. The minimum positive pressure of 0.10 inch of water (24.9 Pa) and a maximum positive pressure of 0.25 inch of water (62.2 Pa) with respect to occupied floors are not required at the floors of recall with the doors open. | 909.21.1 Pressurization requirements. | Elevator hoistways shall be pressurized to maintain a minimum positive pressure of 0.10 inch of water (25 Pa) and a maximum positive pressure of 0.25 inch of water (67 Pa) with respect to adjacent occupied space on all floors. This pressure shall be measured at the midpoint of each hoistway door, with all elevator cars at the floor of recall and all hoistway doors on the floor of recall open and all other hoistway doors closed. The pressure differentials shall be measured between the hoistway and the adjacent elevator landing. The opening and closing of hoistway doors at each level must be demonstrated during this test. The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet. Exceptions: 1. On floors containing only Group R occupancies, the pressure differential is permitted to be measured be-tween the hoistway and a dwelling unit or sleeping unit. 2. Where an elevator opens into a lobby enclosed in accordance with Section 3007.6 or 3008.6, the pressure differential is permitted to be measured between the hoistway and the space immediately outside the door(s) from the floor to the enclosed lobby. 3. The pressure differential is permitted to be measured relative to the outdoor atmosphere on floors other than the following: 3.1. The fire floor. 3.2. The two floors immediately below the fire floor. 3.3. The floor immediately above the fire floor. 4. The minimum positive pressure of 0.10 inch of water (25 Pa) and a maximum positive pressure of 0.25 inch of water (67 Pa) with respect to occupied floors are not required at the floor of recall with the doors open.
909.18.10 Reacceptance testing. | The smoke control system shall require a reacceptance test after any modifications to the system or physical changes to the building that may affect system performance. Reacceptance testing shall be a retest of the entire system in accordance with Sections 909.18.1 through 909.18.9.
909.21.1.1 Use of ventilation systems. | Ventilation systems, other than hoistway supply air systems, are permitted to be used to exhaust air from adjacent spaces on the fire floor, two floors immediately below and one floor immediately above the fire floor to the building’s exterior where necessary to maintain positive pressure relationships as required in Section 909.21.1 during operation of the elevator shaft pressurization system. | 909.21.1.1 Use of ventilation systems. | Ventilation systems, other than hoistway supply air systems, are permitted to be used to exhaust air from adjacent spaces on the fire floor, two floors immediately below and one floor immediately above the fire floor to the building’s exterior where necessary to maintain positive pressure relationships as required in Section 909.21.1 during operation of the elevator shaft pressurization system.
909.21.2 Rational analysis. | A rational analysis complying with Section 909.4 shall be submitted with the construction documents. | 909.21.2 Rational analysis. | A rational analysis complying with Section 909.4 shall be submitted with the construction documents.
909.21.3 Ducts for system. | Any duct system that is part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure. | 909.21.3 Ducts for system. | Any duct system that is part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure.
909.21.4 Fan system. | The fan system provided for the pressurization system shall be as required by Sections 909.21.4.1 through 909.21.4.4. | 909.21.4 Fan system. | The fan system provided for the pressurization system shall be as required by Sections 909.21.4.1 through 909.21.4.4.
909.21.4.1 Fire resistance. | Where located within the building, the fan system that provides the pressurization shall be protected with the same fire-resistance rating required for the elevator shaft enclosure. | 909.21.4.1 Fire resistance. | Where located within the building, the fan system that provides the pressurization shall be protected with the same fire-resistance rating required for the elevator shaft enclosure.
909.21.4.2 Smoke detection. | The supply fan system shall be equipped with a smoke detector that will automatically shut down the supply fan system when smoke is detected within the system. | 909.21.4.2 Smoke detection. | The fan system shall be equipped with a smoke detector that will automatically shut down the fan system when smoke is detected within the system.
909.21.4.3 Separate systems. | A separate fan system shall be used for each elevator hoistway. | 909.21.4.3 Separate systems. | A separate fan system shall be used for each elevator hoistway.
909.21.4.4 Fan capacity. | The supply fan capacity shall be specified by a registered design professional to meet the requirements of a designed pressurization system in accordance with the rational analysis required by Section 909.21.2. | 909.21.4.4 Fan capacity. | The supply fan shall be either adjustable with a capacity of not less than 1,000 cubic feet per minute (0.4719 m3/s) per door, or that specified by a registered design professional to meet the requirements of a designed pressurization system.
909.21.5 Standby power. | The pressurization system, including ventilation systems used per Section 909.21.1.1, shall be provided with standby power in accordance with Section 2702. | 909.21.5 Standby power. | The pressurization system shall be provided with standby power in accordance with Section 2702.
909.21.6 Activation of pressurization system. | The elevator pressurization system shall be activated upon activation of either the building fire alarm system or the elevator landing smoke detectors. Where both a building fire alarm system and elevator landing smoke detectors are present, each shall be independently capable of activating the pressurization system. | 909.21.6 Activation of pressurization system. | The elevator pressurization system shall be activated upon activation of either the building fire alarm system or the elevator lobby smoke detectors. Where both a building fire alarm system and elevator lobby smoke detectors are present, each shall be independently capable of activating the pressurization system.
909.21.8 Marking and identification. | Detection and control systems shall be marked in accordance with Section 909.14. | 909.21.8 Marking and identification. | Detection and control systems shall be marked in accordance with Section 909.14.
909.21.9 Control diagrams. | Control diagrams shall be provided in accordance with Section 909.15. | 909.21.9 Control diagrams. | Control diagrams shall be provided in accordance with Section 909.15.
909.21.11 System response time. | Hoistway pressurization systems shall comply with the requirements for smoke control system response time in Section 909.17. | 909.21.11 System response time. | Hoistway pressurization systems shall comply with the requirements for smoke control system response time in Section 909.17.
910.1 General. | Where required by this code, smoke and heat vents or mechanical smoke removal systems shall conform to the requirements of this section. | 910.1 General. | Where required by this code, smoke and heat vents or mechanical smoke removal systems shall conform to the requirements of this section.
909.20.4.5 Door opening force. | Door opening force shall not exceed limits in Section 1010.1.3.
910.2 Where required. | Smoke and heat vents or a mechanical smoke removal system shall be installed as required by Sections 910.2.1 and 910.2.2. Exceptions: 1. Frozen-food warehouses used solely for storage of Class I and II commodities where protected by an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Smoke and heat removal shall not be required in areas of buildings equipped with early suppression fast-response (ESFR) sprinklers. 3. Smoke and heat removal shall not be required in areas of buildings equipped with control mode special application sprinklers with a response time index of 50 (m · s)1/2 or less that are listed to control a fire in stored commodities with 12 or fewer sprinklers. | 910.2 Where required. | Smoke and heat vents or a mechanical smoke removal system shall be installed as required by Sections 910.2.1 and 910.2.2. Exceptions: 1. Frozen food warehouses used solely for storage of Class I and II commodities where protected by an ap-proved automatic sprinkler system. 2. Smoke and heat removal shall not be required in areas of buildings equipped with early suppression fast-response (ESFR) sprinklers. 3. Smoke and heat removal shall not be required in areas of buildings equipped with control mode special ap-plication sprinklers with a response time index of 50 (m × s)1/2 or less that are listed to control a fire in stored commodities with 12 or fewer sprinklers.
910.2.1 Group F-1 or S-1. | Smoke and heat vents installed in accordance with Section 910.3 or a mechanical smoke removal system installed in accordance with Section 910.4 shall be installed in buildings and portions thereof used as a Group F-1 or S-1 occupancy having more than 50,000 square feet (4645.2 m2) of undivided area. In occupied portions of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where the upper surface of the story is not a roof assembly, a mechanical smoke removal system in accordance with Section 910.4 shall be installed. Exception: Group S-1 aircraft repair hangars. | 910.2.1 Group F-1 or S-1. | Smoke and heat vents installed in accordance with Section 910.3 or a mechanical smoke removal system installed in accordance with Section 910.4 shall be installed in buildings and portions thereof used as a Group F-1 or S-1 occupancy having more than 50,000 square feet (4645 m2) of undivided area. In occupied portions of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 where the upper surface of the story is not a roof assembly, a mechanical smoke removal system in accordance with Section 910.4 shall be installed. Exception: Group S-1 aircraft repair hangars.
909.20.6 Ventilating equipment. | The activation of ventilating equipment required by the alternatives in Sections 909.20.4 and 909.20.5 shall be by smoke detectors installed at each floor level at an approved location at the entrance to the smokeproof enclosure. When the closing device for the stairway and ramp shaft and vestibule doors is activated by smoke detection or power failure, the mechanical equipment shall activate and operate at the required performance levels. Smoke detectors shall be installed in accordance with Section 907.3.
910.2.2 High-piled combustible storage. | Smoke and heat removal for buildings and portions thereof containing high-piled combustible storage shall be installed in accordance with the New York City Fire Code and Section 413 of this code. Installation shall also be in conformance with Section 910.3 in unsprinklered buildings and portions thereof. | 910.2.2 High-piled combustible storage. | Smoke and heat removal required by Table 3206.2 of the International Fire Code for buildings and portions thereof containing high-piled combustible storage shall be installed in accordance with Section 910.3 in unsprinklered buildings. In buildings and portions thereof containing high-piled combustible storage equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, a smoke and heat removal system shall be installed in accordance with Section 910.3 or 910.4. In occupied portions of a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, where the upper surface of the story is not a roof assembly, a mechanical smoke removal system in accordance with Section 910.4 shall be installed.
909.20.6.1 Ventilation systems. | Smokeproof enclosure ventilation systems shall be independent of other building ventilation systems. The equipment, control wiring, power wiring and ductwork shall comply with one of the following: 1. Equipment, control wiring, power wiring and ductwork shall be located exterior to the building and directly connected to the smokeproof enclosure or connected to the smokeproof enclosure by ductwork enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. 2. Equipment, control wiring, power wiring and ductwork shall be located within the smokeproof enclosure with intake or exhaust directly from and to the outside or through ductwork enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. 3. Equipment, control wiring, power wiring and ductwork shall be located within the building if separated from the remainder of the building, including other mechanical equipment, by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Exceptions: 1. Control wiring and power wiring utilizing a 2-hour rated cable or cable system in accordance with UL 2196. 2. Where encased with not less than 2 inches (50.8 mm) of concrete. 3. Control wiring and power wiring protected by a listed electrical circuit protective system with a fire-resistance rating of not less than 2 hours.
910.3 Smoke and heat vents. | The design and installation of smoke and heat vents shall be in accordance with Sections 910.3.1 through 910.3.3. | 910.3 Smoke and heat vents. | The design and installation of smoke and heat vents shall be in accordance with Sections 910.3.1 through 910.3.3.
909.20.6.2 Standby power. | Mechanical vestibule and stairway and ramp shaft ventilation systems and automatic fire detection systems shall be provided with standby power in accordance with Sections 403.4.8 and 2702.
910.3.1 Listing and labeling. | Smoke and heat vents shall be listed and labeled to indicate compliance with UL 793 or FM 4430. | 910.3.1 Listing and labeling. | Smoke and heat vents shall be listed and labeled to indicate compliance with UL 793 or FM 4430.
909.20.6.3 Acceptance and testing. | Before the mechanical equipment is approved, the system shall be tested in the presence of the department or approved agency to confirm that the system is operating in compliance with these requirements.
910.3.2 Smoke and heat vent locations. | Smoke and heat vents shall be located 20 feet (6096 mm) or more from adjacent lot lines and fire walls and 10 feet (3048 mm) or more from fire barriers. Vents shall be uniformly located within the roof in the areas of the building where the vents are required to be installed by Section 910.2 with consideration given to roof pitch, sprinkler location and structural members. | 910.3.2 Smoke and heat vent locations. | Smoke and heat vents shall be located 20 feet (6096 mm) or more from adjacent lot lines and fire walls and 10 feet (3048 mm) or more from fire barriers. Vents shall be uniformly located within the roof in the areas of the building where the vents are required to be installed by Section 910.2 with consideration given to roof pitch, sprinkler location and structural members.
910.3.3 Smoke and heat vents area. | The required aggregate area of smoke and heat vents shall be calculated as follows: | 910.3.3 Smoke and heat vents area. | The required aggregate area of smoke and heat vents shall be calculated as follows:
910.4 Mechanical smoke removal systems. | Mechanical smoke removal systems shall be designed and installed in accordance with Sections 910.4.1 through 910.4.7. ‡ | 910.4 Mechanical smoke removal systems. | Mechanical smoke removal systems shall be designed and installed in accordance with Sections 910.4.1 through 910.4.7.
910.4.1 Automatic sprinklers required. | The building shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1. | 910.4.1 Automatic sprinklers required. | The building shall be equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1.
910.4.2 Exhaust fan construction. | Exhaust fans that are part of a mechanical smoke removal system shall be rated for operation at 221°F (105°C). Exhaust fan motors shall be located outside of the exhaust fan air stream. | 910.4.2 Exhaust fan construction. | Exhaust fans that are part of a mechanical smoke removal system shall be rated for operation at 221°F (105°C). Exhaust fan motors shall be located outside of the exhaust fan air stream.
910.4.3 System design criteria. | The mechanical smoke removal system shall be sized to exhaust the building at a minimum rate of two air changes per hour based upon the volume of the building or portion thereof without contents. The capacity of each exhaust fan shall not exceed 30,000 cubic feet per minute (14.2 m3/sec). | 910.4.3 System design criteria. | The mechanical smoke removal system shall be sized to exhaust the building at a minimum rate of two air changes per hour based on the volume of the building or portion thereof without contents. The capacity of each exhaust fan shall not exceed 30,000 cubic feet per minute (14.2 m3/s).
910.4.3.1 Makeup air. | No portion of the makeup air openings shall be higher than 6 feet (1828.8 mm) above the floor level. Operation of makeup air openings shall be manual or, if properly coordinated with the smoke removal system, automatic. The minimum gross area of makeup air inlets shall be 8 square feet per 1,000 cubic feet per minute (0.74 m2 per 0.4719 m3/s) of smoke exhaust. | 910.4.3.1 Makeup air. | Makeup air openings shall be provided within 6 feet (1829 mm) of the floor level. Operation of makeup air openings shall be manual or automatic. The minimum gross area of makeup air inlets shall be 8 square feet per 1,000 cubic feet per minute (0.74 m2 per 0.4719 m3/s) of smoke exhaust.
910.4.4 Activation. | The mechanical smoke removal system shall be started by manual controls. | 910.4.4 Activation. | The mechanical smoke removal system shall be activated by manual controls only.
910.4.5 Manual control location. | Manual controls shall be located so as to be accessible to the Fire Department from an exterior door of the building and protected against interior fire exposure by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The location of manual controls is subject to the approval of the Fire Commissioner. | 910.4.5 Manual control location. | Manual controls shall be located where they are able to be accessed by the fire service from an exterior door of the building and separated from the remainder of the building by not less than 1-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both.
910.4.6 Control wiring. | Wiring for operation and control of mechanical smoke removal systems shall be connected ahead of the main disconnect in accordance with the New York City Electrical Code and be protected against interior fire exposure to temperatures in excess of 1,000°F (537.8°C) for a period of not less than 15 minutes. | 910.4.6 Control wiring. | Wiring for operation and control of mechanical smoke removal systems shall be connected ahead of the main disconnect in accordance with Section 701.12E of NFPA 70 and be protected against interior fire exposure to temperatures in excess of 1,000°F (538°C) for a period of not less than 15 minutes.
910.4.7 Controls. | Where building air-handling and mechanical smoke removal systems are combined or where independent building air-handling systems are provided, fans shall automatically shut down in accordance with the New York City Mechanical Code. The manual controls provided for the smoke removal system shall have the capability to override the automatic shutdown of fans that are part of the smoke removal system. | 910.4.7 Controls. | Where building air-handling and mechanical smoke removal systems are combined or where independent building air-handling systems are provided, fans shall automatically shut down in accordance with the International Mechanical Code. The manual controls provided for the smoke removal system shall have the capability to override the automatic shutdown of fans that are part of the smoke removal system.
909.21.7 Testing and special inspections. | Special inspections for performance shall be required in accordance with Section 909.18.8. System acceptance testing shall be in accordance with Section 909.19.
910.5 Maintenance. | Smoke and heat vents and mechanical smoke removal systems shall be maintained in accordance with the New York City Fire Code. | 910.5 Maintenance. | Smoke and heat vents and mechanical smoke removal systems shall be maintained in accordance with the International Fire Code.
911.1 General. | Where required by other sections of this code and in buildings classified as high-rise buildings by this code, a fire command center for Fire Department operations shall be provided and shall comply with Sections 911.1.1 through 911.1.6. | 911.1 General. | Where required by other sections of this code, in buildings classified as high-rise buildings by this code and in all F-1 and S-1 occupancies with a building footprint of over 500,000 square feet (46 452 m2), a fire command center for fire department operations shall be provided and shall comply with Sections 911.1.1 through 911.1.7.
911.1.1 Location and access. | The fire command center location shall be in the lobby of the building on the main entrance floor near the Fire Department designated response point. | 911.1.1 Location and access. | The location and access to the fire command center shall be approved by the fire code official.
909.21.10 Firefighter’s smoke control panel. | A control panel complying with Section 909.16 shall be provided.
911.1.5 Storage. | Storage unrelated to operation of the fire command center shall be prohibited. | 911.1.5 Storage. | Storage unrelated to operation of the fire command center shall be prohibited.
911.1.6 Required features. | The fire command center shall comply with the New York City Fire Code and NFPA 72 and shall include the following features as applicable in their respective control units or panels: | 911.1.6 Required features. | The fire command center shall comply with NFPA 72 and shall contain all of the following features:
912.1 Installation. | Fire Department connections shall be installed in accordance with the NFPA standard applicable to the system design and shall comply with Sections 912.2 through 912.6. | 912.1 Installation. | Fire department connections shall be installed in accordance with the NFPA standard applicable to the system design and shall comply with Sections 912.2 through 912.6.
912.2 Location. | With respect to hydrants, driveways, buildings and landscaping, Fire Department connections shall be so located that fire apparatus and hose connected to supply the system will not obstruct access to the buildings for other fire apparatus. | 912.2 Location. | With respect to hydrants, driveways, buildings and landscaping, fire department connections shall be so located that fire apparatus and hose connected to supply the system will not obstruct access to the buildings for other fire apparatus. The location of fire department connections shall be approved by the fire code official.
912.2.2 Existing buildings. | On existing buildings, wherever the Fire Department connection is not visible to approaching fire apparatus, the Fire Department connection shall be indicated by an approved sign mounted on the street front or on the side of the building. Such sign shall have the letters “FDC” not less than 6 inches (152.4 mm) high and words in letters not less than 2 inches (50.8 mm) high or an arrow to indicate the location. Such signs shall be subject to the approval of the Fire Department. | 912.2.2 Existing buildings. | On existing buildings, wherever the fire department connection is not visible to approaching fire apparatus, the fire department connection shall be indicated by an approved sign mounted on the street front or on the side of the building. Such sign shall have the letters “FDC” not less than 6 inches (152 mm) high and words in letters not less than 2 inches (51 mm) high or an arrow to indicate the location. Such signs shall be subject to the approval of the fire code official.
912.3 Fire hose threads. | Fire hose threads used in connection with standpipe, sprinkler and combination standpipe-sprinkler systems shall be approved and shall be compatible with New York City Fire Department hose threads. | 912.3 Fire hose threads. | Fire hose threads used in connection with standpipe systems shall be approved and shall be compatible with fire department hose threads.
912.4 Access. | Immediate access to Fire Department connections shall be maintained at all times and without obstruction by fences, bushes, trees, walls or any other object. Exception: Fences, where provided with an access gate and a means of emergency operation that shall be maintained operational at all times in accordance with the New York City Fire Code. | 912.4 Access. | Immediate access to fire department connections shall be maintained at all times and without obstruction by fences, bushes, trees, walls or any other fixed or moveable object. Access to fire department connections shall be approved by the fire code official. Exception: Fences, where provided with an access gate equipped with a sign complying with the legend require-ments of this section and a means of emergency operation. The gate and the means of emergency operation shall be approved by the fire code official and maintained operational at all times.
912.4.2 Clear space around connections. | A working space of not less than 36 inches (914.4 mm) in width, 36 inches (914.4 mm) in depth and 78 inches (1981.2 mm) in height shall be provided and maintained in front of and to the sides of wall-mounted Fire Department connections and around the circumference of free-standing Fire Department connections, except as otherwise required or approved by the Fire Commissioner. | 912.4.2 Clear space around connections. | A working space of not less than 36 inches (762 mm) in width, 36 inches (914 mm) in depth and 78 inches (1981 mm) in height shall be provided and maintained in front of and to the sides of wall-mounted fire department connections and around the circumference of free-standing fire department connections, except as otherwise required or approved by the fire code official.
912.4.3 Physical protection. | Where Fire Department connections are subject to impact by a motor vehicle, vehicle impact protection shall be provided in accordance with the New York City Fire Code. | 912.4.3 Physical protection. | Where fire department connections are subject to impact by a motor vehicle, vehicle impact protection shall be provided in accordance with Section 312 of the International Fire Code.
912.5 Signs. | Fire Department connections shall be provided with signage in accordance with Section 912 of the New York City Fire Code. | 912.5 Signs. | A metal sign with raised letters not less than 1 inch (25 mm) in size shall be mounted on all fire department connections serving automatic sprinklers, standpipes or fire pump connections. Such signs shall read: AUTOMATIC SPRINKLERS, STANDPIPES, or TEST CONNECTION, or a combination thereof as applicable. Where the fire department connection does not serve the entire building, a sign shall be provided indicating the portions of the building served.
912.6 Backflow protection. | The potable water supply to automatic sprinkler and standpipe systems shall be protected against backflow as required by the New York City Plumbing Code. | 912.6 Backflow protection. | The potable water supply to automatic sprinkler and standpipe systems shall be protected against backflow as required by the International Plumbing Code.
913.1 General. | Where provided or required, fire pumps shall be installed in accordance with this section, NFPA 20 and other applicable sections of this code. | 913.1 General. | Where provided, fire pumps for fire protection systems shall be installed in accordance with this section and NFPA 20. Exception: Pumps for automatic sprinkler systems installed in accordance with Section 903.3.1.3, or Section P2904 of the International Residential Code.
913.2 Protection against interruption of service. | The fire pump, driver and controller shall be protected in accordance with NFPA 20 against possible interruption of service. | 913.2 Protection against interruption of service. | The fire pump, driver and controller shall be protected in accordance with NFPA 20 against possible interruption of service through damage caused by explosion, fire, flood, earthquake, rodents, insects, windstorm, freezing, vandalism and other adverse conditions.
913.2.1 Protection of fire pump rooms. | Fire pumps shall be located in rooms that are separated from all other areas of the building by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both. Exceptions: 1. In other than high-rise buildings, separation by 1-hour fire barriers constructed in accordance with Section 707 or 1-hour horizontal assemblies constructed in accordance with Section 711, or both, shall be permitted in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. Separation is not required for fire pumps physically separated in accordance with NFPA 20. 3. Separation is not required for a fire pump, other than an automatic standpipe fire pump, where such fire pump is located in a mechanical equipment room, as defined by the New York City Mechanical Code, enclosed by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both. Refrigerants, gas piping, gas consumption devices, gas meters or any other gas equipment and fuel storage or fuel consuming appliances shall not be installed in any space housing a fire pump. | 913.2.1 Protection of fire pump rooms. | Fire pumps shall be located in rooms that are separated from all other areas of the building by 2-hour fire barriers constructed in accordance with Section 707 or 2-hour horizontal assemblies constructed in accordance with Section 711, or both. Exceptions: 1. In other than high-rise buildings, separation by 1-hour fire barriers constructed in accordance with Sec-tion 707 or 1-hour horizontal assemblies constructed in accordance with Section 711, or both, shall be permitted in buildings equipped throughout with an automatic sprinkler system in accordance with Sec-tion 903.3.1.1 or 903.3.1.2. 2. Separation is not required for fire pumps physically separated in accordance with NFPA 20.
913.2.2 Circuits supplying fire pumps. | Cables used for survivability of circuits supplying fire pumps shall be in accordance with the New York City Electrical Code. Electrical circuit protective systems shall be installed in accordance with their listing requirements, and the New York City Electrical Code. | 913.2.2 Circuits supplying fire pumps. | Cables used for survivability of circuits supplying fire pumps shall be protected using one of the following methods: 1. Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 1 hour. 2. Electrical circuit protective systems shall have a fire-resistance rating of not less than 1 hour. Electrical cir-cuit protective systems shall be installed in accordance with their listing requirements. 3. Construction having a fire-resistance rating of not less than 1 hour. 4. The cable or raceway is encased in a minimum of 2 inches (51 mm) of concrete. Exception: This section shall not apply to cables, or portions of cables, located within a fire pump room or gen-erator room which is separated from the remainder of the occupancy with fire-resistance-rated construction.
913.3 Temperature of pump room. | Suitable means shall be provided for maintaining the temperature of a pump room or pump house, where required, above 40°F (4.4°C). | 913.3 Temperature of pump room. | Suitable means shall be provided for maintaining the temperature of a pump room or pump house, where required, above 40°F (5°C).
911.1.2 Reserved.
913.3.1 Engine manufacturer’s recommendation. | Temperature of the pump room, pump house or area where engines are installed shall never be less than the minimum recommended by the engine manufacturer. The engine manufacturer’s recommendations for oil heaters shall be followed. | 913.3.1 Engine manufacturer’s recommendation. | Temperature of the pump room, pump house or area where engines are installed shall never be less than the minimum recommended by the engine manufacturer. The engine manufacturer’s recommendations for oil heaters shall be followed.
911.1.3 Reserved.
913.4 Valve supervision. | Where provided, the fire pump suction, discharge and bypass valves, and isolation valves on the backflow prevention device or assembly shall be supervised open as required by Section 907. | 913.4 Valve supervision. | Where provided, the fire pump suction, discharge and bypass valves, and isolation valves on the backflow prevention device or assembly shall be supervised open by one of the following methods:
911.1.4 Reserved.
913.5 Acceptance test. | Acceptance testing shall be done in accordance with the requirements of Section 1705.30 of this code, the New York City Fire Code and NFPA 20. Refurbished or repaired fire pumps shall be tested in accordance with Section 1705.30 of this code, the New York City Fire Code and NFPA 20. All such tests shall be scheduled to include a department representative as a witness, if required. | 913.5 Acceptance test. | Acceptance testing shall be done in accordance with the requirements of NFPA 20.
914.1 Shaftway markings. | Vertical shafts shall be identified as required by the New York City Fire Code and Sections 914.1.1 and 914.1.2 of this code. | 914.1 Shaftway markings. | Vertical shafts shall be identified as required by Sections 914.1.1 and 914.1.2.
911.2 Secondary fire command center. | Where required in locations described in Appendix G of this code, a secondary fire command center shall be provided subject to the approval of the Fire Department. Design and installation requirements shall be in accordance with NFPA 72.
914.1.1 Exterior access to shaftways. | Outside openings accessible to the Fire Department and that open directly on a hoistway or shaftway communicating between two or more floors in a building shall be plainly marked with the word “SHAFTWAY” in red letters not less than 6 inches (152.4 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible from the outside of the building. | 914.1.1 Exterior access to shaftways. | Outside openings accessible to the fire department and that open directly on a hoistway or shaftway communicating between two or more floors in a building shall be plainly marked with the word “SHAFTWAY” in red letters not less than 6 inches (152 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible from the outside of the building.
914.1.2 Interior access to shaftways. | Door or window openings to a hoistway or shaftway from the interior of the building shall be plainly marked with the word “SHAFTWAY” in red letters not less than 6 inches (152.4 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible. Exception: Markings shall not be required on shaftway openings that are readily discernible as openings onto a shaftway by the construction or arrangement. | 914.1.2 Interior access to shaftways. | Door or window openings to a hoistway or shaftway from the interior of the building shall be plainly marked with the word “SHAFTWAY” in red letters not less than 6 inches (152 mm) high on a white background. Such warning signs shall be placed so as to be readily discernible. Exception: Markings shall not be required on shaftway openings that are readily discernible as openings onto a shaftway by the construction or arrangement.
914.2 Equipment room identification. | Fire protection equipment shall be identified in an approved manner. Rooms containing controls for air-conditioning systems, sprinkler risers and valves or other fire detection, suppression or control elements shall be identified for the use of the Fire Department. Approved signs required to identify fire protection equipment and equipment location shall be constructed of durable materials, permanently installed and readily visible. | 914.2 Equipment room identification. | Fire protection equipment shall be identified in an approved manner. Rooms containing controls for air-conditioning systems, sprinkler risers and valves or other fire detection, suppression or control elements shall be identified for the use of the fire department. Approved signs required to identify fire protection equipment and equipment location shall be constructed of durable materials, permanently installed and readily visible.
912.2.1 Fire Department connections. | The location of Fire Department connections shall be as follows:
912.2.1.1 One Fire Department connection shall be provided for each 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon each street or public space.
912.2.1.2 Where buildings face upon two parallel streets or public spaces without an intersecting street or public space, one connection shall be provided for each 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon each such parallel street or public space.
912.2.1.3 Where a building faces upon two intersecting streets or public spaces and the total length of the exterior building walls facing upon such streets or public spaces does not exceed 300 feet (91 140 mm), only one Fire Department connection need be installed provided the Fire Department connection is located within 15 feet (4572 mm) of the corner and on the street with the longest building frontage.
912.2.1.4 Where a building faces on three streets or public spaces, one Fire Department connection shall be provided for each 300 feet (91 140 mm) of building wall or fraction thereof facing upon such streets or public spaces provided that at least one Fire Department connection is installed on each of the parallel streets or public spaces, and further provided that the Fire Department connections shall be located so that the distance between them does not exceed 300 feet (91 140 mm).
912.2.1.5 Where a building faces upon four streets or public spaces, at least one Fire Department connection shall be provided on each street front or public space; however, only one Fire Department connection need be provided at the corner of two intersecting streets or public spaces if the Fire Department connection is located within 15 feet (4572 mm) of the corner and on the street with the longest building frontage or public space, and if the distances between Fire Department connections, in all cases, do not exceed 300 feet (91 140 mm).
912.2.1.6 In any case where the exterior building walls of a building facing a street or public space are obstructed in part by another building, one Fire Department connection shall be provided for each clear 300 feet (91 140 mm) of exterior building wall or fraction thereof facing upon such street or public space.
912.4.1 Locking Fire Department connection caps. | The Fire Department may require locking caps on Fire Department connections in accordance with the New York City Fire Code.
913.4.1 Test outlet control valve supervision. | Fire pump test outlet control valves shall be supervised in the closed position. Individual hose valves on the test header are not required to be monitored.
915.1 Carbon monoxide alarms and detectors. | Carbon monoxide alarms and detectors shall be provided and installed in accordance with Sections 915.1.1 through 915.7.
915.1.1 Group I-1 and R occupancies. | Listed carbon monoxide alarms or detectors shall be installed as follows:
915.1.1.1 Affected dwelling units. | Carbon monoxide alarms or detectors shall be required within the following dwelling units:
915.1.1.1.1 Required locations within dwelling units. | Carbon monoxide alarms or detectors shall be located within dwelling units as follows:
915.1.1.1.2 Exhaust of Carbon Monoxide in Group R-3 Occupancy (One- and Two-Family dwellings and townhouses). | Means of exhausting carbon monoxide from garages shall be provided when a carbon monoxide alarm or detector is activated in a Group R-3 occupancy, provided such garage is attached within the Group R-3 occupancy. Such exhaust system shall be arranged to operate automatically upon detection of a concentration of carbon monoxide of 35 parts per million (ppm) or greater by approved automatic detection device. The system shall be capable of producing an exhaust rate of 1.5 cfm per square foot of floor area of the garage. Removal of sensor, interruption of power or cut wires shall cause the relay circuit to open and start fan. The relay contact shall close and the fan may shut off when the carbon monoxide level is below 35 ppm. Carbon monoxide exhausting means shall be connected to a separate circuit and provided with a lock and identified at the power source. Such circuit shall not be connected to a power source through an arc-fault or Ground Fault Circuit Interrupter (GFCI) devices. Additionally, when the carbon monoxide exhausting means is connected to the plug-in-type overcurrent protection device, such device shall be secured in place by an additional fastener.
915.1.2 Buildings that are equipped with a fire alarm system and that contain Group A-1, A-2, A-3, Group B or Group M occupancies. | Listed carbon monoxide detectors shall be installed in buildings that are equipped with a fire alarm system and that contain Group A-1, A-2 or A-3, Group B or Group M occupancies. Such carbon monoxide detectors installed pursuant to this section shall have built-in sounder bases, shall transmit a carbon monoxide alarm signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory signal at a constantly attended location. The department shall adopt rules and/or reference standards governing the installation and location of carbon monoxide detectors provided such detectors shall be required within rooms containing carbon monoxide-producing equipment and addressing the installation of such detectors or any alternative means of compliance in existing buildings.
915.1.2.1 Retroactive provisions for existing buildings. | Notwithstanding any other provision of law, listed carbon monoxide detectors shall be installed in existing buildings that are equipped with a fire alarm system and that contain group A-1, A-2, A-3, Group B or Group M occupancies in accordance with Section 915.1.2 by July 1, 2021.
915.2 Group E, I-2 and I-4 occupancies. | Listed carbon monoxide detectors with built-in sounder bases shall transmit a carbon monoxide alarm signal to a central supervising station and shall be permitted to initiate an audible and visual supervisory signal at a constantly attended location.
915.3 Installation requirement for all occupancies. | Where a fire alarm system is required or provided, carbon monoxide detectors with sounder bases shall be installed within any room containing carbon monoxide-producing equipment.
915.3.1 Equipment shutdown. | Activation of a carbon monoxide detector located at the source of carbon monoxide-producing equipment shall shut down that source. Exception: This provision does not apply where the source is a generator.
915.4 Detection equipment. | Carbon monoxide detection required by Sections 915.1 through 915.2 shall be provided by carbon monoxide alarms complying with Section 915.5 or carbon monoxide detection systems complying with Section 915.6, unless otherwise specified in this code.
915.5 Carbon monoxide alarms. | Carbon monoxide alarms shall comply with Sections 915.5.1 through 915.5.4.
915.5.1 Power source. | Carbon monoxide alarms shall receive their primary power from the building wiring where such wiring is served from a commercial source, and when primary power is interrupted, shall receive power from a battery. Wiring shall be permanent and without a disconnecting switch other than that required for overcurrent protection. Exception: Where installed in buildings without commercial power, battery-powered carbon monoxide alarms shall be an acceptable alternative.
915.5.2 Listings. | Carbon monoxide alarms shall be listed in accordance with UL 2034.
915.5.3 Combination alarms. | Combination carbon monoxide/smoke alarms shall be an acceptable alternative to carbon monoxide alarms. Combination carbon monoxide/smoke alarms shall be listed in accordance with UL 2034 and UL 217.
915.5.4 Interconnection of alarms. | When two or more alarms are installed, they shall be interconnected in accordance with NFPA 720.
915.6 Carbon monoxide detection systems. | Carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide alarms and shall comply with Sections 915.6.1 through 915.6.4.
915.6.1 General. | Carbon monoxide detection systems shall comply with NFPA 720. Carbon monoxide detectors shall be listed in accordance with UL 2075.
915.6.2 Locations. | Carbon monoxide detectors shall be installed in the locations specified in Section 915.2. These locations supersede the locations specified in NFPA 720.
915.6.3 Combination detectors. | Combination carbon monoxide/smoke detectors installed in carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide detectors, provided they are listed in accordance with UL 2075 and UL 268.
915.6.4 Wiring and power supply. | Wiring and power supply for carbon monoxide detectors shall comply with Sections 907.6.1 and 907.6.2, respectively.
915.7 Inspection, testing and maintenance. | Carbon monoxide alarms and carbon monoxide detection systems shall be inspected, tested and maintained in accordance with NFPA 720 and the New York City Fire Code.
916.1 General. | This section covers the design, installation and performance criteria of Fire Department In-Building Auxiliary Radio Communication System (ARCS). Such systems shall be designed and installed by the New York City Fire Code, Sections 403 and 907 of this code, or where installed voluntarily, such systems shall be designed and installed in accordance with this section, NFPA 72, the New York City Electrical Code and in accordance with Fire Department requirements.
916.1.1 Construction documents. | Construction documents for ARCS shall be submitted for approval to the Fire Department prior to system installation. Construction documents shall include, but need not be limited to, all of the following:
916.1.2 Acceptance testing, maintenance and operational testing. | Acceptance testing, maintenance and operational testing of the ARCS shall be performed in accordance with the New York City Fire Code and rules promulgated by the Fire Department.
916.2 Instructions. | Operating, testing and maintenance instructions and record drawings (“as-builts”) and detailed specifications of all the components shall be provided at an approved location.
916.3 Where required. | ARCS, which shall be in accordance with this section, shall be required in the following: 1. High-rise buildings constructed in accordance with Section 403. 2. Underground buildings constructed in accordance with Section 405. 3. Buildings having a total gross area exceeding 250,000 square feet (23 225.8 m2). Exceptions: 1. Group R-2 buildings that meet all of the following requirements: a. The highest occupied floor is less than 125 feet (38 100 mm) above the lowest level of Fire Department vehicle access; b. The building has no more than 1 story below grade; and c. The floor area of the building does not exceed 250,000 square feet (23 225.8 m2). 2. Where it is determined by the Fire Department that a radio communication system is not required.
917.1 Scope and purpose. | The purpose of this section is to establish minimum requirements for the design and installation of post-fire smoke purge systems, which are intended for the timely restoration of operations and overhaul activities once a fire is extinguished. Post-fire smoke purge systems are not intended or designed as life safety systems and are not required to meet the provisions of Section 909. Post-fire smoke purge systems shall be required in: 1. High-rise buildings subject to Section 403. 2. Buildings with any story exceeding 50,000 square feet (4645.2 m2) in floor area. 3. Building with spaces exceeding 100 feet (30 480 mm) from natural ventilation openings. Natural ventilation openings shall consist of operable windows and doors of at least 5 percent of the floor area or roof vents per Section 910. 4. High-piled stock or rack storage in accordance with the New York City Fire Code. Exceptions: A post-fire smoke purge system is not required in Group R-2 occupancies where either of the following conditions exists: 1. Openable windows. A post-fire smoke purge system is not required where every habitable room located in dwelling units is provided with windows complying with Chapter 12 and all of the following: 1.1. Minimum window area. Each required window shall provide at least 12 square feet (1.1 m2) of glazed area. The total area of all such windows shall not be less than 10 percent of the floor area of the room or space served. 1.2. Minimum openable area. Each required window shall provide a mini¬mum of 6 square feet (0.56 m2) of openable area. The total area of all such openings shall not be less than 5 percent of the floor area of the room or space served. In addition, each required openable area shall be: 1.2.1. Located wholly at least 30 inches (762 mm) above the finished floor; and 1.2.2. Fully openable to the minimum 6 square feet (0.56 m2), at all times and without limiting stops or devices. Such openings may be achieved through the use of double-hung, sliding, or similar types of windows. However, in the event of the use of casement-, hopper-, pivot-, or awning-type windows, such windows shall satisfy the requirements of this section only when they open to at least 75 degrees (1.22 rad). 1.3 Window guards. This exception shall not apply where the type of window guards installed in compliance with Section 27-2043.1 of the Administrative Code and Section 131.15 of the New York City Health Code requires the installation of limiting devices or stops. 2. Smokeproof enclosures. A post-fire smoke purge system is not required where all exits are constructed as smokeproof enclosures in accordance with Section 1023.11.
917.2 Post-fire smoke purge systems in occupancy groups other than R-2.
917.2.1 General design requirements. | Post-fire smoke purge systems are permitted to use dedicated equipment, the normal building HVAC system or other openings and shall have the capability to exhaust smoke from occupied spaces. Smoke removal may be by either mechanical or natural ven­tilation, but shall be capable of removing cold smoke. Smoke removed from a space must be discharged to a safe location outside the building and shall not be recirculated into the building in accordance with the New York City Mechanical Code.
917.2.2 Exhaust capability. | The system shall have an air supply and smoke exhaust capability that will provide a minimum of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) (0.00508 m3/s·• m2), whichever is greater. The system need not exhaust from all areas at the same time, but is permitted to be zoned based on the largest fire area served. For the purpose of calculating system size, the height of a compartment shall be considered to run from slab to slab and include the volume above suspended ceilings. Provisions shall be made for sufficient make-up air. The provisions may include operable windows, doors, building leakage, or mechanical systems. In buildings having occupied floors located less than 75 feet (22 860 mm) above the lowest level of Fire Department vehicle access, breakable windows may be utilized.
917.2.3 Operation. | The post-fire smoke purge system shall be operated by manual controls that are part of the fire command center, in accordance with Section 911, or fire alarm control unit when a fire command center is not required. Such control center or panel shall display a graphic indicating the portions of the building served by each post-fire smoke purge system. When a system is zoned into areas of operation less than the entire building, each zone shall have an individual control. Fire Department manual controls of post-fire smoke purge systems shall not override the manual or automatic operation of the smoke control system. Such Fire Department manual controls shall override the fire shutdown signal from the fire alarm system.
917.2.4 Interior exit stairways or ramps or exit passageways in occupancies other than Group R-2. | Interior exit stairways or ramps or exit passageways shall not be used as a portion of the post-fire smoke purge system in occupancies other than Group R-2. Doors in interior exit stairways or ramps or exit passageways shall not be permitted to be used as a portion of the post-fire smoke purge system. Air transfer and duct openings associated with the post-fire smoke purge system shall not be permitted in the interior exit stairway or ramp or exit passageway.
917.3 Post-fire smoke purge systems in occupancy Group R-2. | Post-fire smoke purge systems in Group R-2 occupancies shall comply with either Section 917.3.1 or 917.3.2. Smoke removed must be discharged to a safe location outside the building and shall not be recirculated into the building in accordance with the New York City Mechanical Code.
917.3.1 Stair ventilation. | The top of all enclosed exit stairs shall be provided with a reversible fan system capable of introducing fresh air or exhausting air at a rate of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) (0.00508 m3/s·• m2), whichever is greater, based on the area of the largest floor. Such system shall be operated by manual controls that are part of the fire command center, as per Section 911, or fire alarm panel when a fire command center is not required. Such control center or panel shall display a graphic indicating the portions of the building served by each post-fire smoke purge system. The operation of such system shall be controlled by Fire Department personnel by manually opening stair doors at the appropriate story.
917.3.2 Corridor ventilation. | The ducts and fans that provide fresh air supply to the public corridors in accordance with the New York City Mechanical Code shall be provided with reversible fans and duct sizes capable of introducing fresh air to or exhausting air from the corridor at a rate of 6 air changes per hour or 1 cubic foot per minute per square foot (cfm/ft2) (0.00508 m3/s·• m2), whichever is greater, based on the area of the largest apartment plus the area of the public corridor. Such system shall be operated by manual controls that are part of the fire command center, as per Section 911 of this code, or fire alarm panel when a fire command center is not required. Each floor to be ventilated shall be by individual controls. Such control center or panel shall display a graphic indicating the portions of the building served by each postfire smoke purge system.
917.4 Maintenance. | The building owner shall maintain post-fire smoke exhaust systems in good operational condition. Records of testing shall be maintained on the premises for inspection by the department and Fire Department personnel.
918.1 Gas detection systems. | Gas detection systems, including systems designed to detect flammable, toxic, asphyxiants and other gases, required by the New York City Construction Codes or the New York City Fire Code, shall comply with Sections 918.2 through 918.10 of this code.
918.2 Design and installation. | Gas detection systems shall be designed and installed in accordance with this code, the New York City Electrical Code, and manufacturer’s instructions. Such systems shall be inspected, tested and maintained in accordance with the New York City Fire Code.
918.2.1 Construction documents. | Construction documents for gas detection systems shall be submitted for review and approval to the Fire Department prior to system installation. Construction documents shall include, but not be limited to, the following:
918.3 Equipment. | Gas detection system devices and equipment shall be designed for use with the particular gas being detected.
918.4 Reserved.
918.5 Emergency power. | Gas detection systems shall be provided with emergency power in accordance with the New York City Fire Code and Chapter 27 of this code.
918.6 Sensor locations. | Where leaking gases are expected to accumulate, sensors shall be installed in approved locations in accordance with the New York City Fire Code and NFPA 72.
918.7 Gas sampling. | Gas detection systems shall perform continuous gas sampling. Sample analysis shall be processed immediately after sampling, except as follows:
918.8 System activation. | Gas detection systems shall activate and initiate an alarm system in compliance with the requirements of Sections 918.8.1 and 918.8.2.
918.8.1 Activation thresholds. | A gas detection system alarm shall be initiated when a sensor detects a concentration of gas exceeding the following thresholds unless otherwise specified in this code or the New York City Fire Code:
918.8.2 Alarm signals. | The gas detection system shall initiate a local alarm and transmit a signal to a constantly attended control station when a short-term hazard condition is detected. The alarm shall be both visible and audible and shall provide warning both inside and outside the area where gas is detected. The audible alarm shall be distinct from all other alarms.
918.8.3 Shutoff of gas supply. | The gas detection system shall automatically close the shutoff valve at the source of gas supply piping and tubing related to the system being monitored for whichever gas is detected. Exception: Automatic shutdown is not required for reactors utilized for the production of highly toxic or toxic compressed gases where such reactors comply with all of the following: 1. Operated at pressures less than 15 pounds per square inch gauge (psig) (103.4 kPa). 2. Constantly attended. 3. Provided with readily accessible emergency shutoff valves.
918.8.4 Valve closure. | The automatic closure of shutoff valves shall be in accordance with the following: 1. When the gas-detection sampling point initiating the gas detection system alarm is within a gas cabinet or exhausted enclosure, the shutoff valve in the gas cabinet or exhausted enclosure for the specific gas detected shall automatically close. 2. Where the gas-detection sampling point initiating the gas detection system alarm is within a gas room and compressed gas containers are not in gas cabinets or exhausted enclosures, the shutoff valves on all gas lines for the specific gas detected shall automatically close. 3. Where the gas-detection sampling point initiating the gas detection system alarm is within a piping distribution manifold enclosure, the shutoff valve for the compressed container of specific gas detected supplying the manifold shall automatically close. Exception: When the gas-detection sampling point initiating the gas detection system alarm is at a use location or within a gas valve enclosure of a branch line downstream of a piping distribution manifold, the shutoff valve in the gas valve enclosure for the branch line located in the piping distribution manifold enclosure shall automatically close.
918.9 Reserved.
918.10 Fire alarm system connections. | Gas detection systems shall be connected to and monitored at the Fire Command Center or fire alarm control unit where required or provided. Where a Fire Command Center or fire alarm control unit is not required or provided, an approved gas detection system control panel or annunciator shall be installed at the building main front entrance. A gas detection system shall be monitored by a central supervising station. Gas detection supervisory and alarm signals shall be transmitted as separate and distinct signals to the central supervising station.
|  | 901.6.2 Integrated testing. | Where two or more fire protection or life safety systems are interconnected, the intended response of subordinate fire protection and life safety systems shall be verified when required testing of the initiating system is conducted. In addition, integrated testing shall be performed in accordance with Sections 901.6.2.1 and 901.6.2.2.
|  | 901.6.2.1 High-rise buildings. | For high-rise buildings, integrated testing shall comply with NFPA 4, with an integrated test performed prior to issuance of the certificate of occupancy and at intervals not exceeding 10 years, unless otherwise specified by an integrated system test plan prepared in accordance with NFPA 4. If an equipment failure is detected during integrated testing, a repeat of the integrated test shall not be required, except as necessary to verify operation of fire protection or life safety functions that are initiated by equipment that was repaired or replaced.
|  | 901.6.2.2 Smoke control systems. | Where a fire alarm system is integrated with a smoke control system as outlined in Section 909, integrated testing shall comply with NFPA 4, with an integrated test performed prior to issuance of the certificate of occupancy and at intervals not exceeding 10 years, unless otherwise specified by an integrated system test plan prepared in accordance with NFPA 4. If an equipment failure is detected during integrated testing, a repeat of the integrated test shall not be required, except as necessary to verify operation of fire protection or life safety functions that are initiated by equipment that was repaired or replaced.
|  | 901.6.3 Fire alarm systems. | Fire alarm systems required by the provisions of Section 907.2 of this code and Sections 907.2 and 907.9 of the International Fire Code shall be monitored by an approved supervising station in accordance with Section 907.6.6 of this code. Exceptions: 1. Single- and multiple-station smoke alarms required by Section 907.2.11. 2. Smoke detectors in Group I-3 occupancies. 3. Supervisory service is not required for automatic sprinkler systems in one- and two-family dwellings.
|  | 901.6.4 Group H. | Supervision and monitoring of emergency alarm, detection and automatic fire-extinguishing systems in Group H occupancies shall be in accordance with the International Fire Code.
|  | 902.1 Pump and riser room size. | Where provided, fire pump rooms and automatic sprinkler system riser rooms shall be designed with adequate space for all equipment necessary for the installation, as defined by the manufacturer, with sufficient working room around the stationary equipment. Clearances around equipment to elements of permanent construction, including other installed equipment and appliances, shall be sufficient to allow inspection, service, repair or replacement without removing such elements of permanent construction or disabling the function of a required fire-resistance-rated assembly. Fire pump and automatic sprinkler system riser rooms shall be provided with doors and unobstructed passageways large enough to allow removal of the largest piece of equipment.
|  | 902.1.1 Access. | Automatic sprinkler system risers, fire pumps and controllers shall be provided with ready access. Where located in a fire pump room or automatic sprinkler system riser room, the door shall be permitted to be locked provided that the key is available at all times.
|  | 902.1.2 Marking on access doors. | Access doors for automatic sprinkler system riser rooms and fire pump rooms shall be labeled with an approved sign. The lettering shall be in contrasting color to the background. Letters shall have a minimum height of 2 inches (51 mm) with a minimum stroke of 3/8 inch (10 mm).
|  | 902.1.3 Environment. | Automatic sprinkler system riser rooms and fire pump rooms shall be maintained at a temperature of not less than 40°F (4°C). Heating units shall be permanently installed.
|  | 902.1.4 Lighting. | Permanently installed artificial illumination shall be provided in the automatic sprinkler system riser rooms and fire pump rooms.
|  | 903.2.1.5.1 Spaces under grandstands or bleachers. | Enclosed spaces under grandstands or bleachers shall be equipped with an automatic sprinkler system in accordance with Section 903.3.1.1 where either of the following exist:
|  | 903.2.2 Ambulatory care facilities. | An automatic sprinkler system shall be installed throughout the entire floor containing an ambulatory care facility where either of the following conditions exist at any time: 1. Four or more care recipients are incapable of self-preservation. 2. One or more care recipients that are incapable of self-preservation are located at other than the level of exit discharge serving such a facility. In buildings where ambulatory care is provided on levels other than the level of exit discharge, an automatic sprinkler system shall be installed throughout the entire floor as well as all floors below where such care is provid-ed, and all floors between the level of ambulatory care and the nearest level of exit discharge, the level of exit dis-charge, and all floors below the level of exit discharge.
|  | 903.2.4 Group F-1. | An automatic sprinkler system shall be provided throughout all buildings containing a Group F-1 occupancy where one of the following conditions exists:
|  | 903.2.4.2 Group F-1 distilled spirits. | An automatic sprinkler system shall be provided throughout a Group F-1 fire area used for the manufacture of distilled spirits.
|  | 903.2.4.3 Group F-1 upholstered furniture or mattresses. | An automatic sprinkler system shall be provided throughout a Group F-1 fire area that exceeds 2,500 square feet (232 m2) used for the manufacture of upholstered furniture or mattresses.
|  | 903.2.7.2 Group M upholstered furniture or mattresses. | An automatic sprinkler system shall be provided throughout a Group M fire area where the area used for the display and sale of upholstered furniture or mattresses exceeds 5,000 square feet (464 m2).
|  | 903.2.8.1 Group R-3. | An automatic sprinkler system installed in accordance with Section 903.3.1.3 shall be permitted in Group R-3 occupancies.
|  | 903.2.8.2 Group R-4, Condition 1. | An automatic sprinkler system installed in accordance with Section 903.3.1.3 shall be permitted in Group R-4, Condition 1 occupancies.
|  | 903.2.8.3 Group R-4, Condition 2. | An automatic sprinkler system installed in accordance with Section 903.3.1.2 shall be permitted in Group R-4, Condition 2 occupancies.
|  | 903.2.8.4 Care facilities. | An automatic sprinkler system installed in accordance with Section 903.3.1.3 shall be permitted in care facilities with five or fewer individuals in a single-family dwelling.
|  | 903.2.9.1 Repair garages. | An automatic sprinkler system shall be provided throughout all buildings used as repair garages in accordance with Section 406, as shown:
|  | 903.2.9.3 Group S-1 Distilled spirits or wine. | An automatic sprinkler system shall be provided throughout a Group S-1 fire area used for the bulk storage of distilled spirits or wine.
|  | 903.2.9.4 Group S-1 upholstered furniture and mattresses. | An automatic sprinkler system shall be provided throughout a Group S-1 fire area where the area used for the storage of upholstered furniture or mattresses exceeds 2,500 square feet (232 m2). Exception: Self-service storage facilities not greater than one story above grade plane where all storage spac-es can be accessed directly from the exterior.
|  | 903.2.10 Group S-2 parking garages. | An automatic sprinkler system shall be provided throughout buildings classified as parking garages where any of the following conditions exists: 1. Where the fire area of the enclosed parking garage in accordance with Section 406.6 exceeds 12,000 square feet (1115 m2). 2. Where the enclosed parking garage in accordance with Section 406.6 is located beneath other groups. Exception: Enclosed parking garages located beneath Group R-3 occupancies. 3. Where the fire area of the open parking garage in accordance with Section 406.5 exceeds 48,000 square feet (4460 m2).
|  | 903.2.10.2 Mechanical-access enclosed parking garages. | An approved automatic sprinkler system shall be provided throughout buildings used for the storage of motor vehicles in a mechanical-access enclosed parking garage. The portion of the building that contains the mechanical-access enclosed parking garage shall be protected with a specially engineered automatic sprinkler system.
|  | 903.2.11.1 Stories without openings. | An automatic sprinkler system shall be installed throughout all stories, including basements, of all buildings where the floor area exceeds 1,500 square feet (139.4 m2) and where the story does not comply with the following criteria for exterior wall openings:
|  | 903.2.11.1.3 Basements. | Where any portion of a basement is located more than 75 feet (22 860 mm) from openings required by Section 903.2.11.1, or where walls, partitions or other obstructions are installed that restrict the application of water from hose streams, the basement shall be equipped throughout with an approved automatic sprinkler system.
|  | 903.2.11.2 Rubbish and linen chutes. | An automatic sprinkler system shall be installed at the top of rubbish and linen chutes and in their terminal rooms. Chutes shall have additional sprinkler heads installed at alternate floors and at the lowest intake. Where a rubbish chute extends through a building more than one floor below the lowest intake, the extension shall have sprinklers installed that are recessed from the drop area of the chute and protected from freezing in accordance with Section 903.3.1.1. Such sprinklers shall be installed at alternate floors, beginning with the second level below the last intake and ending with the floor above the discharge. Access to sprinklers in chutes shall be provided for servicing.
|  | 903.2.11.3 Buildings 55 feet or more in height. | An automatic sprinkler system shall be installed throughout buildings that have one or more stories with an occupant load of 30 or more located 55 feet (16 764 mm) or more above the lowest level of fire department vehicle access, measured to the finished floor. Exception: Occupancies in Group F-2.
|  | 903.2.11.4 Ducts conveying hazardous exhausts. | Where required by the International Mechanical Code, automatic sprinklers shall be provided in ducts conveying hazardous exhaust or flammable or combustible materials. Exception: Ducts where the largest cross-sectional diameter of the duct is less than 10 inches (254 mm).
|  | 903.2.11.5 Commercial cooking operations. | An automatic sprinkler system shall be installed in commercial kitchen exhaust hood and duct systems where an automatic sprinkler system is used to comply with Section 904.
|  | 903.2.11.6 Other required fire protection systems. | In addition to the requirements of Section 903.2, the provisions indicated in Table 903.2.11.6 require the installation of a fire protection system for certain buildings and areas. |  | See BC09 Tables&Figures
|  | 903.3.1.1.1 Exempt locations. | Automatic sprinklers shall not be required in the following rooms or areas where such rooms or areas are protected with an approved automatic fire detection system in accordance with Section 907.2 that will respond to visible or invisible particles of combustion. Sprinklers shall not be omitted from a room merely because it is damp, of fire-resistance-rated construction or contains electrical equipment.
|  | 903.3.1.1.2 Bathrooms. | In Group R occupancies sprinklers shall not be required in bathrooms that do not exceed 55 square feet (5 m2) in area and are located within individual dwelling units or sleeping units, provided that walls and ceilings, including the walls and ceilings behind a shower enclosure or tub, are of noncombustible or limited-combustible materials with a 15-minute thermal barrier rating.
|  | 903.3.1.2.2 Corridors and balconies in the means of egress. | Sprinkler protection shall be provided in corridors and for balconies in the means of egress where any of the following conditions apply:
|  | 903.3.1.2.3 Attics. | Attic protection shall be provided as follows:
|  | 903.3.5.2 Residential combination services. | A single combination water supply shall be allowed provided that the domestic demand is added to the sprinkler demand as required by NFPA 13R.
|  | 903.3.7 Fire department connections. | Fire department connections for automatic sprinkler systems shall be installed in accordance with Section 912.
|  | 903.4.1 Monitoring. | Alarm, supervisory and trouble signals shall be distinctly different and shall be automatically transmitted to an approved supervising station or, where approved by the fire code official, shall sound an audible signal at a constantly attended location. Exception: Backflow prevention device test valves located in limited area sprinkler system supply piping shall be locked in the open position. In occupancies required to be equipped with a fire alarm system, the backflow preventer valves shall be electrically supervised by a tamper switch installed in accordance with NFPA 72 and separately annunciated.
|  | 904.2 Where permitted. | Automatic fire-extinguishing systems installed as an alternative to the required automatic sprinkler systems of Section 903 shall be approved by the fire code official.
|  | 904.2.1 Restriction on using automatic sprinkler system exceptions or reductions. | Automatic fire-extinguishing systems shall not be considered alternatives for the purposes of exceptions or reductions allowed for automatic sprinkler systems or by other requirements of this code.
|  | 904.2.2 Commercial hood and duct systems. | Each required commercial kitchen exhaust hood and duct system required by Section 606 of the International Fire Code or Chapter 5 of the International Mechanical Code to have a Type I hood shall be protected with an approved automatic fire-extinguishing system installed in accordance with this code.
|  | 904.11.3 Testing and maintenance. | Automatic water mist systems shall be tested and maintained in accordance with the International Fire Code.
|  | 904.12 Aerosol fire-extinguishing systems. | Aerosol fire-extinguishing systems shall be installed, maintained, periodically inspected and tested in accordance with NFPA 2010, and their listing.
|  | 904.13 Commercial cooking systems. | The automatic fire-extinguishing system for commercial cooking systems shall be of a type recognized for protection of commercial cooking equipment and exhaust systems of the type and arrangement protected. Preengineered automatic dry- and wet-chemical extinguishing systems shall be tested in accordance with UL 300 and listed and labeled for the intended application. Other types of automatic fire-extinguishing systems shall be listed and labeled for specific use as protection for commercial cooking operations. The system shall be installed in accordance with this code, NFPA 96, its listing and the manufacturer’s installation instructions. Automatic fire-extinguishing systems of the following types shall be installed in accordance with the referenced standard indicated, as follows: 1. Carbon dioxide extinguishing systems, NFPA 12. 2. Automatic sprinkler systems, NFPA 13. 3. Automatic water mist systems, NFPA 750. 4. Foam-water sprinkler system or foam-water spray systems, NFPA 16. 5. Dry-chemical extinguishing systems, NFPA 17. 6. Wet-chemical extinguishing systems, NFPA 17A. Exception: Factory-built commercial cooking recirculating systems that are tested in accordance with UL 710B and listed, labeled and installed in accordance with Section 304.1 of the International Mechanical Code.
|  | 904.13.1 Manual system operation. | A manual actuation device shall be located at or near a means of egress from the cooking area not less than 10 feet (3048 mm) and not more than 20 feet (6096 mm) from the kitchen exhaust system. The manual actuation device shall be installed not more than 48 inches (1200 mm) or less than 42 inches (1067 mm) above the floor and shall clearly identify the hazard protected. The manual actuation shall require a maximum force of 40 pounds (178 N) and a maximum movement of 14 inches (356 mm) to actuate the fire suppression system. Exception: Automatic sprinkler systems shall not be required to be equipped with manual actuation means.
|  | 904.13.2 System interconnection. | The actuation of the fire suppression system shall automatically shut down the fuel or electrical power supply to the cooking equipment. The fuel and electrical supply reset shall be manual.
|  | 904.13.3 Carbon dioxide systems. | Where carbon dioxide systems are used, there shall be a nozzle at the top of the ventilating duct. Additional nozzles that are symmetrically arranged to give uniform distribution shall be installed within vertical ducts exceeding 20 feet (6096 mm) and horizontal ducts exceeding 50 feet (15 240 mm). Dampers shall be installed at either the top or the bottom of the duct and shall be arranged to operate automatically upon activation of the fire-extinguishing system. Where the damper is installed at the top of the duct, the top nozzle shall be immediately below the damper. Automatic carbon dioxide fire-extinguishing systems shall be sufficiently sized to protect against all hazards venting through a common duct simultaneously.
|  | 904.13.3.1 Ventilation system. | Commercial-type cooking equipment protected by an automatic carbon dioxide-extinguishing system shall be arranged to shut off the ventilation system upon activation.
|  | 904.13.4 Special provisions for automatic sprinkler systems. | Automatic sprinkler systems protecting commercial-type cooking equipment shall be supplied from a separate, indicating-type control valve that is identified. Access to the control valve shall be provided.
|  | 904.13.4.1 Listed sprinklers. | Sprinklers used for the protection of fryers shall be tested in accordance with UL 199E, listed for that application and installed in accordance with their listing.
|  | 904.14 Domestic cooking facilities. | Cooktops and ranges installed in the following occupancies shall be protected in accordance with Section 904.14.1:
|  | 904.14.1 Protection from fire. | Cooktops and ranges shall be protected in accordance with Section 904.14.1.1 or 904.14.1.2.
|  | 904.14.1.1 Automatic fire-extinguishing system. | The domestic recirculating or exterior vented cooking hood provided over the cooktop or range shall be equipped with an approved automatic fire-extinguishing system complying with the following:
|  | 904.14.1.2 Ignition prevention. | Cooktops and ranges shall include burners that have been tested and listed to prevent ignition of cooking oil with burners turned on to their maximum heat settings and allowed to operate for 30 minutes.
|  | 905.2 Installation standard. | Standpipe systems shall be installed in accordance with this section and NFPA 14. Fire department connections for standpipe systems shall be in accordance with Section 912.
|  | 905.3.1 Height. | Class III standpipe systems shall be installed throughout buildings where any of the following conditions exist: 1. Four or more stories are above or below grade plane. 2. The floor level of the highest story is located more than 30 feet (9144 mm) above the lowest level of fire de-partment vehicle access. 3. The floor level of the lowest story is located more than 30 feet (9144 mm) below the highest level of fire de-partment vehicle access. Exceptions: 1. Class I standpipes are allowed in buildings equipped throughout with an automatic sprinkler system in ac-cordance with Section 903.3.1.1 or 903.3.1.2. 2. Class I standpipes are allowed in Group B and E occupancies. 3. Class I standpipes are allowed in parking garages. 4. Class I standpipes are allowed in basements equipped throughout with an automatic sprinkler system. 5. Class I standpipes are allowed in buildings where occupant-use hose lines will not be utilized by trained personnel or the fire department. 6. In determining the lowest level of fire department vehicle access, it shall not be required to consider ei-ther of the following: 6.1. Recessed loading docks for four vehicles or less. 6.2. Conditions where topography makes access from the fire department vehicle to the building im-practical or impossible.
|  | 905.3.3 Covered and open mall buildings. | Covered mall and open mall buildings shall be equipped throughout with a standpipe system where required by Section 905.3.1. Mall buildings not required to be equipped with a standpipe system by Section 905.3.1 shall be equipped with Class I hose connections connected to the automatic sprinkler system sized to deliver water at 250 gallons per minute (946.4 L/min) at the hydraulically most remote hose connection while concurrently supplying the automatic sprinkler system demand. The standpipe system shall be designed to not exceed a 50 pounds per square inch (psi) (345 kPa) residual pressure loss with a flow of 250 gallons per minute (946.4 L/min) from the fire department connection to the hydraulically most remote hose connection. Hose connections shall be provided at each of the following locations:
|  | 905.3.4.1 Hose and cabinet. | The 11/2-inch (38 mm) hose connections shall be equipped with sufficient lengths of 11/2-inch (38 mm) hose to provide fire protection for the stage area. Hose connections shall be equipped with an approved adjustable fog nozzle and be mounted in a cabinet or on a rack.
|  | 905.3.8 Landscaped​​​​​​​ roofs. | Buildings or structures that have landscaped roofs and that are equipped with a standpipe system shall have the standpipe system extended to the roof level on which the landscaped roof is located.
|  | 905.5.1 Groups A-1 and A-2. | In Group A-1 and A-2 occupancies having occupant loads exceeding 1,000 persons, hose connections shall be located on each side of any stage, on each side of the rear of the auditorium, on each side of the balcony and on each tier of dressing rooms.
|  | 905.5.2 Protection. | Fire-resistance-rated protection of risers and laterals of Class II standpipe systems is not required.
|  | 905.5.3 Class II system 1-inch hose. | A minimum 1-inch (25 mm) hose shall be allowed to be used for hose stations in light-hazard occupancies where investigated and listed for this service and where approved by the fire code official.
|  | 905.11 Locking standpipe outlet caps. | The fire code official is authorized to require locking caps on the outlets on standpipes where the responding fire department carries key wrenches for the removal that are compatible with locking FDC connection caps.
|  | 906.1 Where required. | Portable fire extinguishers shall be installed in all of the following locations: 1. In Group A, B, E, F, H, I, M, R-1, R-2, R-4 and S occupancies. Exceptions: 1. In Group R-2 occupancies, portable fire extinguishers shall be required only in locations specified in Items 2 through 6 where each dwelling unit is provided with a portable fire extinguisher having a min-imum rating of 1-A:10-B:C. 2. In Group E occupancies. portable fire extinguishers shall be required only in locations specified in Items 2 through 6 where each classroom is provided with a portable fire extinguisher having a mini-mum rating of 2-A:20-B:C. 3. In storage areas of Group S Occupancies where forklift, powered industrial truck or powered cart op-erators are the primary occupants, fixed extinguishers, as specified in NFPA 10, shall not be required where in accordance with all of the following: 3.1. Use of vehicle-mounted extinguishers shall be approved by the fire code official. 3.2. Each vehicle shall be equipped with a 10-pound, 40A:80B:C extinguisher affixed to the ve-hicle using a mounting bracket approved by the extinguisher manufacturer or the fire code official for vehicular use. 3.3. Not less than two spare extinguishers of equal or greater rating shall be available on site to replace a discharged extinguisher. 3.4. Vehicle operators shall be trained in the proper operation, use and inspection of extinguish-ers. 3.5. Inspections of vehicle-mounted extinguishers shall be performed daily. 2. Within 30 feet (9144 mm) distance of travel from commercial cooking equipment and from domestic cooking equipment in Group I-1; I-2, Condition 1; and R-2 college dormitory occupancies. 3. In areas where flammable or combustible liquids are stored, used or dispensed. 4. On each floor of structures under construction, except Group R-3 occupancies, in accordance with Section 3315.1 of the International Fire Code. 5. Where required by the International Fire Code sections indicated in Table 906.1. 6. Special-hazard areas, including but not limited to laboratories, computer rooms and generator rooms, where re-quired by the fire code official. Exception: Portable fire extinguishers are not required at normally unmanned Group U occupancy buildings or structures where a portable fire extinguisher suitable to the hazard of the location is provided on the vehicle of vis-iting personnel. |  | See BC09 Tables&Figures
|  | 906.2 General requirements. | Portable fire extinguishers shall be selected and installed in accordance with this section and NFPA 10. Exceptions: 1. The distance of travel to reach an extinguisher shall not apply to the spectator seating portions of Group A-5 occupancies. 2. In Group I-3, portable fire extinguishers shall be permitted to be located at staff locations.
|  | 906.3 Size and distribution. | The size and distribution of portable fire extinguishers shall be in accordance with Sections 906.3.1 through 906.3.4.
|  | 906.3.1 Class A fire hazards. | The minimum sizes and distribution of portable fire extinguishers for occupancies that involve primarily Class A fire hazards shall comply with Table 906.3(1). |  | See BC09 Tables&Figures
|  | 906.3.2 Class B fire hazards. | Portable fire extinguishers for occupancies involving flammable or combustible liquids with depths less than or equal to 0.25-inch (6.4 mm) shall be selected and placed in accordance with Table 906.3(2). |  | See BC09 Tables&Figures
|  | 906.3.3 Class C fire hazards. | Portable fire extinguishers for Class C fire hazards shall be selected and placed on the basis of the anticipated Class A or B hazard.
|  | 906.3.4 Class D fire hazards. | Portable fire extinguishers for occupancies involving combustible metals shall be selected and placed in accordance with NFPA 10.
|  | 906.4 Cooking equipment fires. | Fire extinguishers provided for the protection of cooking equipment shall be of an approved type compatible with the automatic fire-extinguishing system agent. Cooking equipment involving solid fuels or vegetable or animal oils and fats shall be protected by a Class K-rated portable extinguisher in accordance with Sections 906.1, Item 2, 906.4.1 and 906.4.2 of the International Fire Code, as applicable.
|  | 906.5 Conspicuous location. | Portable fire extinguishers shall be located in conspicuous locations where they will have ready access and be immediately available for use. These locations shall be along normal paths of travel, unless the fire code official determines that the hazard posed indicates the need for placement away from normal paths of travel.
|  | 906.6 Unobstructed and unobscured. | Portable fire extinguishers shall not be obstructed or obscured from view. In rooms or areas in which visual obstruction cannot be completely avoided, means shall be provided to indicate the locations of extinguishers.
|  | 906.7 Hangers and brackets. | Hand-held portable fire extinguishers, not housed in cabinets, shall be installed on the hangers or brackets supplied. Hangers or brackets shall be securely anchored to the mounting surface in accordance with the manufacturer’s installation instructions.
|  | 906.8 Cabinets. | Cabinets used to house portable fire extinguishers shall not be locked. Exceptions: 1. Where portable fire extinguishers subject to malicious use or damage are provided with a means of ready ac-cess. 2. In Group I-3 occupancies and in mental health areas in Group I-2 occupancies, access to portable fire extin-guishers shall be permitted to be locked or to be located in staff locations provided that the staff has keys.
|  | 906.9 Extinguisher installation. | The installation of portable fire extinguishers shall be in accordance with Sections 906.9.1 through 906.9.3.
|  | 906.9.1 Extinguishers weighing 40 pounds or less. | Portable fire extinguishers having a gross weight not exceeding 40 pounds (18 kg) shall be installed so that their tops are not more than 5 feet (1524 mm) above the floor.
|  | 906.9.2 Extinguishers weighing more than 40 pounds. | Hand-held portable fire extinguishers having a gross weight exceeding 40 pounds (18 kg) shall be installed so that their tops are not more than 3.5 feet (1067 mm) above the floor.
|  | 906.9.3 Floor clearance. | The clearance between the floor and the bottom of installed hand-held portable fire extinguishers shall be not less than 4 inches (102 mm).
|  | 906.10 Wheeled units. | Wheeled fire extinguishers shall be conspicuously located in a designated location.
|  | 907.1.2 Fire alarm shop drawings. | Shop drawings for fire alarm systems shall be prepared in accordance with NFPA 72 and submitted for review and approval prior to system installation.
|  | 907.1.3 Equipment. | Systems and components shall be listed and approved for the purpose for which they are installed.
|  | 907.2 Where required—new buildings and structures. | An approved fire alarm system installed in accordance with the provisions of this code and NFPA 72 shall be provided in new buildings and structures in accordance with Sections 907.2.1 through 907.2.23 and provide occupant notification in accordance with Section 907.5, unless other requirements are provided by another section of this code. Not fewer than one manual fire alarm box shall be provided in an approved location to initiate a fire alarm signal for fire alarm systems employing automatic fire detectors or waterflow detection devices. Where other sections of this code allow elimination of fire alarm boxes due to sprinklers, a single fire alarm box shall be installed. Exceptions: 1. The manual fire alarm box is not required for fire alarm systems dedicated to elevator recall control and su-pervisory service. 2. The manual fire alarm box is not required for Group R-2 occupancies unless required by the fire code offi-cial to provide a means for fire watch personnel to initiate an alarm during a sprinkler system impairment event. Where provided, the manual fire alarm box shall not be located in an area that is open to the public.
|  | 907.2.1.1 System initiation in Group A occupancies with an occupant load of 1,000 or more. | Activation of the fire alarm in Group A occupancies with an occupant load of 1,000 or more shall initiate a signal using an emergency voice/alarm communications system in accordance with Section 907.5.2.2. Exception: Where approved, the prerecorded announcement is allowed to be manually deactivated for a peri-od of time, not to exceed 3 minutes, for the sole purpose of allowing a live voice announcement from an ap-proved, constantly attended location.
|  | 907.2.6.1.1 Smoke alarms. | Single- and multiple-station smoke alarms shall be installed in accordance with Section 907.2.11.
|  | 907.2.6.3 Group I-3 occupancies. | Group I-3 occupancies shall be equipped with a manual fire alarm system and automatic smoke detection system installed for alerting staff.
|  | 907.2.7.1 Occupant notification. | During times that the building is occupied, the initiation of a signal from a manual fire alarm box or from a waterflow switch shall not be required to activate the alarm notification appliances when an alarm signal is activated at a constantly attended location from which evacuation instructions shall be initiated over an emergency voice/alarm communication system installed in accordance with Section 907.5.2.2.
|  | 907.2.8.3 Smoke alarms. | Single- and multiple-station smoke alarms shall be installed in accordance with Section 907.2.11.
|  | 907.2.9.1 Manual fire alarm system. | A manual fire alarm system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R-2 occupancies where any of the following conditions apply: 1. Any dwelling unit or sleeping unit is located three or more stories above the lowest level of exit dis-charge. 2. Any dwelling unit or sleeping unit is located more than one story below the highest level of exit discharge of exits serving the dwelling unit or sleeping unit. 3. The building contains more than 16 dwelling units or sleeping units. Exceptions: 1. A fire alarm system is not required in buildings not more than two stories in height where all dwelling units or sleeping units and contiguous attic and crawl spaces are separated from each other and pub-lic or common areas by not less than 1-hour fire partitions and each dwelling unit or sleeping unit has an exit directly to a public way, egress court or yard. 2. Manual fire alarm boxes are not required where the building is equipped throughout with an automat-ic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2 and the occupant noti-fication appliances will automatically activate throughout the notification zones upon a sprinkler wa-ter flow. 3. A fire alarm system is not required in buildings that do not have interior corridors serving dwelling units and are protected by an approved automatic sprinkler system installed in accordance with Sec-tion 903.3.1.1 or 903.3.1.2, provided that dwelling units either have a means of egress door opening directly to an exterior exit access that leads directly to the exits or are served by open-ended corri-dors designed in accordance with Section 1027.6, Exception 3.
|  | 907.2.9.3 Group R-2 college and university buildings. | An automatic smoke detection system that activates the occupant notification system in accordance with Section 907.5 shall be installed in Group R-2 occupancies operated by a college or university for student or staff housing in all of the following locations: 1. Common spaces outside of dwelling units and sleeping units. 2. Laundry rooms, mechanical equipment rooms and storage rooms. 3. All interior corridors serving sleeping units or dwelling units. Exception: An automatic smoke detection system is not required in buildings that do not have interi-or corridors serving sleeping units or dwelling units and where each sleeping unit or dwelling unit ei-ther has a means of egress door opening directly to an exterior exit access that leads directly to an ex-it or a means of egress door opening directly to an exit. Required smoke alarms in dwelling units and sleeping units in Group R-2 occupancies operated by a college or university for student or staff housing shall be interconnected with the fire alarm system in accordance with NFPA 72.
|  | 907.2.11.1 Group R-1. | Single- or multiple-station smoke alarms shall be installed in all of the following locations in Group R-1:
|  | 907.2.11.2 Groups R-2, R-3, R-4 and I-1. | Single- or multiple-station smoke alarms shall be installed and maintained in Groups R-2, R-3, R-4 and I-1 regardless of occupant load at all of the following locations:
|  | 907.2.11.6 Power source. | In new construction, required smoke alarms shall receive their primary power from the building wiring where such wiring is served from a commercial source and shall be equipped with a battery backup. Smoke alarms with integral strobes that are not equipped with battery backup shall be connected to an emergency electrical system in accordance with Section 2702. Smoke alarms shall emit a signal when the batteries are low. Wiring shall be permanent and without a disconnecting switch other than as required for overcurrent protection. Exception: Smoke alarms are not required to be equipped with battery backup where they are connected to an emergency electrical system that complies with Section 2702.
|  | 907.2.13.1.1 Area smoke detection. | Area smoke detectors shall be provided in accordance with this section. Smoke detectors shall be connected to an automatic fire alarm system. The activation of any detector required by this section shall activate the emergency voice/alarm communication system in accordance with Section 907.5.2.2. In addition to smoke detectors required by Sections 907.2.1 through 907.2.9, smoke detectors shall be located as follows:
|  | 907.2.13.2 Fire department communication system. | Where a wired communication system is approved in lieu of an in-building two-way emergency responder communication coverage system in accordance with Section 510 of the International Fire Code, the wired fire department communication system shall be designed and installed in accordance with NFPA 72 and shall operate between a fire command center complying with Section 911, elevators, elevator lobbies, emergency and standby power rooms, fire pump rooms, areas of refuge and inside interior exit stairways. The fire department communication device shall be provided at each floor level within the interior exit stairway.
|  | 907.2.13.3 Multiple-channel voice evacuation. | In buildings with an occupied floor more than 120 feet (36 576 mm) above the lowest level of fire department vehicle access, voice evacuation systems for high-rise buildings shall be multiple-channel systems.
|  | 907.2.18 Underground buildings with smoke control systems. | Where a smoke control system is installed in an underground building in accordance with this code, automatic smoke detectors shall be provided in accordance with Section 907.2.18.1.
|  | 907.2.19 Deep underground buildings. | Where the lowest level of a structure is more than 60 feet (18 288 mm) below the finished floor of the lowest level of exit discharge, the structure shall be equipped throughout with a manual fire alarm system, including an emergency voice/alarm communication system installed in accordance with Section 907.5.2.2.
|  | 907.2.21 Residential aircraft hangars. | Not fewer than one single-station smoke alarm shall be installed within a residential aircraft hangar as defined in Chapter 2 and shall be interconnected into the residential smoke alarm or other sounding device to provide an alarm that will be audible in all sleeping areas of the dwelling.
|  | 907.2.23 Energy storage systems. | An automatic smoke detection system or radiant-energy detection system shall be installed in rooms, areas and walk-in units containing energy storage systems as required in Section 1207.5.4 of the International Fire Code.
|  | 907.3.2 Special locking systems. | Where special locking systems are installed on means of egress doors in accordance with Sections 1010.2.13 or 1010.2.14, an automatic detection system shall be installed as required by that section.
|  | 907.5 Occupant notification. | Occupant notification by fire alarms shall be in accordance with Sections 907.5.1 through 907.5.2.3.3. Occupant notification by smoke alarms in Group R-1 and R-2 occupancies shall comply with Section 907.5.2.1.3.2.
|  | 907.5.1 Alarm activation and annunciation. | Upon activation, fire alarm systems shall initiate occupant notification and shall annunciate at the fire alarm control unit, or where allowed elsewhere by Section 907, at a constantly attended location.
|  | 907.5.1.1 Presignal feature. | A presignal feature shall be provided only where approved. The presignal shall be annunciated at an approved, constantly attended location, having the capability to activate the occupant notification system in the event of fire or other emergency.
|  | 907.5.2.1.3 Audible signal frequency in Group R-1 and R-2 sleeping rooms. | Audible signal frequency in Group R-1 and R-2 occupancies shall be in accordance with Sections 907.5.2.1.3.1 and 907.5.2.1.3.2.
|  | 907.5.2.1.3.1 Fire alarm system signal. | In sleeping rooms of Group R-1 and R-2 occupancies, the audible alarm activated by a fire alarm system shall be a 520-Hz low-frequency signal complying with NFPA 72.
|  | 907.5.2.1.3.2 Smoke alarm signal in sleeping rooms. | In sleeping rooms of Group R-1 and R-2 occupancies that are required by Section 907.2.8 or 907.2.9 to have a fire alarm system, the audible alarm signal activated by single- or multiple-station smoke alarms in the dwelling unit or sleeping unit shall be a 520-Hz signal complying with NFPA 72. Where a sleeping room smoke alarm is unable to produce a 520-Hz signal, the 520-Hz alarm signal shall be provided by a listed notification appliance or a smoke detector with an integral 520-Hz sounder.
|  | 907.5.2.2.3 Alternative uses. | The emergency voice/alarm communication system shall be allowed to be used for other announcements, provided that the manual fire alarm use takes precedence over any other use.
|  | 907.5.2.2.5 Standby power. | Emergency voice/alarm communications systems shall be provided with standby power in accordance with Section 2702.
|  | 907.5.2.3.1 Public use areas and common use areas. | Visible alarm notification appliances shall be provided in public use areas and common use areas. Exception: Where employee work areas have audible alarm coverage, the notification appliance circuits serving the employee work areas shall be initially designed with not less than 20-percent spare capacity to account for the potential of adding visible notification appliances in the future to accommodate hearing-impaired employee(s).
|  | 907.5.2.3.3 Group R-2. | In Group R-2 occupancies required by Section 907 to have a fire alarm system, each story that contains dwelling units and sleeping units shall be provided with the capability to support future visible alarm notification appliances in accordance with Chapter 11 of ICC A117.1. Such capability shall accommodate wired or wireless equipment.
|  | 907.5.2.3.3.1 Wired equipment. | Where wired equipment is used to comply with the future capability required by Section 907.5.2.3.3, the system shall include one of the following capabilities:
|  | 907.6.3 Initiating device identification. | The fire alarm system shall identify the specific initiating device address, location, device type, floor level where applicable and status including indication of normal, alarm, trouble and supervisory status, as appropriate. 1. Fire alarm systems in single-story buildings less than 22,500 square feet (2090 m2) in area. 2. Fire alarm systems that only include manual fire alarm boxes, waterflow initiating devices and not more than 10 additional alarm-initiating devices. 3. Special initiating devices that do not support individual device identification. 4. Fire alarm systems or devices that are replacing existing equipment.
|  | 907.6.3.1 Annunciation. | The initiating device status shall be annunciated at an approved on-site location.
|  | 907.6.4 Zones. | Each floor shall be zoned separately and a zone shall not exceed 22,500 square feet (2090 m2). The length of any zone shall not exceed 300 feet (91 440 mm) in any direction. Exception: Automatic sprinkler system zones shall not exceed the area permitted by NFPA 13.
|  | 907.6.4.1 Zoning indicator panel. | A zoning indicator panel and the associated controls shall be provided in an approved location. The visual zone indication shall lock in until the system is reset and shall not be canceled by the operation of an audible-alarm silencing switch.
|  | 907.6.4.2 High-rise buildings. | In high-rise buildings, a separate zone by floor shall be provided for each of the following types of alarm-initiating devices where provided:
|  | 907.6.5 Access. | Access shall be provided to each fire alarm device and notification appliance for periodic inspection, maintenance and testing.
|  | 907.6.6 Monitoring. | Fire alarm systems required by this chapter or by the International Fire Code shall be monitored by an approved supervising station in accordance with NFPA 72. Exception: Monitoring by a supervising station is not required for: 1. Single- and multiple-station smoke alarms required by Section 907.2.11. 2. Smoke detectors in Group I-3 occupancies. 3. Automatic sprinkler systems in one- and two-family dwellings.
|  | 907.6.6.1 Transmission of alarm signals. | Transmission of alarm signals to a supervising station shall be in accordance with NFPA 72.
|  | 907.6.6.2 MIY Monitoring. | Direct transmission of alarms associated with monitor it yourself (MIY) transmitters to a public safety answering point (PSAP) shall not be permitted unless approved by the fire code official.
|  | 907.6.6.3 Termination of monitoring service. | Termination of fire alarm monitoring services shall be in accordance with Section 901.9 of the International Fire Code.
|  | 908.3 Fire alarm system interface. | Where an emergency alarm system is interfaced with a building’s fire alarm system, the signal produced at the fire alarm control unit shall be a supervisory signal.
|  | 909.5.3.1 Group I-1, Condition 2; Group I-2; and ambulatory care facilities. | In Group I-1, Condition 2; Group I-2; and ambulatory care facilities, where doors are installed across a corridor, the doors shall be automatic closing by smoke detection in accordance with Section 716.2.6.5 and shall have a vision panel with fire-protection-rated glazing materials in fire protection-rated frames, the area of which shall not exceed that tested.
|  | 909.7 Airflow design method. | Where approved by the fire code official, smoke migration through openings fixed in a permanently open position, which are located between smoke control zones by the use of the airflow method, shall be permitted. The design airflow shall be in accordance with this section. Airflow shall be directed to limit smoke migration from the fire zone. The geometry of openings shall be considered to prevent flow reversal from turbulent effects. Smoke control systems using the airflow method shall be designed in accordance with NFPA 92.
|  | 909.16 Fire fighter’s smoke control panel. | A fire fighter’s smoke control panel for fire department emergency response purposes only shall be provided and shall include manual control or override of automatic control for mechanical smoke control systems. The panel shall be located in a fire command center complying with Section 911 in high-rise buildings or buildings with smoke-protected assembly seating. In all other buildings, the fire fighter’s smoke control panel shall be installed in an approved location adjacent to the fire alarm control panel. The fire fighter’s smoke control panel shall comply with Sections 909.16.1 through 909.16.3.
|  | 909.16.1 Smoke control systems. | Fans within the building shall be shown on the fire fighter’s control panel. A clear indication of the direction of airflow and the relationship of components shall be displayed. Status indicators shall be provided for all smoke control equipment, annunciated by fan and zone, and by pilot-lamp-type indicators as follows:
|  | 909.16.2 Smoke control panel. | The fire fighter’s control panel shall provide control capability over the complete smoke control system equipment within the building as follows: 1. ON-AUTO-OFF control over each individual piece of operating smoke control equipment that can be con-trolled from other sources within the building. This includes stairway pressurization fans; smoke exhaust fans; supply, return and exhaust fans; elevator shaft fans and other operating equipment used or intended for smoke control purposes. 2. OPEN-AUTO-CLOSE control over individual dampers relating to smoke control and that are controlled from other sources within the building. 3. ON-OFF or OPEN-CLOSE control over smoke control and other critical equipment associated with a fire or smoke emergency and that can only be controlled from the fire fighter’s control panel. Exceptions: 1. Complex systems, where approved, where the controls and indicators are combined to control and indi-cate all elements of a single smoke zone as a unit. 2. Complex systems, where approved, where the control is accomplished by computer interface using ap-proved, plain English commands.
|  | 909.18.8 Testing for smoke control. | Smoke control systems shall be tested by a special inspector in accordance with Section 1705.19 .
|  | 909.20.6 Pressurized stair and vestibule alternative. | The provisions of Sections 909.20.6.1 through 909.20.6.3 shall apply to smokeproof enclosures using a pressurized stair and pressurized entrance vestibule.
|  | 909.20.6.1 Vestibule doors. | The door assembly from the building into the vestibule shall be a fire door assembly complying with Section 716.2.2.1. The door assembly from the vestibule to the stairway shall have not less than a 20-minute fire protection rating and meet the requirements for a smoke door assembly in accordance with Section 716.2.2.1. The door shall be installed in accordance with NFPA 105.
|  | 909.20.6.2 Pressure difference. | The stair enclosure shall be pressurized to not less than 0.05 inch of water gage (12.44 Pa) positive pressure relative to the vestibule with all stairway doors closed under the maximum anticipated stack pressures. The vestibule, with doors closed, shall have not less than 0.05 inch of water gage (12.44 Pa) positive pressure relative to the fire floor. The pressure difference across doors shall not exceed 30 pounds (133-N) maximum force to begin opening the door.
|  | 909.20.6.3 Dampered relief opening. | A controlled relief vent having the capacity to discharge not less than 2,500 cubic feet per minute (1180 L/s) of air at the design pressure difference shall be located in the upper portion of the pressurized exit enclosure.
|  | 909.20.7 Ventilating equipment. | The activation of ventilating equipment required by the alternatives in Sections 909.20.4, 909.20.5 and 909.20.6 shall be by smoke detectors installed at each floor level at an approved location at the entrance to the smokeproof enclosure. When the closing device for the stairway and ramp shaft and vestibule doors is activated by smoke detection or power failure, the mechanical equipment shall activate and operate at the required performance levels. Smoke detectors shall be installed in accordance with Section 907.3.
|  | 909.20.7.1 Ventilation systems. | Smokeproof enclosure ventilation systems shall be independent of other building ventilation systems. The equipment, control wiring, power wiring and ductwork shall comply with one of the following: 1. Equipment, control wiring, power wiring and ductwork shall be located exterior to the building and direct-ly connected to the smokeproof enclosure or connected to the smokeproof enclosure by ductwork en-closed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal as-semblies constructed in accordance with Section 711, or both. 2. Equipment, control wiring, power wiring and ductwork shall be located within the smokeproof enclosure with intake or exhaust directly from and to the outside or through ductwork enclosed by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in ac-cordance with Section 711, or both. 3. Equipment, control wiring, power wiring and ductwork shall be located within the building if separated from the remainder of the building, including other mechanical equipment, by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. Exception: 1. Control wiring and power wiring located outside of a 2-hour fire barrier construction shall be protect-ed using any one of the following methods: 1.1. Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 2 hours. 1.2. Where encased with not less than 2 inches (51 mm) of concrete. 1.3. Electrical circuit protective systems shall have a fire-resistance rating of not less than 2 hours. Electrical circuit protective systems shall be installed in accordance with their listing requirements.
|  | 909.20.7.2 Standby power. | Mechanical vestibule and stairway and ramp shaft ventilation systems and automatic fire detection systems shall be provided with standby power in accordance with Section 2702.
|  | 909.20.7.3 Acceptance and testing. | Before the mechanical equipment is approved, the system shall be tested in the presence of the building official to confirm that the system is operating in compliance with these requirements.
|  | 909.21.7 Testing. | Testing for performance shall be required in accordance with Section 909.18.8. System acceptance shall be in accordance with Section 909.19.
|  | 909.21.10 Control panel. | A control panel complying with Section 909.16 shall be provided.
|  | 910.3.4 Vent operation. | Smoke and heat vents shall be capable of being operated by approved automatic and manual means.
|  | 910.3.5 Fusible link temperature rating. | Where vents are installed in areas provided with automatic fire sprinklers and the vents operate by fusible link, the fusible link shall have a temperature rating of 360°F (182°C).
|  | 911.1.2 Separation. | The fire command center shall be separated from the remainder of the building by not less than a 1-hour fire barrier constructed in accordance with Section 707 or horizontal assembly constructed in accordance with Section 711, or both.
|  | 911.1.3 Size. | The fire command center shall be not less than 0.015 percent of the total building area of the facility served or 200 square feet (19 m2) in area, whichever is greater, with a minimum dimension of 0.7 times the square root of the room area or 10 feet (3048 mm), whichever is greater. Where a fire command is required for Group F-1 and S-1 occupancies with a building footprint greater than 500,000 square feet (46 452 m2) in area, the fire command center shall have a minimum size of 96 square feet (9 m2) with a minimum dimension of 8 feet (2348 mm) where approved by the fire code official.
|  | 911.1.4 Layout approval. | A layout of the fire command center and all features required by this section to be contained therein shall be submitted for approval prior to installation.
|  | 911.1.7 Fire command center identification. | The fire command center shall be identified by a permanent easily visible sign reading FIRE COMMAND CENTER located on the door to the fire command center.
|  | 912.2.1 Visible location. | Fire department connections shall be located on the street side of buildings or facing approved fire apparatus access roads, fully visible and recognizable from the street, fire apparatus access road or nearest point of fire department vehicle access or as otherwise approved by the fire code official.
|  | 912.4.1 Locking fire department connection caps. | The fire code official is authorized to require locking caps on fire department connections for water-based fire protection systems where the responding fire department carries appropriate key wrenches for removal.
|  | 913.4.1 Test outlet valve supervision. | Fire pump test outlet valves shall be supervised in the closed position.
|  | 915.1 General. | Carbon monoxide detection shall be installed in new buildings in accordance with Sections 915.1.1 through 915.6. Carbon monoxide detection shall be installed in existing buildings in accordance with Chapter 11 of the International Fire Code.
|  | 915.1.1 Where required. | Carbon monoxide detection shall be provided in Group I-1, I-2, I-4 and R occupancies and in classrooms in Group E occupancies in the locations specified in Section 915.2 where any of the conditions in Sections 915.1.2 through 915.1.6 exist.
|  | 915.1.2 Fuel-burning appliances and fuel-burning fireplaces. | Carbon monoxide detection shall be provided in dwelling units, sleeping units and classrooms that contain a fuel-burning appliance or a fuel-burning fireplace.
|  | 915.1.3 Fuel burning, forced-air furnaces. | Carbon monoxide detection shall be provided in dwelling units, sleeping units and classrooms served by a fuel-burning, forced-air furnace. Exception: Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms if a carbon monoxide detector is provided in the first room or area served by each main duct leaving the furnace, and the carbon monoxide alarm signals are automatically transmitted to an approved location.
|  | 915.1.4 Fuel-burning appliances outside of dwelling units, sleeping units and classrooms. | Carbon monoxide detection shall be provided in dwelling units, sleeping units and classrooms located in buildings that contain fuel-burning appliances or fuel-burning fireplaces. Exceptions: 1. Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms without communicating openings between the fuel-burning appliance or fuel-burning fireplace and the dwelling unit, sleeping unit or classroom. 2. Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms where a carbon monoxide detector is provided in one of the following locations: 2.1. In an approved location between the fuel-burning appliance or fuel-burning fireplace and the dwelling unit, sleeping unit or classroom. 2.2. On the ceiling of the room containing the fuel-burning appliance or fuel-burning fireplace.
|  | 915.1.5 Private garages. | Carbon monoxide detection shall be provided in dwelling units, sleeping units and classrooms in buildings with attached private garages. Exceptions: 1. Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms without communicating openings between the private garage and the dwelling unit, sleeping unit or classroom. 2. Carbon monoxide detection shall not be required in dwelling units, sleeping units and classrooms located more than one story above or below a private garage. 3. Carbon monoxide detection shall not be required where the private garage connects to the building through an open-ended corridor. 4. Where a carbon monoxide detector is provided in an approved location between openings to a private garage and dwelling units, sleeping units or classrooms.
|  | 915.1.6 Exempt garages. | For determining compliance with Section 915.1.5, an open parking garage complying with Section 406.5 or an enclosed parking garage complying with Section 406.6 shall not be considered a private garage.
|  | 915.2 Locations. | Where required by Section 915.1.1, carbon monoxide detection shall be installed in the locations specified in Sections 915.2.1 through 915.2.3.
|  | 915.2.1 Dwelling units. | Carbon monoxide detection shall be installed in dwelling units outside of each separate sleeping area in the immediate vicinity of the bedrooms. Where a fuel-burning appliance is located within a bedroom or its attached bathroom, carbon monoxide detection shall be installed within the bedroom.
|  | 915.2.2 Sleeping units. | Carbon monoxide detection shall be installed in sleeping units. Exception: Carbon monoxide detection shall be allowed to be installed outside of each separate sleeping area in the immediate vicinity of the sleeping unit where the sleeping unit or its attached bathroom does not contain a fuel-burning appliance and is not served by a forced air furnace.
|  | 915.2.3 Group E occupancies. | Carbon monoxide detectors shall be installed in classrooms in Group E occupancies. Carbon monoxide alarm signals shall be automatically transmitted to an on-site location that is staffed by school personnel. Exception: Carbon monoxide alarm signals shall not be required to be automatically transmitted to an on-site lo-cation that is staffed by school personnel in Group E occupancies with an occupant load of 30 or less.
|  | 915.3 Carbon monoxide detection. | Carbon monoxide detection required by Sections 915.1 through 915.2.3 shall be provided by carbon monoxide alarms complying with Section 915.4 or carbon monoxide detection systems complying with Section 915.5.
|  | 915.4 Carbon monoxide alarms. | Carbon monoxide alarms shall comply with Sections 915.4.1 through 915.4.4.
|  | 915.4.1 Power source. | Carbon monoxide alarms shall receive their primary power from the building wiring where such wiring is served from a commercial source, and when primary power is interrupted, shall receive power from a battery. Wiring shall be permanent and without a disconnecting switch other than that required for overcurrent protection. Exception: Where installed in buildings without commercial power, battery-powered carbon monoxide alarms shall be an acceptable alternative.
|  | 915.4.2 Listings. | Carbon monoxide alarms shall be listed in accordance with UL 2034.
|  | 915.4.3 Locations. | Carbon monoxide alarms shall only be installed in dwelling units and in sleeping units. They shall not be installed in locations where the code requires carbon monoxide detectors to be used.
|  | 915.4.4 Combination alarms. | Combination carbon monoxide/smoke alarms shall be an acceptable alternative to carbon monoxide alarms. Combination carbon monoxide/smoke alarms shall be listed in accordance with UL 217 and UL 2034.
|  | 915.5 Carbon monoxide detection systems. | Carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide alarms and shall comply with Sections 915.5.1 through 915.5.3.
|  | 915.5.1 General. | Carbon monoxide detection systems shall comply with NFPA 720. Carbon monoxide detectors shall be listed in accordance with UL 2075.
|  | 915.5.2 Locations. | Carbon monoxide detectors shall be installed in the locations specified in Section 915.2. These locations supersede the locations specified in NFPA 720.
|  | 915.5.3 Combination detectors. | Combination carbon monoxide/smoke detectors installed in carbon monoxide detection systems shall be an acceptable alternative to carbon monoxide detectors, provided that they are listed in accordance with UL 268 and UL 2075.
|  | 915.6 Maintenance. | Carbon monoxide alarms and carbon monoxide detection systems shall be maintained in accordance with the International Fire Code.
|  | 916.1 Gas detection systems. | Gas detection systems required by this code shall comply with Sections 916.2 through 916.11.
|  | 916.2 Permits. | Permits shall be required as set forth in Section 105.6.10 of the International Fire Code.
|  | 916.2.1 Construction documents. | Documentation of the gas detection system design and equipment to be used that demonstrates compliance with the requirements of this code and the International Fire Code shall be provided with the application for permit.
|  | 916.3 Equipment. | Gas detection system equipment shall be designed for use with the gases being detected and shall be installed in accordance with manufacturer’s instructions.
|  | 916.4 Power connections. | Gas detection systems shall be permanently connected to the building electrical power supply or shall be permitted to be cord connected to an unswitched receptacle using an approved restraining means that secures the plug to the receptacle.
|  | 916.5 Emergency and standby power. | Standby or emergency power shall be provided or the gas detection system shall initiate a trouble signal at an approved location if the power supply is interrupted.
|  | 916.6 Sensor locations. | Sensors shall be installed in approved locations where leaking gases are expected to accumulate.
|  | 916.7 Gas sampling. | Gas sampling shall be performed continuously. Sample analysis shall be processed immediately after sampling, except as follows:
|  | 916.8 System activation. | A gas detection alarm shall be initiated where any sensor detects a concentration of gas exceeding the following thresholds:
|  | 916.9 Signage. | Signs shall be provided adjacent to gas detection system alarm signaling devices that advise occupants of the nature of the signals and actions to take in response to the signal.
|  | 916.10 Fire alarm system connections. | Gas sensors and gas detection systems shall not be connected to fire alarm systems unless approved and connected in accordance with the fire alarm equipment manufacturer’s instructions.
|  | 916.11 Inspection, testing and sensor calibration. | Gas detection systems and sensors shall be inspected, tested and calibrated in accordance with the International Fire Code.
|  | 917.1 College and university campuses. | Prior to construction of a new building requiring a fire alarm system on a multiple-building college or university campus having a cumulative building occupant load of 1,000 or more, a mass notification risk analysis shall be conducted in accordance with NFPA 72. Where the risk analysis determines a need for mass notification, an approved mass notification system shall be provided in accordance with the findings of the risk analysis.
|  | 918.1 General. | In-building two-way emergency responder communication coverage shall be provided in all new buildings in accordance with Section 510 of the International Fire Code.

## BC10
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1001.1 General. | Buildings or portions thereof shall be provided with a means of egress system as required by this chapter. The provisions of this chapter shall control the design, construction and arrangement of means of egress components required to provide an approved means of egress from structures and portions thereof. | 1001.1 General. | Buildings or portions thereof shall be provided with a means of egress system as required by this chapter. The provisions of this chapter shall control the design, construction and arrangement of means of egress components required to provide an approved means of egress from structures and portions thereof.
1001.2 Minimum requirements. | It shall be unlawful to alter a building or structure in a manner that will reduce the number of exits or the minimum width or required capacity of the means of egress to less than required by this code. | 1001.2 Minimum requirements. | It shall be unlawful to alter a building or structure in a manner that will reduce the number of exits or the minimum width or required capacity of the means of egress to less than required by this code.
1001.3 Maintenance. | Means of egress shall be maintained in accordance with the New York City Fire Code.
1003.1 Applicability. | The general requirements specified in Sections 1003 through 1015 shall apply to all three elements of the means of egress system, in addition to those specific requirements for the exit access, the exit and the exit discharge detailed elsewhere in this chapter. | 1003.1 Applicability. | The general requirements specified in Sections 1003 through 1015 shall apply to all three elements of the means of egress system, in addition to those specific requirements for the exit access, the exit and the exit discharge detailed elsewhere in this chapter.
1001.3.1 Workplace exits. | Except as specifically provided for in this chapter, no employer or agent of such employer shall lock the doors of or otherwise prohibit exit from any workplace, when by so doing the health or safety of any employee, independent contractor or other individual working in such workplace may become endangered by fire or other hazardous condition. Refer to Article 307 of Title 28 of the Administrative Code.
1003.2 Ceiling height. | The means of egress shall have a ceiling height of not less than 7 feet, 6 inches (2286 mm). Exceptions: 1. Ceilings that are permitted to be less than 7 feet, 6 inches (2286 mm) in accordance with Section 1208.2. 2. Ceilings of dwelling units and sleeping units within residential occupancies in accordance with Section 1208.2. 3. Allowable projections in accordance with Section 1003.3. 4. Stair headroom in accordance with Section 1011.3. 5. Door height in accordance with Section 1010.1.3. 6. Ramp headroom in accordance with Section 1012.5.2. 7. The clear height of floor levels in vehicular and pedestrian traffic areas of public and private parking garages in accordance with Section 406.4.1. 8. Areas above and below mezzanine floors in accordance with Section 505.2. | 1003.2 Ceiling height. | The means of egress shall have a ceiling height of not less than 7 feet 6 inches (2286 mm) above the finished floor.
1001.3.2 Inadequate exits for existing structures. | Every existing structure which is not provided with means of egress as required by this chapter and, in which the means of egress are, in the opinion of the commissioner, inadequate for the safety of the occupants, shall be provided with means of egress or fire protection as directed by the commissioner.
1003.3 Protruding objects. | Protruding objects on circulation paths shall comply with the requirements of Sections 1003.3.1 through 1003.3.4. | 1003.3 Protruding objects. | Protruding objects on circulation paths shall comply with the requirements of Sections 1003.3.1 through 1003.3.4.
1001.4 Fire protection and emergency preparedness plans. | Fire protection plans shall be provided for occupancies and buildings where required by Article 109 of the Administrative Code. Such fire protection plans shall comply with the applicable provisions of Section 28-109.3 of the Administrative Code. Emergency preparedness plans shall be provided for occupancies and buildings where required by the New York City Fire Code. Such emergency preparedness plans shall comply with the applicable provisions of Chapter 4 of the New York City Fire Code.
1003.3.1 Headroom. | Protruding objects are permitted to extend below the minimum ceiling height required by Section 1003.2 where a minimum headroom of 84 inches (2133.6 mm) is provided over any walking surface, including walks, corridors, aisles and passageways. Not more than 50 percent of the ceiling area of a means of egress shall be reduced in height by protruding objects. Exception: Door closers and stops shall not reduce headroom to less than 78 inches (1981.2 mm). | 1003.3.1 Headroom. | Protruding objects are permitted to extend below the minimum ceiling height required by Section 1003.2 where a minimum headroom of 80 inches (2032 mm) is provided over any circulation paths, including walks, corridors, aisles and passageways. Not more than 50 percent of the ceiling area of a means of egress shall be reduced in height by protruding objects.
1002.1 Definitions. | This section contains terms defined elsewhere in the code, and terms with definitions that are specific to this section.
1003.3.2 Post-mounted objects. | A free-standing object mounted on a post or pylon shall not overhang that post or pylon more than 4 inches (101.6 mm) where the lowest point of the leading edge is more than 27 inches (685 mm) and less than 80 inches (2032 mm) above the walking surface. Where a sign or other obstruction is mounted between posts or pylons and the clear distance between the posts or pylons is greater than 12 inches (304.8 mm), the lowest edge of such sign or obstruction shall be 27 inches (685 mm) maximum or 80 inches (2032 mm) minimum above the finished floor or ground. Exception: These requirements shall not apply to sloping portions of handrails between the top and bottom riser of stairs and above the ramp run. | 1003.3.2 Post-mounted objects. | A free-standing object mounted on a post or pylon shall not overhang that post or pylon more than 4 inches (102 mm) where the lowest point of the leading edge is more than 27 inches (686 mm) and less than 80 inches (2032 mm) above the finished floor. Where a sign or other obstruction is mounted between posts or pylons and the clear distance between the posts or pylons is greater than 12 inches (305 mm), the lowest edge of such sign or obstruction shall be 27 inches (686 mm) maximum or 80 inches (2032 mm) minimum above the finished floor or ground.
1002.1.1 Terms defined elsewhere in this code. | The following terms are defined in Chapter 2: ACCESSIBLE MEANS OF EGRESS. AISLE. AISLE ACCESSWAY. ALTERNATING TREAD DEVICE. AREA OF RESCUE ASSISTANCE. ASSEMBLY SPACE. ASSISTED RESCUE PATH. BLEACHERS. BREAKOUT. COMMON PATH OF EGRESS TRAVEL. CORRIDOR. CORRIDOR, INTERIOR. CORRIDOR, PUBLIC. CROSS AISLE. DEAD END. DOOR, BALANCED. EGRESS COURT. EMERGENCY ESCAPE AND RESCUE OPENING. EXIT. EXIT ACCESS. EXIT ACCESS DOORWAY. EXIT ACCESS RAMP. EXIT ACCESS STAIRWAY. EXIT DISCHARGE. EXIT DISCHARGE, LEVEL OF. EXIT, HORIZONTAL. EXIT PASSAGEWAY. EXTERIOR EXIT RAMP. EXTERIOR EXIT STAIRWAY. FIRE EXIT HARDWARE. FIXED SEATING. FLIGHT. FLOOR AREA, GROSS. FLOOR AREA, NET. FOLDING AND TELESCOPIC SEATING. GRANDSTAND. GUARD. HANDRAIL. INTERIOR EXIT RAMP. INTERIOR EXIT STAIRWAY. LOW ENERGY POWER-OPERATED DOOR. MEANS OF EGRESS. MERCHANDISE PAD. NOSING. OCCUPANT LOAD. OCCUPANT SENSOR. OPEN-ENDED CORRIDOR. PANIC HARDWARE. PHOTOSENSOR. POWER-ASSISTED DOOR. POWER-OPERATED DOOR. PUBLIC WAY. RAMP. REFUGE AREA. SCISSOR STAIRWAY. SELF-LUMINOUS. SMOKE-PROTECTED ASSEMBLY SEATING. STAIR. STAIRWAY. STAIRWAY, SPIRAL. WINDER.
1003.3.3 Horizontal projections. | Objects with leading edges more than 27 inches (685 mm) and not more than 80 inches (2032‡ mm) above the floor shall not project horizontally more than 4 inches (101.6 mm) into the circulation path. Exception: Handrails are permitted to protrude 4½ inches (114.3 mm) from the wall. | 1003.3.3 Horizontal projections. | Objects with leading edges more than 27 inches (685 mm) and not more than 80 inches (2030 mm) above the finished floor shall not project horizontally more than 4 inches (102 mm) into the circulation path.
1002.1.2 Definitions specific to this chapter. | The following terms shall, for the purposes of this chapter, have the meanings shown herein:
1003.3.4 Clear width. | Protruding objects shall not reduce the minimum clear width of accessible routes. | 1003.3.4 Clear width. | Protruding objects shall not reduce the minimum clear width of accessible routes.
1003.5 Elevation change. | Where changes in elevation of less than 12 inches (304.8 mm) exist in the means of egress, sloped surfaces shall be used. Where the slope is greater than one unit vertical in 20 units horizontal (5-percent slope), ramps complying with Section 1012 shall be used. Where the difference in elevation is 6 inches (152.4 mm) or less, the ramp shall be equipped with handrails or floor finish materials that contrast with adjacent floor finish materials. Exceptions: At locations that are not required to be accessible by Chapter 11: 1. A single step with a maximum riser height of 7 inches (177.8 mm) is permitted for buildings with occupancies in Groups F, H, R-2, R-3, S and U at exterior doors. 2. A step with a single riser or a stair with two risers and a tread is permitted where the risers and treads comply with Section 1011.5, the minimum depth of the tread is 13 inches (330 mm) and not less than one handrail complying with Section 1014 is provided within 30 inches (762 mm) of the centerline of the normal path of egress travel on the step or stair. 3. A step is permitted in aisles serving seating that has a difference in elevation less than 12 inches (304.8 mm) provided that the risers and treads comply with Section 1029.13 and the aisle is provided with a handrail complying with Section 1029.15. | 1003.5 Elevation change. | Where changes in elevation of less than 12 inches (305 mm) exist in the means of egress, sloped surfaces shall be used. Where the slope is greater than one unit vertical in 20 units horizontal (5-percent slope), ramps complying with Section 1012 shall be used. Where the difference in elevation is 6 inches (152 mm) or less, the ramp shall be equipped with either handrails or floor finish materials that contrast with adjacent floor finish materials.
1003.6 Means of egress continuity. | The path of egress travel along a means of egress shall not be interrupted by a building element other than a means of egress component as specified in this chapter. Obstructions shall not be placed in the minimum width or required capacity of a means of egress component except projections permitted by this chapter. The minimum width or required capacity of a means of egress system shall not be diminished along the path of egress travel. | 1003.6 Means of egress continuity. | The path of egress travel along a means of egress shall not be interrupted by a building element other than a means of egress component as specified in this chapter. Obstructions shall not be placed in the minimum width or required capacity of a means of egress component except projections permitted by this chapter. The minimum width or required capacity of a means of egress system shall not be diminished along the path of egress travel.
1003.7 Elevators, escalators and moving walks. | Elevators, escalators and moving walks shall not be used as a component of a required means of egress from any other part of the building. Exceptions: 1. Elevators used as a component of an accessible means of egress in accordance with Section 1009.4. 2. Elevators permitted to be used for occupant self-evacuation pursuant to Sections 403.5.2 and 403.6.2. | 1003.7 Elevators, escalators and moving walks. | Elevators, escalators and moving walks shall not be used as a component of a required means of egress from any other part of the building.
1004.1 Design occupant load. | In determining means of egress requirements, the number of occupants for whom means of egress facilities shall be provided shall be established by the largest number computed in accordance with Section 1004.1.3, unless otherwise permitted by Section 1004.1.3.1, 1004.1.3.2 or 1004.2. | 1004.1 Design occupant load. | In determining means of egress requirements, the number of occupants for whom means of egress facilities are provided shall be determined in accordance with this section.
1003.4 Floor surface. | Walking surfaces of the means of egress shall have a slip-resistant surface and be securely attached.
1004.1.1 Cumulative occupant loads. | Cumulative occupant loads shall be determined in accordance with Sections 1004.1.1.1 and 1004.1.1.2.
1004.1.1.1 Cumulative occupant loads for interconnected spaces. | Where the path of egress travel includes intervening rooms, areas or spaces, cumulative occupant loads shall be determined in accordance with this section.
1004.1.1.1.1 Intervening spaces or accessory areas. | Where occupants egress from one or more rooms, areas or spaces through others, the design occupant load shall be the combined occupant load of interconnected accessory or intervening spaces. Design of egress path capacity shall be based on the cumulative portion of occupant loads of all rooms, areas or spaces to that point along the path of egress travel.
1004.1.1.1.2 Adjacent levels for mezzanines. | That portion of the occupant load of a mezzanine with required egress through a room, area or space on an adjacent level shall be added to the occupant load of that room, area or space.
1004.1.1.1.3 Adjacent stories. | Other than for the egress components designed for convergence in accordance with Section 1005.6, the occupant load from separate stories shall not be added.
1004.1.1.2 Cumulative occupant loads in Group R-2 occupancies. | Rooms, areas or spaces that are accessory to a Group R-2 occupancy and that comply with the conditions below may have occupant loads calculated individually per room, area, or space, and be classified as Occupancy Group R-2.
1005.1 General. | All portions of the means of egress system shall be sized in accordance with this section. Exception: Aisles and aisle accessways in rooms or spaces used for assembly purposes complying with Section 1029. | 1005.1 General. | All portions of the means of egress system shall be sized in accordance with this section.
1004.1.1.2.1 Maximum occupant load per room. | The occupant load in each individual room, area and space, including those subject to Section 1004.1.1.1.1 where applicable, shall not exceed 74 persons.
1005.2 Minimum width based on component. | The minimum width, in inches (mm), of any means of egress components shall be not less than that specified for such component, elsewhere in this code. | 1005.2 Minimum width based on component. | The minimum width, in inches (mm), of any means of egress components shall be not less than that specified for such component, elsewhere in this code.
1004.1.1.2.2 Separated rooms. | Each individual room, area and space shall be separated from others by minimum 1-hour fire-resistance-rated fire barriers constructed in accordance with Section 707. Opening protectives in accordance with Exception 3 of Section 707.6 shall not be permitted.
1005.3 Required capacity based on occupant load. | The required capacity, in inches (mm), of the means of egress for any room, area, space or story shall be not less than that determined in accordance with Sections 1005.3.1 and 1005.3.2. | 1005.3 Required capacity based on occupant load. | The required capacity, in inches (mm), of the means of egress for any room, area, space or story shall be not less than that determined in accordance with Sections 1005.3.1 and 1005.3.2.
1004.1.1.2.3 Group R-2 accessory spaces as primary function on a story. | Where the aggregate Group R-2 occupancy accessory area of all rooms, areas or spaces, including outdoor spaces that are not provided with independent means of egress and that do not converge into interior means of egress, exceed 50 percent of the building area of the story in which they are located, and the total number of occupants on such story exceeds 150 persons, the following conditions shall apply: The interior corridors or portions thereof serving such accessory spaces shall be constructed as public corridors in accordance with Table 1020.1.2 with 1-hour fire-resistance-rated fire barriers, and 2-hour fire-resistance-rated fire barriers where a dead-end corridor exceeds 40 feet (12 192 mm) in length; 2. Access to the corridors shall be limited to those necessary for exit access through the corridor from normally occupied spaces. Direct openings from the mechanical, electrical and other storage spaces shall not be permitted, except that access to the corridor may be provided through a vestibule constructed with fire barriers, with a minimum fire-resistance rating consistent with the required hourly rating for the corridor; 3. Corridors or portions thereof serving such accessory spaces shall be sufficient to accommodate a total occupant load on the basis of 3 square feet (0.28 m2) per person; 4. The minimum dimension of such corridors shall be sufficient to accommodate the total occupant load discharging into such corridors, but shall in no case be less than 5 feet (1524 mm) in minimum dimension; and 5. In addition to Conditions 1 through 4 above, one of the following conditions shall be met: 5.1. Each of the interior exit stairways and ramps serving such story shall be protected by a smokeproof enclosure in accordance with Section 909.20; 5.2. The corridor or portions of the corridor serving the rooms, areas or spaces that are accessory to the Group R-2 occupancy shall be pressurized in accordance with requirements that are applicable to interior exit stairways. Connecting interior exit stairways need not be pressurized unless otherwise required by this code; 5.3. All passenger elevators serving the rooms, areas, or spaces that are accessory to the Group R-2 occupancy shall comply with occupant self-evacuation elevator requirements in Section 3008.1 through 3008.11; or 5.4. One additional exit stairway meeting the requirements of Sections 1009 and 1023 shall be provided in addition to the minimum number of exits required by Section 1006. The total width of any combination of remaining exit stairways with one exit stairway removed shall not be less than the total width required by Section 1005.3. Rooms, areas or spaces that do not comply with the conditions in Sections 1004.1.1.2.1 and 1004.1.1.2.2, or Section 1004.1.1.2.3 where applicable, shall have occupant loads calculated cumulatively per story and be classified as Occupancy Group A. |  |  |  | See BC10 Tables&Figures
1005.3.1 Stairways. | The capacity, in inches, of means of egress stairways shall be calculated by multiplying the occupant load served by such stairways by a means of egress capacity factor of 0.3 inch (7.6 mm) per occupant. Where stairways serve more than one story, only the occupant load of each story considered individually shall be used in calculating the required capacity of the stairways serving that story. Exceptions: 1. Facilities with smoke-protected assembly seating shall be permitted to use the capacity factors in Table 1029.6.2 indicated for stepped aisles for exit access or exit stairways where the entire path for means of egress from the seating to the exit discharge is provided with a smoke control system complying with Section 909. 2. Facilities with outdoor smoke-protected assembly seating shall be permitted to the capacity factors in Section 1029.6.3 indicated for stepped aisles for exit access or exit stairways where the entire path for means of egress from the seating to the exit discharge is open to the outdoors. | 1005.3.1 Stairways. | The capacity, in inches, of means of egress stairways shall be calculated by multiplying the occupant load served by such stairways by a means of egress capacity factor of 0.3 inch (7.6 mm) per occupant. Where stairways serve more than one story, only the occupant load of each story considered individually shall be used in calculating the required capacity of the stairways serving that story. |  | See BC10 Tables&Figures
1004.1.2 Multiple function occupant load. | Where an area under consideration contains multiple functions having different occupant load factors, the design occupant load for such area shall be based on the floor area of each function calculated independently.
1005.3.2 Other egress components. | The capacity, in inches, of means of egress components other than stairways shall be calculated by multiplying the occupant load served by such component by a means of egress capacity factor of 0.2 inch (5.1 mm) per occupant. Exceptions: 1. Facilities with smoke-protected assembly seating shall be permitted to use the capacity factors in Table 1029.6.2 indicated for level or ramped aisles for means of egress components other than stairways where the entire path for means of egress from the seating to the exit discharge is provided with a smoke control system complying with Section 909. 2. Facilities with outdoor smoke-protected assembly seating shall be permitted to the capacity factors in Section 1029.6.3 indicated for level or ramped aisles for means of egress components other than stairways where the entire path for means of egress from the seating to the exit discharge is open to the outdoors. | 1005.3.2 Other egress components. | The capacity, in inches, of means of egress components other than stairways shall be calculated by multiplying the occupant load served by such component by a means of egress capacity factor of 0.2 inch (5.1 mm) per occupant. |  | See BC10 Tables&Figures
1004.1.3 Areas without fixed seating. | The number of occupants shall be computed at the rate of one occupant per unit of area as prescribed in Table 1004.1.3. For areas without fixed seating, the occupant load shall be not less than that number determined by dividing the floor area under consideration by the occupant load factor assigned to the function of the space as set forth in Table 1004.1.3. |  |  |  | See BC10 Tables&Figures
1005.4 Continuity. | The minimum width or required capacity of the means of egress required from any story of a building shall not be reduced along the path of egress travel until arrival at the public way. | 1005.4 Continuity. | The minimum width or required capacity of the means of egress required from any story of a building shall not be reduced along the path of egress travel until arrival at the public way.
1004.1.3.1 Modifications. | Where the actual number of occupants of any space will be significantly lower than listed in Table 1004.1.3, the commissioner may establish a lower basis for the determination of the number of occupants. |  |  |  | See BC10 Tables&Figures
1005.5 Distribution of minimum width and required capacity. | Where more than one exit, or access to more than one exit, is required, the means of egress shall be configured such that the loss of any one exit, or access to one exit, shall not reduce the available capacity or width to less than 50 percent of the required capacity or width. | 1005.5 Distribution of minimum width and required capacity. | Where more than one exit, or access to more than one exit, is required, the means of egress shall be configured such that the loss of any one exit, or access to one exit, shall not reduce the available capacity or width to less than 50 percent of the required capacity or width.
1004.1.3.2 Unlisted functions. | Where data regarding the square feet area per person for a function is not listed in Table 1004.1.3, the occupant load shall be established by a registered design professional, subject to the approval of the commissioner. |  |  |  | See BC10 Tables&Figures
1005.6 Egress convergence. | Where the means of egress from stories above and below converge at an intermediate level, the capacity of the means of egress from the point of convergence shall be not less than the largest minimum width or the sum of the required capacities for the stairways or ramps serving the two adjacent stories, whichever is larger. | 1005.6 Egress convergence. | Where the means of egress from stories above and below converge at an intermediate level, the capacity of the means of egress from the point of convergence shall be not less than the largest minimum width or the sum of the required capacities for the stairways or ramps serving the two adjacent stories, whichever is larger.
1004.2 Increased occupant load. | The occupant load permitted in any building, or portion thereof, is permitted to be increased from that number established for the functions in Table 1004.1.3, provided that all other requirements of the code are also met based on such modified number and the occupant load shall not exceed one occupant per 5 square feet (0.46 m2) of occupiable floor space, except for safe areas as specified in Section 1029.19.3 and standee areas as specified in Section 1029.18. Where required by the commissioner, an approved aisle, seating or fixed equipment diagram substantiating any increase in occupant load shall be submitted. Where required by the commissioner, such diagram shall be posted. Capacity signs indicating the increased, stated occupant load in accordance with Sections 1029.1.3 and 1029.1.4 shall be posted where required by the commissioner. |  |  |  | See BC10 Tables&Figures
1005.7 Encroachment. | Encroachments into the required means of egress width shall be in accordance with the provisions of this section. | 1005.7 Encroachment. | Encroachments into the required means of egress width shall be in accordance with the provisions of this section.
1004.3 Fixed seating. | For areas having fixed seats and aisles, the occupant load shall be determined by the number of fixed seats installed therein. The occupant load for areas in which fixed seating is not installed, such as waiting spaces, shall be determined in accordance with Section 1004.1.3 and added to the number of fixed seats.
1005.7.1 Doors. | Doors, when fully opened, shall not reduce the required width by more than 7 inches (177.8 mm). Doors in any position shall not reduce the required width by more than one-half. Exceptions: 1. Surface-mounted latch release hardware shall be exempt from inclusion in the 7-inch (177.8 mm) maximum encroachment where both of the following conditions exist: 1.1. The hardware is mounted to the side of the door facing away from the adjacent wall where the door is in the open position. 1.2. The hardware is mounted not less than 34 inches (865 mm) nor more than 48 inches (1220 mm) above the finished floor. 2. The restrictions on door swing shall not apply to doors within individual dwelling units and sleeping units of Group R-2 occupancies and within individual dwelling units of Group R-3 occupancies. | 1005.7.1 Doors. | Doors, when fully opened, shall not reduce the required width by more than 7 inches (178 mm). Doors in any position shall not reduce the required width by more than one-half.
1004.4 Outdoor areas. | Yards, patios, courts and similar outdoor areas accessible to and usable by the building occupants shall be provided with means of egress as required by this chapter. The occupant load of such outdoor areas shall be determined by the design professional subject to the approval of the commissioner. Where outdoor areas are to be used by persons in addition to the occupants of the building, and the path of egress travel from the outdoor areas passes through the building, means of egress requirements for the building shall be based on the sum of the occupant loads of the building plus the outdoor areas. Exceptions: 1. Outdoor areas used exclusively for service of the building need only have one means of egress. 2. Both outdoor areas associated with Group R-3 and individual dwelling units of Group R-2.
1005.7.2 Other projections. | Handrail projections shall be in accordance with the provisions of Section 1014.8. Other nonstructural projections such as trim and similar decorative features shall be permitted to project into the required width not more than 1½ inches (38.1 mm) on each side. Exception: Projections are permitted in corridors within Group I-2 in accordance with Section 407.4.3. | 1005.7.2 Other projections. | Handrail projections shall be in accordance with the provisions of Section 1014.8. Other nonstructural projections such as trim and similar decorative features shall be permitted to project into the required width not more than 11/2 inches (38 mm) on each side.
1004.5 Multiple occupancies. | Where a building contains two or more occupancies, the means of egress requirements shall apply to each portion of the building based on the occupancy of that space. Where two or more occupancies utilize portions of the same means of egress system, those egress components shall meet the more stringent requirements of all occupancies that are served.
1005.7.3 Protruding objects. | Protruding objects shall comply with the applicable requirements of Section 1003.3. | 1005.7.3 Protruding objects. | Protruding objects shall comply with the applicable requirements of Section 1003.3.
1006.1 General. | The number of exits or exit access doorways required within the means of egress system shall comply with the provisions of Section 1006.2 for spaces, including mezzanines, and Section 1006.3 for stories. | 1006.1 General. | The number of exits or exit access doorways required within the means of egress system shall comply with the provisions of Section 1006.2 for spaces, including mezzanines, and Section 1006.3 for stories or occupied roofs.
1006.2 Egress from spaces. | Rooms, areas or spaces, including mezzanines, within a story or basement shall be provided with the number of exits or access to exits in accordance with this section. | 1006.2 Egress from spaces. | Rooms, areas or spaces, including mezzanines, within a story or basement shall be provided with the number of exits or access to exits in accordance with this section.
1006.2.1 Egress based on occupant load and common path of egress travel distance. | Two exits or exit access doorways from any space shall be provided where the design occupant load or the common path of egress travel distance exceeds the values listed in Table 1006.2.1. Exception: Care suites in Group I-2 occupancies complying with Section 407.4. | 1006.2.1 Egress based on occupant load and common path of egress travel distance. | Two exits or exit access doorways from any space shall be provided where the design occupant load or the common path of egress travel distance exceeds the values listed in Table 1006.2.1. The cumulative occupant load from adjacent rooms, areas or spaces shall be determined in accordance with Section 1004.2. |  | See BC10 Tables&Figures
1006.2.1.1 Three or more exits or exit access doorways. | Three exits or exit access doorways shall be provided from any space with an occupant load of 501 to 1,000. Four exits or exit access doorways shall be provided from any space with an occupant load greater than 1,000. | 1006.2.1.1 Three or more exits or exit access doorways. | Three exits or exit access doorways shall be provided from any space with an occupant load of 501 to 1,000. Four exits or exit access doorways shall be provided from any space with an occupant load greater than 1,000.
1006.2.2 Egress based on use. | The numbers of exits or access to exits shall be provided in the uses described in Sections 1006.2.2.1 through 1006.2.2.5. | 1006.2.2 Egress based on use. | The numbers, configuration and types of components of exits or access to exits shall be provided in the uses described in Sections 1006.2.2.1 through 1006.2.2.6.
1006.2.2.1 Boiler, incinerator and furnace rooms. | Two exit access doorways are required in boiler, incinerator and furnace rooms where the area is over 500 square feet (46.5 m2) and any fuel-fired equipment exceeds 400,000 British thermal units (Btu) (422 000 KJ) input capacity. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the length of the maximum overall diagonal dimension of the room. | 1006.2.2.1 Boiler, incinerator and furnace rooms. | Two exit access doorways are required in boiler, incinerator and furnace rooms where the area is over 500 square feet (46 m2) and any fuel-fired equipment exceeds 400,000 British thermal units (Btu) (422 000 KJ) input capacity. Where two exit access doorways are required, one is permitted to be a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the length of the maximum overall diagonal dimension of the room.
1006.2.2.2 Refrigeration machinery rooms. | Machinery rooms larger than 1,000 square feet (92.9 m2) with refrigeration units or systems having a refrigerant circuit containing more than 220 pounds (100 kg) of Group A1 refrigerant, or more than 30 pounds (13.6 kg) of any other group refrigerant, as classified in Section 1103.1 of the New York City Mechanical Code, shall have not less than two exits or exit access doors. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the maximum horizontal dimension of the room. Exception: Where using refrigerants in quantities limited to the amounts based on the volume set forth in the New York City Mechanical Code. | 1006.2.2.2 Refrigeration machinery rooms. | Machinery rooms larger than 1,000 square feet (93 m2) shall have not less than two exits or exit access doorways. Where two exit access doorways are required, one such doorway is permitted to be served by a fixed ladder or an alternating tread device. Exit access doorways shall be separated by a horizontal distance equal to one-half the maximum horizontal dimension of the room.
1006.2.2.3 Refrigerated rooms or spaces. | Rooms or spaces having a floor area larger than 1,000 square feet (92.9 m2) containing a refrigerant evaporator and maintained at a temperature below 68°F (20°C), shall have access to not less than two exits or exit access doorways. | 1006.2.2.3 Refrigerated rooms or spaces. | Rooms or spaces having a floor area larger than 1,000 square feet (93 m2), containing a refrigerant evaporator and maintained at a temperature below 68°F (20°C), shall have access to not less than two exits or exit access doorways.
1006.2.2.5 Vehicular ramps. | Vehicular ramps shall not be considered as an exit access ramp unless provided with pedestrian facilities along the ramp in accordance with Section 1012.1. | 1006.2.2.5 Vehicular ramps. | Vehicular ramps shall not be considered as an exit access ramp unless pedestrian facilities are provided.
1006.3 Egress from stories or occupied roofs. | The means of egress system serving any story, or occupied roof designed for human occupancy or use, shall be provided with the number of exits or access to exits based on the aggregate occupant load served in accordance with this section. The path of egress travel to an exit shall not pass through more than one adjacent story. Exceptions: 1. Interior exit stairways and interior exit ramps are not required in open parking garages where the means of egress serves only the open parking garage. 2. Interior exit stairways and interior exit ramps are not required in outdoor facilities where all portions of the means of egress are essentially open to the outside. | 1006.3 Egress from stories or occupied roofs. | The means of egress system serving any story or occupied roof shall be provided with the number of separate and distinct exits or access to exits based on the aggregate occupant load served in accordance with this section.
1007.1 General. | Exits, exit access doorways, and exit access stairways and ramps serving spaces, including individual building stories, shall be separated in accordance with the provisions of this section. | 1007.1 General. | Exits, exit access doorways, and exit access stairways and ramps serving spaces, including individual building stories, shall be separated in accordance with the provisions of this section.
1007.1.1 Two exits or exit access doorways. | Where two exits, exit access doorways, exit access stairways or ramps, or any combination thereof, are required from any portion of the exit access, they shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between them. Stairs sharing any common wall, floor, ceiling, scissor stair assembly, or other enclosure shall be counted as one exit stairway. Exceptions: 1. Corridor measurements. Where interior exit stairways or ramps are interconnected by a 1-hour fire-resistance-rated corridor conforming to the requirements of Section 1020, the required exit separation shall be measured along the shortest direct line of travel within the corridor. 2. Remote location in sprinklered buildings. Where a building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance shall be not less than one-third of the length of the maximum overall diagonal dimension of the area served. 3. Group R-2 occupancies. In Group R-2 occupancies, where stairs are enclosed in walls having at least a 2-hour fire resistance rating and constructed of masonry or masonry equivalent in accordance with department rules: 3.1. The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and 3.2. Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies or other enclosures provided that the construction separating the stairs is also of at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules. 4. Group B occupancies. In Group B occupancies of construction Type I or II not exceeding 60 feet (18 288 mm) in height, not exceeding 2,000 square feet (185.8 m2) on any story and not exceeding a travel distance of 50 feet (15 240 mm) on any story, where stairs are enclosed in walls having at least a 2-hour fire-resistance rating and constructed of masonry or masonry equivalent in accordance with department rules: 4.1. The exit doors to such stairs shall be placed a distance apart equal to no less than 15 feet (4572 mm); and 4.2. Such stairs shall be permitted to share common walls, floors, ceilings or scissor stairs assemblies. | 1007.1.1 Two exits or exit access doorways. | Where two exits, exit access doorways, exit access stairways or ramps, or any combination thereof, are required from any portion of the exit access, they shall be placed a distance apart equal to not less than one-half of the length of the maximum overall diagonal dimension of the building or area to be served measured in a straight line between them. Interlocking or scissor stairways shall be counted as one exit stairway.
1007.1.1.1 Measurement point. | The separation distance required in Section 1007.1.1 shall be measured in accordance with the following: | 1007.1.1.1 Measurement point. | The separation distance required in Section 1007.1.1 shall be measured in accordance with the following:
1006.2.2.4 Day care means of egress. | Day care facilities, rooms or spaces that are classified under Occupancy Group E providing care for more than 10 children shall have access to not less than two exits or exit access doorways.
1007.1.2 Three or more exits or exit access doorways. | Where access to three or more exits is required, not less than two exit or exit access doorways shall be arranged in accordance with the provisions of Section 1007.1.1. Additional required exit or exit access doorways shall be arranged a reasonable distance apart so that if one becomes blocked, the others will be available. | 1007.1.2 Three or more exits or exit access doorways. | Where access to three or more exits is required, not less than two exit or exit access doorways shall be arranged in accordance with the provisions of Section 1007.1.1. Additional required exit or exit access doorways shall be arranged a reasonable distance apart so that if one becomes blocked, the others will be available.
1007.1.3 Remoteness of exit access stairways or ramps. | Where two exit access stairways or ramps provide the required means of egress to exits at another story, the required separation distance shall be maintained for all portions of such exit access stairways or ramps. | 1007.1.3 Remoteness of exit access stairways or ramps. | Where two exit access stairways or ramps provide the required means of egress to exits at another story, the required separation distance shall be maintained for all portions of such exit access stairways or ramps.
1007.1.3.1 Three or more exit access stairways or ramps. | Where more than two exit access stairways or ramps provide the required means of egress, not less than two shall be arranged in accordance with Section 1007.1.3. | 1007.1.3.1 Three or more exit access stairways or ramps. | Where more than two exit access stairways or ramps provide the required means of egress, not less than two shall be arranged in accordance with Section 1007.1.3.
1006.3.1 Egress based on occupant load. | Each story or occupied roof designed for human occupancy or use shall have the minimum number of exits, or access to exits, as specified in Table 1006.3.1. A single exit or access to a single exit shall be permitted in accordance with Section 1006.3.2. The required number of exits, or exit access stairways or ramps providing access to exits, from any such story or occupied roof shall be maintained until arrival at the exit discharge or a public way. |  |  |  | See BC10 Tables&Figures
1008.1 Means of egress illumination. | Illumination shall be provided in the means of egress in accordance with Section 1008.2. Under emergency power, means of egress illumination shall comply with Section 1008.3. | 1008.1 Means of egress illumination. | Illumination shall be provided in the means of egress in accordance with Section 1008.2. Under emergency power, means of egress illumination shall comply with Section 1008.3.
1006.3.2 Single exits. | A single exit or access to a single exit shall be permitted from any story or occupied roof designed for human occupancy or use where one of the following conditions exists:
1008.2 Illumination required. | Exits, exit discharges and public corridors shall be illuminated at all times by either daylight or electric lighting fixtures. Exit access components shall be illuminated by either daylight or electric lighting fixtures at all times that the space served by the exit access component is occupied.Exceptions: 1. Occupancies in Group U. 2. Aisle accessways in Group A. 3. Dwelling units and sleeping units in Groups I-1, R-1, R-2 and R-3. 4. Sleeping units of Group I occupancies. 5. Areas beyond safe dispersal area where such areas are provided, and designed in accordance with Section 1028.5, Exceptions 1 through 5. | 1008.2 Illumination required. | The means of egress serving a room or space shall be illuminated at all times that the room or space is occupied.
1006.3.2.1 Mixed occupancies. | Where one exit, or exit access stairway or ramp providing access to exits at other stories, is permitted to serve individual stories, mixed occupancies shall be permitted to be served by single exits provided each individual occupancy complies with the applicable requirements of Table 1006.3.2 for that occupancy. Where applicable, cumulative occupant loads from adjacent occupancies shall be considered in accordance with the provisions of Section 1004.1. In each story of a mixed occupancy building, the maximum number of occupants served by a single exit shall be such that the sum of the ratios of the calculated number of occupants of the space divided by the allowable number of occupants indicated in Table 1006.3.2 for each occupancy does not exceed one. Where dwelling units are located on a story with other occupancies, the actual number of dwelling units divided by four plus the ratio from the other occupancy does not exceed one. |  |  |  | See BC10 Tables&Figures
1008.2.1 Illumination level under normal power. | The means of egress illumination level shall be not less than 1 footcandle (11 lux) at the walking surface. Exceptions: 1. For auditoriums, theaters, concert or opera halls and similar assembly occupancies, the externally illuminated walking surface is permitted to be reduced during performances to not less than 0.5 footcandle (5.38 lux) for aisles and cross aisles, and 0.2 footcandle (2.15 lux) for other portions of the space, provided that the required illumination is automatically restored upon activation of a premise’s fire alarm system where such system is provided. 2. Safe areas in assembly occupancies shall be illuminated in accordance with Section 1029.19.3.2. 3. Open exterior spaces used to receive occupants as Class 1 or 2 exits in assembly occupancies shall be illuminated in accordance with Section 1029.19.4. 4. In exits in buildings that contain existing photoluminescent exit path markings tested in laboratory conditions with 2 footcandles (22 lux) of activating illumination, the illumination level shall not be less than 2 footcandles (22 lux). | 1008.2.1 Illumination level under normal power. | The means of egress illumination level shall be not less than 1 footcandle (11 lux) at the walking surface. Along exit access stairways, exit stairways and at their required landings, the illumination level shall not be less than 10 footcandles (108 lux) at the walking surface when the stairway is in use.
1006.4 Open or enclosed parking garages. | Open or enclosed parking garages shall not have less than two exits from each parking tier. An unenclosed vehicle ramp constructed in accordance with Section 1012.1 may serve as one of the required exits when provided with pedestrian facilities along the ramp. Such ramps serving as part of a nonaccessible means of egress in open or enclosed parking garages three stories or less in height and serving not more than one level below grade is permitted to comply with Section 1012.2, Exception 2. Exception: One exit shall be permitted in parking garages complying with Item 3 of Section 1006.3.2.
1008.3 Emergency power for illumination. | The power supply for means of egress illumination shall normally be provided by the premise’s electrical supply. | 1008.3 Emergency power for illumination. | The power supply for means of egress illumination shall normally be provided by the premises’ electrical supply.
1008.3.4 Duration. | The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 2702. | 1008.3.4 Duration. | The emergency power system shall provide power for a duration of not less than 90 minutes and shall consist of storage batteries, unit equipment or an on-site generator. The installation of the emergency power system shall be in accordance with Section 2702.
1008.3.5 Illumination level under emergency power. | Emergency lighting facilities shall be arranged to provide initial illumination that is not less than an average of 1 footcandle (11 lux) and a minimum at any point of 0.1 footcandle (1 lux) measured along the path of egress at floor level. Illumination levels shall be permitted to decline to 0.6 footcandle (6 lux) average and a minimum at any point of 0.06 footcandle (0.6 lux) at the end of the emergency lighting time duration. A maximum-to-minimum illumination uniformity ratio of 40 to 1 shall not be exceeded. In buildings that contain existing photoluminescent exit path markings tested in laboratory conditions with greater than 1 footcandle (11 lux) of activating, the initial illumination shall not be less than that required for activating the approved photoluminescent illumination. In Group I-2 occupancies, failure of any single lighting unit shall not reduce the illumination level to less than 0.2 footcandle (2.2 lux). | 1008.3.5 Illumination level under emergency power. | Emergency lighting facilities shall be arranged to provide initial illumination that is not less than an average of 1 footcandle (11 lux) and a minimum at any point of 0.1 footcandle (1 lux) measured along the path of egress at floor level. Illumination levels shall be permitted to decline to 0.6 footcandle (6 lux) average and a minimum at any point of 0.06 footcandle (0.6 lux) at the end of the emergency lighting time duration. A maximum-to-minimum illumination uniformity ratio of 40 to 1 shall not be exceeded. In Group I-2 occupancies, failure of a single lamp in a luminaire shall not reduce the illumination level to less than 0.2 footcandle (2.2 lux).
1009.1 Accessible means of egress required. | Accessible means of egress shall comply with this section. Accessible spaces shall be provided with not less than one accessible means of egress. Where more than one means of egress are required by Section 1006.2 or 1006.3 from any accessible space, each accessible portion of the space shall be served by not less than two accessible means of egress. Exceptions: 1. Accessible means of egress are not required in alterations to prior code buildings where the level of alterations does not trigger full compliance of accessibility pursuant to Section 28-101.4 of the Administrative Code. 2. One accessible means of egress is required from an accessible mezzanine level in accordance with Section 1009.3, 1009.4 or 1009.5. 3. In assembly areas with ramped aisles or stepped aisles, one accessible means of egress is permitted where the common path of egress travel is accessible and meets the requirements in Section 1029.8. | 1009.1 Accessible means of egress required. | Accessible means of egress shall comply with this section. Accessible spaces shall be provided with not less than one accessible means of egress. Where more than one means of egress is required by Section 1006.2 or 1006.3 from any accessible space, each accessible portion of the space shall be served by not less than two accessible means of egress.
1009.2 Continuity and components. | Each required accessible means of egress shall be continuous to a public way and shall consist of one or more of the following components: | 1009.2 Continuity and components. | Each required accessible means of egress shall be continuous to a public way and shall consist of one or more of the following components:
1008.2.2 Exit discharge. | In Group I-2 occupancies where two or more exits are required, on the exterior landings required by Section 1010.1.6, means of egress illumination levels for the exit discharge shall be provided such that failure of any single lighting unit shall not reduce the illumination level on that landing to less than 1 footcandle (11 lux).
1008.2.3 Sensors and controls. | Automatic, occupant sensor or photosensor lighting controls shall be permitted within means of egress, provided that the illumination level is not reduced to a level below the minimum requirements of Section 1008.2.1, and the switch controllers are equipped for fail-safe operation ensuring that if the sensor or control fails, the lighting levels will be at the levels required by Section 1008.2.1.
1009.3 Stairways. | To be considered part of an accessible means of egress, a stairway between stories shall have a clear width of 48 inches (1220 mm) minimum between handrails and shall either incorporate an area of rescue assistance within an enlarged floor-level landing or shall be accessed from an area of rescue assistance complying with Section 1009.6. Exit access stairways that connect levels in the same story are not permitted as part of an accessible means of egress. | 1009.3 Stairways. | In order to be considered part of an accessible means of egress, a stairway between stories shall comply with Sections 1009.3.1 through 1009.3.3.
1008.3.1 Rooms and spaces that require two or more means of egress. | In the event of power supply failure in rooms and spaces that require two or more means of egress, an emergency electrical system shall automatically illuminate all of the following areas:
1008.3.2 Buildings that require two or more means of egress. | In the event of power supply failure in buildings that require two or more means of egress, an emergency electrical system shall automatically illuminate all of the following areas:
1008.3.3 Specific rooms and spaces. | In the event of power supply failure, an emergency electrical system shall automatically illuminate all of the following areas:
1009.4 Elevators. | To be considered part of an accessible means of egress, an elevator shall comply with the emergency operation and signaling device requirements of Section 2.27 of ASME A17.1 as modified by Appendix K, and Section 1109.7 of this code. Standby power shall be provided in accordance with Chapter 27 and Section 3003. The elevator shall be accessed from an area of rescue assistance complying with Section 1009.6. Exceptions: 1. Areas of rescue assistance are not required at the elevator in open parking garages. 2. Areas of rescue assistance are not required in buildings and facilities equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 3. Areas of rescue assistance are not required at elevators not required to be located in a shaft in accordance with Section 712. 4. Areas of rescue assistance are not required at elevators serving smoke-protected assembly seating areas complying with Section 1029.6.2. 5. Areas of rescue assistance are not required for elevators accessed from a refuge area in conjunction with a horizontal exit. | 1009.4 Elevators. | In order to be considered part of an accessible means of egress, an elevator shall comply with Sections 1009.4.1 and 1009.4.2.
1009.5 Platform lifts. | Platform (wheelchair) lifts shall be permitted to serve as part of an accessible means of egress where allowed as part of a required accessible route in Section 1109.8, except for Item 10. Platform lifts shall be installed in accordance with ASME A18.1. Standby power for the platform lift shall be provided in accordance with Chapter 27 for platform lifts permitted to serve as part of an accessible means of egress. | 1009.5 Platform lifts. | Platform lifts shall be permitted to serve as part of an accessible means of egress where allowed as part of a required accessible route in Section 1110.9 except for Item 10. Standby power for the platform lift shall be provided in accordance with Chapter 27.
1009.2.1 High-rise buildings. | In high-rise buildings subject to Section 403, at least one required accessible means of egress shall be an elevator complying with Section 1009.4. Exceptions: 1. In buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a horizontal exit and located at or above the level of exit discharge. 2. In buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2, the elevator shall not be required on floors provided with a ramp conforming to the provisions of Section 1012. 3. In buildings of Occupancy Group R-2 not subject to the requirements of emergency power in Section 403.
1009.6.1 Travel distance. | The maximum travel distance from any accessible space to an area of rescue assistance shall not exceed the exit access travel distance permitted for the occupancy in accordance with Section 1017.1. | 1009.6.1 Travel distance. | The maximum travel distance from any accessible space to an area of refuge shall not exceed the exit access travel distance permitted for the occupancy in accordance with Section 1017.1.
1009.2.2 Exit discharge. | Where an exit discharge is not accessible, an exterior area for assisted rescue shall be provided in accordance with Section 1009.7. An exterior area for assisted rescue shall not be required where an exit discharge is on an assisted rescue path from a stairway or an elevator.
1009.6.2 Stairway or elevator access. | Every required area of rescue assistance shall have direct access to a stairway complying with Sections 1009.3 and 1023, or an elevator complying with Section 1009.4. Exceptions: The following exceptions apply to the requirements of clear width and area of rescue assistance, and do not supersede the other requirements of the accessible means of egress: 1. Exit access stairways providing means of egress from mezzanines are permitted as part of an accessible means of egress. 2. The clear width of 48 inches (1220 mm) between handrails and the area of rescue assistance is not required at exit access stairways as permitted by Section 1017 or exit stairways in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 3. The clear width of 48 inches (1220 mm) between handrails is not required for interior exit stairways accessed from a refuge area in conjunction with a horizontal exit. 4. Areas of rescue assistance are not required at exit access stairways where two-way communication is provided at the elevator landing in accordance with Section 1009.8. 5. Areas of rescue assistance are not required at stairways in buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. 6. Areas of rescue assistance are not required at stairways serving open parking garages. 7. Areas of rescue assistance are not required for smoke-protected assembly seating areas complying with Section 1029.6.2. 8. Areas of rescue assistance are not required in Group R-2 occupancies. 9. Areas of rescue assistance are not required for stairways accessed from a refuge area in conjunction with a horizontal exit. | 1009.6.2 Stairway or elevator access. | Every required area of refuge shall have direct access to a stairway complying with Sections 1009.3 and 1023 or an elevator complying with Section 1009.4.
1009.2.3 Exterior exit stairway. | Where an exit stairway is open to the exterior, the accessible means of egress shall include either an area of rescue assistance in accordance with Section 1009.6 or an exterior area for assisted rescue in accordance with Section 1009.7.
1009.6.3 Size. | Each area of rescue assistance shall be sized to accommodate one wheelchair space of 30 inches by 48 inches (762 mm by 1220 mm) for each 200 occupants or portion thereof, based on the occupant load of the area of rescue assistance and areas served by the area of rescue assistance. Such wheelchair spaces shall not reduce the means of egress minimum width or required capacity. Access to any of the required wheelchair spaces in an area of rescue assistance shall not be obstructed by more than one adjoining wheelchair space. | 1009.6.3 Size. | Each area of refuge shall be sized to accommodate one wheelchair space of 30 inches by 52 inches (762 mm by 1320 mm) for each 200 occupants or portion thereof, based on the occupant load of the area of refuge and areas served by the area of refuge. Such wheelchair spaces shall not reduce the means of egress minimum width or required capacity. Access to any of the required wheelchair spaces in an area of refuge shall not be obstructed by more than one adjoining wheelchair space.
1009.6.4 Separation. | Each area of rescue assistance shall be separated from the remainder of the story by a smoke barrier complying with Section 709 or a horizontal exit complying with Section 1026. Each area of rescue assistance shall be designed to minimize the intrusion of smoke. Exceptions: 1. Areas of rescue assistance located within an enclosure for interior exit stairways complying with Section 1023. 2. Areas of rescue assistance in outdoor facilities where exit access is essentially open to the outside. | 1009.6.4 Separation. | Each area of refuge shall be separated from the remainder of the story by a smoke barrier complying with Section 709 or a horizontal exit complying with Section 1026. Each area of refuge shall be designed to minimize the intrusion of smoke.
1009.6.5 Two-way communication. | Areas of rescue assistance shall be provided with a two-way communication system complying with Sections 1009.8.1 and 1009.8.2. | 1009.6.5 Two-way communication. | Areas of refuge shall be provided with a two-way communication system complying with Sections 1009.8.1 and 1009.8.2.
1009.7 Exterior areas for assisted rescue. | Exterior areas for assisted rescue shall be accessed by an accessible route from the area served. | 1009.7 Exterior areas for assisted rescue. | Exterior areas for assisted rescue shall be accessed by an accessible route from the area served.
1009.5.1 Openness. | Platform lifts on an accessible means of egress shall not be installed in a fully enclosed hoistway.
1009.7.1 Size. | Each exterior area for assisted rescue shall be sized to accommodate wheelchair spaces in accordance with Section 1009.6.3. | 1009.7.1 Size. | Each exterior area for assisted rescue shall be sized to accommodate wheelchair spaces in accordance with Section 1009.6.3.
1009.6 Areas of rescue assistance. | Every required area of rescue assistance shall be accessible from the space it serves by one or more accessible means of egress components as listed in Section 1009.2.
1009.7.2 Separation. | Exterior walls separating the exterior area of assisted rescue from the interior of the building shall have a minimum fire-resistance rating of 1 hour, rated for exposure to fire from the inside. The fire-resistance-rated exterior wall construction shall extend horizontally 10 feet (3048 mm) beyond the landing on either side of the landing or equivalent fire-resistance-rated construction is permitted to extend out perpendicular to the exterior wall 4 feet (1220 mm) minimum on the side of the landing. The fire-resistance-rated construction shall extend vertically from the ground to a point 10 feet (3048 mm) above the floor level of the area for assisted rescue or to the roof line, whichever is lower. Openings within such fire-resistance-rated exterior walls shall be protected in accordance with Section 716. | 1009.7.2 Separation. | Exterior walls separating the exterior area of assisted rescue from the interior of the building shall have a minimum fire-resistance rating of 1 hour, rated for exposure to fire from the inside. The fire-resistance-rated exterior wall construction shall extend horizontally not less than 10 feet (3048 mm) beyond the landing on either side of the landing or equivalent fire-resistance-rated construction is permitted to extend out perpendicular to the exterior wall not less than 4 feet (1219 mm) on the side of the landing. The fire-resistance-rated construction shall extend vertically from the ground to a point not less than 10 feet (3048 mm) above the floor level of the area for assisted rescue or to the roof line, whichever is lower. Openings within such fire-resistance-rated exterior walls shall be protected in accordance with Section 716.
1009.7.3 Openness. | The exterior area for assisted rescue shall be open to the outside air. The sides other than the separation walls shall be not less than 50 percent open, and the open area shall be distributed so as to minimize the accumulation of smoke or toxic gases. Exception: The clear width of 48 inches (1220 mm) between handrails is not required at stairways serving buildings equipped throughout with an automatic sprinkler system installed in accordance with Section 903.3.1.1 or 903.3.1.2. | 1009.7.3 Openness. | The exterior area for assisted rescue shall be open to the outside air. The sides other than the separation walls shall be not less than 50 percent open, and the open area shall be distributed so as to minimize the accumulation of smoke or toxic gases.
1009.7.4 Stairways. | Stairways that are part of the accessible means of egress for the exterior area for assisted rescue shall provide a clear width of 48 inches (1220 mm) between handrails. | 1009.7.4 Stairways. | Stairways that are part of the means of egress for the exterior area for assisted rescue shall provide a minimum clear width of 48 inches (1219 mm) between handrails.
1009.6.2.1 Elevator lobby. | Where an elevator lobby serves as an area of rescue assistance, the shaft and lobby shall comply with Section 713.14 and Chapter 30.
1009.8 Two-way communication. | A two-way communication system complying with Sections 1009.8.1 and 1009.8.2 shall be provided at the landing serving each elevator or bank of elevators on each accessible floor that is one or more stories above or below the level of exit discharge. Exceptions: 1. Two-way communication systems are not required at the landing serving each elevator or bank of elevators where the two-way communication system is provided within areas of rescue assistance in accordance with Section 1009.6.5. 2. Two-way communication systems are not required on floors provided with ramps conforming to the provisions of Section 1012. 3. Two-way communication systems are not required at the landings serving only service elevators that are not designated as part of the accessible means of egress or serve as part of the required accessible route into a facility. 4. Two-way communication systems are not required at the landings serving only freight elevators that are not designated as part of the accessible means of egress or serve as part of the required accessible route into a facility. 5. Two-way communication systems are not required at the landing serving a private residence elevator. | 1009.8 Two-way communication. | A two-way communication system complying with Sections 1009.8.1 and 1009.8.2 shall be provided at the landing serving each elevator or bank of elevators on each accessible floor that is one or more stories above or below the level of exit discharge.
1009.8.1 System requirements. | Two-way communication systems shall provide communication between each required location and the fire command center or a central control point location approved by the Fire Department. Where the central control point is not a constantly attended location, a two-way communication system shall have a timed automatic telephone dial-out capability to a monitoring location or 911. The two-way communication system shall include both audible and visible signals. | 1009.8.1 System requirements. | Two-way communication systems shall provide communication between each required location and the fire command center or a central control point location approved by the fire department. Where the central control point is not a constantly attended location, the two-way communication system shall have timed, automatic telephone dial-out capability that provides two-way communication with an approved supervising station or 9-1-1. The two-way communication system shall include both audible and visible signals.
1009.8.2 Directions. | Directions for the use of the two-way communication system, instructions for summoning assistance via the two-way communication system and written identification of the location shall be posted adjacent to the two-way communication system. Signage shall comply with the ICC A117.1 requirements for visual characters. | 1009.8.2 Directions. | Directions for the use of the two-way communication system, instructions for summoning assistance via the two-way communication system and written identification of the location shall be posted adjacent to the two-way communication system. Signage shall comply with the ICC A117.1 requirements for visual characters.
1009.9 Signage. | Signage indicating special accessibility provisions shall be provided as shown: | 1009.9 Signage. | Signage indicating special accessibility provisions shall be provided as shown:
1009.10 Directional signage. | Directional signage indicating the location of all other means of egress and which of those are accessible means of egress shall be provided at the following: | 1009.10 Directional signage. | Directional signage indicating the location of all other means of egress and which of those are accessible means of egress shall be provided at the following:
1009.11 Instructions. | In areas of rescue assistance and exterior areas for assisted rescue, instructions on the use of the area under emergency conditions shall be posted. Signage shall comply with the ICC A117.1 requirements for visual characters. The instructions shall include all of the following: | 1009.11 Instructions. | In areas of refuge and exterior areas for assisted rescue, instructions on the use of the area under emergency conditions shall be posted. Signage shall comply with the ICC A117.1 requirements for visual characters. The instructions shall include all of the following:
1010.1.1 Size of doors. | The minimum width and height of each door opening shall be in accordance with this section. | 1010.1.1 Size of doors. | The required capacity of each door opening shall be sufficient for the occupant load thereof and shall provide a minimum clear opening width of 32 inches (813 mm). The clear opening width of doorways with swinging doors shall be measured between the face of the door and the stop, with the door open 90 degrees (1.57 rad). Where this section requires a minimum clear opening width of 32 inches (813 mm) and a door opening includes two door leaves without a mullion, one leaf shall provide a minimum clear opening width of 32 inches (813 mm). In Group I-2, doors serving as means of egress doors where used for the movement of beds shall provide a minimum clear opening width of 411/2 inches (1054 mm). The minimum clear opening height of doors shall be not less than 80 inches (2032 mm).
1010.1.3.1 Location of applied forces. | Forces shall be applied to the latch side of the door. | 1010.1.3.1 Location of applied forces. | Forces shall be applied to the latch side of the door.
1010.1 Doors. | Means of egress doors shall meet the requirements of this section. Doors serving a means of egress system shall meet the requirements of this section and Section 1022.2. Doors provided for egress purposes in numbers greater than required by this code shall meet the requirements of this section.
1010.1.1.1 Door width. | The required capacity of each door opening shall be sufficient for the occupant load thereof and shall provide a minimum clear width of 32 inches (812.2 mm). Clear openings of doorways with swinging doors shall be measured between the face of the door and the stop, with the door open 90 degrees (1.57 rad). Where this section requires a minimum clear width of 32 inches (812.8 mm) and a door opening includes two door leaves without a mullion, one leaf shall provide a clear opening width of 32 inches (812.8 mm). The maximum width of a swinging door leaf shall be 48 inches (1220 mm) nominal. Means of egress doors in a Group I-2 occupancy used for the movement of beds shall provide a clear width not less than 41½ inches (1054.1 mm). Exceptions: 1 The minimum and maximum width shall not apply to door openings that are not part of the required means of egress in Group R-2 and R-3 occupancies. 2. Door openings to resident sleeping units in Group I-3 occupancies shall have a clear width of not less than 28 inches (711.2 mm). 3. Door openings to storage closets less than 10 square feet (0.93 m2) in area shall not be limited by the minimum width. 4. Width of door leaves in revolving doors that comply with Section 1010.1.4.1 shall not be limited. 5. In other than Group R-1 occupancies, the minimum widths shall not apply to interior egress doors within a dwelling unit or sleeping unit that is not required to be an Accessible unit, Type B+NYC or Type B unit. 6. Doors to walk-in freezers and coolers less than 1,000 square feet (92.9 m2) in area shall have a maximum width of 60 inches (1524 mm). 7. In Group R-1 dwelling units or sleeping units not required to be Accessible units, the minimum width shall not apply to doors for showers or saunas.
1010.1.1.2 Projections into clear width. | There shall not be projections into the required clear width lower than 34 inches (863.4 mm) above the floor or ground. Projections into the clear opening width between 34 inches (863.4 mm) and 80 inches (2032 mm) above the floor or ground shall not exceed 4 inches (101.6 mm). Exception: Door closers and door stops shall be permitted to be 78 inches (1980 mm) minimum above the floor.
1010.1.1.3 Height. | The height of doors shall be not less than 80 inches (2032 mm). Exceptions: 1. Door openings within a dwelling unit or sleeping unit shall be not less than 78 inches (1981.2 mm) in height. 2. Exterior door openings in dwelling units and sleeping units, other than the required exit door, shall be not less than 76 inches (1930.4 mm) in height.
1010.1.2 Door swing. | Egress doors shall be installed in accordance with this section.
1010.1.2.1 Mounting. | Egress doors shall be of the pivoted or side-hinged swinging type.Exceptions: 1. Private garages, office areas, factory and storage areas with an occupant load of 10 or less. 2. Group I-3 occupancies used as a place of detention. 3. Critical or intensive care patient rooms within suites of health care facilities. 4. Doors within or serving a single dwelling unit in Groups R-2 and R-3. 5. In other than Group H occupancies, revolving doors complying with Section 1010.1.4.1. 6. In other than Group H occupancies, special purpose horizontal sliding, accordion or folding door assemblies complying with Section 1010.1.4.3. 7. Power-operated doors in accordance with Section 1010.1.4.2. 8. Doors serving a bathroom within an individual sleeping unit in Group R-1. 9. In other than Group H occupancies, manually operated horizontal sliding doors are permitted in a means of egress from spaces with an occupant load of 10 or less.
1010.1.2.2 Direction of swing. | Doors shall swing in the direction of egress travel where serving: 1. Group F or H occupancies. 2. Rooms or spaces with an occupant load of 75 or more persons. 3. Rooms or spaces requiring more than one exit door. 4. Automatic teller machines in accordance with Section 10-160 of the Administrative Code. Exception: Doors need not swing in the direction of egress travel for exterior street floor exit doors from lobbies serving only Group R-2 or R-3 occupancies.
1010.1.3 Door opening force. | The force for pushing or pulling open interior swinging egress doors, other than fire doors, shall not exceed 5-pounds (22.2 N). These forces do not apply to the force required to retract latch bolts or disengage other devices that hold the door in a closed position. For other swinging doors, as well as sliding and folding doors, the door latch shall release when subjected to a 15-pound (66.7 N) force. The door shall be set in motion when subjected to a 30-pound (133.4 N) force. The door shall swing to a full-open position when subjected to a 15-pound (66.7 N) force.
1010.1.4 Special doors. | Special doors and security grilles shall comply with the requirements of Sections 1010.1.4.1 through 1010.1.4.4.
1010.1.4.1 Revolving doors. | Revolving doors shall comply with the following:
2000-10-01
2000-10-01
1010.1.4.1.1 Egress component. | A revolving door used as a component of a means of egress shall comply with Section 1010.1.4.1 and the following three conditions:
1010.1.4.1.2 Other than egress component. | A revolving door used as other than a component of a means of egress shall comply with Section 1010.1.4.1. The breakout force of a revolving door not used as a component of a means of egress shall not be more than 180 pounds (800.7 N). Exception: A breakout force in excess of 180 pounds (800.7 N) is permitted if the collapsing force is reduced to not more than 130 pounds (578.3 N) when not less than one of the following conditions is satisfied: 1. There is a power failure or power is removed to the device holding the door wings in position. 2. There is an actuation of the automatic sprinkler system where such system is provided. 3. There is an actuation of a smoke detection system that is installed in accordance with Section 907 to provide coverage in areas within the building that are within 75 feet (22 860 mm) of the revolving doors. 4. There is an actuation of a manual control switch, in an approved location and clearly identified, that reduces the breakout force to not more than 130 pounds (578.3 N).
1010.1.4.2 Power-operated doors. | Where means of egress doors are operated or assisted by power, the design shall be such that in the event of power failure, the door is capable of being opened manually to permit means of egress travel or closed where necessary to safeguard means of egress. The forces required to open these doors manually shall not exceed those specified in Section 1010.1.3, except that the force to set the door in motion shall not exceed 50 pounds (222.4 N). The door shall be capable of swinging open from any position to the full width of the opening in which such door is installed when a force is applied to the door on the side from which egress is made. Power-operated swinging doors, power-operated sliding doors and power-operated folding doors shall comply with BHMA A156.10. Power-assisted swinging doors and low-energy power-operated swinging doors shall comply with BHMA A156.19. Exceptions: 1. Occupancies in Group I-3. 2. Horizontal sliding doors complying with Section 1010.1.4.3. 3. For a biparting door in the emergency breakout mode, a door leaf located within a multiple-leaf opening shall be exempt from the minimum 32-inch (812.8 mm) single-leaf requirement of Section 1010.1.1, provided a minimum 32-inch (812.8 mm) clear opening is provided when the two biparting leaves meeting in the center are broken out.
1010.1.4.3 Special purpose horizontal sliding, accordion or folding doors. | In other than Group H occupancies, special purpose horizontal sliding, accordion or folding door assemblies permitted to be a component of a means of egress in accordance with Exception 6 to Section 1010.1.2.1 shall comply with all of the following criteria:
1010.1.4.4 Security grilles. | In Groups B, M and S, horizontal sliding or vertical security grilles are permitted at the main entrance where the opening of such grilles are essential to the operation of the establishments. Such grilles shall be installed in accordance with the following criteria:
1010.1.5 Floor elevation. | There shall be a floor or landing on each side of a door. Such floor or landing shall be at the same elevation on each side of the door. Landings shall be level except for exterior landings, which are permitted to have a slope not to exceed 0.25 unit vertical in 12 units horizontal (2-percent slope). Exceptions: 1. Doors serving individual dwelling units in Groups R-2 and R-3 where the following apply: 1.1. A door is permitted to open at the top step of an interior flight of stairs within the dwelling unit, provided the door does not swing over the top step. 1.2. Screen doors and storm doors are permitted to swing over stairs or landings. 2. Exterior doors as provided for in Section 1003.5, Exception 1, and Section 1022.2, which are not on an accessible route. 3. In Group R-3 occupancies not required to be Accessible units, Type B+NYC units or Type B units, the landing at an exterior doorway shall be not more than 7¾ inches (186.9 mm) below the top of the threshold, provided the door, other than an exterior storm or screen door, does not swing over the landing. 4. Variations in elevation due to differences in finish materials, but not more than ½ inch (12.7 mm). 5. Exterior spaces of Type B+NYC units and Type B units where permitted pursuant to the exception to Section 1107.4. 6. Doors serving equipment spaces not required to be accessible in accordance with Section 1103.2.9 and serving an occupant load of five or less shall be permitted to have a landing on one side to be not more than 7 inches (177.8 mm) above or below the landing on the egress side of the door.
1010.1.6 Landings at doors. | Landings shall have a width not less than the width of the stairway or the door, whichever is greater. Doors in the fully open position shall not reduce a required dimension by more than 7 inches (177.8 mm). At any stairway landing, or when a door landing serves an occupant load of 50 or more, doors in any position shall not reduce the landing to less than 75 percent of its required width. Landings shall have a length measured in the direction of travel of not less than 44 inches (1117.6 mm). Exceptions: 1. Landing length in the direction of travel in Groups R-3 and U and within individual units of Group R-2 need not exceed 36 inches (914.4 mm). 2. In Group R-2 occupancies, where 36 inches wide stairways are permitted pursuant to Section 1011.2, Exception 1.2, such stairway landing length in the direction of travel shall be permitted to be not less than 36 inches (914.4 mm) or the width of the stairway, whichever is greater. Doors opening onto such stairway landings shall not reduce the landing width.
1010.1.7 Thresholds. | Thresholds at doorways shall not exceed ¾ inch (19.1 mm) in height above the finished floor or landing for sliding doors serving dwelling units or ½ inch (12.7 mm) above the finished floor or landing for other doors. Raised thresholds and floor level changes greater than ¼ inch (6.4 mm) at doorways shall be beveled with a slope not greater than one unit vertical in two units horizontal (50-percent slope). Exceptions: 1. In occupancy Group R-2 or R-3, threshold heights for sliding and side-hinged exterior doors shall be permitted to be up to 7¾ inches (196.9 mm) in height if all of the following apply: 1.1. The door is not part of the required means of egress. 1.2. The door is not part of an accessible route as required by Chapter 11. 1.3. The door is not part of an Accessible unit, Type B+NYC unit or Type B unit. 1.4. The exterior door, other than a storm or screen door, does not swing over the landing or step. 2. In Type B+NYC units and Type B units, where permitted pursuant to the exception to Section 1107.4, the threshold height on the exterior side of the door shall not exceed 4¾ inches (120.7 mm) in height above the exterior deck, patio or balcony for sliding doors or 4½ inches (114.3 mm) above the exterior deck, patio or balcony for other doors.
1010.1.8 Door arrangement. | Space between two doors in a series shall be 48 inches (1220 mm) minimum plus the width of a door swinging into the space. Doors in series shall swing either in the same direction or away from the space between the doors. Exceptions: 1. The minimum distance between horizontal sliding power-operated doors in a series shall be 48 inches (1220 mm). 2. Storm and screen doors serving individual dwelling units in Groups R-2 and R-3 need not be spaced 48 inches (1220 mm) from the other door. 3. Doors within individual dwelling units in Group R-3. 4. Doors within individual dwelling units in Group R-2 that are not required to comply with Section 1107. 5. Exterior doors in vestibules in Group R-2 occupancies shall not be required to swing either in the same direction or away from the space between doors provided that the 48-inch (1220 mm) minimum space between door swings is maintained.
1010.1.9 Door operations. | Except as specifically permitted by this section, egress doors shall be readily openable from the egress side without the use of a key or special knowledge or effort.
1010.1.9.1 Hardware. | Door handles, pulls, latches, locks and other operating devices on doors required to be accessible by Chapter 11 shall not require tight grasping, tight pinching or twisting of the wrist to operate.
1010.1.9.2 Hardware height. | Door handles, pulls, latches, locks and other operating devices shall be installed 34 inches (863.4 mm) minimum and 48 inches (1220 mm) maximum above the finished floor. Locks used only for security purposes and not used for normal operation are permitted at any height. Exception: Access doors or gates in barrier walls and fences protecting pools, spas and hot tubs shall be permitted to have operable parts in compliance with Section 3109.4.2 or 3109.5.1.7, as applicable.
1010.1.9.3 Locks and latches. | Locks and latches shall be permitted to prevent operation of doors where any of the following exist:
1010.1.9.4 Bolt locks. | Manually operated flush bolts or surface bolts are not permitted. Exceptions: 1. On doors not required for egress in individual dwelling units or sleeping units. 2. Where a pair of doors serves a storage or equipment room, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf. 3. Where a pair of doors serves an occupant load of less than 75 persons in a Group B, F or S occupancy, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf. The inactive leaf shall not contain doorknobs, panic bars or similar operating hardware. 4. Where a pair of doors serves a Group B, F or S occupancy, manually operated edge- or surface-mounted bolts are permitted on the inactive leaf provided such inactive leaf is not needed to meet egress capacity requirements and the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The inactive leaf shall not contain doorknobs, panic bars or similar operating hardware. 5. Where a pair of doors serves patient care rooms in Group I-2 occupancies, self-latching edge- or surface-mounted bolts are permitted on the inactive leaf provided that the inactive leaf is not needed to meet egress capacity requirements and the inactive leaf shall not contain doorknobs, panic bars or similar operating hardware.
1010.1.9.5 Unlatching. | The unlatching of any door or leaf shall not require more than one operation.Exception: More than one operation is permitted for unlatching doors in the following locations: 1. Places of detention or restraint. 2. Where manually operated bolt locks are permitted by Section 1010.1.9.4. 3. Doors from individual dwelling units and sleeping units of Group R occupancies as permitted by Section 1010.1.9.3, Items 4 and 5.
1010.1.9.5.1 Closet and bathroom doors in certain Group R occupancies. | In community residences or intermediate-care facilities classified as Group R-1, R-2 or R-3 occupancies pursuant to Section 308.3.2, Exception 1, 2 or 3, within such facilities, closet doors that latch in the closed position shall be openable from inside the closet, and bathroom doors that latch in the closed position shall be capable of being unlocked from the ingress side.
1010.1.9.6 Controlled egress doors in Groups I-1 and I-2. | Electric locking systems, including electro-mechanical locking systems and electromagnetic locking systems, shall be permitted to be locked in the means of egress in Group I-1 or I-2 occupancies where the clinical needs of persons receiving care require their containment. Controlled egress doors shall be permitted in such occupancies where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Section 907, provided that the doors are installed and operate in accordance with all of the following: 1. The door locks shall unlock on actuation of the automatic sprinkler system or automatic fire detection system. 2. The door locks shall unlock on loss of power controlling the lock or lock mechanism. 3. The door locking system shall be installed to have the capability of being unlocked by a switch located at the fire command center, a nursing station or other approved location. The switch shall directly break power to the lock. 4. A building occupant shall not be required to pass through more than one door equipped with a controlled egress locking system before entering an exit. 5. The procedures for unlocking the doors shall be described and approved as part of the emergency planning and preparedness required by the New York City Fire Code. 6. All clinical staff shall have the keys, codes or other means necessary to operate the locking systems. 7. Emergency lighting shall be provided at the door. 8. The door locking system units shall be listed in accordance with UL 294. Exceptions: 1. Items 1 through 4 shall not apply to doors to areas occupied by persons who, because of clinical needs, require restraint or containment as part of the function of a psychiatric treatment area. 2. Items 1 through 4 shall not apply to doors to areas where a listed egress control system is utilized to reduce the risk of child abduction from nursery and obstetric areas of a Group I-2 hospital.
1010.1.9.7 Delayed egress locking systems. | Subject to special review and approval by the commissioner, approved, listed, delayed egress locking systems may be permitted on doors serving spaces where extra safeguards are required in buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or an approved automatic smoke or heat detection system installed in accordance with Section 907, provided that the doors unlock in accordance with Items 1 through 8 below. 1. The delay electronics of the delayed egress locking system shall deactivate upon actuation of the automatic sprinkler system or automatic fire detection system, allowing immediate, free egress. 2. The delay electronics of the delayed egress locking system shall deactivate upon loss of power controlling the lock or lock mechanism, allowing immediate free egress. 3. The delayed egress locking system shall have the capability of being deactivated at the fire command center and other approved locations. 4. An attempt to egress shall initiate an irreversible process that shall allow such egress in not more than 15 seconds when a physical effort of 15 pounds (66.7 N) is applied to the egress side door hardware for not more than 3 seconds. Initiation of the irreversible process shall activate an audible signal in the vicinity of the door. Once the delay electronics have been deactivated, rearming the delay electronics shall be by manual means only. Except where approved by the department, a delay of not more than 30 seconds is permitted on a delayed egress door. 5. The egress path from any point shall not pass through more than one delayed egress locking system. Except where approved by the department, in Group I-2 or I-3 occupancies, the egress path from any point in the building shall pass through not more than two delayed egress locking systems provided the combined delay does not exceed 30 seconds. 6. A sign shall be provided on the door and shall be located above and within 12 inches (304.8 mm) of the door exit hardware. Except where approved by the department, in Group I occupancies, the installation of a sign is not required where care recipients who because of clinical needs require restraint or containment as part of the function of the treatment area. 6.1. For doors that swing in the direction of egress, the sign shall read: PUSH UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 15 SECONDS. Except where not more than 30 seconds is permitted on a delayed egress door is approved by the department, such sign shall read: PUSH UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 30 SECONDS. 6.2. For doors that swing in the opposite direction of egress, the sign shall read: PULL UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 15 SECONDS. Except where not more than 30 seconds is permitted on a delayed egress door is approved by the department, such sign shall read: PULL UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 30 SECONDS. 6.3. The sign shall comply with the visual character requirements in ICC A117.1. 7. Emergency lighting shall be provided on the egress side of the door. 8. The delayed egress locking system units shall be listed in accordance with UL 294. Exceptions: 1. Delayed egress locking systems shall not be permitted in buildings or spaces in Group A, E, F and H occupancies. However, in museums, delayed egress locks may be installed on exit doors subject to special review by the commissioner and Fire Commissioner. 2. Places of detention or restraints in Group I-3 are permitted to install delayed egress locking systems without the special review by the commissioner, provided that the installation complies with all of the other requirements of this section.
1010.1.9.8 Sensor release of electrically locked egress doors. | The electric locks on sensor released doors located in a means of egress in buildings with an occupancy in Group A, B, E, M, R-1 or R-2 and entrance doors to tenant spaces in occupancies in Group A, B, E, M, R-1 or R-2 are permitted where installed and operated in accordance with all of the following criteria:
1010.1.9.9 Electromagnetically locked egress doors. | Doors in the means of egress in buildings with an occupancy in Group A, B, E, M, R-1 or R-2 and doors to tenant spaces in Group A, B, E, M, R-1 or R-2 shall be permitted to be locked with an electromagnetic locking system where equipped with hardware that incorporates a built-in switch and where installed and operated in accordance with all of the following:
1010.1.9.10 Locking arrangements in correctional facilities. | In occupancies in Groups A-2, A-3, A-4, B, E, F, I-2, I-3, M and S within correctional and detention facilities, doors in means of egress serving rooms or spaces occupied by persons whose movements are controlled for security reasons shall be permitted to be locked where equipped with egress control devices that shall unlock manually and by not less than one of the following means:
1010.1.9.11 Stairway doors. | Interior stairway means of egress doors shall be openable from both sides without the use of a key or special knowledge or effort.1. Stairway discharge doors shall be openable from the egress side and shall only be locked from the opposite side. 2. This section shall not apply to doors arranged in accordance with Section 403.5.3. 3. In stairways serving not more than four stories, doors are permitted to be locked from the side opposite the egress side, provided they are openable from the egress side and capable of being unlocked simultaneously without unlatching upon a signal from the fire command center, if present, or a signal by emergency personnel from a single location inside the main entrance to the building. 4. This section shall not apply to buildings permitted to be served by one exit in accordance with Item 5 or 6 of Section 1006.3.2. 5. In schools classified as Group E occupancies that require lockdown drills as per New York State Education Law 807, stairway egress doors from occupied spaces are permitted to be locked from the side opposite the egress side for the duration of the lockdown drill, provided that they are openable from the occupied side for egress and are unlocked upon directions from the school administrative personnel following the completion of the lockdown drill.
1010.1.10 Panic and fire exit hardware. | Doors serving the following shall not be provided with a latch or lock other than panic hardware or fire exit hardware: 1. Group H occupancies; 2. A room or space with an occupant load of 75 or more in a Group A or E occupancy; 3. A building or nonaccessory tenant space used for assembly purposes that is permitted to be classified as a Group B occupancy pursuant to Section 303.1.2; and 4. An accessory room or space used for assembly purposes where permitted to be classified as a Group B occupancy or as part of the occupancy it is accessory to, pursuant to Section 303.1.3. Exceptions: 1. A main exit of a Group A occupancy shall be permitted to be locking in accordance with Section 1010.1.9.3, Item 2. 2. Doors serving a Group A or E occupancy shall be permitted to be electromagnetically locked in accordance with Section 1010.1.9.9.
1010.1.10.1 Rooms with electrical equipment. | Exit or exit access doors serving transformer vaults, rooms designated for batteries or energy storage systems, or modular data centers shall be equipped with panic hardware or fire exit hardware. Where rooms contain electrical rooms with equipment rated 800 amperes or more that contain overcurrent devices, switching devices or control devices and where the exit or exit access door is less than 25 feet (7629 mm) from the equipment working space, shall be equipped with panic hardware or fire exit hardware. The doors shall swing in the direction of egress travel.
1010.1.10.2 Refrigeration machinery room. | Swinging doors in refrigeration machinery rooms, where required by Section 1006.2.2.3, shall not be provided with a latch or lock other than panic hardware or fire exit hardware.
1010.1.10.3 Installation. | Where panic or fire exit hardware is installed, it shall comply with the following:
1011.1 General. | Stairways serving occupied portions of a building shall comply with the requirements of Sections 1011.2 through 1011.13. Alternating tread devices shall comply with Section 1011.14. Ships ladders shall comply with Section 1011.15. Ladders shall comply with Section 1011.16. Exception: Within rooms or spaces used for assembly purposes, stepped aisles shall comply with Section 1029. | 1011.1 General. | Stairways serving occupied portions of a building shall comply with the requirements of Sections 1011.2 through 1011.13. Alternating tread devices shall comply with Section 1011.14. Ship’s ladders shall comply with Section 1011.15. Ladders shall comply with Section 1011.16.
1010.1.10.4 Balanced doors. | If balanced doors are used and panic hardware is required, the panic hardware shall be the push-pad type and the pad shall not extend more than one-half the width of the door measured from the latch side.
1011.2 Width and capacity. | The required capacity of stairways shall be determined as specified in Section 1005, but the minimum width shall be not less than 44 inches 1117.6 mm). See Section 1009.3 for accessible means of egress stairways. Exceptions: 1. A width of not less than 36 inches (914.4 mm) shall be permitted in: 1.1. A stairway that serves an occupant load of 50 or less cumulative for all stories; or 1.2. A stairway that provides egress to the exit discharge solely for the use of Group R-2 occupancies, provided the building it serves is 125 feet (38 100 mm) or less in height, and provided such a stairway serves not more than 30 occupants per floor. 2. Spiral stairways as provided for in Section 1011.10. 3. Where an inclined platform lift or a stairway chairlift is installed on stairways serving occupancies in Group R-3, or within dwelling units in occupancies in Group R-2, a clear passage width not less than 20 inches (508 mm) shall be provided. Where the seat and platform can be folded when not in use, the distance shall be measured from the folded position. | 1011.2 Width and capacity. | The required capacity of stairways shall be determined as specified in Section 1005.1, but the minimum width shall be not less than 44 inches (1118 mm). See Section 1009.3 for accessible means of egress stairways.
1010.2 Gates. | Gates serving the means of egress system shall comply with the requirements of this section. Gates used as a component in a means of egress shall conform to the applicable requirements for doors. Exception: Horizontal sliding or swinging gates exceeding the 4-foot (1220 mm) maximum leaf width limitation are permitted in fences and walls surrounding a stadium.
1011.3 Headroom. | Stairways shall have a headroom clearance of not less than 84 inches (2133.6 mm) measured vertically from a line connecting the edge of the nosings. Such headroom shall be continuous above the stairway to the point where the line intersects the landing below, one tread depth beyond the bottom riser. The minimum clearance shall be maintained the full width of the stairway and landing. Projections into the required width shall not be limited above the minimum headroom height. Exceptions: 1. In Group R-2 and R-3 occupancies stairways shall have a headroom clearance of not less than 80 inches (2032 mm). 2. Spiral stairways complying with Section 1011.10 are permitted a 78-inch (1981.2 mm) headroom clearance. 3. In Group R-3 occupancies; within dwelling units in Group R-2 occupancies; and in Group U occupancies that are accessory to a Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies; where the nosings of treads at the side of a flight extend under the edge of a floor opening through which the stair passes, the floor opening shall be allowed to project horizontally into the required headroom not more than 4¾ inches (120.7 mm). | 1011.3 Headroom. | Stairways shall have a headroom clearance of not less than 80 inches (2032 mm) measured vertically from a line connecting the edge of the nosings. Such headroom shall be continuous above the stairway to the point where the line intersects the landing below, one tread depth beyond the bottom riser. The minimum clearance shall be maintained the full width of the stairway and landing.
1010.2.1 Stadiums. | Panic hardware is not required on gates surrounding stadiums where such gates are under constant immediate supervision while the public is present, and where safe dispersal areas based on 3 square feet (0.28 m2) per occupant are located between the fence and enclosed space. Such required safe dispersal areas shall not be located less than 50 feet (15 240 mm) from the enclosed space. See Section 1028.5 for means of egress from safe dispersal areas.
1011.4 Walkline. | The walkline across winder treads shall be concentric to the direction of travel through the turn and located 12 inches (304.8 mm) from the side where the winders are narrower. The 12-inch (304.8 mm) dimension shall be measured from the widest point of the clear stair width at the walking surface of the winder. Where winders are adjacent within the flight, the point of the widest clear stair width of the adjacent winders shall be used. | 1011.4 Walkline. | The walkline across winder treads shall be concentric to the direction of travel through the turn and located 12 inches (305 mm) from the side where the winders are narrower. The 12-inch (305 mm) dimension shall be measured from the widest point of the clear stair width at the walking surface of the winder. Where winders are adjacent within the flight, the point of the widest clear stair width of the adjacent winders shall be used.
1010.3 Turnstiles. | Turnstiles or similar devices that restrict travel to one direction shall not be placed so as to obstruct any required means of egress. Where portable turnstiles are installed for ticketing purposes, such turnstiles shall be moved from the egress path for proper exiting. 1. Manually-operated turnstiles. Manually-operated turnstiles that consist of revolving devices that turn freely in the direction of exit travel may be used in any occupancy where revolving doors are permitted. Each manually-operated turnstile or similar device shall be credited with no more than a 50-person capacity where all of the following provisions are met: 1.1. Each device shall turn free manually in the direction of egress travel when primary power is lost, and upon the manual release by an employee in the area. 1.2. Such devices are not given credit for more than 50 percent of the required egress capacity or width. 1.3. Each device is not more than 39 inches (990.6 mm) high. 1.4. Each device has not less than 16½ inches (419.1 mm) clear width at and below a height of 39 inches (990.6 mm) and not less than 22 inches (558.8 mm) clear width at heights above 39 inches (990.6 mm). 1.5 Where located as part of an accessible route, turnstiles shall have not less than 36 inches (914.4 mm) clear at and below a height of 34 inches (863.4 mm), not less than 32 inches (812.8 mm) clear width between 34 inches (863.4 mm) and 80 inches (2032 mm) and shall consist of a mechanism other than a revolving device. 2. Automatic turnstiles. Automatic turnstiles that consist of mechanisms other than revolving devices, and are operated by power, such as turnstiles with a photoelectric-actuated mechanism to open the turnstile upon the approach of a person, may be used in any occupancy where revolving doors are permitted. Automatic turnstiles may serve a means of egress system where all of the following provisions are met: 2.1. Each automatic turnstile shall have minimum widths sufficient for the occupant load served and shall provide at least 32 inches (812.8 mm) of clear width at and below a height of 80 inches (2032 mm). 2.2. The design shall be such that in the event of power failure, each automatic turnstile is capable of breaking away manually to permit means of egress travel. The force required to break away these turnstiles manually shall not exceed 13 pounds (57.8 N). The turnstile shall be capable of swinging from any position to the full, clear opening width of the turnstile when a force is applied to the turnstile on the side from which egress is made. 2.3. Each automatic turnstile shall be operable from the egress side without special knowledge or effort. 2.4. Each automatic turnstile shall be connected to the building fire alarm system. Activation of the building fire alarm system shall automatically release each such turnstile to its full, clear opening width, and each such turnstile shall remain in its open position until the fire alarm system has been reset. 2.5 Each automatic turnstile shall, upon actuation of a manual release device, automatically open to its full, clear opening width, and shall remain in its open position until the automatic turnstile’s access control system is reset. The manual release device shall be clearly identified with ready access that results in direct interruption of power to each turnstile. The manual release device shall be positioned at the fire command center or, if a fire command center is not required, at an approved location near the building entrance where the automatic turnstiles are located. 2.6 Each automatic turnstile shall have an integrated emergency power supply. 2.7 Each automatic turnstile power supply shall be electrically supervised. 2.8 Turnstiles provided for egress purposes in numbers greater than the egress capacity required by this code shall meet the requirements of this section. 2.9 Where located as part of an accessible route, such turnstiles shall have at least 36 inches (914.4 mm) clear width at and below a height of 34 inches (863.4 mm), at least 32 inches (812.8 mm) clear width between 34 inches (863.4 mm) and 80 inches (2032 mm).
1011.5 Stair treads and risers. | Stair treads and risers shall comply with Sections 1011.5.1 through 1011.5.5.3. | 1011.5 Stair treads and risers. | Stair treads and risers shall comply with Sections 1011.5.1 through 1011.5.5.3.
1010.3.1 High turnstile. | Turnstiles more than 39 inches (990.6 mm) high shall meet the requirements for revolving doors.
1011.5.1 Dimension reference surfaces. | For the purpose of this section, all dimensions are exclusive of carpets, rugs or runners. | 1011.5.1 Dimension reference surfaces. | For the purpose of this section, all dimensions are exclusive of carpets, rugs or runners.
1010.3.2 Additional door. | Where serving an occupant load greater than 300, each manually-operated turnstile and automatic turnstile that is not portable shall have a side-hinged swinging door that conforms to Section 1010.1 within 50 feet (15 240 mm).
1011.5.2 Riser height and tread depth. | Stair riser heights shall be 7 inches (177.8 mm) maximum and 4 inches (101.6 mm) minimum. The riser height shall be measured vertically between the nosings of adjacent treads. Rectangular tread depths shall be 11 inches (279.4 mm) minimum measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s nosing. The greatest tread depth within any flight of stairs shall not exceed the smallest by more than ⅜ inch (9.5 mm). Winder treads shall have a minimum tread depth of 11 inches (279.4 mm) between the vertical planes of the foremost projection of adjacent treads at the intersections with the walkline and a minimum tread depth of 10 inches (254 mm) within the clear width of the stair. Exceptions: 1. Spiral stairways in accordance with Section 1011.10. 2. Stairways connecting stepped aisles to cross aisles or concourses shall be permitted to use the riser/tread dimension in Section 1029.13.2. 3. In Group R-2 occupancies: 3.1. Sum of treads and risers. The sum of two risers plus one tread exclusive of nosing shall be not less than 24 inches (609.6 mm) nor more than 25½ inches (647.7 mm). 3.2. Dimensions of treads and risers. The maximum riser height shall be 7¾ inches (196.85 mm) and the minimum tread depth shall be 9½ inches (241.3 mm) plus nosing. Treads may be undercut a distance equal to the nosing. A nosing not less than ¾ inch (19 mm) but not more than 1¼ inches (31.8 mm) shall be provided on stairways with solid risers where the tread depth is less than 11 inches (279.4 mm). 3.3. Tolerances. The greatest riser height, tread depth, and nosing projection, within any flight of stairs shall not exceed the smallest by more than ⅜ inch (9.5 mm). 4. In Group R-3 occupancies; and in Group U occupancies that are accessory to Group R-3 occupancy or accessory to individual dwelling units in Group R-2 occupancies: 4.1. Sum of treads and risers. The sum of two risers plus one tread exclusive of nosing shall be not less than 24 inches (609.6 mm) nor more than 25½ inches (647.7 mm). 4.2. Dimensions of treads and risers. The maxi¬mum riser height shall be 8¼ inches (209.6 mm) and the minimum tread depth shall be 9 inches (228.6 mm) plus nosing. Treads may be undercut a distance equal to the nosing. A 1¼-inch (31.75 mm) nosing shall be provided on stairways with solid risers where the tread depth is less than 11 inches (279.4 mm). 4.3. Tolerances. The greatest riser height, tread depth, and nosing projection, within any flight of stairs shall not exceed the smallest by more than 3/8 inch (9.5 mm). 5. In Group R-3 occupancies; and within dwelling units in Group R-2 occupancies; winders shall have a minimum tread depth of 10 inches (254 mm) measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s leading edge, when measured at a point 12 inches (304.8 mm) from the side where the treads are narrower. Winder treads shall have a minimum tread depth of 6 inches (152.4 mm) at any point. Within any flight of stairs, the greatest winder tread depth at the 12-inch (304.8 mm) walk line shall not exceed the smallest by more than ⅜ inch (9.5 mm). 6. In Group I-3 facilities, stairways providing access to guard towers, observation stations and control rooms, not more than 250 square feet (23.2 m2) in area, shall be permitted to have a maximum riser height of 8 inches (203.2 mm) and a minimum tread depth of 9 inches (228.6 mm). | 1011.5.2 Riser height and tread depth. | Stair riser heights shall be 7 inches (178 mm) maximum and 4 inches (102 mm) minimum. The riser height shall be measured vertically between the nosings of adjacent treads or between the stairway landing and the adjacent tread. Rectangular tread depths shall be 11 inches (279 mm) minimum measured horizontally between the vertical planes of the foremost projection of adjacent treads and at a right angle to the tread’s nosing. Winder treads shall have a minimum tread depth of 11 inches (279 mm) between the vertical planes of the foremost projection of adjacent treads at the intersections with the walkline and a minimum tread depth of 10 inches (254 mm) within the clear width of the stair.
1010.4 Security requirements for doors and windows. | The provisions of Sections 1010.4.1 through 1010.4.4 shall apply to Group R-2 occupancies.
1011.5.3 Winder treads. | Winder treads are not permitted in means of egress stairways except within a dwelling unit. Exceptions: 1. Curved stairways in accordance with Section 1011.9. 2. Spiral stairways in accordance with Section 1011.10. | 1011.5.3 Winder treads. | Winder treads are not permitted in means of egress stairways except within a dwelling unit.
1010.4.1 Entrance doors. | Building entrance doors and other exterior exit doors shall be equipped with heavy duty lock sets with auxiliary latch bolts to prevent the latch from being manipulated by means other than a key. Latch sets shall have stop-work in the inside cylinder controlled by a master key only. Outside cylinders of main entrance door locks shall be operated by the tenants’ key, which shall not be keyed to also open the tenants’ apartment door. A light or lights shall be provided at or near the outside of the front entranceway of the building providing not less than 5-footcandles (53.82 lux) intensity measured at the floor level for the full width of the entranceway.
Note on A78: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: some sections are missing such as 1011.5.4

## BC11
2022 NYC BC Section # | 2022 NYC BC Text | ICC BC Section # | 2021 ICC Text | 2022 NYC BC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1101.1 Scope. | The provisions of this chapter and Appendices E and N shall control the design and construction of facilities for accessibility for individuals with disabilities. | 1101.1 Scope. | The provisions of this chapter shall control the design and construction of facilities for accessibility for individuals with disabilities.
1101.2 Design. | Buildings and facilities shall be designed and constructed to be accessible in accordance with ICC A117.1 and this code.
1101.3 Special provisions for prior code buildings. | The provisions of this chapter shall apply to alterations, including minor alterations but excluding ordinary repairs, and changes of use or occupancy to prior code buildings, portions of such buildings, and spaces within such buildings in accordance with Sections 1101.3.1 through 1101.3.5. Alterations within prior code buildings affecting an area containing a primary function shall comply with the requirements of Section 1101.4. This section shall not impose a requirement for greater accessibility than that which would be required for new construction, nor shall it reduce or have the effect of reducing accessibility. Exception: The provisions of this chapter are not applicable to: 1. Group R-3 occupancies in buildings with first occupancy on or before March 13, 1991. 2. Group R-3 occupancies in buildings with first occupancy after March 13, 1991, and originally constructed in a single structure with fewer than four dwelling or sleeping units.
1103.1 Where required. | Sites, buildings, structures, facilities, elements and spaces, temporary or permanent, shall be accessible to individuals with disabilities. | 1103.1 Where required. | Sites, buildings, structures, facilities, elements and spaces, temporary or permanent, shall be accessible to individuals with disabilities.
1101.3.1 Requirements based on change of occupancy or how a space is used. | Accessible features and construction governed by this chapter shall be provided:
1103.2 General exceptions. | Sites, buildings, structures, facilities, elements and spaces shall be exempt from this chapter to the extent specified in this section. | 1103.2 General exceptions. | Sites, buildings, structures, facilities, elements and spaces shall be exempt from this chapter to the extent specified in this section.
1101.3.2 Requirements based on value of alterations. | Accessible features and construction governed by this chapter shall be provided:
1103.2.1 Specific requirements. | Accessibility is not required in buildings and facilities, or portions thereof, to the extent permitted by Sections 1104 through 1111. | 1103.2.1 Specific requirements. | Accessibility is not required in buildings and facilities, or portions thereof, to the extent permitted by Sections 1104 through 1112.
1101.3.3 Directional accessibility signage. | Directional signage shall be provided in accordance with Section 1111.2 at or in close proximity to inaccessible building entrances, inaccessible public toilets and bathing facilities, and elevators not serving an accessible route, indicating the route to the nearest like accessible element where such accessible element is provided, such that an individual with disabilities will not be required to retrace the approach route from the inaccessible element.
1103.2.2 Employee work areas. | Spaces and elements within employee work areas shall only be required to comply with Sections 907.5.2.3.1, 1009 and 1104.3.1, and shall be designed and constructed so that individuals with disabilities can approach, enter and exit the work area. In addition, at least one but not less than five percent of fixed seating, tables, desks, and/or work surfaces, if provided, within employee work areas shall be located on an accessible route and comply with Section 902 (Dining Surfaces and Work Surfaces) of ICC A117.1. Work areas, or portions of work areas, other than raised courtroom stations in accordance with Section 1108.4.1.4, that are less than 300 square feet (27.8 m2) in area and located 7 inches (177.8 mm) or more above or below the ground or finished floor where the change in elevation is critical to the work operation shall be exempt from all requirements. | 1103.2.2 Employee work areas. | Spaces and elements within employee work areas shall only be required to comply with Sections 907.5.2.3.1, 1009 and 1104.3.1 and shall be designed and constructed so that individuals with disabilities can approach, enter and exit the work area. Work areas, or portions of work areas, other than raised courtroom stations in accordance with Section 1109.4.1.4, that are less than 300 square feet (30 m2) in area and located 7 inches (178 mm) or more above or below the ground or finished floor where the change in elevation is essential to the function of the space shall be exempt from all requirements.
1101.3.4 Identifying accessibility signage. | Identifying accessibility signage shall be provided in accordance with Item 5 of Section 1111.1 at accessible building entrances where not all entrances are accessible.
1103.2.3 Detached dwellings. | Detached one- and two-family dwellings, their accessory structures and their associated sites and facilities are not required to comply with this chapter. | 1103.2.3 Detached dwellings. | Detached one- and two- family dwellings, their accessory structures and their associated sites and facilities are not required to comply with this chapter.
1101.3.5 Waiver of requirements. | The commissioner may waive the requirements of this chapter for the alteration of prior code buildings, provided that such waiver would not significantly adversely affect provisions for health, safety and security and that equally safe and proper alternatives are prescribed and, that such waiver is based upon a specific finding that strict compliance with the requirement:
1103.2.4 Utility buildings. | Group U occupancies are not required to comply with this chapter other than the following: | 1103.2.4 Utility buildings. | Group U occupancies are not required to comply with this chapter other than the following:
1101.3.5.1 Application process. | Each application for a waiver shall be made to the commissioner in writing, setting forth each requirement sought to be waived and the specific reason or reasons therefore. The commissioner shall determine, under all of the circumstances presented by such application, which of such requirements may appropriately be waived. The commissioner shall render such determination in writing, which shall set forth in detail, the commissioner’s findings and conclusions with respect to each requirement sought to be waived. A copy of such written determination shall be forwarded to the applicant. Such written determination shall be filed with the department and shall be available for public inspection.
1103.2.5 Construction sites. | Structures, sites and equipment directly associated with the actual processes of construction including, but not limited to, scaffolding, bridging, materials hoists, materials storage or construction trailers are not required to comply with this chapter. | 1103.2.5 Construction sites. | Structures, sites and equipment directly associated with the actual processes of construction including, but not limited to, scaffolding, bridging, materials hoists, materials storage or construction trailers are not required to comply with this chapter.
1101.3.5.2 Waiver recommendation. | The Mayor’s Office for People with Disabilities or its successor agency shall be consulted by and shall advise the commissioner concerning each application for a waiver under Section 1101.3.5.
1103.2.6 Raised areas. | Raised areas used for purposes of security, life safety or fire safety including, but not limited to, observation galleries, prison guard towers, fire towers or lifeguard stands are not required to comply with this chapter. | 1103.2.6 Raised areas. | Raised areas used primarily for purposes of security, life safety or fire safety including, but not limited to, observation galleries, prison guard towers, fire towers or lifeguard stands are not required to comply with this chapter.
1101.4 Alterations affecting an area containing a primary function. | Where an alteration affects the accessibility to, or contains an area of primary function, the route to the primary function area shall be accessible. The costs of providing the accessible route are not required to exceed 20 percent of the value of the alterations affecting the area of primary function. The accessible route to the primary function area shall include toilet facilities and drinking fountains serving the area of primary function. Exceptions: 1. This provision does not apply to alterations limited solely to windows, hardware, operating controls, electrical outlets and signs. 2. This provision does not apply to alterations limited solely to mechanical systems, electrical systems, installation or alteration of fire protection systems and abatement of hazardous materials. 3. This provision does not apply to alterations undertaken for the primary purpose of increasing the accessibility of a facility. 4. This provision does not apply to altered areas limited within a Type B or Type B+NYC dwelling unit.
1103.2.7 Limited access spaces. | Spaces accessed only by ladders, catwalks, crawl spaces, freight elevators that are not part of an accessible route, or very narrow passageways are not required to comply with this chapter. | 1103.2.7 Limited access spaces. | Spaces accessed only by ladders, catwalks, crawl spaces, freight elevators or very narrow passageways are not required to comply with this chapter.
1102.1 Definitions. | The following terms are defined in Chapter 2:
1103.2.9 Equipment spaces. | Spaces frequented only by service personnel for maintenance, repair or occasional monitoring of equipment are not required to comply with this chapter. Such spaces include, but are not limited to, elevator pits, elevator penthouses, mechanical, electrical or communications equipment rooms, piping or equipment catwalks, water or sewerage treatment pump rooms and stations, electrical substations and transformer vaults, and highway and tunnel utility facilities. | 1103.2.9 Equipment spaces. | Spaces frequented only by service personnel for maintenance, repair or occasional monitoring of equipment are not required to comply with this chapter.
1103.2.13 Detention and correctional facilities. | In detention and correctional facilities, common use areas that are used only by inmates or detainees and security personnel, and that do not serve holding cells or housing cells required to be Accessible units, are not required to comply with this chapter. | 1103.2.13 Detention and correctional facilities. | In detention and correctional facilities, common use areas that are used only by inmates or detainees and security personnel, and that do not serve holding cells or housing cells required to be Accessible units, are not required to comply with this chapter.
1103.2.14 Walk-in coolers and freezers. | Walk-in coolers and freezers intended for employee use only are not required to comply with this chapter. | 1103.2.14 Walk-in coolers and freezers. | Walk-in cooler and freezer equipment accessed only from employee work areas is not required to comply with this chapter.
1104.1 Site arrival points. | At least one accessible route within the site shall be provided from public transportation stops, accessible parking, accessible passenger loading zones, and public streets or sidewalks to the accessible building entrance served. | 1104.1 Site arrival points. | At least one accessible route within the site shall be provided from public transportation stops, accessible parking, accessible passenger loading zones, and public streets or sidewalks to the accessible building entrance served.
1104.2 Within a site. | At least one accessible route shall connect accessible buildings, accessible facilities, accessible elements and accessible spaces that are on the same site and shall comply with Section 1104.5. Exceptions: 1. An accessible route is not required between accessible buildings, accessible facilities, accessible elements and accessible spaces that have, as the only means of access between them, a vehicular way not providing for pedestrian access. 2. An accessible route to recreational facilities shall only be required to the extent specified in Section 1110. | 1104.2 Within a site. | At least one accessible route shall connect accessible buildings, accessible facilities, accessible elements and accessible spaces that are on the same site.
1104.3 Connected spaces. | When a building or portion of a building is required to be accessible, at least one accessible route shall be provided to each portion of the building, to accessible building entrances connecting accessible pedestrian walkways and to the public way. Exceptions: 1. Stories and mezzanines exempted by Section 1104.4. 2. In a building, room or space used for assembly purposes with fixed seating, an accessible route shall not be required to serve levels where wheelchair spaces are not provided as permitted by other sections of this chapter. 3. Vertical access to elevated employee work stations within a courtroom complying with Section 1108.4.1.4. 4. An accessible route to recreational facilities shall only be required to the extent specified in Section 1110. | 1104.3 Connected spaces. | Where a building or portion of a building is required to be accessible, at least one accessible route shall be provided to each portion of the building, to accessible building entrances connecting accessible pedestrian walkways and to the public way.
1103.2.8 Reserved.
1104.3.1 Employee work areas. | Common use circulation paths within employee work areas shall be accessible routes. Exceptions: The following exceptions apply only to the common use circulation paths within an employee work area and are not intended to remove the requirement of Section 1103.2.2 that employee work areas be designed and constructed so that individuals with disabilities can approach, enter and exit the employee work area. 1. Common use circulation paths, located within employee work areas that are less than 300 square feet (27.9 m2) in size and defined by permanently installed partitions, counters, casework or furnishings not serving accessible employee work stations that are required in Section 1103.2.2, shall not be required to be accessible routes. 2. Common use circulation paths, located within employee work areas, that are an integral component of equipment, shall not be required to be accessible routes. | 1104.3.1 Employee work areas. | Common use circulation paths within employee work areas shall be accessible routes.
1104.3.2 Press boxes. | Press boxes in a building, room or space used for assembly purposes shall be on an accessible route. Exceptions: 1. An accessible route shall not be required to press boxes in bleachers that have a single point of entry from the bleachers, provided that the aggregate area of all press boxes for each area of sport activity is not more than 500 square feet (46.5 m2). 2. An accessible route shall not be required to free-standing press boxes that are more than 12 feet (3657.6 mm) above grade provided that the aggregate area of all press boxes for each area of sport activity is not more than 500 square feet (46.5 m2). | 1104.3.2 Press boxes. | Press boxes in a building, room or space used for assembly purposes shall be on an accessible route.
1103.2.10 Reserved.
1103.2.11 Reserved.
1104.5 Location. | Accessible routes shall coincide with or be located in the same area as a general circulation path. Where the circulation path is interior, the accessible route shall also be interior. Where only one accessible route is provided, the accessible route shall not pass through kitchens, storage rooms, restrooms, closets or similar spaces. | 1104.5 Location. | Accessible routes shall coincide with or be located in the same area as a general circulation path. Where the circulation path is interior, the accessible route shall be interior. Where only one accessible route is provided, the accessible route shall not pass through kitchens, storage rooms, restrooms, closets or similar spaces.
1103.2.12 Reserved.
1104.6 Security barriers. | Security barriers including, but not limited to, security bollards and security check points shall not obstruct a required accessible route or accessible means of egress. | 1104.6 Security barriers. | Security barriers including, but not limited to, security bollards and security check points shall not obstruct a required accessible route or accessible means of egress.
1105.1 Public entrances. | In addition to accessible entrances required by Sections 1105.1.1 through 1105.1.8, all public entrances shall be accessible. | 1105.1 Public entrances. | In addition to accessible entrances required by Sections 1105.1.2 through 1105.1.8, at least 60 percent of all public entrances shall be accessible.
1104.4 Multilevel buildings and facilities. | At least one accessible route shall connect each accessible level and mezzanine in multilevel buildings and facilities.
1105.1.1 Parking garage entrances. | Where provided, direct access for pedestrians from parking structures to buildings or facility entrances shall be accessible.
1105.1.2 Entrances from tunnels or elevated walkways. | Where direct access is provided for pedestrians from a pedestrian tunnel or elevated walkway to a building or facility, entrances from such access to the building or facility shall be accessible.
1105.1.3 Restricted entrances. | Where restricted entrances are provided to a building or facility, all such restricted entrances to the building or facility shall be accessible.
1105.1.4 Entrances for inmates and detainees. | Where entrances used only by inmates or detainees and security personnel are provided at judicial facilities, detention facilities or correctional facilities, all such entrances shall be accessible.
1105.1.5 Service entrances. | If a service entrance is the only entrance to a building or a tenant space in a facility, that entrance shall be accessible.
1105.1.6 Tenant spaces. | All entrances to tenant spaces that are required to be accessible shall be accessible entrances.
1105.1.7 Dwelling units and sleeping units. | Doors and doorways at entrance(s) to Accessible units and Type B+NYC units, including hardware, shall comply with Section 404 (Doors and Doorways) of ICC A117.1. Doors and doorways, including hardware, at entrance(s) to Type B units shall comply with Section 1003.5 (Doors and doorways) of ICC A117.1.
1105.1.8 Automatic doors. | In facilities with the occupancies and building occupant loads indicated in Table 1105.1.8, at least one accessible public entrance shall be either a full power-operated door or a low-energy power-operated door. |  |  |  | See BC11 Tables&Figures
1106.1 Required. | Where parking is provided, 5 percent of the total number of parking spaces provided for a facility, but not less than one parking space, shall be accessible parking spaces except as otherwise required by Sections 1106.2 through 1106.4 of this code. Van-accessible parking spaces shall be provided in accordance with Section 1106.5 of this code. Accessible parking spaces shall be designed and con­structed in accordance with Section 502 (Parking Spaces) of ICC A117.1. Where more than one parking facility is provided on a site, the number of parking spaces required to be accessible shall be calculated separately for each parking facility. Where a determination of the minimum number of parking spaces results in a number containing a decimal of 0.5 or more, the next highest integer shall be used.
1106.2 Groups R-2 and R-3. | Where parking is provided for occupancies in Groups R-2 and R-3, which are required to have Accessible, Type B+NYC, or Type B units, the number of accessible parking spaces shall be in compliance with Section 1106.1 and such number of accessible parking spaces shall be dispersed in accordance with Section 1106.6. Where parking is provided within or beneath a building, accessible parking spaces shall also be provided within or beneath the building.
1106.2.1 Lease, rental, or assignment of spaces. | In a parking facility accessory to Occupancy Group R-2 or R-3 serving only the residents or employees of the management of such occupancy, or provided in compliance with Section 25-412 of the New York City Zoning Resolution, the accessible parking spaces in such facility may be leased, rented or assigned to an individual without disabilities on a no longer than month-to-month basis. Such leases, rentals, or assignments of the accessible parking spaces to individuals without disabilities shall be on written condition that such spaces be relinquished immediately at the end of the term of such lease, rental, or assignment to a resident or employee of the management of such occupancy who is an individual with disabilities.
1106.3 Hospital outpatient facilities. | At least 10 percent, but not less than one, of care recipient and visitor parking spaces provided to serve hospital outpatient facilities shall be accessible.
1107.1 General. | In addition to the other requirements of this chapter, occupancies having dwelling units or sleeping units shall be provided with accessible features in accordance with this section. | 1107.1 General. | Electrical vehicle charging stations shall comply with Section 1107.2. Fuel-dispensing systems shall comply with Section 1107.3.
1106.4 Rehabilitation facilities and outpatient physical therapy facilities. | At least 20 percent, but not less than one, of the portion of care recipient and visitor parking spaces serving rehabilitation facilities specializing in treating conditions that affect mobility and outpatient physical therapy facilities shall be accessible.
1106.5 Van spaces. | For every six or fraction of six accessible parking spaces, at least one shall be a van-accessible parking space. Van-accessible parking spaces shall be designed and constructed in accordance with ICC A117.1, including Section 502 (Parking Spaces).
1106.6 Location. | Accessible parking spaces shall be located on the shortest accessible route of travel from adjacent parking to an accessible building entrance. In parking facilities that do not serve a particular building, accessible parking spaces shall be located on the shortest route to an accessible pedestrian entrance to the parking facility. Where buildings have multiple accessible entrances with adjacent parking, accessible parking spaces shall be dispersed and located near the accessible entrances. In Occupancy Groups R-2 and R-3, at least one of each type of parking space shall be accessible.
1106.7 Passenger loading zones. | Passenger loading zones shall be designed and constructed in accordance with ICC A117.1 including Section 503 (Passenger Loading Zones).
1106.7.1 Continuous loading zones. | Where passenger loading zones are provided, at least one accessible passenger loading zone shall be provided within each continuous 100 linear feet (30 400 mm) of loading zone space, or fraction thereof, so that travel between accessible passenger loading zones will not exceed 100 linear feet (30 400 m).
1108.1 General. | In addition to the other requirements of this chapter and applicable provisions of Appendices E and N, the requirements of Sections 1108.2 through 1108.5 shall apply to specific occupancies. | 1108.1 General. | In addition to the other requirements of this chapter, occupancies having dwelling units or sleeping units shall be provided with accessible features in accordance with this section.
1106.7.2 Medical facilities. | A passenger loading zone shall be provided at an accessible entrance to licensed medical and long-term care facilities where people receive physical or medical treatment or care and where the period of stay exceeds 24 hours.
1106.7.3 Valet and attended parking. | The number of accessible parking spaces in facilities that utilize valet and attended parking services shall be provided in accordance with Table 1106.7.3, and Sections 1106.7.3.1 and 1106.7.3.2. |  |  |  | See BC11 Tables&Figures
1106.7.3.1 Valet parking. | In a facility utilizing valet parking services in which vehicles are parked and later returned to their drivers by a valet employed by the facility, the number of accessible parking spaces shall be provided in accordance with Table 1106.7.3 of this code. A passenger loading zone complying with Section 1106.7 of this code shall be provided at valet parking services where the valet shall take control of the vehicles. Passenger loading zones shall comply with Section 503 (Passenger Loading Zones) of ICC A117.1. |  |  |  | See BC11 Tables&Figures
1106.7.3.2 Attended parking. | In an attended parking facility in which vehicles customarily are parked and later returned to their drivers by an attendant employed by the parking facility, the number of accessible parking spaces shall be provided in accordance with Table 1106.7.3 of this code. |  |  |  | See BC11 Tables&Figures
1106.7.3.2.1 Passenger loading zone. | A passenger loading zone complying with Section 1106.7 of this code shall be provided where an attendant shall take control of the vehicles. Passenger loading zones shall comply with Section 503 (Passenger Loading Zones) of ICC A117.1.
1106.7.3.2.2 Retrieval of vehicles. | The attendant shall park and retrieve all vehicles not equipped with special controls entering the facility in which an individual with disabilities is either the driver or a passenger, provided accessible parking space is available.
1106.7.4 Mechanical access parking garages. | Mechanical access parking garages shall provide at least one passenger loading zone in compliance with Section 1106.7 at vehicle drop-off and vehicle pick-up areas.
1106.8 Electrical vehicle charging stations. | Electrical vehicle charging stations shall comply with Sections 1106.8.1 through 1106.8.5.
1106.8.1 Number of accessible vehicle charging stations. | Where provided for common use, at least five percent of the total number of electrical vehicle charging stations per facility, but not less than one for each type of electric vehicle charging station, shall be accessible. Where a multiport electric vehicle charging station can simultaneously charge more than one vehicle, the number of electric vehicle charging stations shall be counted as the number of electric vehicles that can be simultaneously charged. The number of accessible vehicle charging stations are in addition to the required accessible parking spaces.
1106.8.2 Electric vehicle charging space. | At each electrical vehicle charging station required to be accessible, the charging space shall comply with the requirements for a van accessible parking space complying with Sections 502.2 through 502.5 of ICC A117.1.
1106.8.3 Accessible route. | At each electric vehicle charging station required to be accessible, the charging station shall be located along an accessible route. An accessible route shall be provided between the charging station and the charging space.
1106.8.4 Obstructions. | Electric vehicle charging stations shall be designed so accessible routes are not obstructed by cables or other elements.
1106.8.5 Electrical vehicle charging station controls. | Electric vehicle charging stations and electric vehicle charging station controls shall comply with Sections 309.2 and 309.3 of ICC A117.1.
1107.2 Design. | Dwelling units and sleeping units which are required to be Accessible units, Type B+NYC units, or Type B units shall comply with this code and the applicable provisions of Chapter 10 of ICC A117.1. Type B+NYC units shall further comply with Section 1004 (Type B Units) of ICC A117.1, including any modifications made by Sections 1107.2.1 through 1107.2.8 of this code. Units required to be Type B+NYC units or Type B units are permitted to be designed and constructed as Accessible units.
1107.2.1 Type B+NYC unit doors and doorways. | Doors and doorways at the entrance(s) to Type B+NYC dwelling or sleeping units shall comply with Section 1105.1.7 of this code. All other doors and doorways within the dwelling or sleeping unit, and patio or balcony doors of such dwelling or sleeping unit, meant for human passage shall comply with Section 1003.5 (Doors and Doorways) of ICC A117.1. Doors and doorways serving toilet and bathing rooms shall comply with Section 1003.5 of ICC A117.1.
1107.2.2 Type B+NYC unit toilet and bathing rooms. | Where toilet and bathing rooms are provided in a Type B+NYC dwelling unit or sleeping unit, all such toilet and bathing rooms shall comply with Sections 1107.2.2.1 through 1107.2.2.9. Within each such toilet room, at least one lavatory, and one water closet shall comply with Sections 1107.2.2.1 through 1107.2.2.7. Within each bathing room, at least one lavatory, one water closet, and either a bathtub or shower shall comply with Sections 1107.2.2.1 through 1107.2.2.8. Toilet and bathing fixtures shall be in a single room, such that travel between fixtures does not require travel beyond the room in which the fixtures of such toilet or bathing room is located. Additional fixtures shall comply with Section 1107.2.2.9.
1107.2.2.1 Accessible route. | At least one accessible route shall connect all spaces and elements with each toilet and bathing room within a dwelling unit or sleeping unit unless as permitted in Section 1107.2.5, Item 3 of this code. Accessible routes shall comply with ICC A117.1.
1107.2.2.2 Operable parts. | Lighting controls, electrical switches and receptacle outlets, and environmental controls shall comply with Section 309 of ICC A117.1.
1107.2.2.3 Knee and toe clearance. | Clear floor space at fixtures shall be permitted to include knee and toe clearances complying with Section 306 of ICC A117.1.
1107.2.2.4 Overlap. | Clear floor or ground spaces and clearances are permitted to overlap.
1107.2.2.5 Lavatory. | Lavatories shall comply with Section 606 of ICC A117.1.
1107.2.2.6 Mirrors and medicine cabinets. | Mirrors above lavatories shall have the bottom edge of the reflecting surface 40 inches (1016 mm) maximum above the floor or ground. Medicine cabinets, if provided, must include a storage shelf no higher than 44 inches (1117.6 mm) above the floor.
1107.2.2.7 Water closet. | Water closets shall comply with Sections 1107.2.2.7.1 through 1107.2.2.7.6.
1107.2.2.7.1 Location. | The water closet shall be positioned with a wall to the rear and to one side. The centerline of the water closet shall be 18 inches (457.2 mm) from the side wall.
1107.2.2.7.2 Clearance. | Clearance around the water closet shall comply with Sections 1107.2.2.7.2.1 through 1107.2.2.7.2.3.
1107.2.2.7.2.1 Parallel approach. | Where only a parallel approach is provided to the water closet, the clearance shall be 56 inches (1422 mm) minimum, measured per­pendicular from the rear wall, and 48 inches (1220 mm) minimum, measured perpendicular from the sidewall. A lavatory complying with Section 1107.2.2.5 shall be permitted on the rear wall, 18 inches (457.2 mm) minimum from the water closet centerline.
1107.2.2.7.2.2 Forward approach. | Where only a forward approach is provided to the water closet, the clearance shall be 66 inches (1676 mm) minimum, measured perpendicular from the rear wall, and 48 inches (1220 mm) minimum, measured perpendicular from the side wall. A lavatory complying with Section 1107.2.2.5 shall be permitted on the rear wall, 18 inches (457.2 mm) minimum from the water closet centerline.
1107.2.2.7.2.3 Parallel and forward approach. | Where both a parallel and a forward approach are provided to the water closet, the clearance shall be 56 inches (1422 mm) minimum, measured perpendicular from the rear wall, and 60 inches (1524 mm) minimum, measured perpendicular from the side wall. No fixtures or obstructions, other than the water closet, shall be within the clearance.
1107.2.2.7.3 Grab bars. | Grab bars for water closets shall comply with Section 609 of ICC A117.1 and shall be provided in accordance with Sections 1107.2.2.7.3.1 through 1107.2.2.7.3.2 of this code. Mounting heights of grab bars shall comply with Section 609.4 of ICC A117.1.
1107.2.2.7.3.1 Fixed side wall grab bars. | Fixed side wall grab bars shall be 42 inches (1066.8 mm) minimum in length, located 12 inches (304.8 mm) maximum from the rear wall and extending 54 inches (1371.6 mm) minimum from the rear wall. In addition, a vertical grab bar 18 inches (457.2 mm) minimum in length shall be mounted with the bottom of the bar located between 39 inches (990.6 mm) and 41 inches (1041.4 mm) above the floor, and with the center of the bar located at 30 inches (762 mm) from the rear wall.
1107.2.2.7.3.2 Rear wall grab bars. | The rear wall grab bar shall be 36 inches (914.4 mm) minimum in length, and extend from the centerline of the water closet 12 inches (304.8 mm) minimum on the side closet to the wall, and 24 inches (609.2 mm) minimum on the transfer side.
1107.2.2.7.4 Height. | The top of the toilet seat shall be 15 inches (381 mm) minimum and 19 inches (482.6 mm) maximum above the floor or ground.
1107.2.2.7.5 Flush controls. | Flush controls shall comply with Section 309 of ICC A117.1. Flush controls shall be located in accordance with one of the following:
1107.2.2.7.6 Dispensers. | Toilet paper dispensers shall comply with this section. The outlet of the dispenser shall be located within an area 24 inches (609.2 mm) minimum and 42 inches (1066.8 mm) maximum from the rear wall. The outlet of the dispenser shall be located 18 inches (457.2 mm) minimum above the floor. Dispensers shall comply with Section 609.3 of ICC A117.1.
1107.2.2.8 Bathing facilities. | Where provided, a bathtub shall comply with Section 1107.2.2.8.1, and a shower compartment shall comply with Section 1107.2.2.8.2.
1107.2.2.8.1 Bathtubs. | Bathtubs shall comply with Section 607 of ICC A117.1. Lavatories complying with Section 1107.2.2.5 of this code shall be permitted in the clearance required by Section 607.2 of ICC A117.1. Bathtub seats shall not be required.
1107.2.2.8.1.1 Grab bars. | Grab bars for bathtubs shall comply with Section 609 of ICC A117.1 and shall be provided in accordance with Section 607.4 of ICC A117.1.
1107.2.2.8.2 Showers. | Showers shall comply with Section 608 of ICC A117.1.
1107.2.2.8.2.1 Grab bars and seats. | Grab bars and seats for showers shall comply with Sections 609 and 610 of ICC A117.1 and shall be provided in accordance with Sections 608.2.3.2 and 608.3 of ICC A117.1.
1107.2.2.9 Additional fixtures. | Additional fixtures provided within toilet and bathing rooms shall comply with Sections 1004.11.1 (Grab Bar and Shower Seat Reinforcement), 1004.11.3.1.1 (Lavatory), 1004.11.3.1.2 (Water Closet) and 1004.11.3.1.3 (Bathing Fixtures) of ICC A117.1.
1107.2.3 Type B+NYC unit kitchen and kitchenette. | Where kitchens and kitchenettes are provided in a Type B+NYC dwelling unit or sleeping unit, the primary kitchen or kitchenette shall be constructed in accordance with the kitchen requirements of Section 1003.12 (Kitchen) and 1003.3.2 (Turning Space) of ICC A117.1, including any modifications made by Sections 1107.2.3.1 through 1107.2.3.5 of this code. Secondary kitchens and kitchenettes within the same dwelling unit or sleeping unit shall be required to comply only with Section 1004.12 (Kitchens) of ICC A117.1.
1107.2.3.1 Kitchen counters. | A kitchen counter that is required to comply with Section 1003.12.3.2 or 1003.12.4.2 (Height) of ICC A117.1 shall be permitted to be adjustable or designed to be replaceable as a unit at variable heights between 29 inches and 36 inches (736.6 mm and 914.4 mm), measured from the floor to the top of the work surface. The owner shall adjust or replace such countertop at the time an individual with disabilities takes occupancy of the unit, or within 10 days of the date the request is made by such individual, whichever is later, at the owner’s expense.
1107.2.3.2 Appliances in kitchen and kitchenette. | Appliances in kitchens and kitchenettes shall comply with Section 1003.12.5 (Appliances) of ICC A117.1.
1109.1 General. | Accessible building features and facilities shall be provided in accordance with Sections 1109.2 through 1109.15 of this code. | 1109.1 General. | In addition to the other requirements of this chapter, the requirements of Sections 1109.2 through 1109.4 shall apply to specific occupancies.
1107.2.3.3 Refrigerator/freezers. | Combination refrigerators and freezers shall comply with Section 1003.12.5.6 (Refrigerator/Freezer) of ICC A117.1. In addition, where less than 100 percent of storage volume of the freezer is located within 54 inches (1371.6 mm) maximum above the floor, such freezer shall be a self-defrosting type.
1107.2.3.4 Cooktops and ovens. | Cooktops and ovens shall comply with Sections 1003.12.5.4 and 1003.12.5.5 of ICC A117.1, respectively. However, oven controls shall not be required to be located on either side of the oven door, provided such controls comply with Section 1003.12.5.5.4 of ICC A117.1. Where double ovens are provided, at least one oven interior and its controls shall comply with Section 309.3 (Height) of ICC A117.1.
1107.2.3.5 Kitchen and kitchenette storage. | Kitchen storage, kitchen cabinets, drawers, and shelf storage areas, within kitchen and kitchenettes shall comply with Section 905 (Storage Facilities) of ICC A117.1 pursuant to Section 1107.2.3 of this code, except overhead cabinets. In addition, at least one storage shelf or cabinet, mounted above the work surface at 48 inches (1220 mm) maximum above the floor, shall be provided.
1107.2.4 Type B+NYC unit operable windows. | All operable windows required to provide natural ventilation and/or an emergency escape and rescue opening in rooms or spaces in a Type B+NYC dwelling unit or sleeping unit shall comply with Section 1003.13 (Windows) of ICC A117.1.
1107.2.5 Type B+NYC multistory units. | Multistory Type B+NYC dwelling units or sleeping units shall comply with the following:
1107.2.6 Type B+NYC unit raised or sunken floor area. | Where a raised or sunken floor area in a portion of a living, dining, or sleeping room within a Type B+NYC dwelling unit or sleeping unit that is permitted by Section 1004.3 (Accessible route, Exception 1 and 2) of ICC A117.1 is provided, steps complying with Section 504 (Stairways) of ICC A117.1 with a minimum clear width of 36 inches (914.4 mm) shall connect such portion of raised or sunken floor area to an accessible route. In addition, a minimum area of 80 square feet (7.4 m2), and 8 feet (2438.4 mm) in one dimension, of each of such living, dining, or sleeping room shall be connected by an accessible route that is in compliance with Section 1004.3.2 (Components) of ICC A117.1.
1107.2.7 Type B+NYC unit storage facilities. | Where storage facilities are provided within a Type B+NYC dwelling unit or sleeping unit, they shall comply with Section 905 (Storage Facilities) of ICC A117.1.
1107.2.8 Type B+NYC unit laundry equipment. | Where washing machines or clothes dryers are provided within a Type B+NYC dwelling unit or sleeping unit, such equipment shall comply with Section 611 (Washing Machines and Clothes Dryers) of ICC A117.1 and shall be front loading. Laundry equipment in accessible common-use areas as required in Section 1107.3 shall comply with Section E105.2 of Appendix E of this code.
1107.3 Accessible spaces. | Rooms and spaces available to the general public or available for common use by residents and serving Accessible units, Type B+NYC units or Type B units shall be accessible. Accessible spaces shall include, but not be limited to, spaces for residents’ use, such as laundry rooms, refuse disposal and storage locations, mailbox areas, recreational facilities, assembly and tenants’ meeting rooms, storage rooms, management offices, parking areas, toilet and bathing rooms, kitchen, living and dining areas and any exterior spaces, including patios, terraces and balconies.
1107.3.1 Mailboxes. | Except as otherwise provided by rules of the department for the purposes of complying with rules and regulations established by the United States Postal Service and/or the United States Department of Housing and Urban Development, where mailboxes are provided for each dwelling unit or sleeping unit in an interior location, 100 percent of such mailboxes shall comply with ICC A117.1, and the operable parts of such mailboxes shall be no higher than 48 inches (1220 mm) above the finished floor.
1107.4 Accessible route. | At least one accessible route shall connect accessible building or facility entrances with the required accessible entrance(s) of each Accessible unit, Type B+NYC unit, and Type B unit within the building or facility and with those exterior and interior spaces and facilities that serve the units.
1107.5 Group I. | Accessible units shall be provided in Group I occupancies in accordance with Sections 1107.5.1 through 1107.5.5.
1107.5.1 Group I-1 Accessible units. | In Group I-1 occupancies, at least 10 percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. The remainder shall be Type B+NYC units with all grab bars installed where grab bar reinforcements are required.
1107.5.2 Group I-2 nursing homes. | In nursing homes of Group I-2 occupancies 100 percent of the dwelling units and sleeping units shall be Accessible units.
1107.5.3 Group I-2 hospitals. | In general purpose hospitals, psychiatric facilities, detoxification facilities and residential care/assisted living facilities of Group I-2 occupancies, 100 percent of the dwelling units and sleeping units shall be Accessible units.
1107.5.3.1 Accessible unit entry doors. | Entry doors to accessible dwelling units or sleeping units shall not be required to provide the maneuvering clearance beyond the latch side of the door.
1107.5.4 Group I-2 rehabilitation facilities. | In hospitals and rehabilitation facilities of Group I-2 occupancies that specialize in treating conditions that affect mobility, or units within either that specialize in treating conditions that affect mobility, 100 percent of the dwelling units and sleeping units shall be Accessible units.
1107.5.4.1 Enriched assisted living residences (EALR) and special needs assisted living residences (SNALR). | In enriched assisted living residences (EALR) and special needs assisted living residences (SNALR) licensed by the New York State Department of Health, at least ten percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. The remainder shall be Type B+NYC units with all grab bars installed where grab bar reinforcements are required.
1107.5.5 Group I-3. | Accessible units shall be provided in Group I-3 occupancies in accordance with Sections 1107.5.5.1 through 1107.5.5.3.
1107.5.5.1 Group I-3 sleeping units. | In Group I-3 occupancies, at least 3 percent of the total number of sleeping units in the facility, but not less than one unit in each classification level, shall be Accessible units.
1107.5.5.2 Special holding cells and special housing cells or rooms. | In addition to the Accessible units required by Section 1107.5.5.1, where special holding cells or special housing cells or rooms are provided, at least one serving each purpose shall be an Accessible unit. Cells or rooms subject to this requirement include, but are not limited to, those used for purposes of orientation, protective custody, administrative or disciplinary detention or segregation, detoxification and medical isolation.
1107.5.5.3 Medical care facilities. | In addition to any medical isolation cells required by Section 1107.5.5.2 to be Accessible units, 100 percent of the patient sleeping units or cells in medical facilities of Group I-3 occupancies shall be Accessible units.
1107.6 Group R. | Accessible units, Type B+NYC units and Type B units shall be provided in Group R occupancies in accordance with Sections 1107.6.1 through 1107.6.3.
1107.6.1 Group R-1. | Accessible units, Type B+NYC units, and Type B units shall be provided in Group R-1 occupancies in accordance with Sections 1107.6.1.1 through 1107.6.1.3.
1107.6.1.1 Accessible units. | Accessible dwelling units and sleeping units shall be provided in accordance with Table 1107.6.1.1. Where buildings contain more than 50 dwelling units or sleeping units, the number of Accessible units shall be determined per building. Where buildings contain 50 or fewer dwelling units or sleeping units, all dwelling units and sleeping units on a site shall be considered to determine the total number of Accessible units. Accessible units shall be dispersed among the various classes of units. Roll-in showers provided in Accessible units shall include a permanently mounted folding shower seat. |  |  |  | See BC11 Tables&Figures
1107.6.1.2 Type B+NYC units. | In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence and not required to be an Accessible unit shall be a Type B+NYC unit unless the number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4. Where no Type B+NYC units are required per Section 1107.7.4, all units not required to be Accessible units shall be Type B units.
1107.6.1.3 Doors and doorways. | In all units, including those not required to be Accessible units, Type B+NYC units, or Type B units, entrances, doors, and doorways providing user passage into and within units shall comply with Section 404.2.2 (Clear Width) of ICC A117.1.
1107.6.1.4 Boarding houses, dormitories, fraternity houses and sorority houses in Group R-1. | Accessible units and Type B+NYC units shall be provided in boarding houses, dormitories, fraternity houses and sorority houses in Group R-1 occupancies in accordance with Sections 1107.6.1.4.1 and 1107.6.1.4.2. Where the building or part thereof contains sleeping units where residents share bathroom or kitchen facilities, or both, bedrooms shall be counted as sleeping units for the purpose of determining the number of units. Where the sleeping units are grouped in suites, only one sleeping unit in each suite shall be permitted to count towards the number of required Accessible units.
1107.6.1.4.1 Accessible units. | Accessible dwelling units and sleeping units shall be provided in accordance with Table 1107.6.1.1. |  |  |  | See BC11 Tables&Figures
1107.6.1.4.2 Type B+NYC units. | Every dwelling unit and every sleeping unit not required to be an Accessible unit shall be a Type B+NYC unit unless the number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4. Where no Type B+NYC units are required in accordance with Section 1107.7.4, all units shall be Type B units.
1107.6.2 Group R-2. | Type B+NYC units and Type B units shall be provided in Group R-2 occupancies in accordance with Section 1107.6.2.1.
1107.6.2.1 Type B+NYC units. | Every dwelling unit and sleeping unit shall be a Type B+NYC unit.
1107.6.2.2 Type B units. | Where no Type B+NYC units are required in accordance with Section 1107.7.4, all units intended to be occupied as a residence shall be Type B units.
1107.6.3 Group R-3. | In Group R-3 occupancies where there are four or more dwelling units or sleeping units intended to be occupied as a residence in a single structure, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
1107.7 General exceptions for Type B units. | Where specifically permitted by Section 1107.6, the required number of Type B units is permitted to be reduced in accordance with Sections 1107.7.1 through 1107.7.3.
1107.7.1 Structures without elevator service where Type B units are required. | Where no elevator service is provided in a structure or required by other sections of this code, only the dwelling units and sleeping units that are located on stories indicated in Sections 1107.7.1.1 and 1107.7.1.2 are required to be Type B units.
1107.7.1.1 One story with Type B units required. | At least one story containing dwelling units or sleeping units intended to be occupied as a residence shall be provided with an accessible entrance and accessible route from the exterior of the structure and all units intended to be occupied as a residence on that story shall be Type B units.
1107.7.1.2 Other stories with Type B units required. | If other stories containing dwelling units or sleeping units intended to be occupied as a residence are served by a building entrance that is in proximity to arrival points as indicated in Items 1 and 2, such building entrance shall be accessible and all dwelling units and sleeping units intended to be occupied as a residence served by that entrance on that story shall be Type B units.
1107.7.2 Multistory units where Type B units are required. | A multistory dwelling unit or sleeping unit that is not provided with elevator service is not required to be a Type B unit. Where a multistory unit is provided with external elevator service to only one floor, the floor provided with elevator service shall be the primary entry to the unit, shall comply with the requirements for a Type B unit and, where provided within the unit, a living area, a kitchen and a toilet facility shall be provided on that floor.
1107.7.3 Elevator service to the lowest story with Type B units. | Where elevator service in the building provides an accessible route only to the lowest story containing dwelling units or sleeping units intended to be occupied as a residence, only the units on that story that are intended to be occupied as a residence on the lowest story served by the elevator are required to be Type B units.
1107.7.4 General exceptions for Type B+NYC units. | Where specifically permitted by Sections 1107.5 and 1107.6, the required number of Type B+NYC units is permitted to be reduced in accordance with Section 1107.7.4.1.
1107.7.4.1 Buildings or structures without elevator service where Type B+NYC units are required. | In buildings or structures where no elevator service is provided or required by other sections of this code, only the dwelling units and sleeping units that are located on stories indicated in Section 1107.7.4.1.1 are required to be Type B+NYC units.
1107.7.4.1.1 Units located in the cellar, basement, or first floor. | In buildings or structures where the lowest story containing dwelling or sleeping units is the cellar, basement, or first floor, at least one such story containing dwelling or sleeping units, regardless of intent to occupy as a residence, shall be provided with an accessible entrance and accessible route from the exterior of the building or structure and all units on that story, regardless of intent to occupy as a residence, shall be Type B+NYC units. Where no dwelling units or sleeping units are located in the cellar, basement, or first floor, Type B units shall be provided where required by Section 1107.7.1 through 1107.7.3.
1108.2 Assembly area seating. | Assembly areas with seating shall comply with Sections 1108.2.1 through 1108.2.5. Lawn seating shall comply with Section 1108.2.6. Assistive listening systems shall comply with Section 1108.2.7. Performance areas viewed from assembly seating areas shall comply with Section 1108.2.8. Dining and drinking areas shall comply with Section 1108.2.9.
1108.2.1 Services. | If a service or facility is provided in an area that is not required to be accessible in accordance with Section 1108.2.9, the same service or facility shall be provided on an accessible level and shall be accessible.
1108.2.2 Wheelchair spaces. | In theaters, bleachers, grandstands, stadiums, arenas and other assembly areas, accessible wheelchair spaces, companion seats, and designated aisle seats complying with ICC A117.1, including Section 802 (Assembly Areas), shall be provided in accordance with Sections 1108.2.2.1 through 1108.2.2.4 of this code. Required accessible wheelchair spaces and their companion seats as required in Section 1108.2.5 shall be delineated on the approved seating plans. Such spaces and seats which are unsold 1 day (24 hours) before the event shall be permitted to be released for sale to the public, including individuals without disabilities.
1108.2.2.1 General seating. | Wheelchair spaces shall be provided in accordance with Table 1108.2.2.1. |  |  |  | See BC11 Tables&Figures
1108.2.2.2 Luxury boxes, club boxes and suites. | In each luxury box, club box and suite within arenas, stadiums and grandstands, wheelchair spaces shall be provided in accordance with Table 1108.2.2.1. |  |  |  | See BC11 Tables&Figures
1108.2.2.3 Other boxes. | In boxes other than those required to comply with Section 1108.2.2.2, the total number of wheelchair spaces provided shall be determined in accordance with Table 1108.2.2.1. Wheelchair spaces shall be located in not less than 20 percent of all boxes provided. |  |  |  | See BC11 Tables&Figures
1108.2.3 Companion seats. | At least one companion seat complying with ICC A117.1, including Section 802.7 (Companion Seat), shall be provided for each wheelchair space required by Sections 1108.2.2.1 through 1108.2.2.3 of this code.
1108.2.4 Dispersion of wheelchair spaces in multilevel assembly seating areas. | In multilevel assembly seating areas, wheelchair spaces shall be provided on the main floor level and on one of each two additional floor or mezzanine levels. Wheelchair spaces shall be provided in each luxury box, club box and suite within assembly facilities.
1108.2.5 Designated aisle seats. | At least 5 percent, but not less than one, of the total number of aisle seats provided shall be designated aisle seats and shall be the aisle seats located closest to accessible routes, and shall comply with ICC A117.1, including Section 802.8 (Designated Aisle Seats).
1108.2.6 Lawn seating. | Lawn seating areas and exterior overflow seating areas, where fixed seats are not provided, shall connect to an accessible route.
1108.2.7 Assistive listening systems. | Each building, room or space used for assembly purposes where audible communications are integral to the use of the space, regardless of the occupancy load of such space, shall have an assistive listening system in compliance with ICC A117.1, including Section 706 (Assistive Listening Systems) and Appendix N of this code.
1108.2.7.1 Receivers. | The number and type of receivers shall be provided for assistive listening systems in accordance with Table 1108.2.7.1 of this code. |  |  |  | See BC11 Tables&Figures
1108.2.7.2 Ticket windows. | Where ticket windows are provided, at least one window at each location shall have an assistive listening system.
1108.2.7.3 Public address systems. | Where stadiums, arenas and grandstands provide audible public announcements, they shall also provide equivalent text information regarding events and facilities in compliance with Sections 1108.2.7.3.1 and 1108.2.7.3.2.
1108.2.7.3.1 Prerecorded text messages. | Where electronic signs are provided and have the capability to display prerecorded text messages containing information that is the same, or substantially equivalent, to information that is provided audibly, signs shall display text that is equivalent to audible announcements.
1108.2.7.3.2 Real-time messages. | Where electronic signs are provided and have the capability to display real-time messages containing information that is the same, or substantially equivalent, to information that is provided audibly, signs shall display text that is equivalent to audible announcements.
1108.2.8 Performance areas. | An accessible route shall directly connect the performance area to the assembly seating area where a circulation path directly connects a performance area to an assembly seating area. An accessible route shall be provided from performance areas to ancillary areas or facilities used by performers.
1108.2.9 Dining and drinking areas. | In dining and drinking areas, all interior and exterior floor areas shall be accessible and be on an accessible route.
1108.2.9.1 Dining surfaces. | Where dining surfaces for the consumption of food or drink are provided, at least 10 percent of the total number of seating and standing spaces, but not less than one, of each type of dining surfaces shall be accessible and be distributed throughout the facility and located on a level accessed by an accessible route.
1108.2.9.2 Dining and drinking counters. | Where seating is provided at dining or drinking counters, at least one 60 inch (1524 mm) long portion of the counter shall be provided with two accessible seating spaces. Such accessible seating space shall comply with Section 902 (Dining Surfaces and Work Surfaces) of ICC A117.1, and shall not be located within 40 inches (1016 mm) of either end of the counter, so as to provide individuals with disabilities with the same level of service and experience as that provided to others.
1108.3 Self-service storage facilities. | Self-service storage facilities shall provide accessible individual self-storage spaces in compliance with Section 1104 of this code and ICC A117.1, including Section 905 (Storage Facilities). The number of required self-storage spaces shall be in accordance with Table 1108.3 of this code. |  |  |  | See BC11 Tables&Figures
1108.3.1 Dispersion. | Accessible individual self-service storage spaces shall be dispersed throughout the various classes of spaces provided. Where more classes of spaces are provided than the number of required accessible spaces, the number of accessible spaces shall not be required to exceed that required by Table 1108.3. Accessible spaces are permitted to be dispersed in a single building of a multibuilding facility. |  |  |  | See BC11 Tables&Figures
1108.4 Judicial facilities. | Judicial facilities shall comply with Sections 1108.4.1 and 1108.4.2 of this code.
1108.4.1 Courtrooms. | Each courtroom shall be accessible and comply with ICC A117.1, including Section 807 (Courtrooms), and Sections 1108.4.1.1 through 1108.4.1.5 of this code.
1108.4.1.1 Jury box. | A wheelchair space complying with ICC A117.1 shall be provided within the jury box.
1108.4.1.2 Gallery seating. | Wheelchair spaces complying with ICC A117.1 shall be provided in accordance with Table 1108.2.2.1 of this code. Designated aisle seats shall be provided in accordance with Section 1108.2.5 of this code. |  |  |  | See BC11 Tables&Figures
1108.4.1.3 Assistive listening systems. | An assistive listening system must be provided. Receivers shall be provided for the assistive listening system in accordance with Section 1108.2.7.1 of this code.
1108.4.1.4 Employee work stations. | The judge’s bench, clerk’s station, bailiff’s station, deputy clerk’s station and court reporter’s station shall be located on an accessible route. The vertical access to elevated employee work stations within a courtroom is not required at the time of initial construction, provided a ramp, lift or elevator complying with ICC A117.1 can be installed without requiring reconfiguration or extension of the courtroom or extension of the electrical system.
1108.4.1.5 Other work stations. | The litigant’s and counsel stations, including the lectern, shall be accessible in accordance with ICC A117.1.
1108.4.2 Holding cells. | Central holding cells and court-floor holding cells shall comply with Sections 1108.4.2.1 and 1108.4.2.2.
1108.4.2.1 Central holding cells. | Where separate central holding cells are provided for adult males, juvenile males, adult females or juvenile females, one of each type shall be accessible. Where central holding cells are provided and are not separated by age or gender, at least one accessible cell shall be provided.
1108.4.2.2 Court-floor holding cells. | Where separate court-floor holding cells are provided for adult males, juvenile males, adult females or juvenile females, each courtroom shall be served by one accessible cell of each type. Where court-floor holding cells are provided and are not separated by age or gender, courtrooms shall be served by at least one accessible cell. Accessible cells shall be permitted to serve more than one courtroom.
1108.5 Assembly areas without seating. | Assembly areas without seating shall comply with Section 1108.2.7.
1109.2 Toilet and bathing rooms. | Each toilet room and bathing room shall be accessible. Where a floor level is not required to be connected by an accessible route, the only toilet rooms or bathing rooms provided within the facility shall not be located on the inaccessible floor. Except as provided for in Sections 1109.2.2 and 1109.2.3 of this code, at least one of each type of fixture, element, control or dispenser in each accessible toilet room and bathing room shall be accessible.
1109.2.1 Family or assisted-use toilet and bathing rooms. | In assembly and mercantile occupancies, an accessible family or assisted-use toilet room shall be provided where an aggregate of six or more male and female water closets is required. In buildings of mixed occupancy, only those water closets required for the assembly or mercantile occupancy shall be used to determine the family or assisted-use toilet room requirement. In recreational facilities where separate-sex bathing rooms are provided, an accessible family or assisted-use bathing room shall be provided. Fixtures located within family or assisted-use toilet and bathing rooms required by this section are permitted to be included in the number of fixtures required by the New York City Plumbing Code for either the male or female occupants.
1109.2.1.1 Standard. | Family or assisted-use toilet and bathing rooms shall comply with Sections 1109.2.1.2 through 1109.2.1.7 of this code.
1109.2.1.2 Family or assisted-use toilet rooms. | Family or assisted-use toilet rooms shall include only one water closet and only one lavatory. A family or assisted-use bathing room in accordance with Section 1109.2.1.3 shall be considered a family or assisted-use toilet room.
1109.2.1.3 Family or assisted-use bathing rooms. | Family or assisted-use bathing rooms shall include only one shower or bathtub fixture. Family or assisted-use bathing rooms shall also include one water closet and one lavatory. Where storage facilities are provided for separate-sex bathing rooms, accessible storage facilities complying with Section 1109.9 shall be provided for family or assisted-use bathing rooms.
1109.2.1.4 Location. | Family or assisted-use toilet and bathing rooms shall be located on an accessible route. Family or assisted-use toilet rooms shall be located not more than one story above or below separate-sex toilet rooms. The accessible route from any separate-sex toilet room to a family or assisted-use toilet room shall not exceed 500 feet (152 m).
1109.2.1.5 Prohibited location. | In passenger transportation facilities and airports, the accessible route from separate-sex toilet rooms to a family or assisted-use toilet room shall not pass through security checkpoints.
1109.2.1.6 Clear floor space. | Where doors swing into a family or assisted-use toilet or bathing room, a clear floor space not less than 30 inches by 48 inches (762 mm by 1220 mm) shall be provided, within the room, beyond the area of the door swing.
1109.2.1.7 Privacy. | Doors to family or assisted-use toilet and bathing rooms shall be securable from within the room.
1109.2.2 Water closet compartment. | Where water closet compartments are provided in a toilet room or bathing room, at least 5 percent, but not less than one of the total number of compartments shall be wheelchair accessible. Where the combined total water closet compartments and urinals provided in a toilet room or bathing room is six or more, at least 5 percent, but not less than one of the total number of compartments shall be ambulatory accessible, provided in addition to the wheelchair-accessible compartment. Wheelchair-accessible and ambulatory-accessible compartments shall comply with ICC A117.1 including Sections 604.9 (Wheelchair Accessible Compartments) and 604.10 (Ambulatory Accessible Compartments).
1109.2.3 Lavatories. | Where lavatories are provided, at least 5 percent, but not less than one, shall be accessible. Where an accessible lavatory is located within the accessible water closet compartment, at least one additional accessible lavatory shall be provided in the multicompartment toilet room outside the accessible water closet compartment. Where the total lavatories provided in a toilet room or bathing facility is six or more, at least one lavatory with enhanced reach ranges shall be provided.
1109.2.4 Diaper changing accommodations. | In assembly and mercantile occupancies on each floor level containing a public toilet room, both male and female occupants shall have access to at least one safe, sanitary and convenient diaper changing station, deck, table or similar amenity, which shall comply with Section 603.5 (Diaper Changing Tables) of ICC A117.1.
1109.3 Sinks. | Where sinks are provided, at least 5 percent but not less than one provided in accessible spaces shall comply with ICC A117.1, including Section 606 (Lavatories and Sinks).
1109.4 Kitchens, kitchenettes and wet bars. | Where kitchen, kitchenettes and wet bars not located within dwelling or sleeping units, are provided in accessible spaces or rooms, they shall be accessible in accordance with ICC A117.1 including Section 804 (Kitchens and Kitchenettes), and Section 1109.9 of this code for storage.
1109.5 Drinking fountains. | Where drinking fountains are provided on an exterior site, on a floor or within a secured area, the drinking fountains shall be provided in accordance with Sections 1109.5.1 and 1109.5.2.
1109.5.1 Minimum number. | No fewer than two drinking fountains shall be provided. One drinking fountain shall comply with the requirements for people who use a wheelchair and one drinking fountain shall comply with the requirements for standing persons.
1109.5.2 More than the minimum number. | Where more than the minimum number of drinking fountains specified in Section 1109.5.1 is provided, 50 percent of the total number of drinking fountains provided shall comply with the requirements for people who use a wheelchair and 50 percent of the total number of drinking fountains provided shall comply with the requirements for standing persons.
1109.5.3 Container faucets. | Where a separate faucet designed for filling a container is provided at the drinking fountain pursuant to Section 410.1 of the New York City Plumbing Code, such container faucet shall comply with Section 606.4 of ICC A117.1.
1109.6 Saunas and steam rooms. | Where provided, saunas and steam rooms shall be accessible. Such saunas and steam rooms shall comply with Section 612 of ICC A117.1.
1109.7 Elevators. | All passenger elevators on an accessible route shall be accessible and comply with ICC A117.1 and Chapter 30 of this code.
1109.7.1 Limited-Use/Limited-Application (LULA) elevators. | LULA elevators shall comply with Section 408 (Limited-Use/Limited-Application Elevators) of ICC A117.1 and with Part 5.2 of ASME A17.1 as modified by Appendix K of this code, and shall be limited to a maximum rise of not more than 25 feet (7620 mm). In new construction, such LULA elevators shall be permitted:
1109.7.1.1 Prior code buildings. | In prior code buildings, LULA elevators shall comply with Section 408 (Limited-use/Limited-Application Elevators) of ICC A117.1 and with Part 5.2 of ASME A17.1 as modified by Appendix K of this code. LULA elevators shall be limited to a maximum rise of not more than 25 feet (7620 mm) and shall be permitted to be a part of the required accessible route as follows:
1109.7.2 Destination–oriented elevators. | Where destination-oriented elevators are provided, hall call consoles shall comply with Sections 1109.7.2.1 through 1109.7.2.3. Responding elevator cars shall comply with Section 1109.7.2.5.
1109.7.2.1 Hall call console number and location. | Hall call consoles shall be located and provided in a number complying with Section 1109.7.2.1.1 or 1109.7.2.1.2, as applicable. Where provided, hall call consoles shall be located on accessible routes connecting to the elevator landings they serve.
1109.7.2.1.1 Transfer floors, sky lobbies and floors containing building entrances. | Elevator landings on transfer floors, sky lobbies and floors containing building entrances shall provide at least one wall-mounted hall call console adjacent to each elevator hoistway entrance. When the accessibility function button is activated, the system shall assign an elevator car located to one side (left or right) of the hall call console to be the responding elevator.
1109.7.2.1.2 Other floors. | Floors other than those subject to Section 1109.7.2.1.1 shall provide one hall call console for every five elevators, or fraction thereof, on each side of the elevator landing. The hall call console shall be located immediately adjacent to one or more elevator hoistway entrances. When the accessibility function button is activated, the system shall assign the elevator car located closest to one side (left or right) of the hall call console to be the responding elevator.
1109.7.2.2 Required features. | Hall call consoles shall include the features specified in this section. Consoles shall not be flush with the surrounding surfaces and shall protrude or be recessed a minimum of ¾ inch (19 mm) and a maximum 4 inches (101.6 mm).
1109.7.2.2.1 Accessibility function button. | Hall call consoles shall provide accessibility function buttons complying with Section 1109.7.2.2.1.
1109.7.2.2.1.1 Upon Activation. | The accessibility function button shall be programed to activate the audio output required by Section 1109.7.2.2.2.
1109.7.2.2.1.2 Identification. | Accessibility function buttons shall be visibly and tactilely identified. The visible identification shall consist of the International Symbol of Accessibility or the dynamic accessibility symbol and shall be a minimum height of 5/8 inch (15.9 mm). The visible symbol shall contrast with its background, light-on-dark or dark-on-light. The tactile identification shall consist of three raised dots. All dots shall be the same size and shall have a base diameter of 0.059 inch (1.5 mm) minimum and 0.063 inch (1.6 mm) maximum. Dot height shall be 0.025 inch (0.6 mm) minimum and 0.037 inch (0.9 mm) maximum. The dots shall be spaced ¼ inch (6.4 mm) at base diameter, measured center to center, and shall be arranged in the form of an equilateral triangle with the vertex pointing up.
1109.7.2.2.2 Audio output. | Audio output shall be provided for floor selection and responding elevator identification. Audio output shall be initiated upon activation of the accessibility function button and shall comply with Sections 1109.7.2.2.2.1 and 1109.7.2.2.2.
1109.7.2.2.2.1 Content. | Audio output shall include all the information necessary to successfully call and locate the responding elevator without the use of a visual display including, but not limited to operating instructions, floor selection options, confirmation of floor selection, responding elevator car designation, directions to the responding elevator car and error messages.
1109.7.2.2.2.2 Delivery method and volume. | Audio output shall be provided through a mechanism that does not require the use of private listening devices, and that is located at the hall call console. Audio output shall commence within one second of the activation of the accessibility function button. Audio output shall be synthesized speech or recorded or digitized human speech. Volume shall be a minimum of 10 dBA above ambient sound level, measured during peak occupancy, but shall not exceed 80 dB, measured horizontally 36 inches (914.4 mm) from the source. Audio output for floor selection shall commence at the hall call console used within one second of activation of the accessibility function button. Audio output for responding car identification shall commence when the elevator arrives and shall be repeated until the elevator doors begin to close.
1109.7.2.2.3 Visible display screen. | Visible display screens, including touchscreens, shall be provided in accordance with this section.
1109.7.2.2.3.1 Contrast. | Characters, numbers and symbols shall contrast with the background on which they are displayed at a ratio of 4.5:1 (relative illuminance). The background shall be solid and static.
1109.7.2.2.3.2 Size. | Characters, numbers and symbols shall be a minimum height of 5/8 inch (15.9 mm).
1109.7.2.2.3.3 Duration. | Elevator assignment characters and numbers shall be displayed for a minimum of five seconds.
1109.7.2.2.4 Floor selection controls. | Hall call consoles shall provide a method of floor selection that does not require user vision. Input methods shall comply with Section 1109.7.2.2.4.1 or 1109.7.2.2.4.2.
1109.7.2.2.4.1 Numeric keypad. | Numeric keypads shall be a minimum of 2¾ inches (69.9 mm) wide by 5 inches (127 mm) high and shall be arranged in a 12-key ascending telephone keypad layout. Individual keys shall be tactilely discernible, and the number five key shall be tactilely distinct from the other keys. Where the keypad provides an alphabetic overlay on numeric keys, the relationships between letters and digits shall conform to ITU-T Recommendation E.161.
1109.7.2.2.4.2 Step scanner. | Step scanners shall consist of three horizontally arranged buttons. The center button shall serve as the “select” button and may also serve as the accessibility function button. The button to the right of the center button shall be the “up” button and the button to the left of the center button shall be the “down” button. When the “up” and “down” buttons are pressed and released, the scanner shall announce the next floor above and below, respectively. When the user releases the “up” or “down” button, the system shall pause to allow the user to press the “select” button. If the “select” button is not chosen, the system shall resume at the next floor in the sequence when the button is again depressed. In buildings with more than ten floor levels, when the “up” or “down” buttons are depressed and held for more than three seconds, the scanner shall present options for floor selection in groups of ten beginning with the next group of ten above or below the floor last announced. An interval of silence, one second minimum and two seconds maximum, shall be provided between such announcements.
1109.7.2.2.5 Tactile discernibility. | Accessibility function buttons and floor selection controls shall be tactilely discernible and shall be raised above surrounding surfaces. When pressed, buttons shall provide mechanical motion to indicate activation. Where a step scanner complying with Section 1109.7.2.2.4.2 is provided, the “up” and “down” arrows shall include tactilely discernible “up” and “down” arrows. The “up” and “down” arrows shall be tactilely distinct from the tactile marking on the accessibility function button.
1109.7.2.3 Hall call console arrangement. | Features of hall call consoles shall be arranged in accordance with Section 1109.7.2.3. Where an accessibility function button complying with Sections 1109.7.2.2.1 and 1109.7.2.3.1 also serves as the “select” button, the provisions of Section 1109.7.2.3.2 shall not apply.
1109.7.2.3.1 Accessibility function button. | The accessibility function button shall be located at a height of 36 inches (914.4 mm) minimum and a maximum of 42 inches (1066.8 mm) above the finish floor and shall be nominally centered on the hall call console.
1109.7.2.3.2 Floor selection controls. | Floor selection controls shall be located above the accessibility function button and shall be no higher than 48 inches (1220 mm) above the finish floor and shall be nominally centered on the console.
1109.7.2.3.3 Display screens. | Where provided, display only screens shall be located above the floor selection controls.
1109.7.2.4 Instructions. | Where hall call consoles are provided, written instructions on the proper use shall be posted in a conspicuous location, adjacent to such devices. The instructions shall include, but are not limited to, operating instructions, and console features.
1109.7.2.5 Responding car. | When an elevator car responds to a call following activation of the accessibility function button, it shall provide audio output complying with Section 1109.7.2.2.2. In addition, during travel, the responding car shall provide an in-car announcement of all floors on which it stops.
1109.8 Lifts. | Platform (wheelchair) lifts shall not be a part of a required accessible route in new construction except as indicated in Items 1 through 10. Platform (wheelchair) lifts shall be installed in accordance with Section 410 (Platform Lifts) of ICC A117.1, ASME A18.1, and Chapter 30 of this code. Platform (wheelchair) lifts are permitted to be part of a required accessible route in new construction as follows:
1109.8.1 Prior code buildings. | In prior code buildings, platform (wheelchair) lifts installed in accordance with Section 410 (Platform Lifts) of ICC A117.1, ASME A18.1, and Chapter 30 of this code, shall be permitted to be a part of the required accessible route.
1109.9 Storage. | Where fixed or built-in storage elements including but not limited to cabinets, coat hooks, shelves, medicine cabinets, lockers, closets and drawers are provided in required accessible spaces, at least 5 percent, but not less than one of each type shall be accessible.
1109.9.1 Equity. | Accessible facilities and spaces shall be provided with the same storage elements as provided in the similar nonaccessible facilities and spaces.
1109.9.2 Shelving and display units. | Self-service shelves and display units shall be located on an accessible route. Such shelving and display units shall not be required to comply with reach-range provisions.
1109.9.3 Cycle storage. | Cycle storage shall comply with Section 905 (Storage Facilities) of ICC A117.1 and Sections 1109.9.3.1 through 1109.9.3.4 of this code.
1109.9.3.1 Accessible cycle storage. | Where cycle storage is provided, 10 percent of the total number, but not less than one, shall be a minimum of 86 inches (2184.4 mm) long and 42 inches (1066.8 mm) wide to accommodate the storage of an accessible cycle.
1109.9.3.2 Accessible route. | At least one accessible route shall connect to the accessible cycle storage area.
1109.9.3.3 Turning space. | A turning space shall be provided and comply with Section 304 (Turning Space) of ICC A117.1.
1109.9.3.4 Loading area. | A clear floor space shall be located on the long side of the accessible cycle storage and shall comply with Section 305 (Clear Floor Space) of ICC A117.1.
1109.10 Detectable warnings. | Detectable warnings shall be provided where required in Sections 1109.10.1 through 1109.10.3.
1109.10.1 Detectable warnings at passenger transit platforms. | Passenger transit platform edges bordering a drop-off and not protected by platform screens or guards shall have a detectable warning.
1109.10.2 Detectable warnings at pools. | The edges of reflecting pools and similar decorative pools without physical barriers, and in which occupants are not expected or permitted to engage in swimming, bathing, therapeutic or other physical activities, shall be provided with detectable warnings.
1109.10.3 Detectable warnings at curb ramps. | A curb ramp shall have a detectable warning. The detectable warning shall extend the full width and a depth of 24 inches (609.2 mm) along the curb ramp. The curb ramp shall comply with Section 406 of ICC A117.1.
1109.11 Seating at tables, counters and work surfaces. | Where seating or standing space at fixed or built-in tables, counters or work surfaces is provided in accessible spaces, at least 10 percent of the total number of seating and standing spaces, but not less than one of each type, shall be accessible.
1109.11.1 Dispersion. | Accessible fixed or built-in seating at tables, counters or work surfaces shall be distributed throughout the space or facility containing such elements and located on a level accessed by an accessible route.
1109.11.2 Visiting areas. | Visiting areas in judicial facilities and Group I-3 shall comply with Sections 1109.11.2.1 and 1109.11.2.2.
1109.11.2.1 Cubicles and counters. | At least 5 percent, but not less than one of the cubicles, shall be accessible on both the visitor and detainee sides. Where counters are provided, at least one shall be accessible on both the visitor and detainee sides.
1109.11.2.2 Partitions. | Where solid partitions or security glazing separate visitors from detainees, at least one of each type of cubicle or counter partition shall be accessible.
1109.12 Service facilities. | Service facilities shall provide for accessible features in accordance with Sections 1109.12.1 through 1109.12.5.
1109.12.1 Dressing, fitting and locker rooms. | Where dressing rooms, fitting rooms or locker rooms are provided, at least 5 percent, but not less than one, of each type of use in each cluster provided shall be accessible.
1109.12.2 Check-out aisles. | Where check-out aisles are provided, accessible check-out aisles shall be provided in accordance with Table 1109.12.2. Where check-out aisles serve different functions, accessible check-out aisles shall be provided in accordance with Table 1109.12.2 for each function. Where check-out aisles are dispersed throughout the building or facility, accessible check-out aisles shall also be dispersed. Traffic control devices, security devices and turnstiles located in accessible check-out aisles or lanes shall be accessible. |  |  |  | See BC11 Tables&Figures
1109.12.3 Point of sale and service counters. | Where counters are provided for sales or distribution of goods or services, at least one of each type provided shall be accessible. Where such counters are dispersed throughout the building or facility, accessible counters shall also be dispersed.
1109.12.4 Food service lines. | Food service lines shall be accessible. Where self-service shelves are provided, at least 50 percent, but not less than one, of each type provided shall be accessible.
1109.12.5 Queue and waiting lines. | Queue and waiting lines servicing accessible counters or check-out aisles shall be accessible.
1109.13 Controls, operating mechanisms and hardware. | Controls, operating mechanisms and hardware intended for operation by the occupant, including switches that control lighting and ventilation and electrical convenience outlets, in accessible spaces, along accessible routes or as parts of accessible elements shall be accessible.
1109.13.1 Operable windows. | Where operable windows are provided in rooms or spaces that are required to be accessible in accordance with Sections 1107.5.1, 1107.5.2, 1107.5.3, 1107.5.4, 1107.6.1.1, or 1107.6.1.4.1, at least one window in each room shall be accessible and each required operable window shall be accessible. Where operable windows are provided in Type B+NYC units in accordance with Section 1107.6.2, such windows shall comply with Section 1107.2.4.
1109.14 Fuel-dispensing systems. | Fuel-dispensing systems shall be accessible.
1109.15 Gaming machines and gaming tables. | Five percent, but not less than one, of each type of gaming table provided shall be accessible and provided with a front approach. Five percent of gaming machines provided shall be accessible and provided with a front approach. Accessible gaming machines shall be distributed throughout the different types of gaming machines provided.
1109.16 Stairways. | Stairways located alongside accessible routes connecting floor levels that are not connected by an elevator shall be designed and constructed to comply with ICC A117.1 and Chapter 10 of this code.
1109.17 Refuse disposal, refuse recyclable and refuse storage rooms. | Refuse disposal, refuse recyclable and refuse storage rooms intended for common-use shall comply with this section. Each room must comply with Section 304 (Turning Space), Section 305 (Clear Floor Space), Section 309 (Operable Parts) and Section 404 (Doors and Doorways) of ICC A117.1. The room door is permitted to swing into the room provided that a clear floor space not less than 30 inches by 48 inches (762 mm by 1220 mm) is provided within the room and beyond the arc of the door swing.
1110.1 General. | Recreational facilities shall be provided with accessible features in accordance with Sections 1110.2 through 1110.4. | 1110.1 General. | Accessible building features and facilities shall be provided in accordance with Sections 1110.2 through 1110.16.
1110.2 Facilities serving Group R-2 and R-3 occupancies. | Recreational facilities that serve Group R-2 and R-3 occupancies shall comply with Sections 1110.2.1 through 1110.2.3, as applicable.
1110.2.1 Facilities serving Accessible units. | In Group R-2 occupancies where recreational facilities serve Accessible units, every recreational facility of each type serving Accessible units shall be accessible.
1110.2.2 Facilities serving Type A, Type B+NYC and Type B units in a single building. | In Group R-2 and R-3 occupancies and where there are four or more dwelling units, where common recreational facilities serve a single building containing Type A, Type B+NYC units or Type B units, 25 percent, but not less than one, of each type of recreational facility shall be accessible. Every recreational facility of each type on a site shall be considered to determine the total number of each type that is required to be accessible.
1110.2.3 Facilities serving Type A, Type B+NYC and Type B units in multiple buildings. | In Group R-2 and R-3 occupancies, where there are four or more dwelling units within a single structure, on a single site where multiple buildings containing Type A, Type B+NYC units or Type B units are served by common recreational facilities, 25 percent, but not less than one, of each type of recreational facility serving each building shall be accessible. The total number of each type of recreational facility that is required to be accessible shall be determined by considering every recreational facility of each type serving each building on the site.
1110.3 Other occupancies. | Recreational facilities not falling within the purview of Section 1110.2 shall be accessible.
1110.4 Recreational facilities. | Recreational facilities shall be accessible and shall be on an accessible route to the extent specified in this section.
1110.4.1 Area of sport activity. | Each area of sport activity shall be on an accessible route and shall not be required to be accessible except as provided for in Sections 1110.4.2 through 1110.4.14.
1110.4.2 Team or player seating. | At least one wheelchair space shall be provided in team or player seating areas serving areas of sport activity.
1110.4.3 Bowling lanes. | An accessible route shall be provided to at least 5 percent, but not less than one, of each type of bowling lane.
1110.4.4 Court sports. | In court sports, at least one accessible route shall directly connect both sides of the court.
1110.4.5 Raised boxing or wrestling rings. | Raised boxing or wrestling rings are not required to be accessible or to be on an accessible route.
1110.4.6 Raised refereeing, judging and scoring areas. | Raised structures used solely for refereeing, judging or scoring a sport are not required to be accessible or to be on an accessible route.
1110.4.7 Animal containment areas. | Animal containment areas that are not within public use areas are not required to be accessible or to be on an accessible route.
1110.4.8 Amusement rides. | Amusement rides that move persons through a fixed course within a defined area shall comply with Sections 1110.4.8.1 through 1110.4.8.3.
1110.4.8.1 Load and unload areas. | Load and unload areas serving amusement rides shall be accessible and be on an accessible route. Where load and unload areas have more than one loading or unloading position, at least one loading and unloading position shall be on an accessible route.
1110.4.8.2 Wheelchair spaces, ride seats designed for transfer and transfer devices. | Where amusement rides are in the load and unload position, the following shall be on an accessible route.
1110.4.8.3 Minimum number. | Amusement rides shall provide at least one wheelchair space, amusement ride seat designed for transfer or a transfer device.
1110.4.9 Recreational boating facilities. | Boat slips required to be accessible by Sections 1110.4.9.1 and 1110.4.9.2 and boarding piers at boat launch ramps required to be accessible by Section 1110.4.9.3 shall be on an accessible route.
1110.4.9.1 Boat slips. | Accessible boat slips shall be provided in accordance with Table 1110.4.9.1. All units on the site shall be combined to determine the number of accessible boat slips required. Where the number of boat slips is not identified, each 40 feet (12 m) of boat slip edge provided along the perimeter of the pier shall be counted as one boat slip for the purpose of this section. |  |  |  | See BC11 Tables&Figures
1110.4.9.2 Dispersion. | Accessible boat slips shall be dispersed throughout the various types of boat slips provided. Where the minimum number of accessible boat slips has been met, no further dispersion shall be required.
1110.4.9.3 Boarding piers at boat launch ramps. | Where boarding piers are provided at boat launch ramps, at least 5 percent, but not less than one, of the boarding piers shall be accessible.
1110.4.10 Exercise machines and equipment. | At least one of each type of exercise machine and equipment shall be on an accessible route and shall be in compliance with Section 1104 (Exercise Machines and Equipment) of ICC A117.1.
1110.4.11 Fishing piers and platforms. | Fishing piers and platforms shall be accessible and be located on an accessible route and shall be in compliance with Section 1105 (Fishing Piers and Platforms) of ICC A117.1.
1110.4.12 Miniature golf facilities. | Miniature golf facilities shall be accessible and shall comply with Section 1107 (Miniature Golf Facilities) of ICC A117.1.
1110.4.13 Swimming pools, wading pools, hot tubs and spas. | Swimming pools, wading pools, hot tubs and spas shall be accessible and be on an accessible route.
1110.4.13.1 Raised diving boards and diving platforms. | Raised diving boards and diving platforms are not required to be accessible or to be on an accessible route.
1110.4.13.2 Water slides. | Water slides are not required to be accessible or to be on an accessible route.
1110.4.14 Shooting facilities with firing positions. | Where shooting facilities with firing positions are designed and constructed at a site, at least 10 percent, but not less than one, of each type of firing position shall be accessible and be on an accessible route.
1111.1 Signs. | Required accessible elements shall be identified by the dynamic accessibility symbol, in accordance with Figure 1111.1, at the following locations.
1111.2 Directional signage. | Directional signage indicating the route to the nearest like accessible element shall be provided at or in close proximity to the following locations, such that an individual with disabilities will not be required to retrace the approach route from the inaccessible element.
1111.3 Other signs. | Signage indicating special accessibility provisions shall be provided as follows:
1111.4 Variable message signs. | Where provided in the locations in Sections 1111.4.1 and 1111.4.2 of this code, variable message signs shall comply with the variable message sign requirements of ICC A117.1.
1111.4.1 Transportation facilities. | Where provided in transportation facilities, variable message signs conveying transportation-related information shall comply with Section 1111.4 of this code.
1111.4.2 Emergency shelters. | Where provided in buildings that are designated as emergency shelters, variable message signs conveying emergency-related information shall comply with Section 1111.4 of this code.
|  | 1102.1 Design. | Buildings and facilities shall be designed and constructed to be accessible in accordance with this code and ICC A117.1.
|  | 1103.2.8 Areas in places of religious worship. | Raised or lowered areas, or portions of areas, in places of religious worship that are less than 300 square feet (30 m2) in area and located 7 inches (178 mm) or more above or below the finished floor and used primarily for the performance of religious ceremonies are not required to comply with this chapter.
|  | 1103.2.10 Highway tollbooths. | Highway tollbooths where the access is provided only by bridges above the vehicular traffic or underground tunnels are not required to comply with this chapter.
|  | 1103.2.11 Residential Group R-1. | Buildings of Group R-1 containing not more than five sleeping units for rent or hire that are also occupied as the residence of the proprietor are not required to comply with this chapter.
|  | 1103.2.12 Day care facilities. | Where a day care facility is part of a dwelling unit, only the portion of the structure utilized for the day care facility is required to comply with this chapter.
|  | 1104.4 Multistory buildings and facilities. | At least one accessible route shall connect each accessible story, mezzanine and occupied roofs in multilevel buildings and facilities.
|  | 1105.1.1 Automatic doors. | In facilities with the occupancies and building occupant loads indicated in Table 1105.1.1, public entrances that are required to be accessible shall have one door be either a full power-operated door or a low-energy power-operated door. Where the public entrance includes a vestibule, at least one door into and one door out of the vestibule shall meet the requirements of this section. |  | See BC11 Tables&Figures
|  | 1105.1.2 Parking garage entrances. | Where provided, direct access for pedestrians from parking structures to buildings or facility entrances shall be accessible.
|  | 1105.1.3 Entrances from tunnels or elevated walkways. | Where direct access is provided for pedestrians from a pedestrian tunnel or elevated walkway to a building or facility, at least one entrance to the building or facility from each tunnel or walkway shall be accessible.
|  | 1105.1.4 Restricted entrances. | Where restricted entrances are provided to a building or facility, at least one restricted entrance to the building or facility shall be accessible.
|  | 1105.1.5 Entrances for inmates or detainees. | Where entrances used only by inmates or detainees and security personnel are provided at judicial facilities, detention facilities or correctional facilities, at least one such entrance shall be accessible.
|  | 1105.1.6 Service entrances. | If a service entrance is the only entrance to a building or a tenant space in a facility, that entrance shall be accessible.
|  | 1105.1.7 Tenant spaces. | At least one accessible entrance shall be provided to each tenant in a facility.
|  | 1105.1.8 Dwelling units and sleeping units. | At least one accessible entrance shall be provided to each dwelling unit and sleeping unit in a facility.
|  | 1106.1 General. | Parking shall comply with Sections 1106.2 through 1106.8. Passenger loading zones shall comply with Section 1106.9.
|  | 1106.2 Required. | Where parking is provided, accessible parking spaces shall be provided in compliance with Table 1106.2, except as required by Sections 1106.3 through 1106.5. Where more than one parking facility is provided on a site, the number of parking spaces required to be accessible shall be calculated separately for each parking facility. |  | See BC11 Tables&Figures
|  | 1106.3 Groups I-1, R-1, R-2, R-3 and R-4. | Accessible parking spaces shall be provided in Group I-1, R-1, R-2, R-3 and R-4 occupancies in accordance with Items 1 through 4 as applicable.
|  | 1106.4 Hospital outpatient facilities. | At least 10 percent, but not less than one, of care recipient and visitor parking spaces provided to serve hospital outpatient facilities shall be accessible.
|  | 1106.5 Rehabilitation facilities and outpatient physical therapy facilities. | At least 20 percent, but not less than one, of the portion of care recipient and visitor parking spaces serving rehabilitation facilities specializing in treating conditions that affect mobility and outpatient physical therapy facilities shall be accessible.
|  | 1106.6 Van spaces. | For every six or fraction of six accessible parking spaces, at least one shall be a van-accessible parking space.
|  | 1106.7 Location. | Accessible parking spaces shall be located on the shortest accessible route of travel from adjacent parking to an accessible building entrance. In parking facilities that do not serve a particular building, accessible parking spaces shall be located on the shortest route to an accessible pedestrian entrance to the parking facility. Where buildings have multiple accessible entrances with adjacent parking, accessible parking spaces shall be dispersed and located near the accessible entrances.
|  | 1106.8 Parking meters and pay stations. | Where parking meters and pay stations serve accessible parking spaces, such parking meters and pay stations shall be accessible.
|  | 1106.9 Passenger loading zones. | Passenger loading zones shall be accessible.
|  | 1106.9.1 Continuous loading zones. | Where passenger loading zones are provided, one passenger loading zone in every continuous 100 linear feet (30.4 m) maximum of loading zone space shall be accessible.
|  | 1106.9.2 Medical facilities. | A passenger loading zone shall be provided at an accessible entrance to licensed medical and long-term care facilities where people receive physical or medical treatment or care and where the period of stay exceeds 24 hours.
|  | 1106.9.3 Valet parking. | A passenger loading zone shall be provided at valet parking services.
|  | 1106.9.4 Mechanical access parking garages. | Mechanical access parking garages shall provide at least one passenger loading zone at vehicle drop-off and vehicle pick-up areas.
|  | 1107.2 Electrical vehicle charging stations. | Electrical vehicle charging stations shall comply with Sections 1107.2.1 and 1107.2.2.
|  | 1107.2.1 Number of accessible vehicle spaces. | Not less than 5 percent of vehicle spaces on the site served by electrical vehicle charging systems, but not fewer than one for each type of electric vehicle charging system, shall be accessible.
|  | 1107.2.2 Vehicle space size. | Accessible vehicle spaces shall comply with the requirements for a van accessible parking space that is 132 inches (3350 mm) minimum in width with an adjoining access aisle that is 60 inches (1525 mm) minimum in width.
|  | 1107.3 Fuel-dispensing systems. | Fuel-dispensing systems shall be accessible.
|  | 1108.2 Design. | Dwelling units and sleeping units that are required to be Accessible units, Type A units and Type B units shall comply with the applicable portions of Chapter 11 of ICC A117.1. Units required to be Type A units are permitted to be designed and constructed as Accessible units. Units required to be Type B units are permitted to be designed and constructed as Accessible units or as Type A units.
|  | 1108.3 Accessible spaces. | Rooms and spaces available to the general public or available for use by residents and serving Accessible units, Type A units or Type B units shall be accessible. Accessible spaces shall include toilet and bathing rooms, kitchen, living and dining areas and any exterior spaces, including patios, terraces and balconies.
|  | 1108.4 Accessible route. | Not fewer than one accessible route shall connect accessible building or facility entrances with the primary entrance of each Accessible unit, Type A unit and Type B unit within the building or facility and with those exterior and interior spaces and facilities that serve the units.
|  | 1108.5 Group I. | Accessible units and Type B units shall be provided in Group I occupancies in accordance with Sections 1108.5.1 through 1108.5.5.
|  | 1108.5.1 Group I-1. | Accessible units and Type B units shall be provided in Group I-1 occupancies in accordance with Sections 1108.5.1.1 and 1108.5.1.3.
|  | 1108.5.1.1 Accessible units. | In Group I-1, Condition 1, at least 4 percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. Accessible dwelling units and sleeping units shall be dispersed among the various classes of units.
|  | 1108.5.1.2 Accessible units in Group I-1, Condition 2. | In Group I-1, Condition 2, at least 10 percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units. Accessible dwelling units and sleeping units shall be dispersed among the various classes of units.
|  | 1108.5.1.3 Type B units. | In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.5.2 Group I-2 nursing homes. | Accessible units and Type B units shall be provided in nursing homes of Group I-2, Condition 1 occupancies in accordance with Sections 1108.5.2.1 and 1108.5.2.2.
|  | 1108.5.2.1 Accessible units. | At least 50 percent but not less than one of each type of the dwelling units and sleeping units shall be Accessible units.
|  | 1108.5.2.2 Type B units. | In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.5.3 Group I-2 hospitals. | Accessible units and Type B units shall be provided in general-purpose hospitals, psychiatric facilities and detoxification facilities of Group I-2 occupancies in accordance with Sections 1108.5.3.1 and 1108.5.3.2.
|  | 1108.5.3.1 Accessible units. | At least 10 percent, but not less than one, of the dwelling units and sleeping units shall be Accessible units.
|  | 1108.5.3.2 Type B units. | In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.5.4 Group I-2 rehabilitation facilities. | In hospitals and rehabilitation facilities of Group I-2 occupancies that specialize in treating conditions that affect mobility, or units within either that specialize in treating conditions that affect mobility, 100 percent of the dwelling units and sleeping units shall be Accessible units.
|  | 1108.5.5 Group I-3. | Accessible units shall be provided in Group I-3 occupancies in accordance with Sections 1108.5.5.1 through 1108.5.5.3.
|  | 1108.5.5.1 Group I-3 sleeping units. | In Group I-3 occupancies, at least 3 percent of the total number of sleeping units in the facility, but not less than one unit in each classification level, shall be Accessible units.
|  | 1108.5.5.2 Special holding cells and special housing cells or rooms. | In addition to the Accessible units required by Section 1108.5.5.1, where special holding cells or special housing cells or rooms are provided, at least one serving each purpose shall be an Accessible unit. Cells or rooms subject to this requirement include, but are not limited to, those used for purposes of orientation, protective custody, administrative or disciplinary detention or segregation, detoxification and medical isolation.
|  | 1108.5.5.3 Medical care facilities. | Patient sleeping units or cells required to be Accessible units in medical care facilities shall be provided in addition to any medical isolation cells required to comply with Section 1108.5.5.2.
|  | 1108.6 Group R. | Accessible units, Type A units and Type B units shall be provided in Group R occupancies in accordance with Sections 1108.6.1 through 1108.6.4.
|  | 1108.6.1 Group R-1. | Accessible units and Type B units shall be provided in Group R-1 occupancies in accordance with Sections 1108.6.1.1 and 1108.6.1.2.
|  | 1108.6.1.1 Accessible units. | Accessible dwelling units and sleeping units shall be provided in accordance with Table 1108.6.1.1. On a multiple-building site, where structures contain more than 50 dwelling units or sleeping units, the number of Accessible units shall be determined per structure. On a multiple-building site, where structures contain 50 or fewer dwelling units or sleeping units, all dwelling units and sleeping units on a site shall be considered to determine the total number of Accessible units. Accessible units shall be dispersed among the various classes of units. |  | See BC11 Tables&Figures
|  | 1108.6.1.2 Type B units. | In structures with four or more dwelling units or sleeping units intended to be occupied as a residence, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.6.2 Group R-2. | Accessible units, Type A units and Type B units shall be provided in Group R-2 occupancies in accordance with Sections 1108.6.2.1 through 1108.6.2.3.
|  | 1108.6.2.1 Live/work units. | In live/work units constructed in accordance with Section 419, the nonresidential portion is required to be accessible. In a structure where there are four or more live/work units intended to be occupied as a residence, the residential portion of the live/work unit shall be a Type B unit.
|  | 1108.6.2.2 Apartment houses, monasteries and convents. | Type A units and Type B units shall be provided in apartment houses, monasteries and convents in accordance with Sections 1108.6.2.2.1 and 1108.6.2.2.2. Bedrooms in monasteries and convents shall be counted as units for the purpose of determining the number of units. Where the bedrooms are grouped in sleeping units, only one bedroom in each sleeping unit shall count toward the number of required Type A units.
|  | 1108.6.2.2.1 Type A units. | In Group R-2 occupancies containing more than 20 dwelling units or sleeping units, at least 2 percent but not less than one of the units shall be a Type A unit. All Group R-2 units on a site shall be considered to determine the total number of units and the required number of Type A units. Type A units shall be dispersed among the various classes of units.
|  | 1108.6.2.2.2 Type B units. | Where there are four or more dwelling units or sleeping units intended to be occupied as a residence in a single structure, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.6.2.3 Group R-2 other than live/work units, apartment houses, monasteries and convents. | In Group R-2 occupancies, other than live/work units, apartment houses, monasteries and convents falling within the scope of Sections 1108.6.2.1 and 1108.6.2.2, Accessible units and Type B units shall be provided in accordance with Sections 1108.6.2.3.1 and 1108.6.2.3.2. Bedrooms within congregate living facilities, dormitories, sororities, fraternities and boarding houses shall be counted as sleeping units for the purpose of determining the number of units. Where the bedrooms are grouped into dwelling or sleeping units, only one bedroom in each dwelling or sleeping unit shall be permitted to count toward the number of required Accessible units.
|  | 1108.6.2.3.1 Accessible units. | Accessible dwelling units and sleeping units shall be provided in accordance with Table 1108.6.1.1. |  | See BC11 Tables&Figures
|  | 1108.6.2.3.2 Type B units. | Where there are four or more dwelling units or sleeping units intended to be occupied as a residence in a single structure, every dwelling unit and every sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.6.3 Group R-3. | In Group R-3 occupancies where there are four or more dwelling units or sleeping units intended to be occupied as a residence in a single structure, every dwelling unit and sleeping unit intended to be occupied as a residence shall be a Type B unit. Bedrooms within congregate living facilities, dormitories, sororities, fraternities, and boarding houses shall be counted as sleeping units for the purpose of determining the number of units.
|  | 1108.6.4 Group R-4. | Accessible units and Type B units shall be provided in Group R-4 occupancies in accordance with Sections 1108.6.4.1 and 1108.6.4.2. Bedrooms in Group R-4 facilities shall be counted as sleeping units for the purpose of determining the number of units.
|  | 1108.6.4.1 Accessible units. | In Group R-4, Condition 1, at least one of the sleeping units shall be an Accessible unit. In Group R-4, Condition 2, at least two of the sleeping units shall be an Accessible unit.
|  | 1108.6.4.2 Type B units. | In structures with four or more sleeping units intended to be occupied as a residence, every sleeping unit intended to be occupied as a residence shall be a Type B unit.
|  | 1108.7 General exceptions. | Where specifically permitted by Section 1108.5 or 1108.6, the required number of Type A units and Type B units is permitted to be reduced in accordance with Sections 1108.7.1 through 1108.7.5.
|  | 1108.7.1 Structures without elevator service. | Where elevator service is not provided in a structure, only the dwelling units and sleeping units that are located on stories indicated in Sections 1108.7.1.1 and 1108.7.1.2 are required to be Type A units and Type B units, respectively. The number of Type A units shall be determined in accordance with Section 1108.6.2.2.1.
|  | 1108.7.1.1 One story with Type B units required. | At least one story containing dwelling units or sleeping units intended to be occupied as a residence shall be provided with an accessible entrance from the exterior of the structure and all units intended to be occupied as a residence on that story shall be Type B units.
|  | 1108.7.1.2 Additional stories with Type B units. | Where stories have entrances not included in determining compliance with Section 1108.7.1.1, and such entrances are proximate to arrival points intended to serve units on that story, as indicated in Items 1 and 2, all dwelling units and sleeping units intended to be occupied as a residence served by that entrance on that story shall be Type B units.
|  | 1108.7.2 Multistory units. | A multistory dwelling unit or sleeping unit that is not provided with elevator service is not required to be a Type B unit. Where a multistory unit is provided with external elevator service to only one floor, the floor provided with elevator service shall be the primary entry to the unit, shall comply with the requirements for a Type B unit and, where provided within the unit, a living area, a kitchen and a toilet facility shall be provided on that floor.
|  | 1108.7.3 Elevator service to the lowest story with units. | Where elevator service in the building provides an accessible route only to the lowest story containing dwelling units or sleeping units intended to be occupied as a residence, only the units on that story that are intended to be occupied as a residence are required to be Type B units.
|  | 1108.7.4 Site impracticality. | On a site with multiple nonelevator buildings, the number of units required by Section 1108.7.1 to be Type B units is permitted to be reduced to a percentage that is equal to the percentage of the entire site having grades, prior to development, that are less than 10 percent, provided that all of the following conditions are met:
|  | 1108.7.5 Flood hazard areas. | Type A units and Type B units shall not be required for buildings without elevator service that are located in flood hazard areas as established in Section 1612.3, where the minimum required elevation of the lowest floor or lowest supporting horizontal structural member, as applicable, results in all of the following:
|  | 1109.2 Assembly area seating. | A building, room or space used for assembly purposes with fixed seating shall comply with Sections 1109.2.1 through 1109.2.5. Lawn seating shall comply with Section 1109.2.6. Assistive listening systems shall comply with Section 1109.2.7. Performance areas viewed from assembly seating areas shall comply with Section 1109.2.8. Dining areas shall comply with Section 1109.2.9.
|  | 1109.2.1 Services. | If a service or facility is provided in an area that is not accessible, the same service or facility shall be provided on an accessible level and shall be accessible.
|  | 1109.2.2 Wheelchair spaces. | In rooms and spaces used for assembly purposes with fixed seating, accessible wheelchair spaces shall be provided in accordance with Sections 1109.2.2.1 through 1109.2.2.3.
|  | 1109.2.2.1 General seating. | Wheelchair spaces shall be provided in accordance with Table 1109.2.2.1. |  | See BC11 Tables&Figures
|  | 1109.2.2.2 Luxury boxes, club boxes and suites. | In each luxury box, club box and suite within arenas, stadiums and grandstands, wheelchair spaces shall be provided in accordance with Table 1109.2.2.1. |  | See BC11 Tables&Figures
|  | 1109.2.2.3 Other boxes. | In boxes other than those required to comply with Section 1109.2.2.2, the total number of wheelchair spaces provided shall be determined in accordance with Table 1109.2.2.1. Wheelchair spaces shall be located in not less than 20 percent of all boxes provided. |  | See BC11 Tables&Figures
|  | 1109.2.3 Companion seats. | At least one companion seat shall be provided for each wheelchair space required by Sections 1109.2.2.1 through 1109.2.2.3.
|  | 1109.2.4 Dispersion of wheelchair spaces in multilevel assembly seating areas. | In multilevel assembly seating areas, wheelchair spaces shall be provided on the main floor level and on one of each two additional floor or mezzanine levels. Wheelchair spaces shall be provided in each luxury box, club box and suite within assembly facilities.
|  | 1109.2.5 Designated aisle seats. | At least 5 percent, but not less than one, of the total number of aisle seats provided shall be designated aisle seats and shall be the aisle seats located closest to accessible routes.
|  | 1109.2.6 Lawn seating. | Lawn seating areas and exterior overflow seating areas, where fixed seats are not provided, shall connect to an accessible route.
|  | 1109.2.7 Assistive listening systems. | Each building, room or space used for assembly purposes where audible communications are integral to the use of the space shall have an assistive listening system.
|  | 1109.2.7.1 Receivers. | The number and type of receivers shall be provided for assistive listening systems in accordance with Table 1109.2.7.1. |  | See BC11 Tables&Figures
|  | 1109.2.7.2 Ticket windows. | Where ticket windows are provided in stadiums and arenas, at least one window at each location shall have an assistive listening system.
|  | 1109.2.7.3 Public address systems. | Where stadiums, arenas and grandstands have 15,000 fixed seats or more and provide audible public announcements, they shall also provide prerecorded or real-time captions of those audible public announcements.
|  | 1109.2.8 Performance areas. | An accessible route shall directly connect the performance area to the assembly seating area where a circulation path directly connects a performance area to an assembly seating area. An accessible route shall be provided from performance areas to ancillary areas or facilities used by performers.
|  | 1109.2.9 Dining and drinking areas. | In dining and drinking areas, all interior and exterior floor areas shall be accessible and be on an accessible route.
|  | 1109.2.9.1 Dining surfaces. | Where dining surfaces for the consumption of food or drink are provided, at least 5 percent, but not less than one, of the dining surfaces for the seating and standing spaces shall be accessible and be distributed throughout the facility and located on a level accessed by an accessible route.
|  | 1109.3 Self-service storage facilities. | Self-service storage facilities shall provide accessible individual self-storage spaces in accordance with Table 1109.3. |  | See BC11 Tables&Figures
|  | 1109.3.1 Dispersion. | Accessible individual self-service storage spaces shall be dispersed throughout the various classes of spaces provided. Where more classes of spaces are provided than the number of required accessible spaces, the number of accessible spaces shall not be required to exceed that required by Table 1109.3. Accessible spaces are permitted to be dispersed in a single building of a multiple-building facility. |  | See BC11 Tables&Figures
|  | 1109.4 Judicial facilities. | Judicial facilities shall comply with Sections 1109.4.1 and 1109.4.2.
|  | 1109.4.1 Courtrooms. | Each courtroom shall be accessible and comply with Sections 1109.4.1.1 through 1109.4.1.5.
|  | 1109.4.1.1 Jury box. | A wheelchair space shall be provided within the jury box.
|  | 1109.4.1.2 Gallery seating. | Wheelchair spaces shall be provided in accordance with Table 1109.2.2.1. Designated aisle seats shall be provided in accordance with Section 1109.2.5. |  | See BC11 Tables&Figures
|  | 1109.4.1.3 Assistive listening systems. | An assistive listening system must be provided. Receivers shall be provided for the assistive listening system in accordance with Section 1109.2.7.1.
|  | 1109.4.1.4 Employee work stations. | The judge’s bench, clerk’s station, bailiff’s station, deputy clerk’s station and court reporter’s station shall be located on an accessible route. The vertical access to elevated employee work stations within a courtroom is not required at the time of initial construction, provided a ramp, lift or elevator can be installed without requiring reconfiguration or extension of the courtroom or extension of the electrical system.
|  | 1109.4.1.5 Other work stations. | The litigant’s and counsel stations, including the lectern, shall be accessible.
|  | 1109.4.2 Holding cells. | Central holding cells and court-floor holding cells shall comply with Sections 1109.4.2.1 and 1109.4.2.2.
|  | 1109.4.2.1 Central holding cells. | Where separate central holding cells are provided for adult males, juvenile males, adult females or juvenile females, one of each type shall be accessible. Where central holding cells are provided and are not separated by age or sex, at least one accessible cell shall be provided.
|  | 1109.4.2.2 Court-floor holding cells. | Where separate court-floor holding cells are provided for adult males, juvenile males, adult females or juvenile females, each courtroom shall be served by one accessible cell of each type. Where court-floor holding cells are provided and are not separated by age or sex, courtrooms shall be served by at least one accessible cell. Accessible cells shall be permitted to serve more than one courtroom.
|  | 1110.2 Toilet and bathing facilities. | Each toilet room and bathing room shall be accessible. Where a floor level is not required to be connected by an accessible route, the only toilet rooms or bathing rooms provided within the facility shall not be located on the inaccessible floor. Except as provided for in Sections 1110.2.4 and 1110.2.5, at least one of each type of fixture, element, control or dispenser in each accessible toilet room and bathing room shall be accessible.
|  | 1110.2.1 Family or assisted-use toilet and bathing rooms. | In assembly and mercantile occupancies, an accessible family or assisted-use toilet room shall be provided where an aggregate of six or more male and female water closets is required. In buildings of mixed occupancy, only those water closets required for the assembly or mercantile occupancy shall be used to determine the family or assisted-use toilet room requirement. In recreational facilities where separate-sex bathing rooms are provided, an accessible family or assisted-use bathing room shall be provided. Fixtures located within family or assisted-use toilet and bathing rooms shall be included in determining the number of fixtures provided in an occupancy.
|  | 1110.2.1.1 Standard. | Family or assisted-use toilet and bathing rooms shall comply with Sections 1110.2.1.2 through 1110.2.1.6.
|  | 1110.2.1.2 Family or assisted-use toilet rooms. | Family or assisted-use toilet rooms shall include only one water closet and only one lavatory. A family or assisted-use bathing room in accordance with Section 1110.2.1.3 shall be considered to be a family or assisted-use toilet room.
|  | 1110.2.1.3 Family or assisted-use bathing rooms. | Family or assisted-use bathing rooms shall include only one shower or bathtub fixture. Family or assisted-use bathing rooms shall also include one water closet and one lavatory. Where storage facilities are provided for separate-sex bathing rooms, accessible storage facilities shall be provided for family or assisted-use bathing rooms.
|  | 1110.2.1.4 Location. | Family or assisted-use toilet and bathing rooms shall be located on an accessible route. Family or assisted-use toilet rooms shall be located not more than one story above or below separate-sex toilet rooms. The accessible route from any separate-sex toilet room to a family or assisted-use toilet room shall not exceed 500 feet (152 m).
|  | 1110.2.1.5 Prohibited location. | In passenger transportation facilities and airports, the accessible route from separate-sex toilet rooms to a family or assisted-use toilet room shall not pass through security checkpoints.
|  | 1110.2.1.6 Privacy. | Doors to family or assisted-use toilet and bathing rooms shall be securable from within the room and be provided with an “occupied” indicator.
|  | 1110.2.2 Water closets designed for assisted toileting. | Water closets designed for assisted toileting shall comply with Sections 1110.2.2.1 through 1110.2.2.6.
|  | 1110.2.2.1 Location. | The centerline of the water closet shall be not less than 24 inches (610 mm) and not greater than 26 inches (660 mm) from one side of the required clearance.
|  | 1110.2.2.2 Clearance. | Clearance around the water closet shall comply with Sections 1110.2.2.2.1 through 1110.2.2.2.3.
|  | 1110.2.2.2.1 Clearance width. | Clearance around a water closet shall be not less than 66 inches (1675 mm) in width, measured perpendicularly from the side of the clearance that is not less than 24 inches (610 mm) and not greater than 26 inches (660 mm) from the water closet centerline.
|  | 1110.2.2.2.2 Clearance depth. | Clearance around the water closet shall be not less than 78 inches (1980 mm) in depth, measured perpendicularly from the rear wall
|  | 1110.2.2.2.3 Clearance overlap. | The required clearance around the water closet shall permit overlaps per ICC A117.1, Section 604.3.3
|  | 1110.2.2.3 Height. | The height of the water closet seats shall comply with ICC A117.1, Section 604.4.
|  | 1110.2.2.4 Swing-up grab bars. | Swing-up grab bars shall comply with ICC A117.1, Sections 609.2 and 609.8. Swing-up grab bars shall be provided on both sides of the water closet and shall comply with all of the following:
|  | 1110.2.2.5 Flush controls. | Flush controls shall comply with ICC A117.1, Section 604.6.
1110.2.2.6 Dispensers Toilet paper dispensers shall be mounted on at least one of the swing-up grab bars and the outlet of the dispenser shall be located not less than 24 inches (610 mm) and not greater than 36 inches (915 mm) from the rear wall.
|  | 1110.2.3 Standard roll-in-type shower compartment designed for assisted bathing. | Standard roll-in-type shower compartments designed for assisted bathing shall comply with Sections 1110.2.3.1 through 1110.2.3.9.
|  | 1110.2.3.1 Size. | Standard roll-in-type shower compartments shall have a clear inside dimension of not less than 60 inches (1525 mm) in width and 30 inches (760 mm) in depth, measured at the center point of opposing sides. An entry not less than 60 inches (1525 mm) in width shall be provided.
|  | 1110.2.3.2 Clearance. | A clearance of not less than 60 inches (1525 mm) in length adjacent to the 60-inch (1525 mm) width of the open face of the shower compartment, and not less than 30 inches (760 mm) in depth, shall be provided.
|  | 1110.2.3.3 Grab bars. | Grab bars shall comply with ICC A117.1, Section 609 and shall be provided in accordance with Sections 1110.2.3.3.1 and 1110.2.3.3.2. In standard roll-in-type shower compartments, grab bars shall be provided on three walls. Where multiple grab bars are used, required horizontal grab bars shall be installed at the same height above the floor. Grab bars can be separate bars or one continuous bar.
|  | 1110.2.3.3.1 Back-wall grab bar. | The back-wall grab bar shall extend the length of the back wall and extend within 6 inches (150 mm) maximum from the two adjacent sidewalls.
|  | 1110.2.3.3.2 Sidewall grab bars. | The sidewall grab bars shall extend the length of the wall and extend within 6 inches (150 mm) of the adjacent back wall.
|  | 1110.2.3.4 Seats. | Wall-mounted folding seats shall not be installed.
|  | 1110.2.3.5 Controls and hand showers. | In standard roll-in-type showers, the controls and hand shower shall be located not less than 38 inches (965 mm) and not greater than 48 inches (1220 mm) above the shower floor. Controls shall be located to facilitate caregiver access.
|  | 1110.2.3.6 Hand showers. | Hand showers shall comply with ICC A117.1, Section 608.5.
|  | 1110.2.3.7 Thresholds. | Thresholds shall comply with ICC A117.1, Section 608.6.
|  | 1110.2.3.8 Shower enclosures. | Shower compartment enclosures for shower compartments shall comply with ICC A117.1, Section 608.7.
|  | 1110.2.3.9 Water temperature. | Water temperature shall comply with ICC A117.1, Section 608.8.
|  | 1110.2.4 Water closet compartment. | Where water closet compartments are provided in a toilet room or bathing room, at least 5 percent of the total number of compartments shall be wheelchair accessible. Where the combined total water closet compartments and urinals provided in a toilet room or bathing room is six or more, at least 5 percent of the total number of compartments shall be ambulatory accessible, provided in addition to the wheelchair-accessible compartment.
|  | 1110.2.5 Lavatories. | Where lavatories are provided, at least 5 percent, but not less than one, shall be accessible. Where an accessible lavatory is located within the accessible water closet compartment at least one additional accessible lavatory shall be provided in the multicompartment toilet room outside the water closet compartment. Where the total lavatories provided in a toilet room or bathing facility is six or more, at least one lavatory with enhanced reach ranges shall be provided.
|  | 1110.3 Sinks. | Where sinks are provided, at least 5 percent but not less than one provided in accessible spaces shall be accessible.
|  | 1110.4 Kitchens and kitchenettes. | Where kitchens and kitchenettes are provided in accessible spaces or rooms, they shall be accessible.
|  | 1110.5 Drinking fountains. | Where drinking fountains are provided on an exterior site, on a floor or within a secured area, the drinking fountains shall be provided in accordance with Sections 1110.5.1 and 1110.5.2.
|  | 1110.5.1 Minimum number. | Not fewer than two drinking fountains shall be provided. One drinking fountain shall comply with the requirements for people who use a wheelchair and one drinking fountain shall comply with the requirements for standing persons.
|  | 1110.5.2 More than the minimum number. | Where more than the minimum number of drinking fountains specified in Section 1110.5.1 is provided, 50 percent of the total number of drinking fountains provided shall comply with the requirements for persons who use a wheelchair and 50 percent of the total number of drinking fountains provided shall comply with the requirements for standing persons.
|  | 1110.6 Bottle-filling stations. | Where bottle-filling stations are provided, they shall be accessible.
|  | 1110.7 Saunas and steam rooms. | Where provided, saunas and steam rooms shall be accessible.
|  | 1110.8 Elevators. | Passenger elevators on an accessible route shall be accessible and comply with Chapter 30.
|  | 1110.9 Lifts. | Platform (wheelchair) lifts are permitted to be a part of a required accessible route in new construction where indicated in Items 1 through 10. Platform (wheelchair) lifts shall be installed in accordance with ASME A18.1.
|  | 1110.10 Storage. | Where fixed or built-in storage elements such as cabinets, coat hooks, shelves, medicine cabinets, lockers, closets and drawers are provided in required accessible spaces, at least 5 percent, but not less than one of each type shall be accessible.
|  | 1110.10.1 Equity. | Accessible facilities and spaces shall be provided with the same storage elements as provided in the similar nonaccessible facilities and spaces.
|  | 1110.10.2 Shelving and display units. | Self-service shelves and display units shall be located on an accessible route. Such shelving and display units shall not be required to comply with reach-range provisions.
|  | 1110.11 Detectable warnings. | Passenger transit platform edges bordering a drop-off and not protected by platform screens or guards shall have a detectable warning.
|  | 1110.12 Seating at tables, counters and work surfaces. | Where seating or standing space at fixed or built-in tables, counters or work surfaces is provided in accessible spaces, at least 5 percent of the seating and standing spaces, but not less than one, shall be accessible.
|  | 1110.12.1 Dispersion. | Accessible fixed or built-in seating at tables, counters or work surfaces shall be distributed throughout the space or facility containing such elements and located on a level accessed by an accessible route.
|  | 1110.12.2 Visiting areas. | Visiting areas in judicial facilities and Group I-3 shall comply with Sections 1110.12.2.1 and 1110.12.2.2.
|  | 1110.12.2.1 Cubicles and counters. | At least 5 percent, but not less than one of the cubicles, shall be accessible on both the visitor and detainee sides. Where counters are provided, at least one shall be accessible on both the visitor and detainee sides.
|  | 1110.12.2.2 Partitions. | Where solid partitions or security glazing separate visitors from detainees, at least one of each type of cubicle or counter partition shall be accessible.
|  | 1110.13 Service facilities. | Service facilities shall provide for accessible features in accordance with Sections 1110.14 through 1110.13.4.
|  | 1110.13.1 Check-out aisles. | Where check-out aisles are provided, accessible check-out aisles shall be provided in accordance with Table 1110.13.1. Where check-out aisles serve different functions, accessible check-out aisles shall be provided in accordance with Table 1110.13.1 for each function. Where check-out aisles are dispersed throughout the building or facility, accessible check-out aisles shall also be dispersed. Traffic control devices, security devices and turnstiles located in accessible check-out aisles or lanes shall be accessible. |  | See BC11 Tables&Figures
|  | 1110.13.2 Sales and service counters and windows. | Where counters or windows are provided for sale or distribution of goods or services, at least one of each type of counter and window provided shall be accessible. Where such counters or windows are dispersed throughout the building or facility, accessible counters or windows shall also be dispersed.
|  | 1110.13.3 Food service lines. | Food service lines shall be accessible. Where self-service shelves are provided, at least 50 percent, but not less than one, of each type provided shall be accessible.
|  | 1110.13.4 Queue and waiting lines. | Queue and waiting lines servicing accessible counters or check-out aisles shall be accessible.
|  | 1110.14 Dressing, fitting and locker rooms. | Where dressing rooms, fitting rooms or locker rooms are provided, at least 5 percent, but not less than one, of each type of use in each cluster provided shall be accessible.
|  | 1110.15 Controls, operating mechanisms and hardware. | Controls, operating mechanisms and hardware intended for operation by the occupant, including switches that control lighting and ventilation and electrical convenience outlets, in accessible spaces, along accessible routes or as parts of accessible elements shall be accessible.
|  | 1110.16 Gaming machines and gaming tables. | At least two percent of the total, but not fewer than one, of each gaming machine type and gaming table type shall be accessible. Where multiple gaming areas occur, accessible gaming machines and gaming tables shall be distributed throughout.
|  | 1111.1 General. | Recreational facilities shall be provided with accessible features in accordance with Sections 1111.2 through 1111.4.
|  | 1111.2 Facilities serving Group R-2, R-3 and R-4 occupancies. | Recreational facilities that serve Group R-2, R-3 and Group R-4 occupancies shall comply with Sections 1111.2.1 through 1111.2.3, as applicable.
|  | 1111.2.1 Facilities serving Accessible units. | In Group R-2 and R-4 occupancies where recreational facilities serve Accessible units, every recreational facility of each type serving Accessible units shall be accessible.
|  | 1111.2.2 Facilities serving Type A and Type B units in a single building. | In Group R-2, R-3 and R-4 occupancies where recreational facilities serve a single building containing Type A units or Type B units, 25 percent, but not less than one, of each type of recreational facility shall be accessible. Every recreational facility of each type on a site shall be considered to determine the total number of each type that is required to be accessible.
|  | 1111.2.3 Facilities serving Type A and Type B units in multiple buildings. | In Group R-2, R-3 and R-4 occupancies on a single site where multiple buildings containing Type A units or Type B units are served by recreational facilities, 25 percent, but not less than one, of each type of recreational facility serving each building shall be accessible. The total number of each type of recreational facility that is required to be accessible shall be determined by considering every recreational facility of each type serving each building on the site.
|  | 1111.3 Other occupancies. | Recreational facilities not falling within the purview of Section 1111.2 shall be accessible.
|  | 1111.4 Recreational facilities. | Recreational facilities shall be accessible and shall be on an accessible route to the extent specified in this section.
|  | 1111.4.1 Area of sport activity. | Each area of sport activity shall be on an accessible route and shall not be required to be accessible except as provided for in Sections 1111.4.2 through 1111.4.15.
|  | 1111.4.2 Team or player seating. | At least one wheelchair space shall be provided in team or player seating areas serving areas of sport activity.
|  | 1111.4.3 Bowling lanes. | An accessible route shall be provided to at least 5 percent, but not less than one, of each type of bowling lane.
|  | 1111.4.4 Court sports. | In court sports, at least one accessible route shall directly connect both sides of the court.
|  | 1111.4.5 Raised boxing or wrestling rings. | Raised boxing or wrestling rings are not required to be accessible or to be on an accessible route.
|  | 1111.4.6 Raised refereeing, judging and scoring areas. | Raised structures used solely for refereeing, judging or scoring a sport are not required to be accessible or to be on an accessible route.
|  | 1111.4.7 Animal containment areas. | Animal containment areas that are not within public use areas are not required to be accessible or to be on an accessible route.
|  | 1111.4.8 Amusement rides. | Amusement rides that move persons through a fixed course within a defined area shall comply with Sections 1111.4.8.1 through 1111.4.8.3.
|  | 1111.4.8.1 Load and unload areas. | Load and unload areas serving amusement rides shall be accessible and be on an accessible route. Where load and unload areas have more than one loading or unloading position, at least one loading and unloading position shall be on an accessible route.
|  | 1111.4.8.2 Wheelchair spaces, ride seats designed for transfer and transfer devices. | Where amusement rides are in the load and unload position, the following shall be on an accessible route.
|  | 1111.4.8.3 Minimum number. | Amusement rides shall provide at least one wheelchair space, amusement ride seat designed for transfer or transfer device.
|  | 1111.4.9 Recreational boating facilities. | Boat slips required to be accessible by Sections 1111.4.9.1 and 1111.4.9.2 and boarding piers at boat launch ramps required to be accessible by Section 1111.4.9.3 shall be on an accessible route.
|  | 1111.4.9.1 Boat slips. | Accessible boat slips shall be provided in accordance with Table 1111.4.9.1. All units on the site shall be combined to determine the number of accessible boat slips required. Where the number of boat slips is not identified, each 40 feet (12 m) of boat slip edge provided along the perimeter of the pier shall be counted as one boat slip for the purpose of this section. |  | See BC11 Tables&Figures
|  | 1111.4.9.2 Dispersion. | Accessible boat slips shall be dispersed throughout the various types of boat slips provided. Where the minimum number of accessible boat slips has been met, further dispersion shall not be required.
|  | 1111.4.9.3 Boarding piers at boat launch ramps. | Where boarding piers are provided at boat launch ramps, at least 5 percent, but not less than one, of the boarding piers shall be accessible.
|  | 1111.4.10 Exercise machines and equipment. | At least one of each type of exercise machine and equipment shall be on an accessible route.
|  | 1111.4.11 Fishing piers and platforms. | Fishing piers and platforms shall be accessible and be on an accessible route.
|  | 1111.4.12 Miniature golf facilities. | Miniature golf facilities shall comply with Sections 1111.4.12.1 through 1111.4.12.3.
|  | 1111.4.12.1 Minimum number. | At least 50 percent of holes on miniature golf courses shall be accessible.
|  | 1111.4.12.2 Miniature golf course configuration. | Miniature golf courses shall be configured so that the accessible holes are consecutive. Miniature golf courses shall provide an accessible route from the last accessible hole to the course entrance or exit without requiring travel through any other holes on the course.
|  | 1111.4.12.3 Accessible route. | Holes required to comply with Section 1111.4.12.1, including the start of play, shall be on an accessible route.
|  | 1111.4.13 Play areas. | Play areas containing play components designed and constructed for children shall be located on an accessible route.
|  | 1111.4.14 Swimming pools, wading pools, cold baths, hot tubs and spas. | Swimming pools, wading pools, cold baths, hot tubs and spas shall be accessible and be on an accessible route.
|  | 1111.4.14.1 Raised diving boards and diving platforms. | Raised diving boards and diving platforms are not required to be accessible or to be on an accessible route.
|  | 1111.4.14.2 Water slides. | Water slides are not required to be accessible or to be on an accessible route.
|  | 1111.4.15 Shooting facilities with firing positions. | Where shooting facilities with firing positions are designed and constructed at a site, at least 5 percent, but not less than one, of each type of firing position shall be accessible and be on an accessible route.
|  | 1112.1 Signs. | Required accessible elements shall be identified by the International Symbol of Accessibility at the following locations.
|  | 1112.2 Signs identifying toilet or bathing rooms. | Signs required in Section 403.4 of the International Plumbing Code identifying toilet rooms and bathing rooms shall be visual characters, raised characters and braille complying with ICC A117.1. Where pictograms are provided as designations for toilet rooms and bathing rooms, the pictograms shall have visual characters, raised characters and braille complying with ICC A117.1.
|  | 1112.3 Directional signage. | Directional signage indicating the route to the nearest like accessible element shall be provided at the following locations. These directional signs shall include the International Symbol of Accessibility and sign characters shall meet the visual character requirements in accordance with ICC A117.1.
|  | 1112.4 Other signs. | Signage indicating special accessibility provisions shall be provided as shown.
|  | 1112.5 Variable message signs. | Where provided in the locations in Sections 1112.5.1 and 1112.5.2, variable message signs shall comply with the variable message sign requirements of ICC A117.1.
|  | 1112.5.1 Transportation facilities. | Where provided in transportation facilities, variable message signs conveying transportation-related information shall comply with Section 1112.5.
|  | 1112.5.2 Emergency shelters. | Where provided in buildings that are designated as emergency shelters, variable message signs conveying emergency-related information shall comply with Section 1112.5.

## BC12
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1201.1 Scope. | The provisions of this chapter shall govern ventilation, temperature control, lighting, yards and courts, sound transmission, room dimensions, surrounding materials and rodent proofing associated with the interior spaces of buildings. | 1201.1 Scope. | The provisions of this chapter shall govern ventilation, temperature control, lighting, yards and courts, sound transmission, room dimensions, surrounding materials and rodentproofing associated with the interior spaces of buildings.
1202.1 Definitions. | The following terms are defined in Chapter 2:
1203.1 General. | Buildings shall be provided with ventilation in accordance with Section 1203.5 of this code and the New York City Mechanical Code.
1203.2 Ventilation required. | Enclosed attics and enclosed rafter spaces formed where ceilings are applied directly to the underside of roof framing members shall have cross ventilation for each separate space by ventilation openings protected against the entrance of rain and snow. Blocking and bridging shall be arranged so as not to interfere with the movement of air. An airspace of not less than 1 inch (25.4 mm) shall be provided between the insulation and the roof sheathing. The net free ventilating area shall be not less than 1/150 of the area of the space ventilated. Ventilators shall be installed in accordance with the manufacturer’s instructions.
1203.2.1 Openings into attic. | Exterior openings into the attic space of any building intended for human occupancy shall be protected to prevent the entry of birds, squirrels, rodents, snakes and other similar creatures. Openings for ventilation having a least dimension of not less than 1/16 inch (1.6 mm) and not more than ¼ inch (6.4 mm) shall be permitted. Openings for ventilation having a least dimension larger than ¼ inch (6.4 mm) shall be provided with corrosion-resistant wire cloth screening, hardware cloth, perforated vinyl or similar material with openings having a least dimension of not less than 1/16 inch (1.6 mm) and not more than ¼ inch (6.4 mm). Where combustion air is obtained from an attic area, it shall be in accordance with Chapter 7 of the New York City Mechanical Code.
1203.3 Unvented attic and unvented enclosed rafter assemblies. | Unvented attics and unvented enclosed roof framing assemblies created by ceilings applied directly to the underside of the roof framing members/rafters and the structural roof sheathing at the top of the roof framing members shall be permitted where all the following conditions are met: 1. The unvented attic space is completely within the building thermal envelope. 2. No interior Class I vapor retarders are installed on the ceiling side (attic floor) of the unvented attic assembly or on the ceiling side of the unvented enclosed roof framing assembly. 3. Where wood shingles or shakes are used, a minimum ¼-inch (6.4 mm) vented airspace separates the shingles or shakes and the roofing underlayment above the structural sheathing. 4. Insulation shall be located in accordance with the following: 4.1. Item 4.1.1, 4.1.2, 4.1.3 or 4.1.4 shall be met, depending on the air permeability of the insulation directly under the structural roof sheathing. 4.1.1. Where only air-impermeable insulation is provided, it shall be applied in direct contact with the underside of the structural roof sheathing. 4.1.2. Where air-permeable insulation is provided inside the building thermal envelope, it shall be installed in accordance with Item 4.1. In addition to the air-permeable insulation installed directly below the structural sheathing, rigid board or sheet insulation shall be installed directly above the structural roof sheathing in accordance with the R values in Table 1203.3 for condensation control. 4.1.3. Where both air-impermeable and air-permeable insulation are provided, the air-impermeable insulation shall be applied in direct contact with the underside of the structural roof sheathing in accordance with Item 4.1.1 and shall be in accordance with the R values in Table 1203.3 for condensation control. The air-permeable insulation shall be installed directly under the air-impermeable insulation. 4.1.4. Alternatively, sufficient rigid board or sheet insulation shall be installed directly above the structural roof sheathing to maintain the monthly average temperature of the underside of the structural roof sheathing above 45°F (7°C). For calculation purposes, an interior air temperature of 68°F (20°C) is assumed and the exterior air temperature is assumed to be the monthly average outside air temperature of the three coldest months. 4.2. Where preformed insulation board is used as the air-permeable insulation layer, it shall be sealed at the perimeter of each individual sheet interior surface to form a continuous layer. Exception: Section 1203.3 does not apply to special use structures or enclosures such as swimming pool enclosures, data processing centers, hospitals or art galleries. |  |  |  | See BC12 Tables&Figures
1203.4 Under-floor ventilation. | The space between the bottom of the floor joists and the surface under any building except spaces occupied by basements or cellars shall be provided with ventilation openings through foundation walls or exterior walls. Such openings shall be placed so as to provide cross ventilation of the under-floor space.
1203.4.1 Openings for under-floor ventilation. | The net area of ventilation openings shall be not less than 1 square foot for each 150 square feet (304.8 mm2 for each 45 720 mm2) of crawl space area. Ventilation openings shall be covered for their height and width with any of the following materials, provided that the least dimension of the covering shall be not greater than ¼ inch (6.4 mm):
1203.4.2 Exceptions. | The following are exceptions to Sections 1203.4 and 1203.4.1: 1. Where warranted by climatic conditions, ventilation openings to the outdoors are not required if ventilation openings to the interior are provided. 2. The total area of ventilation openings is permitted to be reduced to 1/1,500 of the under-floor area where the ground surface is covered with a Class I vapor retarder material and the required openings are placed so as to provide cross ventilation of the space. The installation of operable louvers, in accordance with Section 1203.4.1, shall not be prohibited. 3. Ventilation openings are not required where continuously operated mechanical ventilation is provided at a rate of 1.0 cubic foot per minute (cfm) for each 50 square feet (1.02 L/s for each 10 m2) of crawl space floor area and the ground surface is covered with a Class I vapor retarder. 4. Ventilation openings are not required where the ground surface is covered with a Class I vapor retarder, the perimeter walls are insulated and the space is conditioned in accordance with the New York City Energy Conservation Code. 5. Openings for under-floor ventilation for buildings in flood hazard areas shall also comply with the additional requirements of Appendix G.
1203.5 Natural ventilation. | Natural ventilation of occupiable and habitable space shall be through openings to the outdoors. The openings shall be of a type permitted under Sections 1203.5.1.1, 1203.5.1.2, 1203.5.1.3 and 1203.5.1.4. The operating mechanism for such openings shall be provided with ready access so that the openings are readily controllable by the building occupants. Exception: An opening providing the required dimensional operable area shall be permitted to be reduced by limiting devices in accordance with the New York City Health Code, provided that the owner shall remove such limiting devices where requested by the occupant. In such cases, where required by the New York City Health Code, alternative means of compliance shall be provided in accordance with the New York City Health Code.
1203.5.1 Ventilation area required. | Ventilation areas shall be as set forth in Sections 1203.5.1.1 through 1203.5.1.4.
1203.5.1.1 Occupiable spaces. | Where occupiable spaces are not required to be provided with mechanical ventilation in accordance with the New York City Mechanical Code, natural ventilation shall be provided in accordance with Section 1203.5.1.1. Openings providing required natural ventilation to occupiable spaces shall be windows, doors, louvers, skylights or other similar ventilating openings. Exceptions: 1. Bathrooms and toilet rooms in Group R or I-1 occupancies shall comply with Section 1203.5.1.3. 2. Kitchenettes in Group R or I-1 occupancies shall comply with Section 1203.5.1.4.
1203.5.1.1.1 Minimum opening. | The minimum openable area to the outdoors shall be 4 percent of the floor area of the occupiable space being ventilated.
1203.5.1.1.2 Adjoining spaces. | Where occupiable rooms and spaces without openings to the outdoors are ventilated through an adjoining room, the opening to the adjoining room shall be unobstructed and shall have an area of not less than 8 percent of the floor area of the interior room or space, but not less than 25 square feet (2.3 m2). The openable area of the openings to the outdoors shall be based on the total floor area being ventilated. Exception: Exterior openings required for ventilation shall be permitted to open into a sunroom or covered patio provided that the openable area between such sunroom addition or covered patio and the interior room shall have an area of not less than 8 percent of the floor area of the interior room or space, but not less than 20 square feet (1.9 m2). The openable area of the openings to the outdoors shall be based on the total floor area being ventilated.
1203.5.1.1.3 Openings below grade. | Where openings below grade provide required natural ventilation, the outside horizontal clear space measured perpendicular to the opening shall be one and one-half times the depth of the opening. The depth of the opening shall be measured from the average adjoining ground level to the bottom of the opening.
1203.5.1.1.4 Mezzanines. | Where an interior balcony or mezzanine opens to form part of another room or space, its area shall be added to the area of the room or space in which it is located to compute the ventilation required for both spaces.
1203.5.1.2 Habitable spaces. | All habitable spaces shall be provided with natural ventilation in accordance with this section. Openings providing required natural ventilation to habitable spaces shall be windows and/or glazed doors to the outdoors. Exception: Group R-3 occupancies. Openable skylights opening directly to the outer air, transparent or translucent panels, or other natural light-transmitting media may be substituted for window openings in Group R-3 occupancies provided that they meet the minimum dimensional requirements of Section 1203.5.1.2.1.
1203.5.1.2.1 Minimum opening. | The minimum openable area to the outdoors shall be 5 percent of the floor area of the habitable space being ventilated. Every opening providing required natural ventilation shall be at least 12 square feet (1.1 m2) of glazed area, providing a minimum of 6 square feet (0.56 m2) of openable area. Exceptions: 1. Where fresh air is furnished in any habitable room or space by mechanical means supplying a minimum of 40 cubic feet per minute (0.02 m3/s), the free openable area of the openings may be reduced to 2½ percent of the floor area but each such opening shall provide not less than 5½ square feet (0.51 m2) of openable area. 2. The minimum free openable area of a mullioned casement window shall be 5½ square feet (0.51 m2), provided that the minimum ratio of floor area to openable area is met.
1203.5.1.2.2 Adjoining spaces. | An alcove or room opening off another room or space shall be considered as a separate room in determining its requirements for ventilation. Exceptions: 1. Alcoves within Group R-3 dwelling units. In Group R-3 occupancies, where an opening between the alcove and the room or space is at least 80 percent of the area of the common wall and the floor area of the alcove does not exceed twice the area of the opening, the alcove and the room opening into the alcove may be considered as a single space. 2. Balconies, partially enclosed. Exterior openings required for ventilation shall be permitted to open upon a partially enclosed balcony or space above a setback when: 2.1. Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206; 2.2. The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space; 2.3. The enclosure of the balcony or space is not more than one story in height; and 2.4. The front of a partially enclosed balcony or space above a setback shall be open to the outer air with an open area equal to at least 75 percent of the floor surface area of such balcony or space. 3. Balconies, fully enclosed. Exterior openings required for ventilation shall be permitted to open upon a fully enclosed balcony or space above a setback, including sunroom and patio covers, when: 3.1. Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206; 3.2. The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space; 3.3. The enclosure of the balcony or space is not more than one story in height; 3.4. The building is of Type I or II construction; 3.5. The outer enclosing walls of the balcony or space are glazed with an area at least 50 percent of the area of the interior enclosing walls of such balcony or space; the glazing may be clear plate glass or slow burning plastic; 3.6. At least 50 percent of the glazed area required by Exception 3.5 of this section is openable; and 3.7. No window from any bathroom, toilet room, kitchen or kitchenette shall open on such balcony or space. 4. Mezzanines and split-level rooms. Where a habitable mezzanine or portion of a split-level room or space is not directly served by an opening providing natural ventilation in accordance with Section 1203.5.1.2, such mezzanine or space shall open for its full width with no obstruction, except for railings, to an adjoining habitable room which is provided with natural ventilation. The floor area of such mezzanine or portion of the split-level room or space shall be added to the floor area of the adjoining room to compute the required ventilation in accordance with Section 1203.5.1.2.1. The combined space shall also comply with Section 1203.5.1.2.4. When required natural ventilation is not provided, mechanical ventilation shall be provided to the mezzanine and split-level rooms in accordance with the New York City Mechanical Code capable of providing 2 cubic feet per minute (0.00094 m3/s) of fresh air per 1 square foot (0.09 m2) of floor area of mezzanine.
1203.5.1.2.3 Basements and cellars. | Where openings provide natural ventilation to habitable spaces located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.
1203.5.1.2.4 Maximum depth of room. | No part of any room shall be more than 30 feet (9144 mm) from a window opening onto a street or yard unless such room also opens onto a court complying with Section 1206. Exception: In dwelling units containing more than three habitable rooms in Group R-1 or R-2 occupancies in buildings of Type I or II construction, rooms may be greater than 30 feet (9144 mm) in depth provided that all other requirements of Section 1203.5.1.2 are met and that the required windows are so located as to properly light all portions of the room in accordance with Section 1205.
1203.5.1.3 Bathrooms and toilet rooms in Group R and I-1 occupancies. | Bathrooms and toilet rooms in Group R or I-1 occupancies shall be provided with natural ventilation in accordance with Section 1203.5.1.3, unless provided with ventilation in accordance with the New York City Mechanical Code. Openings providing required natural ventilation shall be windows. Exception: Openable skylights may be substituted for windows provided that the bathroom or toilet room is on the top story.
1203.5.1.3.1 Minimum opening. | The minimum openable area to the outdoors shall be 5 percent of the floor area of the space being ventilated. Every window or skylight providing required natural ventilation shall be at least 3 square feet (0.28 m2) providing a minimum of 1½ square feet (0.14 m2) of openable area.
1203.5.1.3.2 Adjoining spaces. | Natural ventilation for bathrooms and toilet rooms may not be through openings from another room or space. Exception: A bathroom or toilet room may open onto a partially enclosed balcony or space above a setback conforming with Exception 2 of Section 1203.5.1.2.2.
1203.5.1.3.3 Basements and cellars. | Where openings provide natural ventilation to bathrooms or toilet rooms located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.
1203.5.1.4 Kitchenettes in Group R and I-1 occupancies. | Kitchenettes in Group R or I-1 occupancies shall be provided with natural ventilation in accordance with Section 1203.5.1.4, unless provided with ventilation in accordance with the New York City Mechanical Code. Openings providing required natural ventilation shall be windows. Exception: Openable skylights may be substituted for windows provided that: 1. The kitchenette is on the top story; 2. The skylight is 12 inches (304.8 mm) in its least dimensions; 3. The skylight is at least 4 square feet (0.37 m2) or one-eighth of the area of the kitchenette, whichever is greater; and 4. The skylight provides ventilating openings for at least one-half of its area.
1203.5.1.4.1 Minimum opening. | The minimum openable area to the outdoors shall be 5 percent of the floor area of the space being ventilated. Every window or other opening providing required natural ventilation shall be at least 1 foot (304.8 mm) wide and at least 3 square feet (0.28 m2) in total area, providing a minimum of 1½ square feet (0.14 m2) of openable area. Exception: Skylights shall comply with the exception of Section 1203.5.1.4.
1203.5.1.4.2 Adjoining spaces. | Natural ventilation for kitchenettes shall not be through openings off another room or space. Exception: A kitchenette may open onto a partially enclosed balcony or space above a setback conforming with Exception 2 of Section 1203.5.1.2.2.
1203.5.1.4.3 Basements and cellars. | Where openings provide natural ventilation to kitchenettes less than 80 square feet (7.4 m2) located in basements or cellars, such opening shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.
1203.5.2 Contaminants exhausted. | Contaminant sources in naturally ventilated spaces, including kitchens, kitchenettes, toilet rooms and bathing rooms, shall be exhausted in accordance with the New York City Mechanical Code.
1203.5.2.1 Bathrooms. | Rooms containing bathtubs, showers, spas and similar bathing fixtures in other than Group R and I-1 occupancies shall be mechanically ventilated in accordance with the New York City Mechanical Code, whether or not they are also provided with natural ventilation.
1203.5.3 Openings on yards or courts. | Natural ventilation shall be provided by openings to a public street, space, alley, park, highway, or right-of-way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206. No such opening shall be on a recess of less than 6 feet (1828.8 mm) in width. Exceptions: 1. Openings providing natural ventilation to habitable spaces located in basements or cellars shall also comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law. 2. A kitchenette, a bathroom, or a water closet compartment may be located on a recess of less than 6 feet (1828.8 mm) in width.
1203.5.4 Measurement of openings. | Dimensions of windows and other openings shall always be taken between stop beads or, if there are no stop beads, between the sides, head, and sill of the sash opening.
1205.1 General. | Every room and space in every building shall be provided with artificial light in accordance with Section 1205.3. Every habitable room and space shall also be provided with natural light by means of exterior glazed openings in accordance with Section 1205.2. Exceptions: Artificial light need not be provided in rooms or spaces: 1. Occupied exclusively during the daylight hours between 1 hour after sunrise and 1 hour before sunset, and which are provided with natural light meeting the requirements of Section 1205.2; or 2. With less than 40 square feet (3.7 m2) of floor area if they are used exclusively for storage purposes or for mechanical facilities containing no rotating or moving parts, no combustion equipment, or no other hazardous equipment. | 1205.1 General. | This section shall apply to yards and courts adjacent to exterior openings that provide natural light or ventilation. Such yards and courts shall be on the same lot as the building.
1203.6 Other ventilation and exhaust systems. | Ventilation and exhaust systems for occupancies and operations involving flammable or combustible hazards or other contaminant sources as covered in the New York City Mechanical Code or the New York City Fire Code shall be provided as required by both codes.
1204.1 Equipment and systems. | Interior spaces intended for human occupancy shall be provided with active or passive space heating systems capable of maintaining an indoor temperature as indicated in Table 1204.1 at a point 3 feet (914.4 mm) above the finished floor. The heating capacity of heat-producing devices and equipment which are contained in the room and in constant use during occupancy may be deducted from the capacity of the heating system. Portable heating systems shall not be considered as contributing to the capacity of the heating system. Exception: Where specific rooms or spaces are not listed, the temperature shall be determined by the requirements of the listed space to which they most nearly conform or as determined by the registered design professional. Exceptions: 1. Heating systems are not required when occupancy is seasonal and the rooms or buildings are not occupied between November 1st and May 1st of the following year. 2. Heating systems are not required when the processes or activities normally conducted in the space will generate sufficient heat to maintain the prescribed temperatures during the time of occupancy. 3. Spaces where strict process requirements mandate temperatures other than those cited above shall be exempt from the minimum requirements listed in Table 1204.1. |  |  |  | See BC12 Tables&Figures
1204.2 Air conditioning. | Interior spaces intended for human occupancy that are provided with air conditioning shall be provided with active or passive systems that are capable of maintaining 78°F (26°C) at 50-percent relative humidity when the outdoor air temperature is 89°F (32°C) and the coincident wet bulb temperature is 73°F (23°C). Interior spaces without air conditioning shall be provided with mechanical or natural ventilation in compliance with other subsections of this code.
1204.3 Freeze protection. | All interior spaces shall be provided with active or passive systems or with methods of construction capable of preventing wet piping systems and vessels from freezing at all times, including permanently installed pipe heat tracing systems.
1204.4 System design. | The heating system and air-conditioning system, as applicable, shall be designed to provide sufficient capacity to meet the temperature and humidity requirements of Section 1204 when considering the outdoor air ventilation requirements and all losses in the system and ancillary uses, such as domestic hot water, for which the system is used. The system shall be designed and installed to meet all other applicable provisions of this code.
1205.2 Natural light. | Every opening providing required natural light shall be so located so as to properly light all portions of the room. Openings providing required natural light shall be windows or glazed doors. Exception: Group R-3 occupancies. Skylights, opening directly to the outer air, transparent or translucent panels, or other light-transmitting media, may be substituted for window openings in Group R-3 occupancies provided that they meet the minimum dimensional requirements of Section 1205.2.1.
1205.2.1 Minimum opening. | The minimum net glazed area shall be not less than 10 percent of the floor area of the room served. Every opening providing required natural light shall be at least 12 square feet (1.1 m2) of glazed area. Exception: For Group R-3 occupancies, the net glazed area shall be not less than 10 percent of the floor area of the room served, or 12 square feet (1.1 m2), whichever is greater.
1205.2.2 Adjoining spaces. | An alcove or room opening off another room or space shall be considered as a separate room in determining its requirements for natural lighting. Exceptions: 1. Alcoves within Group R-3 dwelling units. In Group R-3 occupancies, where an opening between the alcove and the room or space is at least 80 percent of the area of the common wall and the floor area of the alcove does not exceed twice the area of the opening, the alcove and the room opening into the alcove may be considered as a single space. 2. Balconies, partially enclosed. Exterior openings required for natural light shall be permitted to open upon a partially enclosed balcony or space above a setback when: 2.1. Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206; 2.2. The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the exterior wall forming the partial or full enclosure of the balcony or space; 2.3. The enclosure of the balcony or space is not more than one story in height; and 2.4. The front of a partially enclosed balcony or space above a setback shall be open to the outer air with an open area equal to at least 75 percent of the floor surface area of such balcony or space. 3. Balconies, fully enclosed. Exterior openings required for natural lighting shall be permitted to open upon a fully enclosed balcony or space above a setback, including thermally isolated sunroom additions and covered patios, when: 3.1. Such balcony or space faces upon a public street, space, alley, park, highway, or right of way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206; 3.2. The maximum depth of any habitable room is 30 feet (9144 mm) measured from the outer face of the wall forming the partial or full enclosure of the balcony or space; 3.3. The enclosure of the balcony or space is not more than one story in height; 3.4. The building is of Type I or II construction; 3.5. The outer enclosing walls of the balcony or space are glazed with an area at least 50 percent of the area of the interior enclosing walls of such balcony or space; the glazing may be clear plate glass or slow burning plastic; 3.6. At least 50 percent of the glazed area required by Exception 3.5 of this section is openable; and 3.7. No window from any bathroom, toilet room, kitchen or kitchenette shall open on such balcony or space. 4. Mezzanines and split-level rooms. Where a habitable mezzanine or portion of a split-level room or space is not directly served by an opening providing natural lighting in accordance with Section 1205.2, such space shall be open for its full width with no obstruction, except for railings, to an adjoining habitable room which is provided with such window or other opening. The floor area of the mezzanine or portion of the split level room or space shall be added to the floor area of the adjoining room to compute the required lighting in accordance with Section 1205.2.1. The combined space shall also comply with Sections 1205.2.4 and 1205.2.7.
1205.2.3 Basements and cellars. | Where openings provide natural light to habitable spaces located in basements or cellars, such openings shall comply with Sections 1205.2.3.1 through 1205.2.3.2.
1205.2.3.1 Adequate adjacent space for multiple dwellings. | Where rooms within a dwelling unit in a multiple dwelling are located in a cellar or a basement, such rooms shall have at least one-half of their height and all of their required window surfaces above every part of an “adequate adjacent space.” Such “adequate adjacent space” shall be open to the sky and shall be a continuous surface area not less than 30 feet (9144 mm) in its least dimension abutting at same level or directly below the exterior walls of every part of the basement and cellar portions of such dwelling unit. Such “adequate adjacent space” shall be spaces that are located on the same tax lot or plot in compliance with Section 1206.1 as the building or a public street, space, alley, park, highway or right of way and the level of such areas which abut or adjoin the habitable room shall be at least 6 inches (152.4 mm) below the window sills of any windows.
1205.2.3.2 Other applicable laws. | Where openings provide natural lighting to habitable spaces located in basements or cellars, such opening shall comply with the applicable provisions of Sections 27-2081 through 27-2087 of the New York City Housing Maintenance Code and Sections 26(8) and 34 of the New York State Multiple Dwelling Law.
1205.2.4 Maximum depth of room. | No part of any room shall be more than 30 feet (9144 mm) from a window opening on a street or yard unless such room also opens onto a legal court in compliance with Section 1206.1. Exception: In dwelling units containing more than three habitable rooms in Group R- 1 or R-2 occupancies in buildings of Type I or II construction, rooms may be greater than 30 feet (9144 mm) in depth provided that all other requirements of Section 1205.2 are met and that the required windows are located so as to properly light all portions of the room.
1205.2.5 Openings on yards or courts. | Exterior glazed openings shall open directly onto a public street, space, alley, park, highway, or right-of-way; or upon a yard, court, plaza, or space above a setback where such yard, court, plaza, or space above a setback complies with Section 1206. No such opening shall be on a recess of less than 6 feet (1828.8 mm) in width. Exception: Spaces located in basements or cellars shall also comply with Section 1205.2.3.
1205.2.6 Measurement of glazed areas. | Dimensions of windows and other glazed areas shall always be taken between stop beads or, if there are no stop beads, between the sides, head, and sill.
1205.2.7 Height of glazed areas. | Height of glazed areas on openings providing natural light shall comply with Sections 1205.2.7.1 and 1205.2.7.2.
1205.2.7.1 | Only that portion of glazed areas higher than 30 inches (9144 mm) above the floor shall be considered as providing the required natural lighting.
1205.2.7.2 | The top of at least one window or other opening providing required natural lighting to a habitable room shall be a minimum of 7 feet (2133.6 mm) above the floor of the room or space served by the window or opening. Exception: Mezzanines. Where the required natural lighting for a habitable mezzanine level is provided by a window(s) on the lower level in accordance with Section 1205.2.2, Exception 4, and where compliance with Section 1205.2.7.2 is not feasible on the mezzanine floor, Section 1205.2.7.2 shall not apply to such mezzanine floor provided that such window(s) is on the opposite wall from the mezzanine, and the top of such window is at least 12 inches (304.8 mm) above the floor of the mezzanine.
1205.3 Artificial light. | Artificial light shall be provided in accordance with Sections 1205.3.1 through 1205.3.5.
1205.3.1 General. | Artificial light shall meet the minimum illumination standards set forth in Section 1205.3. Artificial light shall not exceed maximum energy consumption requirements, if applicable, as required by the New York City Energy Conservation Code.
1205.3.2 Rooms and spaces. | Artificial light shall be adequate to provide an average illumination of 10 footcandles (107 lux) over the area of the room at a height of 30 inches (762 mm) above the floor level.
1205.3.3 Stairways. | Stairways within dwelling units and exterior stairways serving a dwelling unit shall have an illumination level on tread runs of not less than 1 footcandle (11 lux). Stairs in other occupancies shall be governed by Chapter 10.
1205.3.4 Means of egress. | The means of egress shall be illuminated in accordance with Section 1008. Exterior lights near entranceways to multiple dwellings shall also comply with Section 27-2040 of the New York City Housing Maintenance Code.
1205.3.5 Places of assembly. | Places of assembly shall be illuminated in accordance with Chapter 10.
1205.4 Reserved.
1205.5 Reserved.
1206.1 General. | This section shall apply to yards and courts adjacent to exterior openings that provide required natural light or required natural ventilation. Such yards and courts shall be on the same zoning lot as the building. Where such yard or court is wholly or partially on a different tax lot from the exterior opening which the yard or court serves, a light and air easement or restrictive declaration acceptable to the commissioner shall be recorded against the tax lot or lots where such yard or court is located.
1206.2 Yards. | Yards shall be not less than the dimensions prescribed by the New York City Zoning Resolution and other applicable laws, rules, and regulations.
1206.2.1 Rear yard access for multiple dwellings. | For multiple dwellings, there shall be direct access from the street to every rear yard through a noncombustible 2-hour fire-resistance-rated passage either in a direct line or through a court, except that the passage may be 1-hour fire-resistance-rated for dwellings not exceeding three stories in height and occupied by not more than two families on any story. Such passage shall be at least 36 inches (914.4 mm) in clear width and 7 feet (2133.6 mm) in height. Exceptions: No such passage shall be required for: 1. Buildings of Type IA or IB construction. 2. Buildings not exceeding three stories in height, and occupied by not more than one family on any story nor more than three families in all. 3. Buildings not exceeding two stories in height, and occupied by not more than two families on any story nor more than four families in all.
1206.3 Courts. | Courts shall not be less than the dimensions prescribed by the New York City Zoning Resolution and other applicable laws, rules and regulations.
1206.3.1 Court access. | Access shall be provided to the bottom of courts for cleaning purposes.
1206.3.2 Air intake. | Courts more than two stories in height shall be provided with a horizontal air intake at the bottom not less than 10 square feet (0.93 m2) in area and leading to the exterior of the building unless abutting a yard or public way. Exception: For multiple dwellings more than two stories in height, an air intake with a vertical cross-sectional area of 21 square feet (1.95 m2) and a least minimum dimension of 3 feet (914.4 mm) shall be provided at or near the lowest level of any court, in accordance with Section 26(7)(a) of the New York State Multiple Dwelling Law.
1206.3.3 Court drainage. | The bottom of every court shall be properly graded and drained to a public sewer or other approved disposal system complying with the New York City Plumbing Code. For Group R and I-1 occupancies, such grading and drainage shall also comply with Section 27-2027 of the New York City Housing Maintenance Code. For Group R-1, R-2 and I-1 occupancies, such grading and drainage shall also comply with Section 77 of the New York State Multiple Dwelling Law.
1206.3.4 Court walls for multiple dwellings. | All walls enclosing courts of multiple dwellings shall be of light colored materials or shall be painted a light color. Exceptions: 1. Outer courts that open to a street. 2. Courts that exceed the minimum dimension set forth in the New York City Zoning Resolution by at least 50 percent.
1206.4 Lighting in courts and yards. | In Group I-1, R-1 or R-2 occupancies, all yards and courts shall be artificially illuminated with a minimum intensity of not less than 1 footcandle (11 lux) measured 30 inches (762 mm) above the floor of the lowest level of such yards or courts. Exception: Such lighting is not required in an inner court that is accessible only from the interior of the building and to which access is restricted for clean-out purposes.
1207.1 Scope. | This section shall apply to common interior walls, partitions and floor/ceiling assemblies between adjacent dwelling units, between dwelling units and adjacent mechanical equipment spaces, or between dwelling units and adjacent occupancies, and public areas such as halls, corridors, stairs or service areas.
1207.2 Air-borne sound. | Walls, partitions and floor/ceiling assemblies separating dwelling units from each other, from adjacent occupancies, from public or service areas, from stairs or from mechanical equipment spaces, including boiler rooms, or elevator or other shafts shall have a sound transmission class (STC) for air-borne noise of not less than 50 based upon laboratory measurements made in accordance with ASTM E 90, or not less than 45 if field tested in accordance with ASTM E 336. Dwelling unit entrance doors shall be installed of assemblies having an STC of not less than 30 based upon laboratory measurements made in accordance with ASTM E 90. Penetrations or openings in construction assemblies for piping; electrical devices; recessed cabinets; bathtubs; soffits; or heating, ventilating or exhaust ducts shall be sealed, lined, insulated or otherwise treated to maintain the required ratings.
1207.2.1 Masonry. | The sound transmission class of concrete masonry and clay masonry assemblies shall be calculated in accordance with TMS 302 or determined through testing in accordance with ASTM E 90.
1207.2.2 Machine and equipment rooms. | Elevator machine rooms and machinery spaces containing equipment totaling more than 75 rated h.p. shall not be located vertically or horizontally adjacent to dwelling units unless the total sound pressure level output of all the equipment in the machine room or space is certified not to exceed the maximum sound pressure levels of Table 1207.2.1 in any octave band. |  |  |  | See BC12 Tables&Figures
125
1207.3 Structure-borne sound. | Floor/ceiling assemblies between dwelling units and sleeping units or between a dwelling unit or sleeping unit and a public or service area stair, exterior mechanical equipment, or other mechanical equipment space, including boiler rooms, shall be constructed of assemblies having an impact insulation class (IIC) rating of not less than 50 based upon laboratory measurements made in accordance with ASTM E 492, or not less than 45 if field tested in accordance with ASTM E 1007 in completed construction. See Chapter 30 of this code for additional sound control requirements for elevator machinery.
1207.3.1 Refuse chutes. | Metal refuse chutes, metal chute supports, and metal chute bracing shall be free of direct contact with the shaft enclosure and the openings provided in the floor construction. Metal chutes shall be resiliently supported at each structural support location. Isolators shall provide a minimum static deflection of 0.3 inches (7.62 mm). All chutes shall be plumb.
1207.4 Field testing. | Where conditions indicate that the installed construction or equipment does not meet the noise control prescribed in Section 1207, measurements shall be taken to determine conformance or nonconformance.
1208.1 Minimum room widths. | Habitable spaces, other than a kitchen, shall be not less than 8 feet (2438.4 mm) in any plan dimension. Kitchens and kitchenettes shall have a clear passageway of not less than 3 feet (914.4 mm) between counter fronts and appliances or counter fronts and walls. Exceptions: 1. A room that complies with the requirements for natural light and natural ventilation and in addition has an unobstructed opening of not less than 60 square feet (5.6 m2) into an immediately adjoining room shall be not less than 7 feet (2133.6 mm) in any plan dimension. 2. A habitable dining space that complies with the requirements for natural light and natural ventilation may be less than 8 feet (2438.4 mm) in any plan dimension. 3. One-half the number of bedrooms in a dwelling unit containing three or more bedrooms shall be not less than 7 feet (2133.6 mm) in any plan dimension. 4. A room in a Group R-1 dwelling or sleeping unit shall be not less than 6 feet (1828.8 mm) in any plan dimension. | 1208.1 Minimum room widths. | Habitable spaces, other than a kitchen, shall be not less than 7 feet (2134 mm) in any plan dimension. Kitchens shall have a clear passageway of not less than 3 feet (914 mm) between counter fronts and appliances or counter fronts and walls.
1208.2 Minimum ceiling heights. | Habitable rooms and spaces shall have a ceiling height of not less than 8 feet (2438.4 mm). Occupiable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm). Bathrooms, toilet rooms, kitchens in other than Group I-1 and R occupancies, kitchenettes in Group I-1 or R occupancies, storage rooms and laundry rooms shall have a ceiling height of not less than 7 feet (2133.6 mm). All measurements shall be taken from the finished floor to the finished underside of the ceiling or ceiling beams. Exceptions: 1. In one- and two-family dwellings, beams or girders spaced not less than 4 feet (1220 mm) on center may project not more than 6 inches (152.4 mm) below the required ceiling height, provided that a clear height of 7 feet (2133.6 mm) is maintained. 2. Habitable rooms in basements of one- or two-family dwellings, including any projecting beams, shall have a ceiling height of not less than 7 feet (2133.6 mm). 3. Habitable rooms in basements of multiple dwellings may have as many as four beams crossing the ceiling if none of the beams exceeds 12 inches (304.8 mm) in width or extends below the ceiling more than 6 inches (152.4 mm). 4. Spaces above and below a mezzanine, other than habitable spaces, shall have a ceiling height of not less than 7 feet (2133.6 mm). | 1208.2 Minimum ceiling heights. | Occupiable spaces, habitable spaces and corridors shall have a ceiling height of not less than 7 feet 6 inches (2286 mm) above the finished floor. Bathrooms, toilet rooms, kitchens, storage rooms and laundry rooms shall have a ceiling height of not less than 7 feet (2134 mm) above the finished floor. Exceptions: 1. In one- and two-family dwellings, beams or girders spaced not less than 4 feet (1219 mm) on center shall be permitted to project not more than 6 inches (152 mm) below the required ceiling height. 2. If any room in a building has a sloped ceiling, the prescribed ceiling height for the room is required in one-half the area thereof. Any portion of the room measuring less than 5 feet (1524 mm) from the finished floor to the ceiling shall not be included in any computation of the minimum area thereof. 3. The height of mezzanines and spaces below mezzanines shall be in accordance with Section 505.2. 4. Corridors contained within a dwelling unit or sleeping unit in a Group R occupancy shall have a ceiling height of not less than 7 feet (2134 mm) above the finished floor.
1208.2.1 Furred ceiling. | Any room with a furred ceiling shall be required to have the minimum ceiling height in two-thirds of the area thereof, but in no case shall the height of the furred ceiling be less than 7 feet (2133.6 mm). Exception: Minimum ceiling heights of habitable rooms and spaces shall be not less than established in Section 1208.2. | 1208.2.1 Furred ceiling. | Any room with a furred ceiling shall be required to have the minimum ceiling height in two-thirds of the area thereof, but in no case shall the height of the furred ceiling be less than 7 feet (2134 mm).
1208.3 Room area. | Minimum net floor areas of rooms shall be in accordance with Sections 1208.3.1 and 1208.3.2. | 1208.3 Room area. | Every dwelling unit shall have not less than one room that shall have not less than 120 square feet (11.2 m2) of net floor area. Other habitable rooms shall have a net floor area of not less than 70 square feet (6.5 m2). Exception: Kitchens are not required to be of a minimum floor area.
1208.3.1 Habitable rooms and spaces. | Every habitable room or space shall have not less than 80 square feet (7.4 m2) in net floor area. Exceptions: 1. A room that complies with the requirements for natural light and natural ventilation and in addition has an unobstructed opening of not less than 60 square feet (5.6 m2) into an immediately adjoining room shall have not less than 70 square feet (6.5 m2) of net floor area. 2. A habitable dining space, as defined by the New York City Housing Maintenance Code, that complies with the requirements for natural light and natural ventilation may have less than 80 square feet (7.4 m2) of net floor area. 3. A room in a Group R-1 dwelling unit shall have not less than 60 square feet (5.6 m2) of net floor area.
1208.3.2 Dwelling units. | In a dwelling unit, at least one habitable room shall have not less than 150 square feet (13.9 m2 ‡) of net floor area. Exception: Group R-1 dwelling or sleeping units.
1208.3.2.1. Single room occupancy of a single room. | Where a single room within a dwelling unit is used for single room occupancy, as such term is used in Section 27-2074(e) of the New York City Housing Maintenance Code, such room shall have not less than 150 square feet (13.9 m2) of net floor area.
1208.3.2.2 Single room occupancy of a suite of rooms. | Where two or more rooms, joined together and separated from all other rooms within a dwelling unit, are used for single room occupancy, as such term is used in Section 27-2074(e) of the New York City Housing Maintenance Code, at least one of such separated rooms shall have not less than 150 square feet (13.9 m2) of net floor area.
1208.4 Reserved.
1209.1 Crawl spaces. | Crawl spaces shall be provided with not fewer than one access opening that shall be not less than 18 inches by 24 inches (457.2 mm by 609.6 mm). All crawl spaces shall have a minimum clear height of 18 inches (457.2 mm). | 1209.1 Crawl spaces. | Crawl spaces shall be provided with not less than one access opening that shall be not less than 18 inches by 24 inches (457 mm by 610 mm).
1209.2 Attic spaces. | An opening not less than 20 inches by 30 inches (508 mm by 762 mm) shall be provided to any attic area having a clear height of over 30 inches (762 mm). Clear headroom of not less than 30 inches (762 mm) shall be provided in the attic space at or above the access opening. | 1209.2 Attic spaces. | An opening not less than 20 inches by 30 inches (559 mm by 762 mm) shall be provided to any attic area having a clear height of over 30 inches (762 mm). Clear headroom of not less than 30 inches (762 mm) shall be provided in the attic space at or above the access opening.
1209.3 Mechanical appliances. | Access to mechanical appliances installed in under-floor areas, in attic spaces and on roofs or elevated structures shall be in accordance with the New York City Mechanical Code. | 1209.3 Mechanical appliances. | Access to mechanical appliances installed in under-floor areas, in attic spaces and on roofs or elevated structures shall be in accordance with the International Mechanical Code.
1210.1 Required fixtures. | The number and type of plumbing fixtures provided in any occupancy shall comply with the New York City Plumbing Code. | 1210.1 Required fixtures. | The number and type of plumbing fixtures provided in any occupancy shall comply with Chapter 29.
1210.2 Finish materials. | Walls, floors and partitions in toilet and bathrooms shall comply with Sections 1210.2.1 through 1210.2.4. | 1210.2 Finish materials. | Walls, floors and partitions in toilet and bathrooms shall comply with Sections 1210.2.1 through 1210.2.4.
1210.2.1 Floors and wall bases. | In other than dwelling units, toilet, bathing and shower room floor finish materials shall have a smooth, hard, nonabsorbent surface. The intersections of such floors with walls shall have a smooth, hard, nonabsorbent vertical base that extends upward onto the walls not less than 4 inches (101.6 mm). Exception: Group I-1, R-1 and R-2 occupancies shall have a vertical base that extends upward onto walls at least 6 inches (152.4 mm). | 1210.2.1 Floors and wall bases. | In other than dwelling units, toilet, bathing and shower room floor finish materials shall have a smooth, hard, nonabsorbent surface. The intersections of such floors with walls shall have a smooth, hard, nonabsorbent vertical base that extends upward onto the walls not less than 4 inches (102 mm).
1210.2.2 Walls and partitions. | Walls and partitions within 2 feet (609.6 mm) of service sinks, urinals and water closets shall have a smooth, hard, nonabsorbent surface, to a height of not less than 4 feet (1220 mm) above the floor, and except for structural elements, the materials used in such walls shall be of a type that is not adversely affected by moisture. Exceptions: 1. Dwelling units. 2. Toilet rooms that are not accessible to the public and that have not more than one water closet. | 1210.2.2 Walls and partitions. | Walls and partitions within 2 feet (610 mm) of service sinks, urinals and water closets shall have a smooth, hard, nonabsorbent surface, to a height of not less than 4 feet (1219 mm) above the floor, and except for structural elements, the materials used in such walls shall be of a type that is not adversely affected by moisture. Exception: This section does not apply to the following buildings and spaces: 1. Dwelling units and sleeping units. 2. Toilet rooms that are not accessible to the public and that have not more than one water closet. Accessories such as grab bars, towel bars, paper dispensers and soap dishes, provided on or within walls, shall be installed and sealed to protect structural elements from moisture.
1210.2.3 Showers. | Shower compartments and walls above bathtubs with installed shower heads shall be finished with a smooth, nonabsorbent surface to a height not less than 72 inches (1828.8 mm) above the drain inlet. | 1210.2.3 Showers. | Shower compartments and walls above bathtubs with installed shower heads shall be finished with a smooth, nonabsorbent surface to a height not less than 72 inches (1829 mm) above the drain inlet.
1210.2.4 Waterproof joints. | Built-in tubs with showers shall have waterproof joints between the tub and adjacent wall. | 1210.2.4 Waterproof joints. | Built-in tubs with showers shall have waterproof joints between the tub and adjacent wall.
1210.3 Privacy. | Privacy at water closets and urinals shall be provided in accordance with Sections 1210.3.1 and 1210.3.2. | 1210.3 Privacy. | Public restrooms shall be visually screened from outside entry or exit doorways to ensure user privacy within the restroom. This provision shall also apply where mirrors would compromise personal privacy. Privacy at water closets and urinals shall be provided in accordance with Sections 1210.3.1 and 1210.3.2. Exception: Visual screening shall not be required for single-occupant toilet rooms with a lockable door.
1210.3.1 Water closet compartment. | Each water closet utilized by the public or employees shall occupy a separate compartment with walls or partitions and a door enclosing the fixtures for privacy. Exceptions: 1. Water closet compartments shall not be required in a single-occupant toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more water closets shall be permitted to have one water closet without an enclosing compartment. 3. This provision is not applicable to toilet areas located within Group I-3 occupancy housing areas. | 1210.3.1 Water closet compartment. | Each water closet utilized by the public or employees shall occupy a separate compartment with walls or partitions and a door enclosing the fixtures to ensure privacy. Exceptions: 1. Water closet compartments shall not be required in a single-occupant toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more water closets shall be permitted to have one water closet without an enclosing compartment. 3. This provision is not applicable to toilet areas located within Group I-3 occupancy housing areas.
1210.3.2 Urinal partitions. | Each urinal utilized by the public or employees shall occupy a separate area with walls or partitions to provide privacy. The walls or partitions shall begin at a height not more than 12 inches (304.8 mm) from and extend not less than 60 inches (1524 mm) above the finished floor surface. The walls or partitions shall extend from the wall surface at each side of the urinal not less than 18 inches (457.2 mm) or to a point not less than 6 inches (152.4 mm) beyond the outermost front lip of the urinal measured from the finished backwall surface, whichever is greater. Exceptions: 1. Urinal partitions shall not be required in a single-occupant or family or assisted-use toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more urinals shall be permitted to have one urinal without partitions. | 1210.3.2 Urinal partitions. | Each urinal utilized by the public or employees shall occupy a separate area with walls or partitions to provide privacy. The walls or partitions shall begin at a height not more than 12 inches (305 mm) from and extend not less than 60 inches (1524 mm) above the finished floor surface. The walls or partitions shall extend from the wall surface at each side of the urinal not less than 18 inches (457 mm) or to a point not less than 6 inches (152 mm) beyond the outermost front lip of the urinal measured from the finished backwall surface, whichever is greater. Exceptions: 1. Urinal partitions shall not be required in a single-occupant or family or assisted-use toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more urinals shall be permitted to have one urinal without partitions.
1210.4 Toilet rooms. | Toilet rooms shall not open directly into a room used for the preparation of food for service to the public. In multiple dwellings no toilet room or bathroom shall open onto any kitchen or kitchenette.
1211.1 Sleeping. | No kitchen or kitchenette shall be occupied for sleeping purposes.
1211.2 Kitchenettes in multiple dwellings. | Except at entrances thereto, every kitchenette in a multiple dwelling shall be surrounded by partitions extending from floor to ceiling, and/or by a soffit dropped 1 foot (304.8 mm) from the ceiling.
1212.1 General. | Rodentproofing shall be in accordance with Appendix F.
1213.1 General. | Multiple dwellings shall comply with Section 81 of the New York State Multiple Dwelling Law and Section 27-2021 of the New York City Housing Maintenance Code. In Group R-2 occupancies, space shall be provided for the storage of refuse and recyclables as a common accessory space. The location of such refuse and recyclables storage space shall be clearly identified on the construction documents and configured to permit separate unobstructed access by building personnel to stored refuse and recyclables. Such refuse and recyclables storage space shall be a minimum of 1.5 square feet (0.140 m2) per dwelling unit, or a minimum of 350 square feet (32.516 m2), whichever is less, for the storage of collected refuse and recyclables. Exceptions: 1. In multiple dwellings required to have a compactor in accordance with Section 1213.2, such refuse and recyclables storage space shall be, in addition to space required for equipment or circulation, a minimum of 1.0 square foot (0.094 m2) per dwelling unit, or a minimum of 350 square feet (32.516 m2), whichever is less, for the storage of collected refuse and recyclables. 2. Refuse and recyclables storage space shall not be required in multiple dwellings equipped with a chute system that provides for source separation of refuse and recyclable materials without cross contamination and an integrated mechanical system to transport such materials off-site that has been approved by the commissioner.
1213.1.1 Interior space. | Where an interior room is provided for the storage of refuse and recyclables, such room shall be completely enclosed by construction that has a fire-resistance rating of not less than 2 hours, with self-closing opening protective having a fire protection rating of not less than 1½ hours.
1213.1.2 Exterior space. | Where space is provided on the exterior of a building for the storage of refuse and recyclables, such refuse and recyclables storage space shall include a minimum of 4 square feet (0.372 m2) in addition to the space per dwelling unit required by Section 1213.1, shall be clearly identified on the construction documents, and shall not be located in the public right-of-way.
1213.2 Compactor. | A refuse compacting system shall be provided in multiple dwellings in a Group I-1 or R-2 occupancy that are four or more stories in height and contain 12 or more dwelling units, and in buildings of any size occupied as a Group R-1 multiple dwelling. Such system shall be located within a refuse storage room constructed in accordance with Section 1213.1 or in a refuse chute termination room constructed in accordance with Section 713.13.4. The floor within such room shall be constructed of concrete and shall be sloped to a floor drain connected to the building sewer. A hose connection shall be provided within such room.
1213.3 Refuse chute. | A multiple dwelling that is five or more stories in height and that contains 9 or more dwelling units shall be provided with a refuse chute, refuse chute access rooms, and refuse chute termination room constructed in accordance with Section 713.13. A minimum of 5 square feet (0.470 m2) of floor area within each refuse chute access room shall be provided for the temporary holding of recyclables. Such floor area shall be clearly identified on the construction documents. In Group I-1 and R-1 occupancies, access to the chute access room shall be permitted to be restricted to employees provided that separate refuse storage rooms are located on each story for general occupant use. Exceptions: 1. In buildings without an elevator, floor area within refuse chute access rooms for the temporary holding of recyclables is not required. 2. In buildings equipped with separate chutes designated for refuse, for paper and cardboard, and for metal, glass and plastic, and in buildings equipped with a chute system that provides for source separation of recyclable materials without cross contamination, floor area within refuse chute access rooms for the temporary holding of recyclables is not required. Chutes for designated recyclable materials shall be constructed in accordance with Section 713.13 of this code. 3. The refuse chute and the occupant use storage rooms shall not be required in transient hotels meeting the following requirements: 3.1. the refuse is removed from rooms by a daily cleaning service, with the staff using a service elevator that is not accessed by hotel guests; 3.2. the building is of Type I or Type II construction; or 3.3. a compactor and refuse storage room is provided in accordance with Section 1213.2.
1213.3.1 Refuse chute access room floor and wall base finish materials. | Refuse chute access rooms shall have a smooth, hard and nonabsorbent surface. The intersection of such floors with walls shall have a smooth, hard and nonabsorbent vertical base that extends upward onto the walls at least 4 inches (101.6 mm).
|  | 1202.1 General. | Buildings shall be provided with natural ventilation in accordance with Section 1202.5, or mechanical ventilation in accordance with the International Mechanical Code.
|  | 1202.2 Roof ventilation. | Roof assemblies shall be ventilated in accordance with this section or shall comply with Section 1202.3.
|  | 1202.2.1 Ventilated attics and rafter spaces. | Enclosed attics and enclosed rafter spaces formed where ceilings are applied directly to the underside of roof framing members shall have cross ventilation for each separate space by ventilation openings protected against the entrance of rain and snow. Blocking and bridging shall be arranged so as not to interfere with the movement of air. An airspace of not less than 1 inch (25 mm) shall be provided between the insulation and the roof sheathing. The net free ventilating area shall be not less than 1/150 of the area of the space ventilated. Ventilators shall be installed in accordance with manufacturer’s installation instructions.
|  | 1202.2.2 Openings into attic. | Exterior openings into the attic space of any building intended for human occupancy shall be protected to prevent the entry of birds, squirrels, rodents, snakes and other similar creatures. Openings for ventilation having a least dimension of not less than 1/16 inch (1.6 mm) and not more than 1/4 inch (6.4 mm) shall be permitted. Openings for ventilation having a least dimension larger than 1/4 inch (6.4 mm) shall be provided with corrosion-resistant wire cloth screening, hardware cloth, perforated vinyl or similar material with openings having a least dimension of not less than 1/16 inch (1.6 mm) and not more than 1/4 inch (6.4 mm). Where combustion air is obtained from an attic area, it shall be in accordance with Chapter 7 of the International Mechanical Code.
|  | 1202.3 Unvented attic and unvented enclosed rafter assemblies. | Unvented attics and unvented enclosed roof framing assemblies created by ceilings applied directly to the underside of the roof framing members/rafters and the structural roof sheathing at the top of the roof framing members shall be permitted where all of the following conditions are met:
|  | 1202.4 Under-floor ventilation. | The space between the bottom of the floor joists and the earth under any building except spaces occupied by basements or cellars shall be provided with ventilation in accordance with Section 1202.4.1, 1202.4.2 or 1202.4.3.
|  | 1202.4.1 Ventilation openings. | Ventilation openings through foundation walls shall be provided. The openings shall be placed so as to provide cross ventilation of the under-floor space. The net area of ventilation openings shall be in accordance with Section 1202.4.1.1 or 1202.4.1.2. Ventilation openings shall be covered for their height and width with any of the following materials, provided that the least dimension of the covering shall be not greater than 1/4 inch (6.4 mm):
|  | 1202.4.1.1 Ventilation area for crawl spaces with open earth floors. | The net area of ventilation openings for crawl spaces with uncovered earth floors shall be not less than 1 square foot for each 150 square feet (0.67 m2 for each 100 m2) of crawl space area.
|  | 1202.4.1.2 Ventilation area for crawl spaces with covered floors. | The net area of ventilation openings for crawl spaces with the ground surface covered with a Class I vapor retarder shall be not less than 1 square foot for each 1,500 square feet (0.67 m2 for each 1000 m2) of crawl space area.
|  | 1202.4.2 Ventilation in cold climates. | In extremely cold climates, where a ventilation opening will cause a detrimental loss of energy, ventilation openings to the interior of the structure shall be provided.
|  | 1202.4.3 Mechanical ventilation. | Mechanical ventilation shall be provided to crawl spaces where the ground surface is covered with a Class I vapor retarder. Ventilation shall be in accordance with Section 1202.4.3.1 or 1202.4.3.2.
|  | 1202.4.3.1 Continuous mechanical ventilation. | Continuously operated mechanical ventilation shall be provided at a rate of 1.0 cubic foot per minute (cfm) for each 50 square feet (1.02 L/s for each 10 m2) of crawl space ground surface area and the ground surface shall be covered with a Class I vapor retarder.
|  | 1202.4.3.2 Conditioned space. | The crawl space shall be conditioned in accordance with the International Mechanical Code and the walls of the crawl space shall be insulated in accordance with the International Energy Conservation Code.
|  | 1202.4.4 Flood hazard areas. | For buildings in flood hazard areas as established in Section 1612.3, the openings for under-floor ventilation shall be deemed as meeting the flood opening requirements of ASCE 24 provided that the ventilation openings are designed and installed in accordance with ASCE 24.
|  | 1202.5 Natural ventilation. | Natural ventilation of an occupied space shall be through windows, doors, louvers or other openings to the outdoors. The operating mechanism for such openings shall be provided with ready access so that the openings are readily controllable by the building occupants.
|  | 1202.5.1 Ventilation area required. | The openable area of the openings to the outdoors shall be not less than 4 percent of the floor area being ventilated.
|  | 1202.5.1.1 Adjoining spaces. | Where rooms and spaces without openings to the outdoors are ventilated through an adjoining room, the opening to the adjoining room shall be unobstructed and shall have an area of not less than 8 percent of the floor area of the interior room or space, but not less than 25 square feet (2.3 m2). The openable area of the openings to the outdoors shall be based on the total floor area being ventilated.
|  | 1202.5.1.2 Openings below grade. | Where openings below grade provide required natural ventilation, the outside horizontal clear space measured perpendicular to the opening shall be one and one-half times the depth of the opening. The depth of the opening shall be measured from the average adjoining ground level to the bottom of the opening.
|  | 1202.5.2 Contaminants exhausted. | Contaminant sources in naturally ventilated spaces shall be removed in accordance with the International Mechanical Code and the International Fire Code.
|  | 1202.5.2.1 Bathrooms. | Rooms containing bathtubs, showers, spas and similar bathing fixtures shall be mechanically ventilated in accordance with the International Mechanical Code.
|  | 1202.5.3 Openings on yards or courts. | Where natural ventilation is to be provided by openings onto yards or courts, such yards or courts shall comply with Section 1205.
|  | 1202.6 Other ventilation and exhaust systems. | Ventilation and exhaust systems for occupancies and operations involving flammable or combustible hazards or other contaminant sources as covered in the International Mechanical Code or the International Fire Code shall be provided as required by both codes.
|  | 1203.1 Equipment and systems. | Interior spaces intended for human occupancy shall be provided with active or passive space heating systems capable of maintaining an indoor temperature of not less than 68°F (20°C) at a point 3 feet (914 mm) above the floor on the design heating day.
|  | 1204.1 General. | Every space intended for human occupancy shall be provided with natural light by means of exterior glazed openings in accordance with Section 1204.2 or shall be provided with artificial light in accordance with Section 1204.3. Exterior glazed openings shall open directly onto a public way or onto a yard or court in accordance with Section 1205.
|  | 1204.2 Natural light. | The minimum net glazed area shall be not less than 8 percent of the floor area of the room served.
|  | 1204.2.1 Adjoining spaces. | For the purpose of natural lighting, any room is permitted to be considered as a portion of an adjoining room where one-half of the area of the common wall is open and unobstructed and provides an opening of not less than one-tenth of the floor area of the interior room or 25 square feet (2.32 m2), whichever is greater.
|  | 1204.2.2 Exterior openings. | Exterior openings required by Section 1204.2 for natural light shall open directly onto a public way, yard or court, as set forth in Section 1205.
|  | 1204.3 Artificial light. | Artificial light shall be provided that is adequate to provide an average illumination of 10 footcandles (107 lux) over the area of the room at a height of 30 inches (762 mm) above the floor level.
|  | 1204.4 Stairway illumination. | Stairways within dwelling units and exterior stairways serving a dwelling unit shall have an illumination level on tread runs of not less than 1 footcandle (11 lux). Stairways in other occupancies shall be governed by Chapter 10.
|  | 1204.4.1 Controls. | The control for activation of the required stairway lighting shall be in accordance with NFPA 70.
|  | 1204.5 Emergency egress lighting. | The means of egress shall be illuminated in accordance with Section 1008.1.
|  | 1205.2 Yards. | Yards shall be not less than 3 feet (914 mm) in width for buildings two stories or less above grade plane. For buildings more than two stories above grade plane, the minimum width of the yard shall be increased at the rate of 1 foot (305 mm) for each additional story. For buildings exceeding 14 stories above grade plane, the required width of the yard shall be computed on the basis of 14 stories above grade plane.
|  | 1205.3 Courts. | Courts shall be not less than 3 feet (914 mm) in width. Courts having windows opening on opposite sides shall be not less than 6 feet (1829 mm) in width. Courts shall be not less than 10 feet (3048 mm) in length unless bounded on one end by a public way or yard. For buildings more than two stories above grade plane, the court shall be increased 1 foot (305 mm) in width and 2 feet (610 mm) in length for each additional story. For buildings exceeding 14 stories above grade plane, the required dimensions shall be computed on the basis of 14 stories above grade plane.
|  | 1205.3.1 Court access. | Access shall be provided to the bottom of courts for cleaning purposes.
|  | 1205.3.2 Air intake. | Courts more than two stories in height shall be provided with a horizontal air intake at the bottom not less than 10 square feet (0.93 m2) in area and leading to the exterior of the building unless abutting a yard or public way.
|  | 1205.3.3 Court drainage. | The bottom of every court shall be properly graded and drained to a public sewer or other approved disposal system complying with the International Plumbing Code.
|  | 1206.1 Scope. | This section shall apply to common interior walls, partitions and floor/ceiling assemblies between adjacent dwelling units and sleeping units or between dwelling units and sleeping units and adjacent public areas.
|  | 1206.2 Airborne sound. | Walls, partitions and floor-ceiling assemblies separating dwelling units and sleeping units from each other or from public or service areas shall have a sound transmission class of not less than 50 where tested in accordance with ASTM E90, or have a Normalized Noise Isolation Class (NNIC) rating of not less than 45 if field tested, in accordance with ASTM E336 for airborne noise. Alternatively, the sound transmission class of walls, partitions and floor-ceiling assemblies shall be established by engineering analysis based on a comparison of walls, partitions and floor-ceiling assemblies having sound transmission class ratings as determined by the test procedures set forth in ASTM E90. Penetrations or openings in construction assemblies for piping; electrical devices; recessed cabinets; bathtubs; soffits; or heating, ventilating or exhaust ducts shall be sealed, lined, insulated or otherwise treated to maintain the required ratings. This requirement shall not apply to entrance doors; however, such doors shall be tight fitting to the frame and sill.
|  | 1206.2.1 Masonry. | The sound transmission class of concrete masonry and clay masonry assemblies shall be calculated in accordance with TMS 302 or determined through testing in accordance with ASTM E90.
|  | 1206.3 Structure-borne sound. | Floor-ceiling assemblies between dwelling units and sleeping units or between a dwelling unit or sleeping unit and a public or service area within the structure shall have an impact insulation class rating of not less than 50 where tested in accordance with ASTM E492, or have a Normalized Impact Sound Rating (NISR) of not less than 45 if field tested in accordance with ASTM E1007. Alternatively, the impact insulation class of floor-ceiling assemblies shall be established by engineering analysis based on a comparison of floor-ceiling assemblies having impact insulation class ratings as determined by the test procedures in ASTM E492.
|  | 1207.1 General. | Enhanced classroom acoustics, where required by this section, shall comply with Section 808 of ICC A117.1.
|  | 1207.2 Where required. | In Group E occupancies, enhanced classroom acoustics shall be provided in all classrooms with a volume of 20,000 cubic feet (566 m3) or less.
|  | 1208.4 Efficiency dwelling units. | Efficiency dwelling units shall conform to the requirements of the code except as modified herein:

## BC13
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1301.1 Scope. | This chapter governs the design and construction of buildings for energy efficiency. | 1301.1 Scope | This chapter governs the design and construction of buildings for energy efficiency.
1301.1.1 Criteria. | Buildings shall be designed and constructed in accordance with the New York City Energy Conservation Code. | 1301.1.1 Criteria | Buildings shall be designed and constructed in accordance with the International Energy Conservation Code.

## BC14
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1401.1 Scope. | The provisions of this chapter shall establish the minimum requirements for exterior: walls; wall coverings; wall openings; windows and doors; architectural trim; balconies; projections; and other appendages. | 1401.1 Scope. | The provisions of this chapter shall establish the minimum requirements for exterior walls; exterior wall coverings; exterior wall openings; exterior windows and doors; and architectural trim.
1401.2 Construction documents. | Construction documents for exterior wall coverings required to be tested in accordance with NFPA 285 pursuant to this code shall include the following data and information:
1402.1 Definitions. | The following terms are defined in Chapter 2:
1403.1 General. | The provisions of this section shall apply to exterior walls, exterior wall coverings and components thereof. | 1403.1 General. | Materials used for the construction of exterior walls shall comply with the provisions of this section. Materials not prescribed herein shall be permitted, provided that any such alternative has been approved.
1403.2 Weather protection. | Exterior walls shall provide the building with a weather-resistant exterior wall envelope. The exterior wall envelope shall include flashing, as described in Section 1405.4. The exterior wall envelope shall be designed and constructed in such a manner as to prevent the accumulation of water within the wall assembly by providing a water-resistive barrier behind the exterior veneer, as described in Section 1404.2, and a means for draining water that enters the assembly to the exterior. Protection against condensation shall be provided as required. Exceptions: 1. A weather-resistant exterior wall envelope shall not be required over concrete and masonry walls designed to resist water penetration and detrimental effects from freeze/thaw cycling and in accordance with Chapters 19 and 21 of this code, as applicable. 2. Compliance with the requirements for a means of drainage, and the requirements of Sections 1404.2 and 1405.4 of this code, shall not be required for an exterior wall envelope that has been demonstrated through testing to resist wind-driven rain, including joints, penetrations and intersections with dissimilar materials, in accordance with ASTM E 331 under the following conditions: 2.1. Exterior wall envelope test assemblies shall include at least one opening, one control joint, and where required, one wall/eave interface and one wall sill. Tested openings and penetrations shall be representative of the intended end-use configuration. 2.2. Exterior wall envelope test assemblies shall be at least 4 feet by 8 feet (1220 mm by 2438.4 mm) in size. 2.3. Exterior wall envelope assemblies shall be tested at a minimum differential pressure of 6.24 pounds per square foot (psf) (0.297 kN/m2) for a duration of 2 hours. The exterior wall envelope assemblies shall also be tested at a minimum differential pressure not less than 20 percent of the positive design wind load as calculated per Chapter 16, or 15 pounds per square foot (psf) (0.718 kN/m2) for a duration of 15 minutes. 2.4. The exterior wall envelope design shall be considered to resist wind-driven rain where the results of testing indicate that water did not penetrate the test assembly including control joints in the exterior wall envelope, joints at the perimeter of openings or intersections of terminations with dissimilar materials. 3. Exterior insulation and finish systems (EIFS) complying with Section 1408.4.1.
1403.3 Structural. | Exterior wall envelope, and the associated openings, shall be designed and constructed to resist safely the superimposed loads required by Chapter 16.
1403.4 Fire resistance. | Exterior wall envelope shall be fire-resistance rated as required by other sections of this code with opening protection as required by Chapter 7.
1403.5 Vertical and lateral flame propagation. | Exterior walls that contain foam plastic insulation including exterior insulation and finish systems (EIFS), metal composite material (MCM) systems, high-pressure decorative exterior-grade compact laminates (HPL), and fiber-reinforced polymer (FRP) shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. Foam plastic insulation assemblies and FRP shall be tested in accordance with Section 2603.5.5. MCM systems shall be tested in accordance with Section 1407.11. HPL systems shall be tested in accordance with Section 1409.11. Approved NFPA 285 tested assembly design documentation shall be included on the submitted construction documents complying with Section 1401.2. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department. Combustible exterior wall coverings shall comply with Section 1406 of this code. Exception: Fiber-reinforced polymer (FRP) where permitted by Section 2613.5 not to be tested.
1403.5.1 Exterior walls with water-resistive barriers. | Exterior walls on buildings of Type I, II, III, or IV construction that are greater than 40 feet (12 192 mm) in height above grade plane and contain a combustible water-resistive barrier shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. For the purposes of this section, fenestration products and flashing of fenestration products and water-resistive barrier flashing and accessories at other locations, including through wall flashings and attachment accessories, shall not be considered part of the water-resistive barrier. Exceptions: 1. Walls in which the water-resistive barrier is the only combustible component and the exterior wall has a wall covering of brick, concrete, stone, terra cotta, stucco or steel with minimum thicknesses in accordance with Table 1405.2 of this code. 2. Walls in which the water-resistive barrier is the only combustible component and the water-resistive barrier has a peak heat release rate of less than 150 kW/m2 (203.9 hp/m2), a total heat release of less than 20 MJ/m2 (18 956 BTU/m2) and an effective heat of combustion of less than 18 MJ/kg (17 060 BTU/lb) as determined in accordance with ASTM E 1354 and has a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E 84 or UL 723. The ASTM E 1354 test shall be conducted on specimens at the thickness intended for use, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2. |  |  |  | See BC14 Tables&Figures
1403.6 Flood resistance. | For buildings in flood hazard areas, the exterior wall envelope extending below the design flood elevation shall be resistant to water damage and shall comply with Appendix G.
1403.7 Thermal and condensation resistance. | The exterior wall envelope shall be designed and constructed for thermal and condensation resistance as necessary to meet the requirements of the New York City Energy Conservation Code.
1403.8 Bird friendly materials. | Bird friendly materials shall be required in accordance with Sections 1403.8.1 through 1403.8.4.
1403.8.1 Exterior wall envelope. | The exterior wall envelope, and any associated openings, shall be constructed with bird friendly materials up to 75 feet (22 860 mm) above grade. Materials other than bird friendly materials shall not exceed an aggregate of 10 square feet (0.93 m²) within any 10 feet (3048 mm) by 10 feet (3048 mm) square area of exterior wall below 75 feet (22 860 mm) above grade. Exceptions: 1. Where ground floor transparency is required by the New York City Zoning Resolution, transparent bird friendly material with a UV-reflective pattern and a maximum threat factor of 27 shall be provided. 2. In areas of special flood hazard and shaded X-Zones where flood resistant glazing is proposed and ground floor transparency is required by the New York City Zoning Resolution, transparent bird friendly material with a UV-reflective pattern and a maximum threat factor of 36 shall be provided.
1403.8.2 Bird hazard installations. | Bird hazard installations shall be constructed of bird friendly materials regardless of their height above grade.
1403.8.3 Fly-through conditions. | Fly-through conditions located 75 feet (22 860 mm) or less above grade shall be constructed with bird friendly materials.
1403.8.4 Adjacency to green roofs. | The exterior wall envelope, and any associated openings, installed adjacent to a green roof system on the same building shall be constructed with bird friendly materials up to 12 feet (3657.6 mm) above the walking surface.
1403.9 Air barrier. | The exterior wall envelope shall be designed and constructed with an air barrier as necessary to meet the requirements of the New York City Energy Conservation Code and this code.
1404.1 General. | Materials used for the construction of exterior walls shall comply with the provisions of this section. Materials not prescribed herein shall be permitted, provided that any such alternative has been approved. | 1404.1 General. | Exterior wall coverings shall be designed and constructed in accordance with the applicable provisions of this section.
1404.2 Water-resistive barrier. | Not fewer than one layer of No. 15 asphalt felt complying with ASTM D 226 for Type 1 felt or other approved materials shall be attached to the studs or sheathing, with flashing as described in Section 1405.4 of this code, in such a manner as to provide a continuous water-resistive barrier behind the exterior wall veneer. Combustible water-resistive barriers shall comply with special inspection requirements of Chapter 17 of this code.
1404.3 Wood. | Exterior walls of wood construction shall be designed and constructed in accordance with Chapter 23.
1404.3.1 Basic hardboard. | Basic hardboard shall conform to the requirements of ANSI A135.4.
1404.3.2 Hardboard siding. | Hardboard siding shall conform to the requirements of ANSI A135.6 and, where used structurally, shall be so identified by the label of an approved agency.
1404.4 Masonry. | Exterior walls of masonry construction shall be designed and constructed in accordance with this chapter and Chapter 21. Masonry units, mortar and metal accessories used in anchored and adhered veneer shall meet the physical requirements of Chapter 21. The backing of anchored and adhered veneer shall be of concrete, masonry, steel framing or wood framing. Continuous insulation meeting the applicable requirements of this code shall be permitted between the backing and the masonry veneer.
1404.5 Metal. | Exterior walls constructed of cold-formed steel, structural steel or aluminum shall be designed in accordance with Chapters 20 and 22, as applicable.
1404.5.1 Aluminum siding. | Aluminum siding shall conform to the requirements of AAMA 1402.
1404.5.2 Cold-rolled copper. | Copper shall conform to the requirements of ASTM B 370.
1404.5.3 Lead-coated copper. | Lead-coated copper shall conform to the requirements of ASTM B 101.
1404.6 Concrete. | Exterior walls of concrete construction shall be designed and constructed in accordance with Chapter 19.
1404.7 Glass-unit masonry. | Exterior walls of glass-unit masonry shall be designed and constructed in accordance with Chapter 21.
1404.8 Plastics. | Plastic panel, apron or spandrel walls as defined in this code shall not be limited in thickness, provided that such plastics and their assemblies conform to the require­ments of Chapter 26 and other applicable requirements of this chapter, and are constructed of approved weather-resistant materials of adequate strength to resist the wind loads for cladding specified in Chapter 16.
1404.9 Vinyl siding. | Vinyl siding shall be certified and labeled as conforming to the requirements of ASTM D 3679 by an approved agency.
1404.10 Fiber-cement siding. | Fiber-cement siding shall conform to the requirements of ASTM C 1186, Type A or ISO 8336, Category A, and shall be so identified on labeling listing an approved agency.
1404.11 Exterior insulation finish system (EIFS). | EIFS shall be designed and constructed in accordance with Section 1408.
1404.12 Polypropylene siding. | Polypropylene siding shall be certified and labeled as conforming to the requirements of ASTM D 7254 and those of Section 1404.12.1 or 1404.12.2 of this code by an approved agency. Polypropylene siding shall be installed in accordance with manufacturer’s instructions and the requirements of Section 1405.18 of this code. Polypropylene siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.
1404.12.1 Flame spread index. | The certification of the flame spread index shall be accompanied by a test report stating that all portions of the test specimen ahead of the flame front remained in position during the test in accordance with ASTM E 84 or UL 723.
1404.12.2 Distance between adjacent buildings. | The distance between a building with polypropylene siding and the adjacent building shall be not less than 10 feet (3048 mm).
1404.13 Foam plastic insulation. | Foam plastic insulation used in exterior wall covering assemblies shall comply with Chapter 26 and be fireblocked in accordance with Section 718.2.6.1.
1405.1 General. | Exterior wall coverings shall be designed and constructed in accordance with the applicable provisions of this section. Installations not prescribed herein shall be permitted, provided that such alternative has been approved. Installations shall be in accordance with approved construction documents where a permit is required. Installations of exterior wall coverings shall comply with the special inspection requirements of Chapter 17.
1405.2 Weather protection. | The exterior wall envelope shall provide weather protection for the building. The materials of the minimum nominal thickness specified in Table 1405.2 shall be acceptable as approved weather coverings. Exception: Weather coverings not meeting the minimum nominal thicknesses specified in Table 1405.2 shall be permitted provided such alternative has been approved. |  |  |  | See BC14 Tables&Figures
1405.3 Vapor retarders. | Vapor retarders as described in Section 1405.3.3 shall be provided based on an approved design using accepted engineering practice for hygrothermal analysis.
1405.3.1 Reserved.
1405.3.2 Reserved.
1405.3.3 Material vapor retarder class. | The vapor retarder class shall be based on the manufacturer’s certified testing or a tested assembly.
1405.3.4 Minimum clear airspaces and vented openings for vented cladding. | For the purposes of this section, vented cladding shall include the following minimum clear airspaces:
1405.4 Flashing. | Flashing shall be installed in such a manner so as to prevent moisture from entering the wall or to redirect moisture to the exterior. Flashing shall be installed where required at the perimeters of exterior door and window assemblies, penetrations and terminations of exterior wall assemblies, exterior wall intersections with roofs, chimneys, porches, decks, balconies and similar projections and at built-in gutters and similar locations where moisture could enter the wall. Flashing with projecting flanges shall be installed on both sides and the ends of copings, under sills and continuously above projecting trim.
1405.4.1 Exterior wall pockets. | In exterior walls of buildings or structures, wall pockets or crevices in which moisture can accumulate shall be avoided or protected with caps or drips, or other approved means shall be provided to prevent water damage.
1405.4.2 Masonry. | Flashing and weep holes in anchored veneer shall be located in the first course of masonry above finished ground level above the foundation wall or slab, and other points of support, including structural floors, shelf angles and lintels where anchored veneers are designed in accordance with Section 1405.6.
1405.5 Wood veneers. | Wood veneers on exterior walls of buildings of Type I, II, III and IV construction shall be not less than 1-inch (25.4 mm) nominal thickness, 0.438-inch (11.1 mm) exterior hardboard siding or 0.375-inch (9.5 mm) exterior-type wood structural panels or particleboard and shall conform to the following:
1405.6 Anchored masonry veneer. | Anchored masonry veneer shall comply with the provisions of Sections 1405.6, 1405.7, 1405.8 and 1405.9 and Sections 12.1 and 12.2 of TMS 402, as modified by Chapter 21 of this code.
1405.6.1 Tolerances. | Anchored masonry veneers in accordance with Chapter 14 are not required to meet the tolerances in Article 3.3 F1 of TMS 602.
1405.6.2 Seismic requirements. | Anchored masonry veneer located in Seismic Design Category C or D shall conform to the requirements of Section 12.2.2.10 of TMS 402, as modified by Chapter 21 of this code.
1405.7 Stone veneer. | Anchored stone veneer units not exceeding 10 inches (254 mm) in thickness shall be anchored directly to masonry, concrete or to stud construction by one of the following methods:
1405.8 Slab-type veneer. | Anchored slab-type veneer units not exceeding 2 inches (50.8 mm) in thickness shall be anchored directly to masonry, concrete or light-frame construction. For veneer units of marble, travertine, granite or other stone units of slab form, ties of corrosion-resistant dowels in drilled holes shall be located in the middle third of the edge of the units, spaced not more than 24 inches (609.6 mm) apart around the periphery of each unit with not less than four ties per veneer unit. Units shall not exceed 20 square feet (1.9 m2) in area. If the dowels are not tight fitting, the holes shall be drilled not more than 0.063 inch (1.6 mm) larger in diameter than the dowel, with the hole countersunk to a diameter and depth equal to twice the diameter of the dowel in order to provide a tight-fitting key of cement mortar at the dowel locations where the mortar in the joint has set. Veneer ties shall be corrosion-resistant metal capable of resisting, in tension or compression, a force equal to two times the weight of the attached veneer. If made of sheet metal, veneer ties shall be not smaller in area than 0.0336 by 1 inch (0.853 by 25.4 mm) or, if made of wire, not smaller in diameter than 0.1483-inch (3.76 mm) wire.
1405.9 Terra cotta. | Anchored terra cotta or ceramic units not less than 1 inch (25.4 mm) thick shall be anchored directly to masonry, concrete or stud construction. Terra cotta or ceramic unit anchorage shall be engineered to transfer loads to stable backup walls utilizing not less than two non-corrosive anchors per unit.
1405.10 Adhered masonry veneer. | Adhered masonry veneer shall comply with the applicable requirements in this section and Sections 12.1 and 12.3 of TMS 402, as modified by Chapter 21 of this code.
1405.10.1 Exterior adhered masonry veneer. | Exterior adhered masonry veneer shall be installed in accordance with the manufacturer’s instructions and Section 1405.10.
1405.10.1.1 Water-resistive barriers. | Water-resistive barriers shall be installed as required in Section 2510.6.
1405.10.1.2 Flashing. | Flashing shall comply with this section and the applicable requirements of Section 1405.4.
1405.10.1.2.1 Flashing at foundation. | A corrosion-resistant screed or flashing of a minimum 0.019-inch (0.48 mm) or 26 gage galvanized or plastic with a minimum vertical attachment flange of 3½ inches (88.9 mm) shall be installed to extend not less than 1 inch (25.4 mm) below the foundation plate line on exterior stud walls in accordance with Section 1405.4. The water-resistive barrier shall lap over the exterior of the attachment flange of the screed or flashing.
1405.10.1.3 Clearances. | On exterior stud walls, adhered masonry veneer shall be installed not less than 4 inches (101.6 mm) above the earth, or not less than 2 inches (50.8 mm) above paved areas, or not less than ½ inch (12.7 mm) above exterior walking surfaces that are supported by the same foundation that supports the exterior wall.
1405.10.1.4 Adhered masonry veneer installed with lath and mortar. | Exterior adhered masonry veneer installed with lath and mortar shall comply with the following.
1405.10.1.4.1 Lathing. | Lathing shall comply with the requirements of Section 2510.
1405.10.1.4.2 Scratch coat. | A nominal ½-inch (12.7 mm) thick layer of mortar complying with the material requirements of Sections 2103 and 2512.2 shall be applied, encapsulating the lathing. The surface of this mortar shall be scored horizontally, resulting in a scratch coat.
1405.10.1.4.3 Adhering veneer. | The masonry veneer units shall be adhered to the mortar scratch coat with a nominal ½-inch (12.7 mm) thick setting bed of mortar complying with Sections 2103 and 2512.2 applied to create a full setting bed for the back of the masonry veneer units. The masonry veneer units shall be worked into the setting bed resulting in a nominal ⅜-inch (9.5 mm) setting bed after the masonry veneer units are applied.
1405.10.1.5 Adhered masonry veneer applied directly to masonry and concrete. | Adhered masonry veneer applied directly to masonry or concrete shall comply with the applicable requirements of Section 1405.10, and with the requirements of Section 1405.10.1.4 or 2510.7.
1405.10.1.6 Cold weather construction. | Cold weather construction of adhered masonry veneer shall comply with the requirements of Sections 2104 and 2512.4.
1405.10.1.7 Hot weather construction. | Hot weather construction of adhered masonry veneer shall comply with the requirements of Section 2104.
1405.10.2 Exterior adhered masonry veneers—porcelain tile. | Adhered units shall not exceed ⅝ inch (15.8 mm) thickness and 24 inches (609.6 mm) in any face dimension nor more than 3 square feet (0.28 m2) in total face area and shall not weigh more than 9 pounds psf (0.43 kN/m2). Porcelain tile shall be adhered to an approved backing system.
1405.10.3 Interior adhered masonry veneers. | Interior adhered masonry veneers shall have a maximum weight of 20 psf (0.958 kg/m2) and shall be installed in accordance with Section 1405.10. The supporting members shall be designed to limit deflection to 1/600 of the span of the supporting members.
1405.11 Metal veneers. | Veneers of metal shall be fabricated from approved corrosion-resistant materials or shall be protected front and back with porcelain enamel, or otherwise be treated to render the metal resistant to corrosion. Such veneers shall be not less than 0.0149-inch (0.378 mm) nominal thickness sheet steel mounted on wood or metal furring strips or approved sheathing on light-frame construction.
1405.11.1 Attachment. | Exterior metal veneer shall be securely attached to the supporting masonry or framing members with corrosion-resistant fastenings, metal ties or by other approved devices or methods. The spacing of the fastenings or ties shall not exceed 24 inches (609.6 mm) either vertically or horizontally, but where units exceed 4 square feet (0.4 m2) in area there shall be not less than four attachments per unit. The metal attachments shall have a cross-sectional area not less than provided by W 1.7 wire. Such attachments and their supports shall be designed and constructed to resist the wind loads as specified in Section 1609 for components and cladding.
1405.11.2 Weather protection. | Metal supports for exterior metal veneer shall be protected by painting, galvanizing or by other approved coating or treatment. Wood studs, furring strips or other wood supports for exterior metal veneer shall be approved pressure-treated wood or protected as required in Section 1403.2. Joints and edges exposed to the weather shall be caulked with approved durable waterproofing material or by other approved means to prevent penetration of moisture.
1405.11.3 Backup. | Masonry backup shall not be required for metal veneer unless required by the fire-resistance requirements of this code.
1405.11.4 Grounding. | Grounding of metal veneers on buildings shall comply with the requirements of the New York City Electrical Code and Chapter 27 of this code.
1405.12 Thin exterior structural glass veneer. | The area of a single section of thin exterior structural glass veneer shall not exceed 10 square feet (0.93 m2) where that section is not more than 15 feet (4572 mm) above the level of the sidewalk or grade level directly below, and shall not exceed 6 square feet (0.56 m2) where it is more than 15 feet (4572 mm) above that level. In no event shall thin exterior structural glass veneer be installed more than 35 feet (10 668 mm) above the level of the sidewalk or grade level directly below.
1405.12.1 Length and height. | The length or height of any section of thin exterior structural glass veneer shall not exceed 48 inches (1220 mm).
1405.12.2 Thickness. | The thickness of thin exterior structural glass veneer shall be not less than 0.344 inch (8.7 mm).
1405.12.3 Application. | Thin exterior structural glass veneer shall be set only after backing is thoroughly dry and after application of an approved bond coat uniformly over the entire surface of the backing so as to effectively seal the surface. Glass shall be set in place with an approved mastic cement in sufficient quantity so that at least 50 percent of the area of each glass unit is directly bonded to the backing by mastic not less than ¼ inch (6.4 mm) thick and not more than ⅝ inch (15.9 mm) thick. The bond coat and mastic shall be evaluated for compatibility and shall bond firmly together.
1405.12.4 Installation at sidewalk level. | Where thin exterior structural glass veneer extends to a sidewalk surface, each section shall rest in an approved metal molding, and be set at least ¼ inch (6.4 mm) above the highest point of the sidewalk. The space between the molding and the sidewalk shall be thoroughly caulked and made water tight.
1405.12.4.1 Installation above sidewalk level. | Where thin exterior structural glass veneer is installed above the level of the top of a bulkhead facing, or at a level more than 36 inches (914.4 mm) above the sidewalk level, the mastic cement binding shall be supplemented with approved nonferrous metal shelf angles located in the horizontal joints in every course. Such shelf angles shall be not less than 0.0478-inch (1.2 mm) thick and not less than 2 inches (50.8 mm) long and shall be spaced at approved intervals, with not less than two angles for each glass unit. Shelf angles shall be secured to the wall or backing with expansion bolts, toggle bolts or by other approved methods.
1405.12.5 Joints. | Unless otherwise specifically approved by the commissioner, abutting edges of thin exterior structural glass veneer shall be ground square. Mitered joints shall not be used except where specifically approved for wide angles. Joints shall be uniformly buttered with an approved jointing compound and horizontal joints shall be held to not less than 0.063 inch (1.6 mm) by an approved nonrigid substance or device. Where thin exterior structural glass veneer abuts nonresilient material at sides or top, expansion joints not less than ¼ inch (6.4 mm) wide shall be provided.
1405.12.6 Mechanical fastenings. | Thin exterior structural glass veneer installed above the level of the heads of show windows and veneer installed more than 12 feet (3657.6 mm) above sidewalk level shall, in addition to the mastic cement and shelf angles, be held in place by the use of fastenings at each vertical or horizontal edge, or at the four corners of each glass unit. Fastenings shall be secured to the wall or backing with expansion bolts, toggle bolts or by other methods. Fastenings shall be so designed as to hold the glass veneer in a vertical plane independent of the mastic cement. Shelf angles providing both support and fastenings shall be permitted.
1405.12.7 Flashing. | Exposed edges of thin exterior structural glass veneer shall be flashed with overlapping corrosion-resistant metal flashing or equivalent and caulked with a waterproof compound in a manner to effectively prevent the entrance of moisture between the glass veneer and the backing.
1405.13 Exterior windows and doors. | Windows and doors installed in exterior walls shall conform to the testing and performance requirements of Section 1709.5.
1405.13.1 Installation. | Windows and doors shall be installed in accordance with the manufacturer’s instructions. Fastener size and spacing shall be provided in such instructions and shall be calculated based on maximum loads and spacing used in the tests.
1405.13.2 Windows in Group R-2 and R-3 occupancies. | Windows in Group R-2 and R-3 occupancies shall comply with Sections 1015.9 and 1015.8, respectively.
1405.14 Vinyl siding. | Vinyl siding conforming to the requirements of this section and complying with ASTM D 3679 shall be permitted on exterior walls of buildings located in areas where the allowable stress design speed Vasd, as determined in accordance with Section 1609.3.1, does not exceed 100 miles per hour (44.7 m/s) and the building height is less than or equal to 40 feet (12 192 mm) in Exposure C. Where construction is located in areas where the allowable stress design speed Vasd, as determined in accordance with Section 1609.3.1, exceeds 100 miles per hour (44.7 m/s), or building heights are in excess of 40 feet (12 192 mm), tests or calculations showing compliance with Chapter 16 of this code shall be submitted. Vinyl siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.
1405.14.1 Application. | The siding shall be applied over sheathing or materials listed in Section 2304.6. Siding shall be applied to conform to the water-resistive barrier requirements in Section 1403. Siding and accessories shall be installed in accordance with the manufacturer’s instructions. Unless otherwise specified in the manufacturer’s instructions, nails used to fasten the siding and accessories shall have a minimum 0.313-inch (7.9 mm) head diameter and ⅛-inch (3.18 mm) shank diameter. The nails shall be corrosion resistant and shall be long enough to penetrate the studs or nailing strip at least ¾ inch (19.1 mm). For cold-formed steel light-frame construction, corrosion-resistant fasteners shall be used. Screw fasteners shall penetrate the cold-formed steel framing at least three exposed threads. Other fasteners shall be installed in accordance with the manufacturer’s instructions. Where the siding is installed horizontally, the fastener spacing shall not exceed 16 inches (406.4 mm) horizontally and 12 inches (304.8 mm) vertically. Where the siding is installed vertically, the fastener spacing shall not exceed 12 inches (304.8 mm) horizontally and 12 inches (304.8 mm) vertically.
1405.15 Cement plaster. | Cement plaster applied to exterior walls shall conform to the requirements specified in Chapter 25.
1405.16 Fiber-cement siding. | Fiber-cement siding complying with Section 1404.10 shall be permitted on exterior walls of Type I, II, III, IV and V construction for wind pressure resistance or wind speed exposures as indicated by the manufacturer’s listing and label, and the installation instructions. Where specified, the siding shall be installed over sheathing or materials listed in Section 2304.6 and shall be installed to conform to the water-resistive barrier requirements in Section 1403. Siding and accessories shall be installed in accordance with the manufacturer’s instructions. Unless otherwise specified in the manufacturer’s instructions, nails used to fasten the siding to wood studs shall be corrosion-resistant round head smooth shank and shall be long enough to penetrate the studs at least 1 inch (25.4 mm). For cold-formed steel light-frame construction, corrosion-resistant fasteners shall be used. Screw fasteners shall penetrate the cold-formed steel framing at least three exposed full threads. Other fasteners shall be installed in accordance with the manufacturer’s instructions.
1405.16.1 Panel siding. | Fiber-cement panels shall comply with the requirements of ASTM C 1186, Type A, minimum Grade II or ISO 8336, Category A, minimum Class 2. Panels shall be installed with the long dimension either parallel or perpendicular to framing. Vertical and horizontal joints shall occur over framing members and shall be protected with sealant, battens or flashing. Alternatively, vertical or horizontal joints shall be shiplap or otherwise designed to comply with Section 1403.2 of this code. Panel siding shall be installed with fasteners in accordance with the manufacturer’s instructions.
1405.16.2 Lap siding. | Fiber-cement lap siding having a maximum width of 12 inches (304.8 mm) shall comply with the requirements of ASTM C 1186, Type A, minimum Grade II or ISO 8336, Category A, minimum Class 2. Lap siding shall be lapped a minimum of 1¼ inches (32 mm) and lap siding not having tongue-and-groove end joints shall have the ends protected with caulking, covered with an H-section joint cover, located over a strip of flashing or shall be otherwise designed to comply with Section 1403.2 of this code. Lap siding courses shall be installed with the fastener heads exposed or concealed in accordance with the manufacturer’s instructions.
1405.17 Fastening. | Weather boarding and wall coverings shall be securely fastened with aluminum, copper, zinc, zinc-coated or other approved corrosion-resistant fasteners in accordance with the nailing schedule in Table 2304.10.1 or the manufacturer’s instructions. Shingles and other weather coverings shall be attached with appropriate standard-shingle nails to furring strips securely nailed to studs, or with approved mechanically bonding nails, except where sheathing is of wood not less than 1-inch (25.4 mm) nominal thickness or of wood structural panels as specified in Table 2308.6.3(3).
1405.18 Polypropylene siding. | Polypropylene siding conforming to the requirements of this section and complying with Section 1404.12 shall be limited to exterior walls of Type VB construction located in areas where the wind speed specified in Chapter 16 does not exceed 100 miles per hour (44.7 m/s) and the building height is less than or equal to 40 feet (12 192 mm) in Exposure C. Where construction is located in areas where the basic wind speed exceeds 100 miles per hour (44.7 m/s), or building heights are in excess of 40 feet (12 192 mm), tests or calculations showing compliance with Chapter 16 shall be submitted. Polypropylene siding shall be installed in accordance with the manufacturer’s instructions. Polypropylene siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.
1406.1 General. | Section 1406 shall apply to exterior wall coverings, exterior balconies and similar projections, bay and oriel windows, decks, porches, porticos, entranceways, and storm enclosures constructed of combustible materials. Combustible water-resistive barriers complying with Section 1403.5.1 shall be permitted in exterior wall coverings. Fireblocking shall be installed in accordance with Section 1406.2.3. Existing building retrofits utilizing combustible exterior wall coverings shall also comply with Section 1406.5. Combustible exterior wall coverings shall be subject to the special inspection requirements of Section 1705.16. | 1406.1 General. | The provisions of this section shall govern the materials, construction and quality of metal composite materials (MCM) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16.
1406.2 Combustible exterior wall coverings. | Combustible exterior wall coverings, including architectural trim, shall comply with this section. Exceptions: 1. Plastics complying with Chapter 26. 2. Metal composite materials (MCM) complying with Section 1407. 3. High-pressure decorative exterior-grade compact laminates (HPL) complying with Section 1409.
1406.2.1 Type I, II, III and IV construction. | In buildings of Type I, II, III and IV construction, exterior wall coverings shall be permitted to be constructed of combustible materials in accordance with Section 1406.2.1.1, subject to the following limitations:
1406.2.1.1 Ignition resistance. | Where permitted by Section 1406.2.1 of this code, combustible exterior wall coverings shall be tested in accordance with NFPA 268. Exceptions: The following materials are not required to be tested in accordance with NFPA 268. However, such materials shall comply with all other provisions of Section 1406 of this code. 1. Wood or wood-based products. 2. Other combustible materials covered with an exterior weather covering other than vinyl sidings included in and complying with the thickness requirements of Table 1405.2 of this code. 3. Aluminum having a minimum thickness of 0.019 inch (0.48 mm). |  |  |  | See BC14 Tables&Figures
1406.2.1.1.1 Fire separation 5 feet or less. | Where installed on exterior walls having a fire separation distance of 5 feet (1524 mm) or less, combustible exterior wall coverings shall not exhibit sustained flaming as defined in NFPA 268.
1406.2.1.1.2 Fire separation greater than 5 feet. | For fire separation distances greater than 5 feet (1524 mm), any exterior wall covering shall be permitted that has been exposed to a reduced level of incident radiant heat flux in accordance with the NFPA 268 test method without exhibiting sustained flaming. The minimum fire separation distance required for the exterior wall covering shall be determined from Table 1406.2.1.1.2 of this code based on the maximum tolerable level of incident radiant heat flux that does not cause sustained flaming of the exterior wall covering. |  |  |  | See BC14 Tables&Figures
1406.2.2 Location. | Combustible exterior wall coverings located along the top of exterior walls shall be completely backed up by the exterior wall and shall not extend over or above the top of the exterior walls.
1406.2.3 Fireblocking. | Exterior wall coverings shall be fireblocked in accordance with Section 718.2.6.
1406.3 Exterior balconies and similar projections. | Exterior wall covering on walls abutting balconies, and cladding on the sides and underside of balconies, shall be constructed of noncombustible materials. Exterior walls abutting balconies shall be noncombustible up to 12 feet (3657.6 mm) above the walking surface or to the underside of the balcony above, whichever is less. On cantilevered balconies, the exterior wall abutting the balcony, plus 3 feet (914.4 mm) on each side, shall be constructed of noncombustible materials. On recessed and semirecessed balconies, the exterior walls abutting the balconies shall be constructed of noncombustible materials. Exception: Combustible exterior wall coverings shall be allowed on balconies in Type V construction with a fire separation distance greater than or equal to 5 feet (1524 mm).
1406.4 Bay and oriel windows, decks, porches, porticos, entranceways, and storm enclosures. | Bay and oriel windows, decks, porches, porticos, entranceways and storm enclosures shall conform to the type of construction required for the building to which they are attached, including required fire rating, unless otherwise modified by the requirements of this section. For the purposes of this section, such structures shall be referred to as, “appendages.” Exception: Plastic complying with Chapter 26.
1406.4.1 Appendages on Type I and II construction. | Appendages on buildings of Type I or II construction shall be constructed of noncombustible materials. However, on buildings not more than three stories or 40 feet (12 192 mm) in height, whichever is less, fire-retardant-treated wood shall be permitted.
1406.4.2 Appendages on Type III, IV and VA construction. | Appendages on buildings of Type III, IV and VA construction may be constructed of combustible materials, provided that all the following conditions are met: 1. Such building does not exceed three stories or 40 feet (12 192 mm) in height, whichever is less. 2. The main use or dominant occupancy of such building is classified in Occupancy Group R-2 or R-3. 3. The appendage has an exterior separation on all exposed sides of at least 15 feet (4572 mm), measured from the outermost surface of the appendage, except that appendages with exposed sides protected by minimum 1-hour fire-rated construction extending at least 36 inches (914.4 mm) above the highest combustible horizontal surface may be located up to a mini¬mum distance of 36 inches (914.4 mm) from any property line. 4. The appendage is so constructed that its removal or destruction will not reduce the structural stability or fire-resistive integrity of the building. 5. The appendage has a superficial area not exceeding 150 square feet (13.9 m2) when viewed from directly above and is included in the area limitations of Table 503 for the entire building. 6. The appendage is not higher than the sills of the second-story windows. 7. The vertical surface area of the combustible portions of the appendage does not exceed 10 percent of the total wall area (windows excluded) of the building. 8. For enclosed appendages, the roof of the appendage has a class A roof covering, and the soffit or ceiling covering the combustible roof framing shall have a minimum 1-hour fire-resistance rating. Exception: Appendages constructed of fire-retardant-treated wood, on buildings not exceeding 3 stories or 40 feet (12 192 mm) in height, whichever is less, need not comply with Items 2 through 8.
1406.4.3 Appendages on Type VB construction. | Appendages may be constructed of combustible materials on buildings of construction Type VB.
1406.5 Retrofit of existing buildings. | Combustible materials shall not be permitted for use at the outermost surface of the exterior wall covering for exterior envelope retrofits of existing nonsprinklered buildings over 75 feet (22 860 mm), unless the following conditions are satisfied:
1407.1 General. | The provisions of this section shall govern the materials, construction and quality of metal composite materi­als (MCM) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16. | 1407.1 General. | The provisions of this section shall govern the materials, construction and quality of exterior insulation and finish systems (EIFS) for use as exterior wall coverings in addition to other applicable requirements of Chapters 7, 14, 16, 17 and 26.
1407.1.1 Plastic core. | The plastic core of the MCM shall not contain foam plastic insulation as defined in Section 202.
1407.1.2 Prohibited locations. | The use of MCM in exterior wall coverings is subject to the following limitations:
1407.2 Exterior wall finish. | MCM used as exterior wall finish or as elements of bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1407.4 through 1407.16.
1407.3 Architectural trim and embellishments. | MCM used as architectural trim or embellishments shall comply with Sections 1407.7 through 1407.14.
1407.4 Structural design. | MCM systems shall be designed and constructed to resist wind loads as required by Chapter 16 for components and cladding.
1407.5 Approval. | Results of approved tests or an engineering analysis shall be submitted to the commissioner to verify compliance with the requirements of Chapter 16 for wind loads.
1407.6 Weather resistance. | MCM systems shall comply with Section 1403 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s installation instructions.
1407.7 Durability. | MCM systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1407 for the duration of use.
1407.8 Fire-resistance rating. | Where MCM systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the commissioner that the required fire-resistance rating is maintained. Exception: MCM systems not containing foam plastic insulation, which are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly, shall not be required to comply with this section.
1407.9 Surface-burning characteristics. | MCM shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested as an assembly in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723.
1407.10 Thermal barriers. | MCM shall be separated from the interior of a building by an approved thermal barrier consisting of 5/8-inch (15.9 mm) Type X gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (121°C) after 20 minutes of fire exposure in accordance with the standard time-temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in accordance with criteria established by testing in accordance with UL 1715, where the thermal barrier shall remain in place for 20 minutes.
1407.11 Full-scale tests. | All MCM systems shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the MCM system with the MCM in the maximum thickness intended for use, including any required fireblocking. Approved NFPA 285 tested assembly design documentation of the MCM system shall be included on the submitted construction documents complying with Section 1401.2 of this code. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department.
1407.12 Reserved.
1407.13 Foam plastic insulation. | MCM systems containing foam plastic insulation shall also comply with the requirements of Section 2603.
1407.14 Labeling. | MCM shall be labeled in accordance with this code and Section 28-113 of the Administrative Code.
1407.15 Special inspection. | MCM shall be subject to special inspection in accordance with Chapter 17.
1407.16 Fireblocking. | MCM installations shall be fireblocked in accordance with Section 718.2.6.1.
1408.1 General. | The provisions of this section shall govern the materials, construction and quality of exterior insulation and finish systems (EIFS) for use as exterior wall coverings in addition to other applicable requirements of Chapters 7, 14, 16, 17 and 26. | 1408.1 General. | The provisions of this section shall govern the materials, construction and quality of High-Pressure Decorative Exterior-Grade Compact Laminates (HPL) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16.
1408.1.1 Prohibited locations. | The use of EIFS containing foam plastic insulation in exterior wall coverings is subject to the following limitations:
1408.2 Performance characteristics. | EIFS shall be constructed such that it meets the performance characteristics required in ASTM E 2568.
1408.3 Structural design. | The underlying structural framing and substrate shall be designed and constructed to resist loads as required by Chapter 16.
1408.4 Weather resistance. | EIFS shall comply with Section 1403 and shall be designed and constructed to resist environmental conditions in accordance with this section, the approved construction documents and manufacturer’s installation instructions.
1408.4.1 EIFS with drainage. | EIFS with drainage shall have an average minimum drainage efficiency of 90 percent when tested in accordance with requirements of ASTM E 2273 and is required on framed walls of Type V construction, residential Group R occupancies.
1408.4.1.1 Water-resistive barrier. | For EIFS with drainage, the water-resistive barrier shall comply with Section 1404.2 of this code or ASTM E 2570.
1408.5 Installation. | Installation of the EIFS and EIFS with drainage shall be in accordance with the EIFS manufacturer’s instructions and this section.
1408.6 Special inspections. | EIFS installations shall comply with the provisions of Chapter 17.
1408.7 Fireblocking. | EIFS installations containing foam plastic insulation shall be fireblocked in accordance with Section 718.2.6.1.
1408.8 Foam plastic insulation. | EIFS installations containing foam plastic insulation shall be tested and comply with the requirements of Section 2603.
1408.9 Thermal barrier. | EIFS installations containing foam plastic insulation shall be separated from the interior of a building in accordance with Section 2603.5.2.
1409.1 General. | The provisions of this section shall govern the materials, construction and quality of High-Pressure Decorative Exterior-Grade Compact Laminates (HPL) for use as exterior wall coverings in addition to other applicable requirements of Chapters 14 and 16.
1409.1.1 Prohibited locations. | The use of HPL in exterior wall coverings is subject to the following limitations:
1409.2 Exterior wall finish. | HPL used as exterior wall covering or as elements of bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1409.4 through 1409.16.
1409.3 Architectural trim and embellishments. | HPL used as architectural trim or embellishments shall comply with Sections 1409.7 through 1409.14.
1409.4 Structural design. | HPL systems shall be designed and constructed to resist wind loads as required by Chapter 16 for components and cladding.
1409.5 Approval. | Results of approved tests or an engineering analysis shall be submitted to the commissioner to verify compliance with the requirements of Chapter 16 for wind loads.
1409.6 Weather resistance. | HPL systems shall comply with Section 1403 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s instructions.
1409.7 Durability. | HPL systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1409 for the duration of use.
1409.8 Fire-resistance rating. | Where HPL systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the commissioner that the required fire-resistance rating is maintained. Exception: HPL systems not containing foam plastic insulation that are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly shall not be required to comply with this section.
1409.9 Surface-burning characteristics. | HPL shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in the minimum and maximum thicknesses intended for use in accordance with ASTM E 84 or UL 723.
1409.10 Thermal barriers. | HPL shall be separated from the interior of a building by an approved thermal barrier consisting of 5/8-inch (15.9 mm) Type X gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (121°C) after 20 minutes of fire exposure in accordance with the standard time temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in accordance with criteria established by testing performed in accordance with UL 1715, where the thermal barrier shall remain in place for 20 minutes.
1409.11 Full-scale tests. | All HPL systems shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the HPL system with the HPL in the minimum and maximum thicknesses intended for use, including any required fireblocking. Approved NFPA 285 tested assembly design documentation of the HPL system shall be included on the submitted construction documents complying with Section 1401.2 of this code. Deviation from the NFPA 285 tested design shall be approved by the registered design professional and additional documentation shall be provided if requested by the department.
1409.12 Reserved.
1409.13 Foam plastic insulation. | HPL systems containing foam plastic insulation shall also comply with the requirements of Section 2603.
1409.14 Labeling. | HPL shall be labeled in accordance with this code and Article 113 of title 28 of the Administrative Code.
1409.15 Special inspection. | HPL shall be subject to the special inspection requirements of Chapter 17.
1409.16 Fireblocking. | HPL installations shall be fireblocked in accordance with Section 718.2.6.1.
1410.1 Plastic composite decking. | Exterior deck boards, stair treads, handrails and guardrail systems constructed of plastic composites, including plastic lumber, shall comply with Section 2612.
|  | 1402.1 General. | The provisions of this section shall apply to exterior walls, wall coverings and components thereof.
|  | 1402.2 Weather protection. | Exterior walls shall provide the building with a weather-resistant exterior wall envelope. The exterior wall envelope shall include flashing, as described in Section 1404.4. The exterior wall envelope shall be designed and constructed in such a manner as to prevent the accumulation of water within the wall assembly by providing a water-resistive barrier behind the exterior veneer, as described in Section 1403.2, and a means for draining water that enters the assembly to the exterior. Protection against condensation in the exterior wall assembly shall be provided in accordance with Section 1404.3. Exceptions: 1. A weather-resistant exterior wall envelope shall not be required over concrete or masonry walls designed in accordance with Chapters 19 and 21, respectively. 2. Compliance with the requirements for a means of drainage, and the requirements of Sections 1403.2 and 1404.4, shall not be required for an exterior wall envelope that has been demonstrated through testing to resist wind-driven rain, including joints, penetrations and intersections with dissimilar materials, in accordance with ASTM E331 under the following conditions: The exterior wall envelope design shall be considered to resist wind-driven rain where the results of testing indicate that water did not penetrate control joints in the exterior wall envelope, joints at the perimeter of openings or intersections of terminations with dissimilar materials. 2.1. Exterior wall envelope test assemblies shall include not fewer than one opening, one control joint, one wall/eave interface and one wall sill. Tested openings and penetrations shall be representative of the intended end-use configuration. 2.2. Exterior wall envelope test assemblies shall be not less than 4 feet by 8 feet (1219 mm by 2438 mm) in size. 2.3. Exterior wall envelope assemblies shall be tested at a minimum differential pressure of 6.24 pounds per square foot (0.297 kN/m2). 2.4. Exterior wall envelope assemblies shall be subjected to a minimum test exposure duration of 2 hours. 3. Exterior insulation and finish systems (EIFS) complying with Section 1407.4.1.
|  | 1402.4 Fire resistance. | Exterior walls shall be fire-resistance rated as required by other sections of this code with opening protection as required by Chapter 7.
|  | 1402.5 Water-resistive barriers. | Exterior walls on buildings of Type I, II, III or IV construction that are greater than 40 feet (12 192 mm) in height above grade plane and contain a combustible water-resistive barrier shall be tested in accordance with and comply with the acceptance criteria of NFPA 285.Combustibility shall be determined in accordance with Section 703.3. For the purposes of this section, fenestration products, flashing of fenestration products and water-resistive-barrier flashing and accessories at other locations, including through wall flashings, shall not be considered part of the water-resistive barrier. Exceptions: 1. Walls in which the water-resistive barrier is the only combustible component and the exterior wall has a wall covering of brick, concrete, stone, terra cotta, stucco or steel with minimum thicknesses in accordance with Table 1404.2. 2. Walls in which the water-resistive barrier is the only combustible component and the water-resistive barrier complies with the following: 2.1. A peak heat release rate of less than 150 kW/m2, a total heat release of less than 20 MJ/m2 and an effective heat of combustion of less than 18 MJ/kg when tested on specimens at the thickness intended for use, in accordance with ASTM E1354, in the horizontal orientation and at an incident radiant heat flux of 50 kW/m2. 2.2. A flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E84 or UL 723, with test specimen preparation and mounting in accordance with ASTM E2404. |  | See BC14 Tables&Figures
|  | 1403.2 Water-resistive barrier. | Not fewer than one layer of water-resistive barrier material shall be attached to the studs or sheathing, with flashing as described in Section 1404.4, in such a manner as to provide a continuous water-resistive barrier behind the exterior wall veneer.
|  | 1403.8 Plastics. | Plastic panel, apron or spandrel walls as defined in this code shall not be limited in thickness, provided that such plastics and their assemblies conform to the requirements of Chapter 26 and are constructed of approved weather-resistant materials of adequate strength to resist the wind loads for cladding specified in Chapter 16.
|  | 1403.9 Vinyl siding. | Vinyl siding shall be certified and labeled as conforming to the requirements of ASTM D3679 by an approved quality control agency.
|  | 1403.10 Fiber-cement siding. | Fiber-cement siding shall conform to the requirements of ASTM C1186, Type A (or ISO 8336, Category A), and shall be so identified on labeling listing an approved quality control agency.
|  | 1403.11 Exterior insulation and finish systems. | Exterior insulation and finish systems (EIFS) and exterior insulation and finish systems (EIFS) with drainage shall comply with Section 1407.
|  | 1403.12 Polypropylene siding. | Polypropylene siding shall be certified and labeled as conforming to the requirements of ASTM D7254 and those of Section 1403.12.1 or 1403.12.2 by an approved quality control agency. Polypropylene siding shall be installed in accordance with the requirements of Section 1404.18 and in accordance with the manufacturer’s instructions. Polypropylene siding shall be secured to the building so as to provide weather protection for the exterior walls of the building.
|  | 1403.12.1 Flame spread index. | The certification of the flame spread index shall be accompanied by a test report stating that all portions of the test specimen ahead of the flame front remained in position during the test in accordance with ASTM E84 or UL 723.
|  | 1403.12.2 Fire separation distance. | The fire separation distance between a building with polypropylene siding and the adjacent building shall be not less than 10 feet (3048 mm).
|  | 1403.13 Foam plastic insulation. | Foam plastic insulation used in exterior wall covering assemblies shall comply with Chapter 26.
|  | 1403.14 Attachments through insulation. | Exterior wall coverings attached to the building structure through foam plastic insulating sheathing shall comply with the attachment requirements of Section 2603.11, 2603.12, or 2603.13.
|  | 1404.2 Weather protection. | Exterior walls shall provide weather protection for the building. The materials of the minimum nominal thickness specified in Table 1404.2 shall be acceptable as approved weather coverings. |  | See BC14 Tables&Figures
|  | 1404.3 Vapor retarders. | Vapor retarder materials shall be classified in accordance with Table 1404.3(1). A vapor retarder shall be provided on the interior side of frame walls in accordance with Tables 1404.3(2) and 1404.3(3), or an approved design using accepted engineering practice for hygrothermal analysis. The appropriate climate zone shall be selected in accordance with Chapter 3 of the International Energy Conservation Code. |  | See BC14 Tables&Figures
|  | 1404.3.1 Class I and II vapor retarders. | Where a Class II vapor retarder is used in combination with foam plastic insulating sheathing installed as continuous insulation on the exterior side of frame walls, the continuous insulation shall comply with Table 1404.3.1 and the Class II vapor retarder shall have a vapor permeance greater than 1 perm when measured by ASTM E96 water method (Procedure B). Use of a Class I interior vapor retarder in frame walls with a Class I vapor retarder on the exterior side shall require an approved design. Exceptions: 1. Basement walls. 2. Below-grade portion of any wall. 3. Construction where accumulation, condensation or freezing of moisture will not damage the materials. 4. Class I and II vapor retarders with vapor permeance greater than 1 perm when measured by ASTM E96 water method (Procedure B) shall be allowed on the interior side of any frame wall in all climate zones. |  | See BC14 Tables&Figures
|  | 1404.3.2 Class III vapor retarders. | Only Class III vapor retarders shall be used on the interior side of frame walls where foam plastic insulating sheathing with a perm rating of less than 1 is applied in accordance with Table 1404.3(3) on the exterior side of the frame wall. |  | See BC14 Tables&Figures
|  | 1404.3.2.1 Spray foam plastic insulation for moisture control with Class III vapor retarders. | For purposes of compliance with Table 1404.3(3), spray foam with a maximum permeance of 1.5 perms at the installed thickness applied to the interior cavity side of wood structural panels, fiberboard, insulating sheathing or gypsum shall be deemed to meet the continuous insulation R-value requirement where the spray foam R-value meets or exceeds the specified continuous insulation R-value. |  | See BC14 Tables&Figures
|  | 1404.3.2.1.1 Hybrid insulation for moisture control with Class III vapor retarders. | For the purposes of compliance with Table 1404.3(3), the combined R-values of spray foam plastic insulation and continuous insulation shall be permitted to be counted toward the continuous R-value requirement. |  | See BC14 Tables&Figures
|  | 1404.4 Flashing. | Flashing shall be installed in such a manner so as to prevent moisture from entering the wall or to redirect that moisture to the surface of the exterior wall finish or to a water-resistive barrier complying with Section 1403.2 and that is part of a means of drainage complying with Section 1402.2. Flashing shall be installed at the perimeters of exterior door and window assemblies, penetrations and terminations of exterior wall assemblies, exterior wall intersections with roofs, chimneys, porches, decks, balconies and similar projections and at built-in gutters and similar locations where moisture could enter the wall. Flashing with projecting flanges shall be installed on both sides and the ends of copings, under sills and continuously above projecting trim. Where self-adhered membranes are used as flashings of fenestration in wall assemblies, those self-adhered flashings shall comply with AAMA 711. Where fluid applied membranes are used as flashing for exterior wall openings, those fluid applied membrane flashings shall comply with AAMA 714.
|  | 1404.4.1 Exterior wall pockets. | In exterior walls of buildings or structures, wall pockets or crevices in which moisture can accumulate shall be avoided or protected with caps or drips, or other approved means shall be provided to prevent water damage.
|  | 1404.4.2 Masonry. | Flashing and weep holes in anchored veneer designed in accordance with Section 1404.6 shall be located not more than 10 inches (245 mm) above finished ground level above the foundation wall or slab. At other points of support including structural floors, shelf angles and lintels, flashing and weep holes shall be located in the first course of masonry above the support.
|  | 1404.5 Wood veneers. | Wood veneers on exterior walls of buildings of Types I, II, III and IV construction shall be not less than 1 inch (25 mm) nominal thickness, 0.438-inch (11.1 mm) exterior hardboard siding or 0.375-inch (9.5 mm) exterior-type wood structural panels or particleboard and shall conform to the following:
|  | 1404.11.2 Weather protection. | Metal supports for exterior metal veneer shall be protected by painting, galvanizing or by other equivalent coating or treatment. Wood studs, furring strips or other wood supports for exterior metal veneer shall be approved pressure-treated wood or protected as required in Section 1402.2. Joints and edges exposed to the weather shall be caulked with approved durable waterproofing material or by other approved means to prevent penetration of moisture.
|  | 1404.11.3 Backup. | Masonry backup shall not be required for metal veneer unless required by the fire-resistance requirements of this code.
|  | 1404.11.4 Grounding. | Grounding of metal veneers on buildings shall comply with the requirements of Chapter 27 of this code.
|  | 1404.13 Exterior windows and doors. | Windows and doors installed in exterior walls shall conform to the testing and performance requirements of Section 1709.5.
|  | 1404.13.1 Installation. | Windows and doors shall be installed in accordance with approved manufacturer’s instructions. Fastener size and spacing shall be provided in such instructions and shall be calculated based on maximum loads and spacing used in the tests.
|  | 1404.14.1.1 Fasteners and fastener penetration for wood construction. | Unless otherwise specified in the approved manufacturer’s instructions, nails used to fasten the siding and accessories shall be corrosion resistant and have not less than a 0.313-inch (7.9 mm) head diameter and 1/8-inch (3.18 mm) shank diameter. The penetration into nailable substrate shall be not less than 11/4 inches (32 mm).
|  | 1404.14.1.2 Fasteners and fastener penetration for cold-formed steel light-fame construction. | For cold-formed steel light-frame construction, corrosion-resistant fasteners shall be used. Screw fasteners shall penetrate through the steel with not fewer than three exposed threads. Other fasteners shall be installed in accordance with the approved construction documents and manufacturer’s instructions.
|  | 1404.14.1.3 Fastener spacing. | Unless specified otherwise by the approved manufacturer’s instructions, fasteners shall be installed in the middle third of the slots of the nail hem and spacing between fasteners shall be not greater than 16 inches (406 mm) for horizontal siding and 12 inches (305 mm) for vertical siding.
|  | 1405.1 Combustible exterior wall coverings. | Combustible exterior wall coverings shall comply with this section. Exception: Plastics complying with Chapter 26.
|  | 1405.1.1 Types I, II, III and IV construction. | On buildings of Types I, II, III and IV construction, exterior wall coverings shall be permitted to be constructed of combustible materials, complying with the following limitations:
|  | 1405.1.1.1 Ignition resistance. | Where permitted by Section 1405.1.1, combustible exterior wall coverings shall be tested in accordance with NFPA 268. Exceptions: 1. Wood or wood-based products. 2. Other combustible materials covered with an exterior weather covering, other than vinyl sidings, included in and complying with the thickness requirements of Table 1404.2. 3. Aluminum having a minimum thickness of 0.019 inch (0.48 mm). |  | See BC14 Tables&Figures
|  | 1405.1.1.1.1 Fire separation 5 feet or less. | Where installed on exterior walls having a fire separation distance of 5 feet (1524 mm) or less, combustible exterior wall coverings shall not exhibit sustained flaming as defined in NFPA 268.
|  | 1405.1.1.1.2 Fire separation greater than 5 feet. | For fire separation distances greater than 5 feet (1524 mm), any exterior wall covering shall be permitted that has been exposed to a reduced level of incident radiant heat flux in accordance with the NFPA 268 test method without exhibiting sustained flaming. The minimum fire separation distance required for the exterior wall covering shall be determined from Table 1405.1.1.1.2 based on the maximum tolerable level of incident radiant heat flux that does not cause sustained flaming of the exterior wall covering. |  | See BC14 Tables&Figures
|  | 1405.1.2 Location. | Combustible exterior wall coverings located along the top of exterior walls shall be completely backed up by the exterior wall and shall not extend over or above the top of the exterior wall.
|  | 1405.1.3 Fireblocking. | Where the combustible exterior wall covering is furred out from the exterior wall and forms a solid surface, the distance between the back of the exterior wall covering and the exterior wall shall not exceed 15/8 inches (41 mm). The concealed space thereby created shall be fireblocked in accordance with Section 718. Exception: The distance between the back of the exterior wall covering and the exterior wall shall be permitted to exceed 15/8 inches (41 mm) where the concealed space is not required to be fireblocked by Section 718.
|  | 1406.2 Exterior wall covering. | MCM used as exterior wall covering or as elements of balconies and similar projections and bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1406.4 through 1406.13 .
|  | 1406.3 Architectural trim and embellishments. | MCM used as architectural trim or embellishments shall comply with Sections 1406.7 through 1406.13 .
|  | 1406.4 Structural design. | MCM systems shall be designed and constructed to resist wind loads as required by Chapter 16 for components and cladding.
|  | 1406.5 Approval. | Results of approved tests or an engineering analysis shall be submitted to the building official to verify compliance with the requirements of Chapter 16 for wind loads.
|  | 1406.6 Weather resistance. | MCM systems shall comply with Section 1402 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s installation instructions.
|  | 1406.7 Durability. | MCM systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1406 for the duration of use.
|  | 1406.8 Fire-resistance rating. | Where MCM systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the building official that the required fire-resistance rating is maintained. Exception: MCM systems that are part of an exterior wall envelope not containing foam plastic insulation and are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly, shall not be required to comply with this section.
|  | 1406.9 Surface-burning characteristics. | Unless otherwise specified, MCM shall have a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in the maximum thickness intended for use in accordance with ASTM E84 or UL 723.
|  | 1406.10 Types I, II, III and IV construction. | Where installed on buildings of Types I, II, III and IV construction, metal composite material (MCM) shall comply with Sections 1406.10.1 and 1406.10.2 for installations up to 40 feet (12 192 mm) above grade plane. Where installed on buildings of Types I, II, III and IV construction, MCMs and MCM systems shall comply with Sections 1406.10.1 through 1406.10.3, for installations greater than 40 feet (12 192 mm) above grade plane.
|  | 1406.10.1 Surface-burning characteristics. | MCM shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in the maximum thickness intended for use in accordance with ASTM E84 or UL 723.
|  | 1406.10.2 Thermal barriers. | MCM shall be separated from the interior of a building by an approved thermal barrier consisting of 1/2-inch (12.7 mm) gypsum wallboard or material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275.​ Exceptions: 1. The MCM system is specifically approved based on tests conducted in accordance with NFPA 286 and with the acceptance criteria of Section 803.1.1.1, UL 1040 or UL 1715. Such testing shall be performed with the MCM in the maximum thickness intended for use. The MCM system shall include seams, joints and other typical details used in the installation and shall be tested in the manner intended for use. 2. The MCM is used as elements of balconies and similar projections, architectural trim or embellishments.
|  | 1406.10.3 Full-scale tests. | The MCM system shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the MCM system with the MCM in the maximum thickness intended for use.
|  | 1406.11 Type V construction. | MCM shall be permitted to be installed on buildings of Type V construction.
|  | 1406.12 Foam plastic insulation. | Where MCM systems are included in an exterior wall envelope containing foam plastic insulation, the exterior wall envelope shall also comply with the requirements of Section 2603.
|  | 1406.13 Labeling. | MCM shall be labeled in accordance with Section 1703.5.
|  | 1407.2 Performance characteristics. | EIFS shall be constructed such that it meets the performance characteristics required in ASTM E2568.
|  | 1407.4 Weather resistance. | EIFS shall comply with Section 1402 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s application instructions.
|  | 1407.4.1 EIFS with drainage. | EIFS with drainage shall have an average minimum drainage efficiency of 90 percent when tested in accordance the requirements of ASTM E2273 and is required on framed walls of Type V construction, Group R1, R2, R3 and R4 occupancies.
|  | 1407.4.1.1 Water-resistive barrier. | For EIFS with drainage, the water-resistive barrier shall comply with Section 1403.2 or ASTM E2570.
|  | 1407.5 Installation. | Installation of the EIFS and EIFS with drainage shall be in accordance with the EIFS manufacturer’s instructions.
|  | 1407.6 Special inspections. | EIFS installations shall comply with the provisions of Sections 1704.2 and 1705.17 .
|  | 1408.2 Exterior wall covering. | HPL used as exterior wall covering or as elements of balconies and similar projections and bay and oriel windows to provide cladding or weather resistance shall comply with Sections 1408.4 through 1408.14.
|  | 1408.3 Architectural trim and embellishments. | HPL used as architectural trim or embellishments shall comply with Sections 1408.7 through 1408.14.
|  | 1408.5 Approval. | Results of approved tests or an engineering analysis shall be submitted to the building official to verify compliance with the requirements of Chapter 16 for wind loads.
|  | 1408.6 Weather resistance. | HPL systems shall comply with Section 1402 and shall be designed and constructed to resist wind and rain in accordance with this section and the manufacturer’s instructions.
|  | 1408.7 Durability. | HPL systems shall be constructed of approved materials that maintain the performance characteristics required in Section 1408 for the duration of use.
|  | 1408.8 Fire-resistance rating. | Where HPL systems are used on exterior walls required to have a fire-resistance rating in accordance with Section 705, evidence shall be submitted to the building official that the required fire-resistance rating is maintained. Exception: HPL systems not containing foam plastic insulation, which are installed on the outer surface of a fire-resistance-rated exterior wall in a manner such that the attachments do not penetrate through the entire exterior wall assembly, shall not be required to comply with this section.
|  | 1408.9 Surface-burning characteristics. | Unless otherwise specified, HPL shall have a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in the minimum and maximum thicknesses intended for use in accordance with ASTM E84 or UL 723.
|  | 1408.10 Types I, II, III and IV construction. | Where installed on buildings of Types I, II, III and IV construction, HPL systems shall comply with Sections 1408.10.1 through 1408.10.4, or Section 1408.11.
|  | 1408.10.1 Surface-burning characteristics. | HPL shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in the minimum and maximum thicknesses intended for use in accordance with ASTM E84 or UL 723.
|  | 1408.10.2 Thermal barriers. | HPL shall be separated from the interior of a building by an approved thermal barrier consisting of 1/2-inch (12.7 mm) gypsum wallboard or a material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275.
|  | 1408.10.3 Thermal barrier not required. | The thermal barrier specified for HPL in Section 1408.10.2 is not required where:
|  | 1408.10.4 Full-scale tests. | The HPL system shall be tested in accordance with, and comply with, the acceptance criteria of NFPA 285. Such testing shall be performed on the HPL system with the HPL in the minimum and maximum thicknesses intended for use.
|  | 1408.11 Alternate conditions. | HPL and HPL systems shall not be required to comply with Sections 1408.10.1 through 1408.10.4 provided that such systems comply with Section 1408.11.1.
|  | 1408.11.1 Installations up to 40 feet in height. | HPL shall be permitted to be installed up to 40 feet (12 190 mm) in height above grade plane where installed in accordance with Section 1408.11.1.1 or 1408.11.1.2.
|  | 1408.11.1.1 Fire separation distance of 5 feet or less. | Where the fire separation distance is 5 feet (1524 mm) or less, the area of HPL shall not exceed 10 percent of the exterior wall surface.
|  | 1408.11.1.2 Fire separation distance greater than 5 feet. | Where the fire separation distance is greater than 5 feet (1524 mm), the area of exterior wall surface coverage using HPL shall not be limited.
|  | 1408.12 Type V construction. | HPL shall be permitted to be installed on buildings of Type V construction.
|  | 1408.13 Foam plastic insulation. | HPL systems containing foam plastic insulation shall comply with the requirements of Section 2603.
|  | 1408.14 Labeling. | HPL shall be labeled in accordance with Section 1703.5.
|  | 1409.1 Plastic composite decking. | Exterior deck boards, stair treads, handrails and guards constructed of plastic composites, including plastic lumber, shall comply with Section 2612.

## BC15
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1501.1 Scope. | The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies, and rooftop structures. | 1501.1 Scope. | The provisions of this chapter shall govern the design, materials, construction and quality of roof assemblies, and rooftop structures.
|  | 1502.1 General. | Design and installation of roof drainage systems shall comply with this section, Section 1611 of this code and Chapter 11 of the International Plumbing Code.
1503.1 General. | Roof decks shall be covered with approved roof coverings secured to the building or structure in accordance with the provisions of this chapter. Roof coverings shall be designed and installed in accordance with this code and the manufacturer’s instructions such that the roof covering shall serve to protect the building or structure. | 1503.1 General. | Roof decks shall be covered with approved roof coverings secured to the building or structure in accordance with the provisions of this chapter. Roof coverings shall be designed in accordance with this code, and installed in accordance with this code and the manufacturer’s approved instructions.
|  | 1502.2 Secondary (emergency overflow) drains or scuppers. | Where roof drains are required, secondary (emergency overflow) roof drains or scuppers shall be provided where the roof perimeter construction extends above the roof in such a manner that water will be entrapped if the primary drains allow buildup for any reason. The installation and sizing of secondary emergency overflow drains, leaders and conductors shall comply with Section 1611 of this code and Chapter 11 of the International Plumbing Code.
1503.2 Flashing. | Flashing shall be installed in such a manner so as to prevent moisture entering the wall and roof through joints in copings, through moisture-permeable materials and at intersections with parapet walls and other penetrations through the roof plane. | 1503.2 Flashing. | Flashing shall be installed in such a manner so as to prevent water from entering the wall and roof through joints in copings, through moisture-permeable materials and at intersections with parapet walls and other penetrations through the roof plane.
|  | 1502.3 Scuppers. | Where scuppers are used for secondary (emergency overflow) roof drainage, the quantity, size, location and inlet elevation of the scuppers shall be sized to prevent the depth of ponding water from exceeding that for which the roof was designed as determined by Section 1611.1. Scuppers shall not have an opening dimension of less than 4 inches (102 mm). The flow through the primary system shall not be considered when locating and sizing scuppers.
1503.2.1 Locations. | Flashing shall be installed at wall and roof intersections, at gutters, wherever there is a change in roof slope or direction and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness of not less than 0.019 inch (0.483 mm) (No. 26 galvanized sheet). | 1503.2.1 Locations. | Flashing shall be installed at wall and roof intersections, at gutters, wherever there is a change in roof slope or direction and around roof openings. Where flashing is of metal, the metal shall be corrosion resistant with a thickness of not less than 0.019 inch (0.483 mm) (No. 26 galvanized sheet).
|  | 1502.4 Gutters. | Gutters and leaders placed on the outside of buildings, other than Group R-3, private garages and buildings of Type V construction, shall be of noncombustible material or not less than Schedule 40 plastic pipe.
|  | 1503.3 Parapet walls. | Parapet walls shall be coped or covered in accordance with Sections 1503.3.1 and 1503.3.2. The top surface of the parapet wall shall provide positive drainage.
|  | 1503.3.1 Fire-resistance-rated parapet walls. | Parapet walls required by Section 705.11 shall be coped or covered with weatherproof materials of a width not less than the thickness of the parapet wall such that the fire-resistance rating of the wall is not decreased.
|  | 1503.3.2 Other parapet walls. | Parapet walls meeting one of the exceptions in Section 705.11 shall be coped or covered with weatherproof materials of a width not less than the thickness of the parapet wall.
1504.1 Wind resistance of roofs. | Roof decks and roof coverings shall be designed for wind loads in accordance with Chapter 16 and Sections 1504.2, 1504.3 and 1504.4. | 1504.1 Wind resistance of roofs. | Roof decks and roof coverings shall be designed for wind loads in accordance with Chapter 16 and Sections 1504.2, 1504.3, 1504.4 and 1504.5
|  | 1503.4 Attic and rafter ventilation. | Intake and exhaust vents shall be provided in accordance with Section 1202.2 and the vent product manufacturer’s installation instructions.
|  | 1503.5 Crickets and saddles. | A cricket or saddle shall be installed on the ridge side of any chimney or penetration greater than 30 inches (762 mm) wide as measured perpendicular to the slope. Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering. Exception: Unit skylights installed in accordance with Section 2405.5 and flashed in accordance with the manufacturer’s instructions shall be permitted to be installed without a cricket or saddle.
|  | 1504.2 Wind resistance of asphalt shingles. | Asphalt shingles shall be tested in accordance with ASTM D7158. Asphalt shingles shall meet the classification requirements of Table 1504.2 for the appropriate maximum basic wind speed. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D7158 and the required classification in Table 1504.2. Exception: Asphalt shingles not included in the scope of ASTM D7158 shall be tested and labeled in accordance with ASTM D3161. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D3161 and the required classification in Table 1504.2. |  | See BC15 Tables&Figures
|  | 1504.3 Wind resistance of clay and concrete tile. | Wind loads on clay and concrete tile roof coverings shall be in accordance with Section 1609.5.
|  | 1504.3.1 Testing. | Testing of concrete and clay roof tiles shall be in accordance with Sections 1504.3.1.1, 1504.3.1.2 and 1504.3.1.3.
|  | 1504.3.1.1 Overturning resistance. | Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with Chapter 15 and either SBCCI SSTD 11 or ASTM C1568.
|  | 1504.3.1.2 Wind tunnel testing. | Where concrete and clay roof tiles do not satisfy the limitations in Chapter 16 for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with ​Chapter 15​ and either SBCCI SSTD 11 or ASTM C1569.
|  | 1504.3.1.3 Air permeability testing. | The lift coefficient for concrete and clay tile shall be 0.2 or shall be determined in accordance with SBCCI SSTD 11 or ASTM C1570.
|  | 1504.4 Wind resistance of nonballasted roofs. | Roof coverings installed on roofs in accordance with Section 1507 that are mechanically attached or adhered to the roof deck shall be designed to resist the design wind load pressures for components and cladding in accordance with Section 1609.5.2. The wind load on the roof covering shall be permitted to be determined using allowable stress design.
|  | 1504.4.1 Other roof systems. | Built-up, modified bitumen, fully adhered or mechanically attached single-ply roof systems, metal panel roof systems applied to a solid or closely fitted deck and other types of membrane roof coverings shall be tested in accordance with FM 4474, UL 580 or UL 1897.
|  | 1504.4.2 Structural metal panel roof systems. | Where the metal roof panel functions as the roof deck and roof covering and it provides both weather protection and support for loads, the structural metal panel roof system shall comply with this section. Structural standing-seam metal panel roof systems shall be tested in accordance with ASTM E1592 or FM 4474. Structural through-fastened metal panel roof systems shall be tested in accordance with ASTM E1592, FM 4474 or UL 580. Exceptions: 1. Metal roofs constructed of cold-formed steel shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2210.1. 2. Metal roofs constructed of aluminum shall be permitted to be designed and tested in accordance with the applicable referenced structural design standard in Section 2002.1.
|  | 1504.4.3 Metal roof shingles. | Metal roof shingles applied to a solid or closely fitted deck shall be tested in accordance with ASTM D3161, FM 4474, UL 580 or UL 1897. Metal roof shingles tested in accordance with ASTM D3161 shall meet the classification requirements of Table 1504.2 for the appropriate maximum basic wind speed and the metal shingle packaging shall bear a label to indicate compliance with ASTM D3161 and the required classification in Table 1504.2. |  | See BC15 Tables&Figures
|  | 1504.5 Ballasted low-slope single-ply roof systems. | Ballasted low-slope (roof slope < 2:12) single-ply roof system coverings installed in accordance with Section 1507.12 shall be designed in accordance with ANSI/SPRI RP-4.
|  | 1504.6 Edge systems for low-slope roofs. | Metal edge systems, except gutters and counterflashing, installed on built-up, modified bitumen and single-ply roof systems having a slope less than 2 units vertical in 12 units horizontal (2:12) shall be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance in accordance with Test Methods RE-1, RE-2 and RE-3 of ANSI/SPRI ES-1, except basic design wind speed, V, shall be determined from Figures 1609.3(1) through 1609.3(12) as applicable.
1505.1 General. | Roof assemblies shall be divided into the classes defined below. Class A, B and C roof assemblies and roof coverings required to be listed by this section shall be tested in accordance with ASTM E 108 or UL 790. In addition, fire-retardant-treated wood roof coverings shall be tested in accordance with ASTM D 2898. The minimum roof coverings installed on buildings shall comply with Table 1505.1 of this code based on the type of construction of the building. Exception: Skylights and sloped glazing that comply with Chapter 24 or Section 2610 of this code. | 1505.1 General. | Roof assemblies shall be divided into the classes defined in this section. Class A, B and C roof assemblies and roof coverings required to be listed by this section shall be tested in accordance with ASTM E108 or UL 790. In addition, fire-retardant-treated wood roof coverings shall be tested in accordance with ASTM D2898. The minimum roof coverings installed on buildings shall comply with Table 1505.1 based on the type of construction of the building. Exception: Skylights and sloped glazing that comply with Chapter 24 or Section 2610. |  | See BC15 Tables&Figures
|  | 1504.6.1 Gutter securement for low-slope roofs. | Gutters that are used to secure the perimeter edge of the roof membrane on low-slope (less than 2:12 slope) built-up, modified bitumen, and single-ply roofs, shall be designed, constructed and installed to resist wind loads in accordance with Section 1609 and shall be tested in accordance with Test Methods G-1 and G-2 of SPRI GT-1.
1505.2 Class A roof assemblies. | Class A roof assemblies are those that are effective against severe fire test exposure. Class A roof assemblies and roof coverings shall be listed and identified as Class A by an approved testing agency. Class A roof assemblies shall be permitted for use in buildings or structures of all types of construction. Exceptions: 1. Class A roof assemblies include those with coverings of brick, masonry, or an exposed concrete roof deck. 2. Class A roof assemblies also include ferrous or copper shingles or sheets, metal sheets and shingles, clay or concrete roof tile or slate installed on noncombustible decks or ferrous, copper or metal sheets installed without a roof deck on noncombustible framing. 3. Class A roof assemblies include minimum 16 ounce per square foot (0.0416 kg/m2) copper sheets installed over combustible decks. 4. Class A roof assemblies include slate installed over ASTM D 226, Type II underlayment over combustible decks. | 1505.2 Class A roof assemblies. | Class A roof assemblies are those that are effective against severe fire test exposure. Class A roof assemblies and roof coverings shall be listed and identified as Class A by an approved testing agency. Class A roof assemblies shall be permitted for use in buildings or structures of all types of construction. Exceptions: 1. Class A roof assemblies include those with coverings of brick, masonry or an exposed concrete roof deck. 2. Class A roof assemblies also include ferrous or copper shingles or sheets, metal sheets and shingles, clay or concrete roof tile or slate installed on noncombustible decks or ferrous, copper or metal sheets installed without a roof deck on noncombustible framing. 3. Class A roof assemblies include minimum 16 ounce per square foot (0.0416 kg/m2) copper sheets installed over combustible decks. 4. Class A roof assemblies include slate installed over ASTM D226, Type II underlayment over combustible decks.
|  | 1504.7 Physical properties. | Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall demonstrate physical integrity over the working life of the roof based on 2,000 hours of exposure to accelerated weathering tests conducted in accordance with ASTM G152, ASTM G154 or ASTM G155. Those roof coverings that are subject to cyclical flexural response due to wind loads shall not demonstrate any significant loss of tensile strength for unreinforced membranes or breaking strength for reinforced membranes when tested as herein required.
1505.3 Class B roof assemblies. | Class B roof assemblies are those that are effective against moderate fire-test exposure. Class B roof assemblies and roof coverings shall be listed and identified as Class B by an approved testing agency. | 1505.3 Class B roof assemblies. | Class B roof assemblies are those that are effective against moderate fire-test exposure. Class B roof assemblies and roof coverings shall be listed and identified as Class B by an approved testing agency.
|  | 1504.8 Impact resistance. | Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall resist impact damage based on the results of tests conducted in accordance with ASTM D3746, ASTM D4272 or the “Resistance to Foot Traffic Test” in FM 4470.
1505.4 Class C roof assemblies. | Class C roof assemblies are those that are effective against light fire-test exposure. Class C roof assemblies and roof coverings shall be listed and identified as Class C by an approved testing agency. | 1505.4 Class C roof assemblies. | Class C roof assemblies are those that are effective against light fire-test exposure. Class C roof assemblies and roof coverings shall be listed and identified as Class C by an approved testing agency.
|  | 1504.9 Wind resistance of aggregate-surfaced roofs. | Parapets shall be provided for aggregate surfaced roofs and shall comply with Table 1504.9. |  | See BC15 Tables&Figures
1505.6 Fire-retardant-treated wood shingles and shakes. | Fire-retardant-treated wood shakes and shingles shall be treated by impregnation with chemicals by the full-cell vacuum-pressure process, in accordance with AWPA C1. Each bundle shall be marked to identify the manufactured unit and the manufacturer, and shall also be labeled to identify the classification of the material in accordance with the testing required in Section 1505.1, the treating company and the quality control agency. | 1505.6 Fire-retardant-treated wood shingles and shakes. | Fire-retardant-treated wood shakes and shingles shall be treated by impregnation with chemicals by the full-cell vacuum-pressure process, in accordance with AWPA C1. Each bundle shall be marked to identify the manufactured unit and the manufacturer, and shall be labeled to identify the classification of the material in accordance with the testing required in Section 1505.1, the treating company and the quality control agency.
1505.7 Special purpose roofs. | Special purpose wood shingle or wood shake roofing shall conform to the grading and application requirements of Section 1507.8 or Section 1507.9. In addition, an underlayment of ⅝-inch (15.9 mm) Type X water-resistant gypsum backing board or gypsum sheathing shall be placed under minimum nominal ½-inch (12.7 mm) thick wood structural panel solid sheathing or 1-inch (25.4 mm) nominal spaced sheathing. | 1505.7 Special purpose roofs. | Special purpose wood shingle or wood shake roofing shall conform to the grading and application requirements of Section 1507.8 or 1507.9. In addition, an underlayment of 5/8-inch (15.9 mm) Type X water-resistant gypsum backing board or gypsum sheathing shall be placed under minimum nominal 1/2-inch-thick (12.7 mm) wood structural panel solid sheathing or 1-inch (25 mm) nominal spaced sheathing.
|  | 1505.5 Nonclassified roofing. | Nonclassified roofing is approved material that is not listed as a Class A, B or C roof covering.
1506.1 Scope. | The requirements set forth in this section shall apply to the application of roof-covering materials specified herein. Roof coverings shall be applied in accordance with this chapter and the manufacturer’s instructions. Installation of roof coverings shall comply with the applicable provisions of Section 1507. | 1506.1 Scope. | The requirements set forth in this section shall apply to the application of roof-covering materials specified herein. Roof coverings shall be applied in accordance with this chapter and the roof covering listing as required by Section 1505. Installation of roof coverings shall comply with the applicable provisions of Section 1507.
1506.2 Material specifications and physical characteristics. | Roof-covering materials shall conform to the applicable standards listed in this chapter. In the absence of applicable standards or where materials are of questionable suitability, testing by an approved agency shall be required by the commissioner to determine the character, quality and limitations of application of the materials. | 1506.2 Material specifications and physical characteristics. | Roof-covering materials shall conform to the applicable standards listed in this chapter.
|  | 1505.8 Building-integrated photovoltaic (BIPV) products. | BIPV products installed as the roof covering shall be tested, listed and labeled for fire classification in accordance with Section 1505.1.
1506.3 Product identification. | Roof-covering materials shall be delivered in packages bearing the manufacturer’s identifying marks and approved testing agency labels required in accordance with Section 1505. Bulk shipments of materials shall be accompanied with the same information issued in the form of a certificate or on a bill of lading by the manufacturer. | 1506.3 Product identification. | Roof-covering materials shall be delivered in packages bearing the manufacturer’s identifying marks and approved testing agency labels required in accordance with Section 1505. Bulk shipments of materials shall be accompanied with the same information issued in the form of a certificate or on a bill of lading by the manufacturer.
|  | 1505.9 Rooftop mounted photovoltaic (PV) panel systems. | Rooftop mounted photovoltaic (PV) panel systems shall be tested, listed and identified with a fire classification in accordance with UL 2703. Listed systems shall be installed in accordance with the manufacturer’s installation instructions and their listing. The fire classification shall comply with Table 1505.1 based on the type of construction of the building. |  | See BC15 Tables&Figures
1507.1 Scope. | Roof coverings shall be applied in accordance with the applicable provisions of this section and the manufacturer’s instructions. | 1507.1 Scope. | Roof coverings shall be applied in accordance with the applicable provisions of this section and the manufacturer’s installation instructions.
|  | 1505.10 Landscaped roofs. | Landscaped roofs shall comply with Sections 1505.1 and 1507.15 and shall be installed in accordance with ANSI/SPRI VF-1.
1507.2 Asphalt shingles. | The installation of asphalt shingles shall comply with the provisions of this section. | 1507.2 Asphalt shingles. | The installation of asphalt shingles shall comply with the provisions of this section.
1507.2.1 Deck requirements. | Asphalt shingles shall be fastened to solidly sheathed decks. | 1507.2.1 Deck requirements. | Asphalt shingles shall be fastened to solidly sheathed decks.
1507.2.2 Slope. | Asphalt shingles shall only be used on roof slopes of two units vertical in 12 units horizontal (17-percent slope) or greater. For roof slopes from two units vertical in 12 units horizontal (17-percent slope) up to four units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.2.8. | 1507.2.2 Slope. | Asphalt shingles shall only be used on roof slopes of 2 units vertical in 12 units horizontal (17-percent slope) or greater. For roof slopes from 2 units vertical in 12 units horizontal (17-percent slope) up to 4 units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.2.8.
1507.2.3 Underlayment. | Unless otherwise noted, required underlayment shall conform to ASTM D 226, Type I, ASTM D 4869, Type I, or ASTM D 6757. | 1507.2.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
|  | 1507.1.1 Underlayment. | Underlayment for asphalt shingles, clay and concrete tile, metal roof shingles, mineral-surfaced roll roofing, slate and slate-type shingles, wood shingles, wood shakes, metal roof panels and photovoltaic shingles shall conform to the applicable standards listed in this chapter. Underlayment materials required to comply with ASTM D226, D1970, D4869 and D6757 shall bear a label indicating compliance with the standard designation and, if applicable, type classification indicated in Table 1507.1.1(1). Underlayment shall be applied in accordance with Table 1507.1.1(2). Underlayment shall be attached in accordance with Table 1507.1.1(3). Exceptions: 1. As an alternative, a minimum 4-inch-wide (102 mm) strip of self-adhering polymer modified bitumen membrane complying with ASTM D1970 and installed in accordance with the manufacturer’s installation instructions for the deck material shall be applied over all joints in the roof decking. An approved underlayment for the applicable roof covering for design wind speeds less than 120 mph (54 m/s) shall be applied over the 4-inch-wide (102 mm) membrane strips. 2. As an alternative, two layers of underlayment complying with ASTM D226 Type II or ASTM D4869 Type IV shall be permitted to be installed as follows: Apply a 19-inch (483 mm) strip of underlayment parallel with the eave. Starting at the eave, apply 36-inch-wide (914 mm) strips of underlayment felt, overlapping successive sheets 19 inches (483 mm). The underlayment shall be attached with corrosion-resistant fasteners in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at side and end laps. End laps shall be 4 inches (102 mm) and shall be offset by 6 feet (1829 mm). Underlayment shall be attached using metal or plastic cap nails with a nominal cap diameter of not less than 1 inch (25.4 mm). Metal caps shall have a thickness of not less than 32-gage sheet metal. Power-driven metal caps shall have a thickness of not less than 0.010 inch (0.254 mm). Thickness of the outside edge of plastic caps shall be not less than 0.035 inch (0.89 mm). The cap nail shank shall be not less than 0.083 inch (2.1 mm) for ring shank cap nails and 0.091 inch (2.3 mm) for smooth shank cap nails. The cap nail shank shall have a length sufficient to penetrate through the roof sheathing or not less than 3/4 inch (19.1 mm) into the roof sheathing. 3. Structural metal panels that do not require a substrate or underlayment. |  | See BC15 Tables&Figures
|  | 1507.1.2 Ice barriers. | In areas where there has been a history of ice forming along the eaves causing a backup of water, an ice barrier shall be installed for asphalt shingles, metal roof shingles, mineral-surfaced roll roofing, slate and slate-type shingles, wood shingles, and wood shakes. The ice barrier shall consist of not less than two layers of underlayment cemented together, or a self-adhering polymer modified bitumen sheet shall be used in place of normal underlayment and extend from the lowest edges of all roof surfaces to a point not less than 24 inches (610 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that do not contain conditioned floor area.
|  | 1507.2.4 Asphalt shingles. | Asphalt shingles shall comply with ASTM D3462.
|  | 1507.2.5 Fasteners. | Fasteners for asphalt shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum 12-gage shank with a minimum 3/8-inch-diameter (9.5 mm) head, of a length to penetrate through the roofing materials and not less than 3/4 inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than 3/4 inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F1667.
|  | 1507.2.6 Attachment. | Asphalt shingles shall have the minimum number of fasteners required by the manufacturer, but not less than four fasteners per strip shingle or two fasteners per individual shingle. Where the roof slope exceeds 21 units vertical in 12 units horizontal (21:12), shingles shall be installed as required by the manufacturer.
|  | 1507.2.7 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.3 Clay and concrete tile. | The installation of clay and concrete tile shall comply with the provisions of this section. | 1507.3 Clay and concrete tile. | The installation of clay and concrete tile shall comply with the provisions of this section.
|  | 1507.2.8 Flashings. | Flashing for asphalt shingles shall comply with this section. Flashing shall be applied in accordance with this section and the asphalt shingle manufacturer’s printed instructions.
1507.3.1 Deck requirements. | Concrete and clay tile shall be installed only over solid sheathing or spaced structural sheathing boards. | 1507.3.1 Deck requirements. | Concrete and clay tile shall be installed only over solid sheathing. Exception: Spaced lumber sheathing shall be permitted in Seismic Design Categories A, B and C.
|  | 1507.2.8.1 Base and cap flashing. | Base and cap flashing shall be installed in accordance with the manufacturer’s instructions. Base flashing shall be of either corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness or mineral-surfaced roll roofing weighing not less than 77 pounds per 100 square feet (3.76 kg/m2). Cap flashing shall be corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness.
1507.3.2 Deck slope. | Clay and concrete roof tile shall be installed on roof slopes of 2½ units vertical in 12 units horizontal (21-percent slope) or greater. For roof slopes from 2½ units vertical in 12 units horizontal (21-percent slope) to four units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.3.3. | 1507.3.2 Deck slope. | Clay and concrete roof tile shall be installed on roof slopes of 21/2 units vertical in 12 units horizontal (21-percent slope) or greater. For roof slopes from 21/2 units vertical in 12 units horizontal (21-percent slope) to 4 units vertical in 12 units horizontal (33-percent slope), double underlayment application is required in accordance with Section 1507.3.3.
|  | 1507.2.8.2 Valleys. | Valley linings shall be installed in accordance with the manufacturer’s instructions before applying shingles. Valley linings of the following types shall be permitted:
1507.3.3 Underlayment. | Unless otherwise noted, required underlayment shall conform to: ASTM D 226, Type II; ASTM D 2626 or ASTM D 6380, Class M mineral-surfaced roll roofing. | 1507.3.3 Underlayment. | Unless otherwise noted, required underlayment shall conform to: ASTM D226, Type II; ASTM D2626 or ASTM D6380, Class M mineral-surfaced roll roofing.
|  | 1507.2.8.3 Drip edge. | A drip edge shall be provided at eaves and rake edges of shingle roofs. Adjacent segments of the drip edge shall be lapped not less than 2 inches (51 mm). The vertical leg of drip edges shall be not less than 11/2 inches (38 mm) in width and shall extend not less than 1/4 inch (6.4 mm) below sheathing. The drip edge shall extend back on the roof not less than 2 inches (51 mm). Underlayment shall be installed over drip edges along eaves. Drip edges shall be installed over underlayment along rake edges. Drip edges shall be mechanically fastened at intervals not greater than 12 inches (305 mm) on center.
1507.3.4 Clay tile. | Clay roof tile shall comply with ASTM C 1167. | 1507.3.4 Clay tile. | Clay roof tile shall comply with ASTM C1167.
1507.3.5 Concrete tile. | Concrete roof tile shall comply with ASTM C 1492. | 1507.3.5 Concrete tile. | Concrete roof tile shall comply with ASTM C1492.
1507.3.6 Fasteners. | Tile fasteners shall be corrosion resistant and not less than 11 gage, 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck a minimum of ¾ inch (19.1 mm) or through the thickness of the deck, whichever is less. Attaching wire for clay or concrete tile shall be not less than 0.083 inch (2.1 mm). Perimeter fastening areas include three tile courses but not less than 36 inches (914.4 mm) from either side of hips or ridges and edges of eaves and gable rakes. | 1507.3.6 Fasteners. | Tile fasteners shall be corrosion resistant and not less than 11-gage, , 5/16-inch (8.0 mm) head, and of sufficient length to penetrate the deck not less than 3/4 inch (19.1 mm) or through the thickness of the deck, whichever is less. Attaching wire for clay or concrete tile shall not be smaller than 0.083 inch (2.1 mm). Perimeter fastening areas include three tile courses but not less than 36 inches (914 mm) from either side of hips or ridges and edges of eaves and gable rakes.
1507.3.7 Attachment. | Clay and concrete roof tiles shall be fastened in accordance with Table 1507.3.7. | 1507.3.7 Attachment. | Clay and concrete roof tiles shall be fastened in accordance with Table 1507.3.7. |  | See BC15 Tables&Figures
1507.3.8 Application. | Tile shall be applied according to the manufacturer’s instructions, based on the following: | 1507.3.8 Application. | Tile shall be applied according to the manufacturer’s installation instructions, based on the following:
1507.3.9 Flashing. | At the juncture of the roof vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s instructions, and where of metal, shall not be less than 0.019-inch (0.483 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25.4 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (101.6 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch (914.4 mm) wide underlayment of either one layer of Type I underlayment running the full length of the valley, or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment or a self-adhering polymer modified bitumen sheet shall be installed. | 1507.3.9 Flashing. | At the juncture of the roof vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall be not less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend not less than 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley, or a self-adhering polymer-modified bitumen sheet bearing a label indicating compliance with ASTM D1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solid cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed.
1507.4 Metal roof panels. | The installation of metal roof panels shall comply with the provisions of this section. | 1507.4 Metal roof panels. | The installation of metal roof panels shall comply with the provisions of this section.
1507.4.1 Deck requirements. | Metal roof panel roof coverings shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced supports. | 1507.4.1 Deck requirements. | Metal roof panel roof coverings shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced supports.
1507.4.2 Deck slope. | The minimum slope for metal roof panels shall comply with the following: | 1507.4.2 Deck slope. | Minimum slopes for metal roof panels shall comply with the following:
1507.4.3 Material standards. | Metal-sheet roof covering systems that incorporate supporting structural members shall be designed in accordance with Chapter 22. Metal-sheet roof coverings installed over structural decking shall comply with Table 1507.4.3(1). The materials used for metal-sheet roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses shown in Table 1507.4.3(2). | 1507.4.3 Material standards. | Metal-sheet roof covering systems that incorporate supporting structural members shall be designed in accordance with Chapter 22. Metal-sheet roof coverings installed over structural decking shall comply with Table 1507.4.3(1). The materials used for metal-sheet roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses shown in Table 1507.4.3(2). |  | See BC15 Tables&Figures
1507.4.4 Attachment. | Metal roof panels shall be secured to the supports in accordance with the approved manufacturer’s fasteners. In the absence of manufacturer recommendations, the following fasteners shall be used: | 1507.4.4 Attachment. | Metal roof panels shall be secured to the supports in accordance with the approved manufacturer’s fasteners. In the absence of manufacturer recommendations, the following fasteners shall be used:
1507.5 Metal roof shingles. | The installation of metal roof shingles shall comply with the provisions of this section. | 1507.5 Metal roof shingles. | The installation of metal roof shingles shall comply with the provisions of this section.
1507.5.1 Deck requirements. | Metal roof shingles shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced sheathing. | 1507.5.1 Deck requirements. | Metal roof shingles shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied to spaced sheathing.
1507.5.2 Deck slope. | Metal roof shingles shall not be installed on roof slopes below three units vertical in 12 units horizontal (25-percent slope). | 1507.5.2 Deck slope. | Metal roof shingles shall not be installed on roof slopes below three units vertical in 12 units horizontal (25-percent slope).
|  | 1507.4.5 Underlayment and high wind. | Underlayment shall comply with Section 1507.1.1.
1507.5.3 Underlayment. | Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869. | 1507.5.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.5.4 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.5.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.5.5 Material standards. | Metal roof shingle roof coverings shall comply with Table 1507.4.3(1). The materials used for metal-roof shingle roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses specified in the standards listed in Table 1507.4.3(2). | 1507.5.5 Material standards. | Metal roof shingle roof coverings shall comply with Table 1507.4.3(1). The materials used for metal-roof shingle roof coverings shall be naturally corrosion resistant or provided with corrosion resistance in accordance with the standards and minimum thicknesses specified in the standards listed in Table 1507.4.3(2). |  | See BC15 Tables&Figures
1507.5.6 Attachment. | Metal roof shingles shall be secured to the roof in accordance with the manufacturer’s instructions. | 1507.5.6 Attachment. | Metal roof shingles shall be secured to the roof in accordance with the approved manufacturer’s installation instructions.
1507.5.7 Flashing. | Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend at least 8 inches (203.2 mm) from the centerline each way and shall have a splash diverter rib not less than ¾ inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (101.6 mm). The metal valley flashing shall have a 36-inch (914.4 mm) wide underlayment directly under it consisting of either one layer of underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to underlayment required for metal roof shingles. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment) or a self-adhering polymer modified bitumen sheet shall be installed. | 1507.5.7 Flashing. | Roof valley flashing shall be of corrosion-resistant metal of the same material as the roof covering or shall comply with the standards in Table 1507.4.3(1). The valley flashing shall extend not less than 8 inches (203 mm) from the centerline each way and shall have a splash diverter rib not less than 3/4 inch (19.1 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing shall have a 36-inch-wide (914 mm) underlayment directly under it consisting of either one layer of underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet bearing a label indicating compliance with ASTM D1970, in addition to underlayment required for metal roof shingles. The metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for roof slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed. |  | See BC15 Tables&Figures
1507.6 Mineral-surfaced roll roofing. | The installation of mineral-surfaced roll roofing shall comply with this section. | 1507.6 Mineral-surfaced roll roofing. | The installation of mineral-surfaced roll roofing shall comply with this section.
1507.6.1 Deck requirements. | Mineral-surfaced roll roofing shall be fastened to solidly sheathed roofs. | 1507.6.1 Deck requirements. | Mineral-surfaced roll roofing shall be fastened to solidly sheathed roofs.
1507.6.2 Deck slope. | Mineral-surfaced roll roofing shall not be applied on roof slopes below one unit vertical in 12 units horizontal (8-percent slope). | 1507.6.2 Deck slope. | Mineral-surfaced roll roofing shall not be applied on roof slopes below one unit vertical in 12 units horizontal (8-percent slope).
1507.6.3 Underlayment. | Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869. | 1507.6.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.6.4 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.6.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.6.5 Material standards. | Mineral-surfaced roll roofing shall conform to ASTM D 3909 or ASTM D 6380. | 1507.6.5 Material standards. | Mineral-surfaced roll roofing shall conform to ASTM D3909 or ASTM D6380.
1507.7 Slate shingles. | The installation of slate shingles shall comply with the provisions of this section. | 1507.7 Slate shingles. | The installation of slate shingles shall comply with the provisions of this section.
1507.7.1 Deck requirements. | Slate shingles shall be fastened to solidly sheathed roofs. | 1507.7.1 Deck requirements. | Slate shingles shall be fastened to solidly sheathed roofs.
1507.7.2 Deck slope. | Slate shingles shall only be used on slopes of four units vertical in 12 units horizontal (4:12) or greater. | 1507.7.2 Deck slope. | Slate shingles shall only be used on slopes of four units vertical in 12 units horizontal (4:12) or greater.
1507.7.3 Underlayment. | Underlayment shall comply with ASTM D 226, Type II or ASTM D 4869, Type III or IV. | 1507.7.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.7.4 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet, shall extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.7.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.7.5 Material standards. | Slate shingles shall comply with ASTM C 406. | 1507.7.5 Material standards. | Slate shingles shall comply with ASTM C406.
1507.7.6 Application. | Minimum headlap for slate shingles shall be in accordance with Table 1507.7.6. Slate shingles shall be secured to the roof with two fasteners per slate. | 1507.7.6 Application. | Minimum headlap for slate shingles shall be in accordance with Table 1507.7.6. Slate shingles shall be secured to the roof with two fasteners per slate. |  | See BC15 Tables&Figures
1507.7.7 Flashing. | Flashing and counterflashing shall be made with sheet metal. Valley flashing shall be a minimum of 15 inches (381 mm) wide. Valley and flashing metal shall be a minimum uncoated thickness of 0.0179-inch (0.455 mm) zinc-coated G90. Chimneys, stucco or brick walls shall have a minimum of two plies of felt for a cap flashing consisting of a 4-inch (101.6 mm) wide strip of felt set in plastic cement and extending 1 inch (25.4 mm) above the first felt and a top coating of plastic cement. The felt shall extend over the base flashing 2 inches (50.8 mm). | 1507.7.7 Flashing. | Flashing and counterflashing shall be made with sheet metal. Valley flashing shall be not less than 15 inches (381 mm) wide. Valley and flashing metal shall be a minimum uncoated thickness of 0.0179-inch (0.455 mm) zinc-coated G90. Chimneys, stucco or brick walls shall have not fewer than two plies of felt for a cap flashing consisting of a 4-inch-wide (102 mm) strip of felt set in plastic cement and extending 1 inch (25 mm) above the first felt and a top coating of plastic cement. The felt shall extend over the base flashing 2 inches (51 mm).
1507.8 Wood shingles. | The installation of wood shingles shall comply with the provisions of this section and Table 1507.8. | 1507.8 Wood shingles. | The installation of wood shingles shall comply with the provisions of this section and Table 1507.8. |  | See BC15 Tables&Figures
1507.8.1 Deck requirements. | Wood shingles shall be installed on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1-inch by 4-inch (25.4 mm by 101.6 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. | 1507.8.1 Deck requirements. | Wood shingles shall be installed on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners.
1507.8.1.1 Solid sheathing required. | Solid sheathing is required. | 1507.8.1.1 Solid sheathing required. | Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water.
1507.8.2 Deck slope. | Wood shingles shall be installed on slopes of not less than three units vertical in 12 units horizontal (25-percent slope). | 1507.8.2 Deck slope. | Wood shingles shall be installed on slopes of not less than three units vertical in 12 units horizontal (25-percent slope).
1507.8.3 Underlayment. | Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869. | 1507.8.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.8.4 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.8.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.8.5 Material standards. | Wood shingles shall be of naturally durable wood and comply with the requirements of Table 1507.8.5. | 1507.8.5 Material standards. | Wood shingles shall be of naturally durable wood and comply with the requirements of Table 1507.8.5. |  | See BC15 Tables&Figures
1507.8.6 Attachment. | Fasteners for wood shingles shall be corrosion resistant with a minimum penetration of ¾ inch (19.1 mm) into the sheathing. For sheathing less than ½ inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shingle shall be attached with a minimum of two fasteners. | 1507.8.6 Attachment. | Fasteners for wood shingles shall be corrosion resistant with a minimum penetration of 3/4 inch (19.1 mm) into the sheathing. For sheathing less than 1/2 inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shingle shall be attached with not fewer than two fasteners.
1507.8.7 Application. | Wood shingles shall be laid with a side lap not less than 1½ inches (38.1 mm) between joints in adjacent courses, and not be in direct alignment in alternate courses. Spacing between shingles shall be ¼ to ⅜ inches (6.4 to 9.5 mm). Weather exposure for wood shingles shall not exceed that set in Table 1507.8.7. | 1507.8.7 Application. | Wood shingles shall be laid with a side lap not less than 11/2 inches (38 mm) between joints in adjacent courses, and not be in direct alignment in alternate courses. Spacing between shingles shall be 1/4 to 3/8 inch (6.4 to 9.5 mm). Weather exposure for wood shingles shall not exceed that set in Table 1507.8.7. |  | See BC15 Tables&Figures
1507.8.8 Flashing. | At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s instructions, and where of metal, shall be not less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25.4 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (101.6 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch (914.4 mm) wide underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope), the metal valley flashing underlayment shall be solid cemented to the roofing underlayment or a self-adhering polymer modified bitumen sheet shall be installed. | 1507.8.8 Flashing. | At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall be not less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend not less than 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet bearing a label indicating compliance with ASTM D1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed.
1507.9 Wood shakes. | The installation of wood shakes shall comply with the provisions of this section and Table 1507.8. | 1507.9 Wood shakes. | The installation of wood shakes shall comply with the provisions of this section and Table 1507.8. |  | See BC15 Tables&Figures
1507.9.1 Deck requirements. | Wood shakes shall only be used on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1-inch by 4-inch (25.4 mm by 101.6 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. Where 1-inch by 4-inch (25.4 mm by 101.6 mm) spaced sheathing is installed at 10 inches (254 mm) on center, additional 1-inch by 4-inch (25.4 mm by 101.6 mm) boards shall be installed between the sheathing boards. | 1507.9.1 Deck requirements. | Wood shakes shall only be used on solid or spaced sheathing. Where spaced sheathing is used, sheathing boards shall be not less than 1-inch by 4-inch (25 mm by 102 mm) nominal dimensions and shall be spaced on centers equal to the weather exposure to coincide with the placement of fasteners. Where 1-inch by 4-inch (25 mm by 102 mm) spaced sheathing is installed at 10 inches (254 mm) on center, additional 1-inch by 4-inch (25 mm by 102 mm) boards shall be installed between the sheathing boards.
1507.9.1.1 Solid sheathing required. | Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water. | 1507.9.1.1 Solid sheathing required. | Solid sheathing is required in areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water.
1507.9.2 Deck slope. | Wood shakes shall only be used on slopes of not less than four units vertical in 12 units horizontal (33-percent slope). | 1507.9.2 Deck slope. | Wood shakes shall only be used on slopes of not less than 4 units vertical in 12 units horizontal (33-percent slope).
|  | 1507.8.9 Label required. | Each bundle of shingles shall be identified by a label of an approved grading or inspection bureau or agency.
1507.9.3 Underlayment. | Underlayment shall comply with ASTM D 226, Type I or ASTM D 4869. | 1507.9.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.9.4 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer-modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.9.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.9.5 Interlayment. | Interlayment shall comply with ASTM D 226, Type I. | 1507.9.5 Interlayment. | Interlayment shall comply with ASTM D226, Type I.
1507.9.6 Material standards. | Wood shakes shall comply with the requirements of Table 1507.9.6. | 1507.9.6 Material standards. | Wood shakes shall comply with the requirements of Table 1507.9.6. |  | See BC15 Tables&Figures
1507.9.7 Attachment. | Fasteners for wood shakes shall be corrosion resistant with a minimum penetration of ¾ inch (19.1 mm) into the sheathing. For sheathing less than ½ inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shake shall be attached with a minimum of two fasteners. | 1507.9.7 Attachment. | Fasteners for wood shakes shall be corrosion resistant with a minimum penetration of 3/4 inch (19.1 mm) into the sheathing. For sheathing less than 1/2 inch (12.7 mm) in thickness, the fasteners shall extend through the sheathing. Each shake shall be attached with not fewer than two fasteners.
1507.9.8 Application. | Wood shakes shall be laid with a side lap not less than 1½ inches (38.1 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be ⅜ to ⅝ inches (9.5 to 15.9 mm) for shakes and taper sawn shakes of naturally durable wood and shall be ¼ to ⅜ inch (6.4 to 9.5 mm) for preservative taper sawn shakes. Weather exposure for wood shakes shall not exceed those set in Table 1507.9.8. | 1507.9.8 Application. | Wood shakes shall be laid with a side lap not less than 11/2 inches (38 mm) between joints in adjacent courses. Spacing between shakes in the same course shall be 3/8 to 5/8 inch (9.5 to 15.9 mm) for shakes and taper sawn shakes of naturally durable wood and shall be 1/4 to 3/8 inch (6.4 to 9.5 mm) for preservative taper sawn shakes. Weather exposure for wood shakes shall not exceed those set in Table 1507.9.8. |  | See BC15 Tables&Figures
1507.9.9 Flashing. | At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s instructions, and where of metal, shall be not less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend at least 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25.4 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (101.6 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch (914.4 mm) wide underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet complying with ASTM D 1970, in addition to other required underlayment. For slopes under seven units vertical in 12 units horizontal (58-percent slope) the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment or a self-adhering polymer-modified bitumen sheet shall be installed. | 1507.9.9 Flashing. | At the juncture of the roof and vertical surfaces, flashing and counterflashing shall be provided in accordance with the manufacturer’s installation instructions, and where of metal, shall be not less than 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage) corrosion-resistant metal. The valley flashing shall extend not less than 11 inches (279 mm) from the centerline each way and have a splash diverter rib not less than 1 inch (25 mm) high at the flow line formed as part of the flashing. Sections of flashing shall have an end lap of not less than 4 inches (102 mm). For roof slopes of three units vertical in 12 units horizontal (25-percent slope) and over, the valley flashing shall have a 36-inch-wide (914 mm) underlayment of either one layer of Type I underlayment running the full length of the valley or a self-adhering polymer-modified bitumen sheet bearing a label indicating compliance with ASTM D1970, in addition to other required underlayment. In areas where the average daily temperature in January is 25°F (-4°C) or less or where there is a possibility of ice forming along the eaves causing a backup of water, the metal valley flashing underlayment shall be solidly cemented to the roofing underlayment for slopes under seven units vertical in 12 units horizontal (58-percent slope) or self-adhering polymer-modified bitumen sheet shall be installed.
1507.10 Built-up roofs. | The installation of built-up roofs shall comply with the provisions of this section. | 1507.10 Built-up roofs. | The installation of built-up roofs shall comply with the provisions of this section.
1507.10.1 Slope. | Built-up roofs shall have a slope designed and built to provide positive roof drainage. | 1507.10.1 Slope. | Built-up roofs shall have a design slope of not less than 1/4 unit vertical in 12 units horizontal (2-percent slope) for drainage, except for coal-tar built-up roofs that shall have a design slope of not less than 1/8 unit vertical in 12 units horizontal (1-percent slope).
1507.10.2 Material standards. | Built-up roof covering materials shall comply with UL 55A or the standards in Table 1507.10.2 of this code. | 1507.10.2 Material standards. | Built-up roof covering materials shall comply with the standards in Table 1507.10.2 or UL 55A. |  | See BC15 Tables&Figures
1507.11 Modified bitumen roofing. | The installation of modified bitumen roofing shall comply with the provisions of this section. | 1507.11 Modified bitumen roofing. | The installation of modified bitumen roofing shall comply with the provisions of this section.
1507.11.1 Slope. | Modified bitumen membrane roofs shall have a slope designed and built to provide positive roof drainage. | 1507.11.1 Slope. | Modified bitumen roofing shall have a design slope of not less than 1/4 unit vertical in 12 units horizontal (2-percent slope) for drainage.
|  | 1507.9.10 Label required. | Each bundle of shakes shall be identified by a label of an approved grading or inspection bureau or agency.
1507.11.2 Material standards. | Modified bitumen roof coverings shall comply with CGSB 37-GP-56M, ASTM D 6162, ASTM D 6163, ASTM D 6164, ASTM D 6222, ASTM D 6223, ASTM D 6298 or ASTM D 6509. | 1507.11.2 Material standards. | Modified bitumen roofing materials shall comply with ASTM D6162, ASTM D6163, ASTM D6164, ASTM D6222, ASTM D6223, ASTM D6298 or ASTM D6509.
1507.12.1 Slope. | Thermoset single-ply membrane roofs shall have a slope designed and built to provide positive roof drainage. | 1507.12.1 Slope. | Single-ply membrane roofs shall have a design slope of not less than 1/4 unit vertical in 12 units horizontal (2-percent slope) for drainage.
1507.12.2 Material standards. | Thermoset single-ply roof coverings shall comply with ASTM D 4637, ASTM D 5019 or CGSB 37-GP-52M. | 1507.12.2 Material standards. | Single-ply roof coverings shall comply with the material standards in Table 1507.12.2. |  | See BC15 Tables&Figures
1507.13.1 Slope. | Thermoplastic single-ply membrane roofs shall have a slope designed and built to provide positive roof drainage. | 1507.13.1 Slope. | Sprayed polyurethane foam roofs shall have a design slope of not less than 1/4 unit vertical in 12 units horizontal (2-percent slope) for drainage.
|  | 1507.11.2.1 Base sheet. | A base sheet that complies with the requirements of Section 1507.11.2, ASTM D1970 or ASTM D4601 shall be permitted to be used with a modified bitumen cap sheet.
1507.13.2 Material standards. | Thermoplastic single-ply roof coverings shall comply with ASTM D 4434, ASTM D 6754, ASTM D 6878 or CAN/CGSB 37-54. | 1507.13.2 Material standards. | Spray-applied polyurethane foam insulation shall comply with ASTM C1029 Type III or IV or ASTM D7425.
|  | 1507.12 Single-ply roofing. | The installation of single-ply roofing shall comply with the provisions of this section.
1507.14.1 Slope. | Sprayed polyurethane foam roofs shall have a slope designed and built to provide positive roof drainage. | 1507.14.1 Slope. | Liquid-applied roofing shall have a design slope of not less than 1/4 unit vertical in 12 units horizontal (2-percent slope).
|  | 1507.12.3 Ballasted low-slope roofs. | Ballasted low-slope roofs (roof slope < 2:12) shall be installed in accordance with this section and Section 1504.5. Stone used as ballast shall comply with ASTM D448 or ASTM D7655.
1507.14.2 Material standards. | Spray-applied polyurethane foam insulation shall comply with Type III or IV as defined in ASTM C 1029. | 1507.14.2 Material standards. | Liquid-applied roofing shall comply with ASTM C836, ASTM C957 or ASTM D3468.
|  | 1507.13 Sprayed polyurethane foam roofing. | The installation of sprayed polyurethane foam roofing shall comply with the provisions of this section.
|  | 1507.13.3 Application. | Foamed-in-place roof insulation shall be installed in accordance with the manufacturer’s instructions. A liquid-applied protective coating that complies with Table 1507.13.3 shall be applied not less than 2 hours nor more than 72 hours following the application of the foam. |  | See BC15 Tables&Figures
|  | 1507.13.4 Foam plastics. | Foam plastic materials and installation shall comply with Chapter 26.
|  | 1507.14 Liquid-applied roofing. | The installation of liquid-applied roofing shall comply with the provisions of this section.
|  | 1507.15 Vegetative roofs and landscaped roofs. | Vegetative roofs and landscaped roofs shall comply with the requirements of this chapter, Section 1607.14.2.2 and the International Fire Code.
|  | 1507.15.1 Structural fire resistance. | The structural frame and roof construction supporting the load imposed on the roof by the vegetative roof or landscaped roofs shall comply with the requirements of Table 601. |  | See BC06 Tables&Figures
|  | 1507.16 Photovoltaic shingles. | The installation of photovoltaic shingles shall comply with the provisions of this section.
|  | 1507.16.1 Deck requirements. | Photovoltaic shingles shall be applied to a solid or closely fitted deck, except where the shingles are specifically designed to be applied over spaced sheathing.
|  | 1507.16.2 Deck slope. | Photovoltaic shingles shall be installed on roof slopes of not less than 2 units vertical in 12 units horizontal (2:12).
1507.17.1 Deck requirements. | Photovoltaic shingles shall be applied to a solid or closely fitted deck, except where the shingles are specifically designed to be applied over spaced sheathing. | 1507.17.1 Deck requirements. | BIPV roof panels shall be applied to a solid or closely fitted deck, except where the roof covering is specifically designed to be applied over spaced sheathing.
|  | 1507.16.3 Underlayment. | Underlayment shall comply with Section 1507.1.1.
1507.17.2 Deck slope. | Photovoltaic shingles shall not be installed on roof slopes less than three units vertical in 12 units horizontal (25-percent slope). | 1507.17.2 Deck slope. | BIPV roof panels shall be used only on roof slopes of 2 units vertical in 12 units horizontal (2:12) or greater.
|  | 1507.16.4 Ice barrier. | Where required, ice barriers shall comply with Section 1507.1.2.
1507.17.3 Underlayment. | Unless otherwise noted, required underlayment shall conform to ASTM D 226, ASTM D 4869 or ASTM D 6757. | 1507.17.3 Underlayment. | Underlayment shall comply with ASTM D226, ASTM D4869 or ASTM D6757.
|  | 1507.16.5 Fasteners. | Fasteners for photovoltaic shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum 12-gage shank with a minimum 3/8-inch-diameter (9.5 mm) head, of a length to penetrate through the roofing materials and not less than 3/4 inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than 3/4 inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F1667.
1507.17.4 Underlayment application. | Underlayment shall be applied shingle fashion, parallel to and starting from the eave, lapped 2 inches (50.8 mm) and fastened sufficiently to hold in place. | 1507.17.4 Underlayment application. | Underlayment shall be applied shingle fashion, parallel to and starting from the eave, lapped 2 inches (51 mm) and fastened sufficiently to hold in place.
|  | 1507.16.6 Material standards. | Photovoltaic shingles shall be listed and labeled in accordance with UL 7103 or with both UL 61730-1 and UL 61730-2.
|  | 1507.16.7 Attachment. | Photovoltaic shingles shall be attached in accordance with the manufacturer’s installation instructions.
1507.17.4.2 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used instead of normal underlayment and extend from the lowest edges of all roof surfaces to a point not less than 24 inches (609.6 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that contain no conditioned floor area. | 1507.17.4.2 Ice barrier. | In areas where there has been a history of ice forming along the eaves causing a back-up of water, an ice barrier consisting of not fewer than two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used instead of normal underlayment and extend from the lowest edges of all roof surfaces to a point not less than 24 inches (610 mm) inside the exterior wall line of the building. Exception: Detached accessory structures that do not contain conditioned floor area.
|  | 1507.16.8 Wind resistance. | Photovoltaic shingles shall comply with the classification requirements of Table 1504.2 for the appropriate maximum nominal design wind speed. |  | See BC15 Tables&Figures
|  | 1507.17 Building-integrated photovoltaic roof panels. | The installation of building-integrated photovoltaic (BIPV) roof panels shall comply with the provisions of this section.
1508.1 General. | The use of above-deck thermal insulation shall be permitted provided such insulation is covered with an approved roof covering and passes the tests of NFPA 276 or UL 1256 when tested as an assembly. Exceptions: 1. Foam plastic roof insulation shall conform to the material and installation requirements of Chapter 26 of this code. 2. Where a concrete roof deck is used and the above-deck thermal insulation is covered with an approved roof covering. | 1508.1 General. | The use of above-deck thermal insulation shall be permitted provided that such insulation is covered with an approved roof covering and passes the tests of NFPA 276 or UL 1256 when tested as an assembly. Exceptions: 1. Foam plastic roof insulation shall conform to the material and installation requirements of Chapter 26. 2. Where a concrete or composite metal and concrete roof deck is used and the above-deck thermal insulation is covered with an approved roof covering.
|  | 1507.17.4.1 High-wind attachment. | Underlayment applied in areas subject to high winds shall be applied in accordance with the manufacturer’s instructions. Fasteners shall be applied along the overlap at not more than 36 inches (914 mm) on center. Underlayment installed where Vasd is not less than 120 mph (54 m/s) shall comply with ASTM D226, Type III, ASTM D4869, Type IV or ASTM D6757. The underlayment shall be attached in a grid pattern of 12 inches (305 mm) between side laps with a 6-inch (152 mm) spacing at the side laps. The underlayment shall be applied in accordance with Section 1507.1.1 except all laps shall be not less than 4 inches (102 mm). Underlayment shall be attached using cap nails or cap staples. Caps shall be metal or plastic with a nominal head diameter of not less than 1 inch (25.4 mm). Metal caps shall have a thickness of not less than 0.010 inch (0.25 mm). Power-driven metal caps shall have a thickness of not less than 0.010 inch (0.25 mm). Thickness of the outside edge of plastic caps shall be not less than 0.035 inch (0.89 mm). The cap nail shank shall be not less than 0.083 inch (2.11 mm) for ring shank cap nails and 0.091 inch (2.31 mm) for smooth shank cap nails. Staple gage shall be not less than 21 gage . Cap nail shank and cap staple legs shall have a length sufficient to penetrate through-the-roof sheathing or not less than 3/4 inch (19.1 mm) into the roof sheathing. Exception: As an alternative, adhered underlayment complying with ASTM D1970 shall be permitted.
1508.2 Material standards. | Above-deck thermal insulation board shall comply with the standards in Table 1508.2. | 1508.2 Material standards. | Above-deck thermal insulation board shall comply with the standards in Table 1508.2. |  | See BC15 Tables&Figures
1509.1 General. | A radiant barrier installed above a deck shall comply with Sections 1509.2 through 1509.4. | 1509.1 General. | The installation of a roof coating on a roof covering shall comply with the requirements of Section 1505 and this section.
|  | 1507.17.5 Material standards. | BIPV roof panels shall be listed and labeled in accordance with UL 7103 or with both UL 61730-1 and UL 61730-2.
|  | 1507.17.6 Attachment. | BIPV roof panels shall be attached in accordance with the manufacturer’s installation instructions.
1510.1 General. | The provisions of this section shall govern the construction of rooftop structures. All rooftop structures shall be subject to the roof area coverage limitations and building height requirements of Chapter 5. Rooftop structures shall be constructed with materials as required for the building, except as provided for in this section. | 1510.1 General. | A radiant barrier installed above a deck shall comply with Sections 1510.2 through 1510.4.
|  | 1509.2 Material standards. | Roof coating materials shall comply with the standards in Table 1509.2. |  | See BC15 Tables&Figures
|  | 1510.2 Fire testing. | Radiant barriers shall be permitted for use above decks where the radiant barrier is covered with an approved roof covering and the system consisting of the radiant barrier and the roof covering complies with the requirements of either FM 4450 or UL 1256.
|  | 1510.3 Installation. | The low emittance surface of the radiant barrier shall face the continuous airspace between the radiant barrier and the roof covering.
|  | 1510.4 Material standards. | A radiant barrier installed above a deck shall comply with ASTM C1313/1313M.
1511.1 General. | Materials and methods of application used for recovering or replacing an existing roof covering shall comply with the requirements of Chapter 15. Exceptions: 1. Section 1504.9 shall not apply if the area to be recovered or replaced is less than 50 percent of the roof area and less than 500 square feet (46.5 m2). 2. Recovering or replacing an existing roof covering shall not be required to meet the requirement for secondary (emergency overflow) drains or scuppers in Section 1503.4 for roofs that provide for positive roof drainage. For the purposes of this exception, existing secondary drainage or scupper systems required in accordance with this code shall not be removed unless they are replaced by secondary drains or scuppers designed and installed in accordance with Section 1503.4. | 1511.1 General. | The provisions of this section shall govern the construction of rooftop structures.
|  | 1511.1.1 Area limitation. | The aggregate area of penthouses and other enclosed rooftop structures shall not exceed one-third the area of the supporting roof deck. Such penthouses and other enclosed rooftop structures shall not be required to be included in determining the building area or number of stories as regulated by Section 503.1. The area of such penthouses shall not be included in determining the fire area specified in Section 901.7.
|  | 1511.2 Penthouses. | Penthouses in compliance with Sections 1511.2.1 through 1511.2.4shall be considered as a portion of the story directly below the roof deck on which such penthouses are located. Other penthouses shall be considered as an additional story of the building.
|  | 1511.2.1 Height above roof deck. | Penthouses constructed on buildings of other than Type I construction shall not exceed 18 feet (5486 mm) in height above the roof deck as measured to the average height of the roof of the penthouse. Penthouses located on the roof of buildings of Type I construction shall not be limited in height. Exception: Where used to enclose tanks or elevators that travel to the roof level, penthouses shall be permitted to have a maximum height of 28 feet (8534 mm) above the roof deck.
|  | 1511.2.2 Use limitations. | Penthouses shall not be used for purposes other than the shelter of mechanical or electrical equipment, tanks, elevators and related machinery, stairways or vertical shaft openings in the roof assembly, including ancillary spaces used to access elevators and stairways.
|  | 1511.2.3 Weather protection. | Provisions such as louvers, louver blades or flashing shall be made to protect the mechanical and electrical equipment and the building interior from the elements.
|  | 1511.2.4 Type of construction. | Penthouses shall be constructed of building elements as required for the type of construction of the building on which such penthouses are built. Exceptions: 1. On buildings of Type I construction, the exterior walls and roofs of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating. The exterior walls and roofs of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall not be required to have a fire-resistance rating. 2. On buildings of Type I construction two stories or less in height above grade plane or of Type II construction, the exterior walls and roofs of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating or a lesser fire-resistance rating as required by Table 705.5 and be constructed of fire-retardant-treated wood. The exterior walls and roofs of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall be permitted to be constructed of fire-retardant-treated wood and shall not be required to have a fire-resistance rating. Interior framing and walls shall be permitted to be constructed of fire-retardant-treated wood. 3. On buildings of Type III, IV or V construction, the exterior walls of penthouses with a fire separation distance greater than 5 feet (1524 mm) and less than 20 feet (6096 mm) shall be permitted to have not less than a 1-hour fire-resistance rating or a lesser fire-resistance rating as required by Table 705.5. On buildings of Type III, IV or VA construction, the exterior walls of penthouses with a fire separation distance of 20 feet (6096 mm) or greater shall be permitted to be of heavy timber construction complying with Sections 602.4 and 2304.11 or noncombustible construction or fire-retardant-treated wood and shall not be required to have a fire-resistance rating.
|  | 1511.3 Tanks. | Tanks having a capacity of more than 500 gallons (1893 L) located on the roof deck of a building shall be supported on masonry, reinforced concrete, steel or heavy timber construction complying with Section 2304.11 provided that, where such supports are located in the building above the lowest story, the support shall be fire-resistance rated as required for Type IA construction.
|  | 1511.3.1 Valve and drain. | In the bottom or on the side near the bottom of the tank, a pipe or outlet, fitted with a suitable quick-opening valve for discharging the contents into a drain in an emergency shall be provided.
|  | 1511.3.2 Location. | Tanks shall not be placed over or near a stairway or an elevator shaft, unless there is a solid roof or floor underneath the tank.
|  | 1511.3.3 Tank cover. | Unenclosed roof tanks shall have covers sloping toward the perimeter of the tanks.
|  | 1511.4 Cooling towers. | Cooling towers located on the roof deck of a building and greater than 250 square feet (23.2 m2) in base area or greater than 15 feet (4572 mm) in height above the roof deck, as measured to the highest point on the cooling tower, where the roof is greater than 50 feet (15 240 mm) in height above grade plane shall be constructed of noncombustible materials. The base area of cooling towers shall not exceed one-third the area of the supporting roof deck. Exception: Drip boards and the enclosing construction shall be permitted to be of wood not less than 1 inch (25 mm) nominal thickness, provided that the wood is covered on the exterior of the tower with noncombustible material.
|  | 1511.5 Towers, spires, domes and cupolas. | Towers, spires, domes and cupolas shall be of a type of construction having fire-resistance ratings not less than required for the building on top of which such tower, spire, dome or cupola is built. Towers, spires, domes and cupolas greater than 85 feet (25 908 mm) in height above grade plane as measured to the highest point on such structures, and either greater than 200 square feet (18.6 m2) in horizontal area or used for any purpose other than a belfry or an architectural embellishment, shall be constructed of and supported on Type I or II construction.
|  | 1511.5.1 Noncombustible construction required. | Towers, spires, domes and cupolas greater than 60 feet (18 288 mm) in height above the highest point at which such structure contacts the roof as measured to the highest point on such structure, or that exceeds 200 square feet (18.6 m2) in area at any horizontal section, or which is intended to be used for any purpose other than a belfry or architectural embellishment, or is located on the top of a building greater than 50 feet (1524 mm) in building height shall be constructed of and supported by noncombustible materials and shall be separated from the building below by construction having a fire-resistance rating of not less than 1.5 hours with openings protected in accordance with Section 711. Such structures located on the top of a building greater than 50 feet (15 240 mm) in building height shall be supported by noncombustible construction.
|  | 1511.5.2 Towers and spires. | Enclosed towers and spires shall have exterior walls constructed as required for the building on top of which such towers and spires are built. The roof covering of spires shall be not less than the same class of roof covering required for the building on top of which the spire is located.
|  | 1511.6 Mechanical equipment screens. | Mechanical equipment screens shall be constructed of the materials specified for the exterior walls in accordance with the type of construction of the building. Where the fire separation distance is greater than 5 feet (1524 mm), mechanical equipment screens shall not be required to comply with the fire-resistance rating requirements.
|  | 1511.6.1 Height limitations. | Mechanical equipment screens shall not exceed 18 feet (5486 mm) in height above the roof deck, as measured to the highest point on the mechanical equipment screen. Exception: Where located on buildings of Type IA construction, the height of mechanical equipment screens shall not be limited.
|  | 1511.6.2 Type I, II, III or IV construction. | Regardless of the requirements in Section 1511.6, mechanical equipment screens that are located on the roof decks of buildings of Type I, II, III or IV construction shall be permitted to be constructed of combustible materials in accordance with any one of the following limitations:
|  | 1511.6.3 Type V construction. | The height of mechanical equipment screens located on the roof decks of buildings of Type V construction, as measured from grade plane to the highest point on the mechanical equipment screen, shall be permitted to exceed the maximum building height allowed for the building by other provisions of this code where complying with any one of the following limitations, provided that the fire separation distance is greater than 5 feet (1524 mm):
|  | 1511.7 Other rooftop structures. | Rooftop structures not regulated by Sections 1511.2 through 1511.6 shall comply with Sections 1511.7.1 through 1511.7.5, as applicable.
|  | 1511.7.1 Aerial supports. | Aerial supports shall be constructed of noncombustible materials. Exception: Aerial supports not greater than 12 feet (3658 mm) in height as measured from the roof deck to the highest point on the aerial supports shall be permitted to be constructed of combustible materials.
|  | 1511.7.2 Bulkheads. | Bulkheads used for the shelter of mechanical or electrical equipment or vertical shaft openings in the roof assembly shall comply with Section 1511.2 as penthouses. Bulkheads used for any other purpose shall be considered as an additional story of the building.
|  | 1511.7.3 Dormers. | Dormers shall be of the same type of construction as required for the roof in which such dormers are located or the exterior walls of the building.
|  | 1511.7.4 Fences. | Fences and similar structures shall comply with Section 1511.6 as mechanical equipment screens.
|  | 1511.7.5 Flagpoles. | Flagpoles and similar structures shall not be required to be constructed of noncombustible materials and shall not be limited in height or number.
|  | 1511.8 Structural fire resistance. | The structural frame and roof construction supporting loads imposed upon the roof by any rooftop structure shall comply with the requirements of Table 601. The fire-resistance reduction permitted by Table 601, Note a, shall not apply to roofs containing rooftop structures. |  | See BC06 Tables&Figures
|  | 1512.1 General. | Materials and methods of application used for recovering or replacing an existing roof covering shall comply with the requirements of Chapter 15. Exceptions: 1. Roof replacement or roof recover of existing low-slope roof coverings shall not be required to meet the minimum design slope requirement of 1/4 unit vertical in 12 units horizontal (2-percent slope) in Section 1507 for roofs that provide positive roof drainage. 2. Recovering or replacing an existing roof covering shall not be required to meet the requirement for secondary (emergency overflow) drains or scuppers in Section 1502.2 for roofs that provide for positive roof drainage. For the purposes of this exception, existing secondary drainage or scupper systems required in accordance with this code shall not be removed unless they are replaced by secondary drains or scuppers designed and installed in accordance with Section 1502.2.
|  | 1512.2 Roof replacement. | Roof replacement shall include the removal of all existing layers of roof assembly materials down to the roof deck. Exception: Where the existing roof assembly includes an ice barrier membrane that is adhered to the roof deck, the existing ice barrier membrane shall be permitted to remain in place and covered with an additional layer of ice barrier membrane in accordance with Section 1507.
|  | 1512.2.1 Roof recover. | The installation of a new roof covering over an existing roof covering shall be permitted where any of the following conditions occur:
|  | 1512.2.1.1 Exceptions. | A roof recover shall not be permitted where any of the following conditions occur: 1. Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing. 2. Where the existing roof covering is slate, clay, cement or asbestos-cement tile. 3. Where the existing roof has two or more applications of any type of roof covering.
|  | 1512.3 Roof recovering. | Where the application of a new roof covering over wood shingle or shake roofs creates a combustible concealed space, the entire existing surface shall be covered with gypsum board, mineral fiber, glass fiber or other approved materials securely fastened in place.
|  | 1512.4 Reinstallation of materials. | Existing slate, clay or cement tile shall be permitted for reinstallation, except that damaged, cracked or broken slate or tile shall not be reinstalled. Existing vent flashing, metal edgings, drain outlets, collars and metal counterflashings shall not be reinstalled where rusted, damaged or deteriorated. Existing ballast that is damaged, cracked or broken shall not be reinstalled. Existing aggregate surfacing materials from built-up roofs shall not be reinstalled.
|  | 1512.5 Flashings. | Flashings shall be reconstructed in accordance with approved manufacturer’s installation instructions. Metal flashing to which bituminous materials are to be adhered shall be primed prior to installation.
1502.1 Definitions. | The following terms are defined in Chapter 2:
1503.3 Coping. | Parapet walls shall be properly coped with noncombustible, weatherproof materials of a width no less than the thickness of the parapet wall.
1503.4 Roof drainage. | Design and installation of roof drainage systems shall comply with Chapter 11 of the New York City Plumbing Code and this section.
1503.4.1 Secondary (emergency overflow) drains or scuppers. | Where roof drains are required, secondary (emergency overflow) roof drains or scuppers shall be provided where the roof perimeter construction extends above the roof in such a manner that water will be entrapped if the primary drains allow buildup for any reason. The installation and sizing of secondary (emergency overflow) drains, leaders and conductors shall comply with Chapter 11 of the New York City Plumbing Code, as applicable.
1503.4.2 Scuppers. | When scuppers are used for secondary (emergency overflow) roof drainage, the quantity, size, location and inlet elevation of the scuppers shall be sized to prevent the depth of ponding water from exceeding that for which the roof was designed as determined by Section 1611.1. Scuppers shall not have an opening dimension of less than 4 inches (101.6 mm). The flow through the primary system shall not be considered when locating and sizing scuppers.
1503.5 Attic and rafter ventilation. | Intake and exhaust vents shall be provided in accordance with Section 1203.2 and the vent product’s manufacturer’s instructions.
1503.6 Crickets and saddles. | A cricket or saddle shall be installed on the ridge side of any chimney or penetration greater than 30 inches (762 mm) wide as measured perpendicular to the slope. Cricket or saddle coverings shall be sheet metal or of the same material as the roof covering.
1504.1.1 Wind resistance of asphalt shingles. | Asphalt shingles shall be tested in accordance with ASTM D 7158. Asphalt shingles shall meet the classification requirements of Table 1504.1.1 of this code for the appropriate maximum wind speed. Asphalt shingle packaging shall bear a label to indicate compliance with ASTM D 7158 and the required classification in Table 1504.1.1 of this code. |  |  |  | See BC15 Tables&Figures
1504.2 Wind resistance of clay and concrete tile. | Wind loads on clay and concrete tile roof coverings shall be in accordance with Section 1609.
1504.2.1 Testing. | Testing of concrete and clay roof tiles shall be in accordance with Sections 1504.2.1.1 and 1504.2.1.2.
1504.2.1.1 Overturning resistance. | Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with SBCCI SSTD 11 and this chapter.
1504.2.1.2 Wind tunnel testing. | Where concrete and clay roof tiles do not satisfy the limitations in Chapter 16 of this code for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with SBCCI SSTD 11 and this chapter.
1504.3 Wind resistance of nonballasted roofs. | Roof coverings installed on roofs in accordance with Section 1507 that are mechanically attached or adhered to the roof deck shall be designed to resist the design wind load pressures for components and cladding in accordance with Section 1609.
1504.3.1 Other roof systems. | Built-up, modified bitumen, fully adhered or mechanically attached single-ply roof systems, metal panel roof systems applied to a solid or closely fitted deck and other types of membrane roof coverings shall be tested in accordance with FM 4474, UL 580 or UL 1897.
1504.3.2 Structural metal panel roof systems. | Where the metal roof panel functions as the roof deck and roof covering and it provides both weather protection and support for loads, the structural metal panel roof system shall comply with this section. Structural standing-seam metal panel roof systems shall be tested in accordance with ASTM E 1592 or FM 4474. Structural through-fastened metal panel roof systems shall be tested in accordance with FM 4474, UL 580 or ASTM E 1592.
1504.4 Ballasted low-slope roof systems. | Ballasted low-slope (roof slope < 2:12) single-ply roof system coverings installed in accordance with Sections 1507.12 and 1507.13 shall be designed in accordance with ANSI/SPRI RP-4 and Section 1504.8 of this code.
1504.5 Edge securement for low-slope roofs. | Low-slope membrane roof systems metal edge securement, except gutters, shall be designed and installed for wind loads in accordance with Chapter 16 and tested for resistance in accordance with Test Methods RE-1, RE-2 and RE-3 of ANSI/SPRI/FM 4435 ES-1, except the basic design wind speed V shall be determined in accordance with Chapter 16 of this code.
1504.6 Physical properties. | Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall demonstrate physical integrity over the working life of the roof based upon 2,000 hours of exposure to accelerated weathering tests conducted in accordance with ASTM G 152, ASTM G 155 or ASTM G 154. Those roof coverings that are subject to cyclical flexural response due to wind loads shall not demonstrate any significant loss of tensile strength for unreinforced membranes or breaking strength for reinforced membranes when tested as herein required.
1504.7 Impact resistance. | Roof coverings installed on low-slope roofs (roof slope < 2:12) in accordance with Section 1507 shall resist impact damage based on the results of tests conducted in accordance with ASTM D 3746, ASTM D 4272, CGSB 37-GP-52M or the “Resistance to Foot Traffic Test” in Section 5.5 of FM 4470.
1504.8 Surfacing and ballast materials. | Aggregate, gravel or crushed stone shall not be used as surfacing for roof coverings.
1504.9 Reflectance. | Roof coverings on roofs or setbacks with slope equal to or less than two units vertical in 12 units horizontal (17 percent) shall have:
1505.5 Construction of sloping roofs. | Roofs having a slope of more than 60 degrees (1.05 rad) to the horizontal shall be constructed of material having the same fire-resistance rating as required for an exterior nonbearing wall of the building of which it is a part. When the slope is 60 degrees (1.05 rad) or less to the horizontal, the sloping roof shall be constructed as required for the roof of the building. Where the back of a false mansard is exposed to the outdoors, the back shall be covered with noncombustible material or with roof covering as required for the roof of the building.
1505.8 Building-integrated photovoltaic products. | Building-integrated photovoltaic products installed as the roof covering shall be tested, listed and labeled for fire classification in accordance with Section 1505.1.
1505.9 Photovoltaic panels and modules. | Rooftop-mounted photovoltaic panel systems shall be tested, listed and identified with a fire classification in accordance with UL 1703. The fire classification shall comply with Table 1505.1 of this code based on the type of construction of the building. |  |  |  | See BC15 Tables&Figures
1505.10 Roof gardens and landscaped roofs. | Roof gardens and landscaped roofs shall comply with Section 1507.16.
1507.2.4 Self-adhering polymer modified bitumen sheet. | Self-adhering polymer modified bitumen sheet shall comply with ASTM D 1970.
1507.2.5 Asphalt shingles. | Asphalt shingles shall comply with ASTM D 225 or ASTM D 3462.
1507.2.6 Fasteners. | Fasteners for asphalt shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum 12-gage (0.105-inch (2.67 mm)) shank with a minimum ⅜ inch-diameter (9.5 mm) head, of a length to penetrate through the roofing materials and a minimum of ¾ inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than ¾ inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F 1667.
1507.2.7 Attachment. | Asphalt shingles shall have the minimum number of fasteners required by the manufacturer, but not less than four fasteners per strip shingle or two fasteners per individual shingle. Where the roof slope exceeds 21 units vertical in 12 units horizontal (21:12), shingles shall be installed as required by the manufacturer.
1507.2.8 Underlayment application. | For roof slopes from two units vertical in 12 units horizontal (17-percent slope) up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be two layers applied in the following manner. Apply a minimum 19-inch (482.6 mm) wide strip of underlayment felt parallel with and starting at the eaves, fastened sufficiently to hold in place. Starting at the eave, apply 36-inch (914.4 mm) wide sheets of underlayment overlapping successive sheets 19 inches (482.6 mm) and fastened sufficiently to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal. For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be one layer applied in the following manner. Underlayment shall be applied shingle fashion, parallel to and starting from the eave and lapped 2 inches (50.8 mm), fastened only as necessary to hold in place. Distortions in the underlayment shall not interfere with the ability of the shingles to seal.
1507.2.8.1 Ice barrier. | An ice barrier that consists of at least two layers of underlayment cemented together or of a self-adhering polymer modified bitumen sheet shall be used in lieu of normal underlayment and extend from the lowest edges of all roof surfaces to a point at least 24 inches (609.6 mm) inside the exterior wall line of the building.
1507.2.9 Flashings. | Flashing for asphalt shingles shall comply with this section. Flashing shall be applied in accordance with this section and the asphalt shingle manufacturer’s instructions.
1507.2.9.1 Base and cap flashing. | Base and cap flashing shall be installed in accordance with the manufacturer’s instructions. Base flashing shall be of either corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness or mineral-surfaced roll roofing weighing a minimum of 77 pounds per 100 square feet (3.76 kg/m2). Cap flashing shall be corrosion-resistant metal of minimum nominal 0.019-inch (0.483 mm) thickness.
1507.2.9.2 Valleys. | Valley linings shall be installed in accordance with the manufacturer’s instructions before applying shingles. Valley linings of the following types shall be permitted:
1507.2.9.3 Drip edge. | A drip edge shall be provided at eaves and rake edges of shingle roofs. Adjacent segments of the drip edge shall be lapped a minimum of 2 inches (50.8 mm). The vertical leg of drip edges shall be a minimum of 1½ inches (38.1 mm) in width and shall extend a minimum of ¼ inch (6.4 mm) below sheathing. The drip edge shall extend back on the roof a minimum of 2 inches (50.8 mm). Underlayment shall be installed over drip edges along eaves. Drip edges shall be installed over underlayment along rake edges. Drip edges shall be mechanically fastened a maximum of 12 inches (304.8 mm) on center.
1507.3.3.1 Low-slope roofs. | For roof slopes from 2½ units vertical in 12 units horizontal (21-percent slope), up to four units vertical in 12 units horizontal (33-percent slope), underlayment shall be a minimum of two layers applied as follows:
1507.3.3.2 High-slope roofs. | For roof slopes of four units vertical in 12 units horizontal (33-percent slope) or greater, underlayment shall be a minimum of one layer of underlayment felt applied shingle fashion, parallel to, and starting from the eaves and lapped 2 inches (50.8 mm), fastened only as necessary to hold in place.
1507.12 Thermoset single-ply roofing. | The installation of thermoset single-ply roofing shall comply with the provisions of this section.
1507.12.3 Ballasted thermoset low-slope roofs. | Ballasted thermoset low-slope roofs (roof slope < 2:12) shall be installed in accordance with this section and Section 1504.4, and subject to the limitations of Section 1504.8.
1507.13 Thermoplastic single-ply roofing. | The installation of thermoplastic single-ply roofing shall comply with the provisions of this section.
1507.13.3 Ballasted thermoplastic low-slope roofs. | Ballasted thermoplastic low-slope roofs (roof slope < 2:12) shall be installed in accordance with this section and Section 1504.4, and subject to the limitations of Section 1504.8.
1507.14 Sprayed polyurethane foam roofing. | The installation of sprayed polyurethane foam roofing shall comply with the provisions of this section.
1507.14.3 Application. | Foamed-in-place roof insulation shall be installed in accordance with the manufacturer’s instructions. A liquid-applied protective coating that complies with Table 1507.14.3 shall be applied no less than 2 hours nor more than 72 hours following the application of the foam. |  |  |  | See BC15 Tables&Figures
1507.14.4 Foam plastics. | Foam plastic materials and installation shall comply with Chapter 26.
1507.15 Liquid-applied roofing. | The installation of liquid-applied roofing shall comply with the provisions of this section.
1507.15.1 Slope. | Liquid-applied roofing shall have a slope designed and built to provide positive roof drainage.
1507.15.2 Material standards. | Liquid-applied roofing shall comply with ASTM C 836, ASTM C 957, ASTM D 1227 or ASTM D 3468, ASTM D 6083, ASTM D 6694 or ASTM D 6947.
1507.16 Vegetative roofs, roof gardens and landscaped roofs. | Vegetative roofs, roof gardens and landscaped roofs shall comply with the provisions of this section and New York City Fire Code.
1507.16.1 Design standards. | Vegetative roofs, roof gardens and landscaped roofs shall comply with ANSI/SPRI RP-14 and ANSI/SPRI VF-1, or with FM DS 1-35. Exceptions: 1. The aggregate area of landscaping materials or growth media or both on any single roof level of a building or structure is 250 square feet (23.2 m2) or less. 2. The roof area is 22 feet (6705.6 mm) or less from grade. 3. The vegetative roof system is a container garden.
1507.16.2 Roof structure. | The roof structure shall comply with Chapter 16 for the design of the vegetative roofs, roof gardens and landscaped roofs.
1507.16.3 Roof covering. | Roof covering shall comply with Section 1507.10, 1507.11, 1507.12, 1507.13 or 1507.15.
1507.16.4 Slope. | The roofing membrane shall have a design slope in accordance with the roof covering utilized. Overburden shall be installed to prevent slippage tested as an assembly.
1507.16.5 Structural fire resistance. | The structural frame and roof construction supporting the load imposed upon the roof by the vegetative roof, roof gardens or landscaped roofs shall comply with the requirements of Table 601. |  |  |  | See BC06 Tables&Figures
1507.17 Photovoltaic shingles. | The installation of photovoltaic shingles shall comply with the provisions of this section.
1507.17.4.1 High wind attachment. | Underlayment applied in areas subject to high winds (Vasd greater than 110 mph (49.1 m/s) as determined in accordance with Section 1609.3.1) shall be applied with corrosion-resistant fasteners in accordance with the manufacturer’s instructions. Fasteners shall be applied along the overlap at not more than 36 inches (914.4 mm) on center. Underlayment installed where Vasd is not less than 120 mph (53.6 m/s) shall comply with ASTM D 226, Type II, ASTM D 4869, Type IV or ASTM D 6757. The underlayment shall be attached in a grid pattern of 12 inches (304.8 mm) between side laps with a 6-inch (152.4 mm) spacing at the side laps. Underlayment shall be applied in accordance with Section 1507.2.8 except all laps shall be a minimum of 4 inches (101.6 mm). Underlayment shall be attached using metal or plastic cap nails with a head diameter of not less than 1 inch (25.4 mm) with a thickness of not less than 32-gage (0.0134 inch (0.34 mm)) sheet metal. The cap nail shank shall be a minimum of 12 gage (0.105 inch (2.67 mm)) with a length to penetrate through the roof sheathing or a minimum of ¾ inch (19.1 mm) into the roof sheathing. Exception: As an alternative, adhered underlayment complying with ASTM D 1970 shall be permitted.
1507.17.5 Fasteners. | Fasteners for photovoltaic shingles shall be galvanized, stainless steel, aluminum or copper roofing nails, minimum 12-gage (0.105 inch (2.67 mm)) shank with a minimum ⅜-inch (9.5 mm) diameter head, of a length to penetrate through the roofing materials and a minimum of ¾ inch (19.1 mm) into the roof sheathing. Where the roof sheathing is less than ¾ inch (19.1 mm) thick, the nails shall penetrate through the sheathing. Fasteners shall comply with ASTM F 1667.
1507.17.6 Material standards. | Photovoltaic shingles shall be listed and labeled in accordance with UL 1703.
1507.17.7 Attachment. | Photovoltaic shingles shall be attached in accordance with the manufacturer’s instructions.
1507.17.8 Wind resistance. | Photovoltaic shingles shall be tested in accordance with procedures and acceptance criteria in ASTM D 3161. Photovoltaic shingles shall comply with the classification requirements of Table 1504.1.1 of this code for the appropriate maximum nominal design wind speed. Photovoltaic shingle packaging shall bear a label to indicate compliance with the procedures in ASTM D 3161 and the required classification from Table 1504.1.1 of this code. |  |  |  | See BC15 Tables&Figures
1508.1.1 Cellulosic fiberboard. | Cellulosic fiberboard roof insulation shall conform to the material and installation requirements of Chapter 23.
1509.2 Fire testing. | Radiant barriers shall be permitted for use above decks where the radiant barrier is covered with an approved roof covering and the system consisting of the radiant barrier and the roof covering complies with the requirements of either FM 4550 or UL 1256.
1509.3 Installation. | The low emittance surface of the radiant barrier shall face the continuous airspace between the radiant barrier and the roof covering.
1509.4 Material standards. | A radiant barrier installed above a deck shall comply with ASTM C 1313/1313M.
1510.2 Bulkheads and penthouses. | Bulkheads and penthouses shall comply with the construction requirements of this Section.
1510.2.1 Type of construction. | Bulkheads and penthouses shall be constructed with walls, floors and roof as required for the building. Exceptions: Where the total aggregate area of all rooftop structures does not exceed 33 percent of the area of the roof of the building upon which they are erected, the following shall apply: 1. Bulkheads on buildings of Type I and II construction. The exterior walls and roofs of such bulkheads with a fire separation distance of more than 5 feet (1524 mm) and less than 30 feet (9144 mm) shall be of at least 1-hour fire-resistance-rated noncombustible construction. Walls and roofs with a fire separation distance of 30 feet (9144 mm) or greater shall be of noncombustible construction. Interior framing and walls shall be of noncombustible construction. 2. Bulkheads on buildings of Type III, IV and V construction. The exterior walls of such bulkheads with a fire separation distance of more than 5 feet (1524 mm) and less than 30 feet (9144 mm) shall be at least 1-hour fire-resistance-rated construction. Walls with a fire separation distance of 30 feet (9144 mm) or greater from a common property line shall be of Type IV construction, or noncombustible construction. Roofs shall be constructed of materials and fire-resistance rated as required in Table 601. Interior framing and walls shall be Type IV or noncombustible or fire-retardant-treated wood construction |  |  |  | See BC06 Tables&Figures
1510.2.2 Penthouses. | Enclosed walls of penthouses shall comply with the requirements for exterior walls as per Tables 601 and 602 for the construction class of the building on which they are erected. Roofs of penthouses shall comply with the requirements for roof construction of Table 601 and Chapter 15. |  |  |  | See BC06 Tables&Figures
1510.2.3 Bulkheads. | An enclosed rooftop structure not intended for human occupancy shall not be used for purposes other than shelter of mechanical equipment or shelter of vertical shaft openings in the roof. Provisions, such as louvers, louver blades or flashing, shall be made to protect the mechanical equipment and the building interior from the elements.
1510.3 Tanks. | Tanks having a capacity of more than 500 gallons (1892.7 L) located on the roof deck of a building shall be supported on masonry, reinforced concrete, steel or Type IV construction provided that, where such supports are located in the building above the lowest story, the support shall be fire-resistance rated as required for Type IA construction.
1510.3.1 Valve and drain. | On the bottom or on the side near the bottom of the tank, a pipe or outlet, fitted with a suitable quick-opening valve for discharging the contents into a drain in an emergency shall be provided.
1510.3.2 Location. | Tanks shall not be placed over or near a stairway or an elevator shaft, unless there is a solid roof or floor underneath the tank.
1510.3.3 Tank cover. | Unenclosed roof tanks shall have covers sloping toward the perimeter of the tanks.
1510.4 Cooling towers. | Cooling towers shall be of noncombustible construction. Exceptions: 1. Fill and drift eliminators of limited combustible materials may be considered noncombustible if the cooling towers are provided with automatic sprinkler protection complying with Section 903. 2. Fill and drift eliminators that comply with Section 908 of the New York City Mechanical Code.
1510.5 Steeples, minarets, spires, domes and cupolas. | Steeples, minarets, spires, domes, cupolas and other similar architectural elements not used for occupancy or storage, shall be constructed of materials consistent with the required type of construction of the building and shall be of a type of construction having fire-resistance ratings not less than required for the building on top of which such steeple, minaret, spire, dome or cupola is built.
1510.5.1 Noncombustible construction required. | Steeples, minarets, spires, domes and cupolas greater than 60 feet (18 288 mm) in height above the highest point at which such structure contacts the roof as measured to the highest point on such structure, or that exceeds 200 square feet (18.6 m2) in area at any horizontal section, or which is intended to be used for any purpose other than as a belfry or architectural embellishment, or is located on the top of a building greater than 50 feet (1524 mm) in building height shall be constructed of and supported by noncombustible materials and shall be separated from the building below by construction having a fire-resistance rating of not less than 1.5 hours with openings protected in accordance with Section 712. Such structures located on the top of a building greater than 50 feet (15 240 mm) in building height, shall be supported by noncombustible construction.
1510.5.2 Steeples, minarets and spires. | Steeples, minarets, and spires shall have exterior walls constructed as required for the building on top of which such steeples, minarets and spires are built. The roof covering of spires shall be not less than the same class of roof covering required for the building on top of which the spire is located.
1510.6 Dormers. | Dormers shall have exterior walls as required for the building to which they are attached. The roof covering of dormers shall be of a class of roof covering as required for the main roof of the rest of the structure.
1510.7 Greenhouses. | Greenhouses used for the cultivation of plants, on the roofs of buildings other than buildings of Type V construction, shall be constructed of noncombustible framework and shall be glazed with plain or wire glass, or light transmitting plastic glazing complying with the requirements of Section 2606. The floors of greenhouses shall be constructed to be at least equal to the requirements for roof construction on Table 601 for the construction class of the building on which it is located. |  |  |  | See BC06 Tables&Figures
1510.8 Protective guards. | Buildings greater than 22 feet (6706 mm) in height with roof slopes less than 2.4 units vertical in 12 units horizontal (20-percent slope) shall be provided with a parapet, guards, fence, or combination thereof, not less than 42 inches (1067 mm) in height. Guards or fences may be located inward from the face of the exterior wall a distance not exceeding 6 feet (1828.8 mm). Guards or fences shall be of noncombustible material, except on buildings of Type V construction. Guards shall be constructed to comply with the requirements of Sections 1015 and 1607.8.
1510.8.1 Fences on roofs used for recreational purposes. | Rooftops used for recreational purposes shall be provided with wire fencing at least 10 feet (3048 mm) in height. Openings in the fence shall not permit the passage of a 4-inch (101.6 mm) diameter sphere. Where ball games are played on rooftops the wire fencing shall be extended to provide an overhead closure.
1510.9 Miscellaneous combustible roof structures. | The following roof structures may be constructed of combustible material if less than 12 feet (3657.6 mm) high above the roof: antenna supports; flagpoles; clothes drying frames; duckboarding; decking or platforms that do not cover more than 20 percent of the contiguous roof area at that level.
1510.10 Mechanical equipment screens. | Mechanical equipment screens shall be constructed of the materials specified for the exterior walls in accordance with the type of construction of the building.
1510.10.1 Type V construction. | The height of mechanical equipment screens located on the roof decks of buildings of Type V construction, as measured from grade plane to the highest point on the mechanical equipment screen, shall be permitted to exceed the maximum building height allowed for the building by other provisions of this code where complying with any one of the following limitations, provided the fire separation distance is greater than 5 feet (1524 mm):
1510.11 Photovoltaic systems. | Rooftop mounted photovoltaic systems shall be designed in accordance with this section.
1510.11.1 Wind resistance. | Rooftop mounted photovoltaic systems shall be designed for wind loads for component and cladding in accordance with Chapter 16 using an effective wind area based on the dimensions of a single unit frame.
1510.11.2 Fire classification. | Rooftop mounted photovoltaic panels and modules shall have the fire classification in accordance with Section 1505.9.
1510.11.3 Installation. | Rooftop mounted photovoltaic panels and modules shall be installed in accordance with the manufacturer’s instructions.
1510.11.4 Photovoltaic panels and modules. | Photovoltaic panels and modules Rooftop mounted on top of a roof shall be listed and labeled in accordance with UL 1703 and shall be installed in accordance with the manufacturer’s instructions.
1511.1.1 Slope. | Reroofs shall provide positive drainage.
1511.2 Structural and construction loads. | Structural roof components shall be capable of supporting the roof-covering system and the material and equipment loads that will be encountered during installation of the system.
1511.3 Roof replacement. | Roof replacement shall include the removal of all existing layers of roof coverings down to the roof deck. Exception: Where the existing roof assembly includes an ice barrier membrane that is adhered to the roof deck, the existing ice barrier membrane shall be permitted to remain in place and covered with an additional layer of ice barrier membrane in accordance with Section 1507.
1511.3.1 Roof recover. | The installation of a new roof covering over an existing roof covering shall be permitted where any of the following conditions occur:
1511.3.1.1 Exceptions. | A roof recover shall not be permitted where any of the following conditions occur: 1. Where the existing roof or roof covering is water soaked or has deteriorated to the point that the existing roof or roof covering is not adequate as a base for additional roofing. 2. Where the existing roof covering is slate, clay, cement or asbestos-cement tile. 3. Where the existing roof has two or more applications of any type of roof covering.
1511.4 Roof recovering. | Where the application of a new roof covering over wood shingle or shake roofs creates a combustible concealed space, the entire existing surface shall be covered with gypsum board, mineral fiber, glass fiber or other approved materials securely fastened in place.
1511.5 Reinstallation of materials. | Existing slate, clay or cement tile shall be permitted for reinstallation, except that damaged, cracked or broken slate or tile shall not be reinstalled. Existing vent flashing, metal edgings, drain outlets, collars and metal counterflashings shall not be reinstalled where rusted, damaged or deteriorated. Aggregate surfacing materials shall not be reinstalled.
1511.6 Flashings. | Flashings shall be reconstructed in accordance with manufacturer’s instructions. Metal flashing to which bituminous materials are to be adhered shall be primed prior to installation.
1511.7 Roof assembly. | Roof assembly shall be designed and constructed to meet the requirements of the New York City Energy Conservation Code.
1512.1 Solar photovoltaic panels/modules. | Solar photovoltaic panels/modules installed upon a roof or as an integral part of a roof assembly shall comply with the requirements of this code and the New York City Fire Code.
1512.1.1 Structural fire resistance. | The structural frame and roof construction supporting the load imposed upon the roof by the photovoltaic panels/modules shall comply with the requirements of Table 601 of this code. |  |  |  | See BC06 Tables&Figures
1512.2 Sustainable roofing zone. | A sustainable roofing zone shall be required on 100 percent of the roof. For such sustainable roofing zone: 1. A contiguous area of a sustainable roofing zone measuring less than 200 square feet (18.5 m2), or in the case of a building five stories or less in height where the main use or dominant occupancy is classified as Group R, such an area measuring less than 100 square feet (9.3 m2), shall be equipped with at least a solar photovoltaic electricity generating system if such system would accommodate at least 5.44 hp (4kW) of solar photovoltaic electricity generating capacity, as determined by the department; and 2. A sustainable roofing zone with a slope less than or equal to two units vertical in 12 units horizontal (17-percent) that would accommodate less than 5.44 hp (4kW) of solar photovoltaic electricity generating capacity, as determined by the department, shall be equipped with at least a green roof system. Exceptions: 1. Areas required to be set aside for setbacks or access pursuant to the New York City Fire Code, the New York City Construction Codes, or the Zoning Resolution of the City of New York. 2. Areas occupied by rooftop structures, mechanical equipment, towers, parapets, guardrails, solar thermal systems, and appurtenances. 3. Areas occupied by obstructions related to stormwater management practices including, but not limited to, cisterns, or reuse systems that are installed to comply with site connection or stormwater construction permits issued by the department of environmental protection. 4. Terraces on setbacks comprising less than 25 percent of the area of the largest floor plate in the building. 5. Recreational spaces that are principal to the use of the building on which the rooftop is located. 6. A roof assembly with a slope greater than two units vertical in 12 units horizontal (17-percent) that would accommodate less than 4kW of solar photovoltaic electricity generating capacity. 7. Areas where site conditions are determined by the department to be unfavorable to either a solar photovoltaic electricity generating system or a green roof system.

## BC16
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1601.1 Scope. | The provisions of this chapter shall govern the structural design of buildings, structures and portions thereof regulated by this code. | 1601.1 Scope. | The provisions of this chapter shall govern the structural design of buildings, structures and portions thereof regulated by this code.
1603.1 General. | Construction documents shall include drawings that show the sizes, sections and relative locations of structural members with floor levels, column centers and offsets fully dimensioned. The design loads and other information pertinent to the structural design required by Sections 1603.1.1 through 1603.1.10 shall be clearly indicated on such drawings of parts of the building or structure. Exception: In lieu of the requirements of Sections 1603.1.1 through 1603.1.10, construction documents for buildings constructed in accordance with the conventional light-frame construction provisions of Section 2308 shall include drawings that indicate the following structural design information: 1. Floor and roof dead and live loads. 2. Ground snow load, Pg. 3. Basic design wind speed, V, miles per hour (mph) (km/hr) and allowable stress design wind speed, Vasd, as determined in accordance with Section 1609.3.1 and wind exposure. 4. Seismic design category and site class. 5. Flood design data, if located in flood hazard areas. 6. Design load-bearing values of soils or rock under shallow foundations and/or the design load capacity of deep foundations.
1603.1.1 Floor live load. | The uniformly distributed, concentrated and impact floor live load used in the design shall be indicated for floor areas. Use of live load reduction in accordance with Section 1607.11 shall be indicated for each type of live load used in the design. | 1603.1 General. | Construction documents shall show the size, section and relative locations of structural members with floor levels, column centers and offsets dimensioned. The design loads and other information pertinent to the structural design required by Sections 1603.1.1 through 1603.1.9 shall be indicated on the construction documents. Exception: Construction documents for buildings constructed in accordance with the conventional light-frame construction provisions of Section 2308 shall indicate the following structural design information: 1. Floor and roof dead and live loads. 2. Ground snow load, pg. 3. Basic design wind speed, V, miles per hour (mph) (km/hr) and allowable stress design wind speed, Vasd, as determined in accordance with Section 1609.3.1 and wind exposure. 4. Seismic design category and site class. 5. Flood design data, if located in flood hazard areas established in Section 1612.3. 6. Design load-bearing values of soils. 7. Rain load data.
|  | 1603.1.1 Floor live load. | The uniformly distributed, concentrated and impact floor live load used in the design shall be indicated for floor areas. Use of live load reduction in accordance with Section 1607.12 shall be indicated for each type of live load used in the design.
1604.1 General. | Building, structures and parts thereof shall be designed and constructed in accordance with strength design, load and resistance factor design, allowable stress design, empirical design or conventional construction methods, as permitted by the applicable material chapters and referenced standards.
1604.2 Strength. | Buildings and other structures, and parts thereof, shall be designed and constructed to support safely the factored loads in load combinations defined in this code without exceeding the appropriate strength limit states for the materials of construction. Alternatively, buildings and other structures, and parts thereof, shall be designed and constructed to support safely the nominal loads in load combinations defined in this code without exceeding the appropriate specified allowable stresses for the materials of construction. Loads and forces for occupancies or uses not covered in this chapter shall be subject to the approval of the commissioner. | 1604.1 General. | Building, structures and parts thereof shall be designed and constructed in accordance with strength design, load and resistance factor design, allowable stress design, empirical design or conventional construction methods, as permitted by the applicable material chapters and referenced standards.
1604.3 Serviceability. | Structural systems and members thereof shall be designed to have adequate stiffness to limit deflections as indicated in Table 1604.3 of this code. Drift limits applicable to earthquake loading shall be in accordance with ASCE 7 Chapter 12, 13, 15 or 16, as applicable. |  |  |  | See BC16 Tables&Figures
1604.3.1 Deflections. | The deflections of structural members shall not exceed the more restrictive of the limitations of Sections 1604.3.2 through 1604.3.5 or that permitted by Table 1604.3. | 1604.2 Strength. | Buildings and other structures, and parts thereof, shall be designed and constructed to support safely the factored loads in load combinations defined in this code without exceeding the appropriate strength limit states for the materials of construction. Alternatively, buildings and other structures, and parts thereof, shall be designed and constructed to support safely the nominal loads in load combinations defined in this code without exceeding the appropriate specified allowable stresses for the materials of construction. |  | See BC16 Tables&Figures
1604.3.2 Reinforced concrete. | The deflection of reinforced concrete structural members shall not exceed that permitted by ACI 318.
1604.3.3 Steel. | The deflection of steel structural members shall not exceed that permitted by AISC 360, AISI S100, ASCE 8, SJI 100 or SJI 200, as applicable. | 1604.3 Serviceability. | Structural systems and members thereof shall be designed to have adequate stiffness to limit deflections as indicated in Table 1604.3. |  | See BC16 Tables&Figures
1604.3.4 Masonry. | The deflection of masonry structural members shall not exceed that permitted by TMS 402, as modified by Chapter 21 of this code.
1604.3.5 Aluminum. | The deflection of aluminum structural members shall not exceed that permitted by AA ADM1. | 1604.3.1 Deflections. | The deflections of structural members shall not exceed the more restrictive of the limitations of Sections 1604.3.2 through 1604.3.5 or that permitted by Table 1604.3. |  | See BC16 Tables&Figures
1604.3.6 Limits. | The deflection limits of Section 1604.3.1 shall be used unless more restrictive deflection limits are required by a referenced standard for the element or finish material.
1604.3.7 Framing supporting glass. | The deflection of framing members supporting glass subjected to 0.6 times the “component and cladding” wind loads shall not exceed either of the following: | 1604.3.2 Reinforced concrete. | The deflection of reinforced concrete structural members shall not exceed that permitted by ACI 318.
1604.4 Analysis. | Load effects on structural members and their connections shall be determined by methods of structural analysis that take into account equilibrium, general stability, geometric compatibility and both short- and long-term material properties.
1604.5 Risk category. | Each building and structure shall be assigned a risk category in accordance with Table 1604.5 of this code. Where a referenced standard specifies an occupancy category, the risk category shall not be taken as lower than the occupancy category specified therein. Where a referenced standard specifies that the assignment of a risk category be in accordance with ASCE 7, Table 1.5-1, Table 1604.5 of this code shall be used in lieu of ASCE 7, Table 1.5-1. | 1604.3.3 Steel. | The deflection of steel structural members shall not exceed that permitted by AISC 360, AISI S100, ASCE 8, SJI 100 or SJI 200, as applicable. |  | See BC16 Tables&Figures
1604.5.1 Multiple occupancies. | Where a building or structure is occupied by two or more occupancies not included in the same risk category, it shall be assigned the classification of the highest risk category corresponding to the various occupancies. Where buildings or structures have two or more portions that are structurally separated, each portion shall be separately classified. Where a separated portion of a building or structure provides required access to, required egress from or shares life safety components with another portion having a higher risk category, both portions shall be assigned to the higher risk category. Exception: Where a storm shelter designed and constructed in accordance with ICC 500 is provided in a building, structure or portion thereof normally occupied for other purposes, the risk category for the normal occupancy of the building shall apply unless the storm shelter is a designated emergency shelter in accordance with Table 1604.5 of this code. |  |  |  | See BC16 Tables&Figures
1604.6 In-situ load tests. | The commissioner is authorized to require an engineering analysis or a load test, or both, of any construction whenever there is reason to question the safety of the construction for the intended occupancy. Engineering analysis and load tests shall be conducted in accordance with Section 1708. | 1604.3.4 Masonry. | The deflection of masonry structural members shall not exceed that permitted by TMS 402.
1604.7 Preconstruction load tests. | Materials and methods of construction that are not capable of being designed by approved engineering analysis or that do not comply with the applicable referenced standards, or alternative test procedures in accordance with Section 1709, shall be load tested in accordance with Section 1710. | 1604.3.5 Aluminum. | The deflection of aluminum structural members shall not exceed that permitted by AA ADM.
1604.8 Anchorage. | Buildings and other structures, and portions thereof, shall be provided with anchorage in accordance with Sections 1604.8.1 through 1604.8.4, as applicable. | 1604.3.6 Limits. | The deflection limits of Section 1604.3.1 shall be used unless more restrictive deflection limits are required by a referenced standard for the element or finish material.
1604.8.1 General. | Anchorage of the roof to walls and columns, and of walls and columns to foundations, shall be provided to resist the uplift and sliding forces that result from the application of the prescribed loads and load combinations. | 1604.3.7 Framing supporting glass. | The deflection of framing members supporting glass subjected to 0.6 times the “component and cladding” wind loads shall not exceed either of the following:
1604.8.2 Structural walls. | Walls that provide vertical load-bearing resistance or lateral shear resistance for a portion of the structure shall be anchored to the roof and to all floors and members that provide lateral support for the wall or that are supported by the wall. The connections shall be capable of resisting the horizontal forces specified in Section 1.4.4 of ASCE 7 for walls of structures assigned to Seismic Design Category A and to Section 12.11 of ASCE 7 for walls of structures assigned to all other seismic design categories. Required anchors in masonry walls of hollow units or cavity walls shall be embedded in a reinforced grouted structural element of the wall. See Sections 1609 of this code for wind design requirements and Section 1613 of this code for earthquake design requirements. | 1604.4 Analysis. | Load effects on structural members and their connections shall be determined by methods of structural analysis that take into account equilibrium, general stability, geometric compatibility and both short- and long-term material properties.
1604.8.3 Decks. | Where supported by attachment to an exterior wall, decks shall be positively anchored to the primary structure and designed for both vertical and lateral loads as applicable. Such attachment shall not be accomplished by the use of toenails or nails subject to withdrawal. Where positive connection to the primary building structure cannot be verified during inspection, decks shall be self-supporting. Connections of decks with cantilevered framing members to exterior walls or other framing members shall be designed for both of the following: | 1604.5 Risk category. | Each building and structure shall be assigned a risk category in accordance with Table 1604.5. Where a referenced standard specifies an occupancy category, the risk category shall not be taken as lower than the occupancy category specified therein. Where a referenced standard specifies that the assignment of a risk category be in accordance with ASCE 7, Table 1.5-1, Table 1604.5 shall be used in lieu of ASCE 7, Table 1.5-1. Exception: The assignment of buildings and structures to Tsunami Risk Categories III and IV is permitted to be in accordance with Section 6.4 of ASCE 7. |  | See BC16 Tables&Figures
1604.9 Wind and seismic detailing. | Lateral force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code and ASCE 7 Chapters 11, 12, 13, 15, 17 and 18 of this code as applicable, even when wind load effects are greater than seismic load effects. Where ASCE 7 references Chapter 14 of ASCE 7 those references shall not apply, except as specifically required in this code. | 1604.5.1 Multiple occupancies. | Where a building or structure is occupied by two or more occupancies not included in the same risk category, it shall be assigned the classification of the highest risk category corresponding to the various occupancies. Where buildings or structures have two or more portions that are structurally separated, each portion shall be separately classified. Where a separated portion of a building or structure provides required access to, required egress from or shares life safety components with another portion having a higher risk category, both portions shall be assigned to the higher risk category. Exception: Where a storm shelter designed and constructed in accordance with ICC 500 is provided in a building, structure or portion thereof normally occupied for other purposes, the risk category for the normal occupancy of the building shall apply unless the storm shelter is a designated emergency shelter in accordance with Table 1604.5. |  | See BC16 Tables&Figures
1604.10 Loads on storm shelters. | Loads and load combinations on storm shelters shall be determined in accordance with ICC 500. | 1604.6 In-situ load tests. | The building official is authorized to require an engineering analysis or a load test, or both, of any construction whenever there is reason to question the safety of the construction for the intended occupancy. Engineering analysis and load tests shall be conducted in accordance with Section 1708.
1605.1 General. | Buildings and other structures and portions thereof shall be designed to resist: | 1604.7 Preconstruction load tests. | Materials and methods of construction that are not capable of being designed by approved engineering analysis or that do not comply with the applicable referenced standards, or alternative test procedures in accordance with Section 1707, shall be load tested in accordance with Section 1709.
1605.1.1 Stability. | Regardless of which load combinations are used to design for strength, where overall structure stability (such as stability against overturning, sliding, or buoyancy) is being verified, use of the load combinations specified in Section 1605.2 or 1605.3 shall be permitted. Where the load combinations specified in Section 1605.2 are used, strength reduction factors applicable to soil resistance shall be provided by a registered design professional. The stability of retaining walls shall be verified in accordance with Section 1807.2. | 1604.8 Anchorage. | Buildings and other structures, and portions thereof, shall be provided with anchorage in accordance with Sections 1604.8.1 through 1604.8.3, as applicable.
|  | 1604.8.1 General. | Anchorage of the roof to walls and columns, and of walls and columns to foundations, shall be provided to resist the uplift and sliding forces that result from the application of the prescribed loads.
1606.1 General. | Dead loads are those loads defined in Chapter 2 of this code. Dead loads shall be considered permanent loads. | 1604.8.2 Structural walls. | Walls that provide vertical load-bearing resistance or lateral shear resistance for a portion of the structure shall be anchored to the roof and to all floors and members that provide lateral support for the wall or that are supported by the wall. The connections shall be capable of resisting the horizontal forces specified in Section 1.4.4 of ASCE 7 for walls of structures assigned to Seismic Design Category A and to Section 12.11 of ASCE 7 for walls of structures assigned to all other seismic design categories. Required anchors in masonry walls of hollow units or cavity walls shall be embedded in a reinforced grouted structural element of the wall. See Sections 1609 for wind design requirements and 1613 for earthquake design requirements.
|  | 1604.8.3 Decks. | Where supported by attachment to an exterior wall, decks shall be positively anchored to the primary structure and designed for both vertical and lateral loads as applicable. Such attachment shall not be accomplished by the use of toenails or nails subject to withdrawal. Where positive connection to the primary building structure cannot be verified during inspection, decks shall be self-supporting. Connections of decks with cantilevered framing members to exterior walls or other framing members shall be designed for both of the following:
|  | 1604.9 Wind and seismic detailing. | Lateral force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code and ASCE 7 Chapters 11, 12, 13, 15, 17 and 18 as applicable, even where wind load effects are greater than seismic load effects. Exception: References within ASCE 7 to Chapter 14 shall not apply, except as specifically required herein.
|  | 1604.10 Loads on storm shelters. | Loads and load combinations on storm shelters shall be determined in accordance with ICC 500.
1607.1 General. | Live loads are those loads defined in Chapter 2 of this code. | 1605.1 General. | Buildings and other structures and portions thereof shall be designed to resist the strength load combinations specified in ASCE 7, Section 2.3, the allowable stress design load combinations specified in ASCE 7, Section 2.4, or the alternative allowable stress design load combinations of Section 1605.2. Exceptions: 1. The modifications to load combinations of ASCE 7 Section 2.3, ASCE 7 Section 2.4, and Section 1605.2 specified in ASCE 7 Chapters 18 and 19 shall apply. 2. Where the allowable stress design load combinations of ASCE 7 Section 2.4 are used, flat roof snow loads of 30 pounds per square foot (1.44 kN/m2) and roof live loads of 30 pounds per square foot (1.44 kN/m2) or less need not be combined with seismic load. Where flat roof snow loads exceed 30 pounds per square foot (1.44 kN/m2), 20 percent shall be combined with seismic loads. 3. Where the allowable stress design load combinations of ASCE 7 Section 2.4 are used, crane hook loads need not be combined with roof live loads or with more than three-fourths of the snow load or one-half of the wind loads.
1607.2 Loads not specified. | For occupancies or uses not designated in Table 1607.1, the live load shall be determined in accordance with a method approved by the commissioner. | 1605.1.1 Stability. | Regardless of which load combinations are used to design for strength, where overall structure stability (such as stability against overturning, sliding, or buoyancy) is being verified, use of the load combinations specified in Section 2.3 or 2.4 of ASCE 7, and in Section 1605.2 shall be permitted. Where the load combinations specified in ASCE 7, Section 2.3 are used, strength reduction factors applicable to soil resistance shall be provided by a registered design professional. The stability of retaining walls shall be verified in accordance with Section 1807.2.3. |  | See BC16 Tables&Figures
1607.3 Uniform live loads. | The live loads used in the design of buildings and other structures shall be the maximum loads expected by the intended use or occupancy but shall in no case be less than the minimum uniformly distributed live loads given in Table 1607.1. | 1606.1 General. | Dead loads are those loads defined in Chapter 2 of this code. Dead loads shall be considered to be permanent loads. |  | See BC16 Tables&Figures
1607.4 Concentrated live loads. | Floors, roofs and other similar surfaces shall be designed to support the uniformly distributed live loads prescribed in Section 1607.3 or the concentrated live loads, given in Table 1607.1, whichever produces the greater load effects. Unless otherwise specified, the indicated concentration shall be assumed to be uniformly distributed over an area of 2½ feet by 2½ feet (762 mm by 762 mm) and shall be located so as to produce the maximum load effects in the structural members. |  |  |  | See BC16 Tables&Figures
1607.5 Partition loads. | In office buildings and in other buildings where partition locations are subject to change, provisions for partition weight shall be made, whether or not partitions are shown on the construction documents, unless the specified live load is 80 psf (3.83 kN/m2) or greater. Weights of all partitions shall be considered, using either actual weights at locations shown on the plans or the equivalent uniform load given in Section 1607.5.2. Partition loads shall be taken as superimposed dead loads. | 1607.1 General. | Live loads are those loads defined in Chapter 2 of this code.
1607.6 Helipads. | Helipads shall be designed for the following live loads: | 1607.2 Loads not specified. | For occupancies or uses not designated in Section 1607, the live load shall be determined in accordance with a method approved by the building official.
|  | 1607.3 Uniform live loads. | The live loads used in the design of buildings and other structures shall be the maximum loads expected by the intended use or occupancy but shall not be less than the minimum uniformly distributed live loads given in Table 1607.1. |  | See BC16 Tables&Figures
|  | 1607.4 Concentrated live loads. | Floors, roofs and other similar surfaces shall be designed to support the uniformly distributed live loads prescribed in Section 1607.3 or the concentrated live loads, given in Table 1607.1, whichever produces the greater load effects. Unless otherwise specified, the indicated concentration shall be assumed to be uniformly distributed over an area of 21/2 feet by 21/2 feet (762 mm by 762 mm) and shall be located so as to produce the maximum load effects in the structural members. |  | See BC16 Tables&Figures
|  | 1607.5 Partition loads. | In office buildings and in other buildings where partition locations are subject to change, provisions for partition weight shall be made, whether or not partitions are shown on the construction documents, unless the specified live load is 80 psf (3.83 kN/m2) or greater. The partition load shall be not less than a uniformly distributed live load of 15 psf (0.72 kN/m2).
|  | 1607.6 Helipads. | Helipads shall be designed for the following live loads:
1608.1 General. | Design snow loads shall be determined in accordance with Chapter 7 of ASCE 7, but the design roof load shall not be less than that determined by Section 1607.
1608.2 Ground snow loads. | The ground snow loads to be used in determining the design snow loads for roofs is 25 psf (1.2 kN/m2). | 1608.1 General. | Design snow loads shall be determined in accordance with Chapter 7 of ASCE 7, but the design roof load shall be not less than that determined by Section 1607.
1608.3 Ponding instability. | Susceptible bays of roofs shall be evaluated for ponding instability in accordance with Chapters 7 and 8 of ASCE 7.
1609.1 Applications. | Buildings, structures and parts thereof shall be designed to withstand the minimum wind loads prescribed herein. Decreases in wind loads shall not be made for the effect of shielding by other structures. | 1608.2 Ground snow loads. | The ground snow loads to be used in determining the design snow loads for roofs shall be determined in accordance with ASCE 7 or Figures 1608.2(1) and 1608.2(2) for the contiguous United States and Table 1608.2 for Alaska. Site-specific case studies shall be made in areas designated “CS” in Figures 1608.2(1) and 1608.2(2). Ground snow loads for sites at elevations above the limits indicated in Figures 1608.2(1) and 1608.2(2) and for all sites within the CS areas shall be approved. Ground snow load determination for such sites shall be based on an extreme value statistical analysis of data available in the vicinity of the site using a value with a 2-percent annual probability of being exceeded (50-year mean recurrence interval). Snow loads are zero for Hawaii, except in mountainous regions as approved by the building official. |  | See BC16 Tables&Figures
1609.1.1 Determination of wind loads. | Wind loads on every building or structure shall be determined in accordance with Chapters 26 to 31 of ASCE 7. The type of opening protection required, the basic design wind speed, V, and the exposure category for a site is permitted to be determined in accordance with Section 1609. Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered. Exceptions: 1. Subject to the limitations of Section 1609.1.1.1, the provisions of ICC 600 shall be permitted for applicable Group R-2 and R-3 buildings. 2. Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AWC WFCM. 3. Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AISI S230. 4. Designs using NAAMM FP 1001. 5. Designs using TIA-222 for antenna-supporting structures and antennas. 6. Wind tunnel tests in accordance with ASCE 49 and Sections 31.4 and 31.5 of ASCE 7. The wind speeds in Section 1609.3 are basic design wind speeds, V, and shall be converted in accordance with Section 1609.3.1 to allowable stress design wind speeds, Vasd, when the provisions of the standards referenced in Exceptions 4 and 5 are used.
1609.1.1.1 Applicability. | The provisions of ICC 600 are applicable only to buildings located within Exposure B or C as defined in Section 1609.4. The provisions of ICC 600, AWC WFCM and AISI S230 shall not apply to buildings sited on the upper half of an isolated hill, ridge or escarpment meeting the following conditions: | 1608.3 Ponding instability. | Susceptible bays of roofs shall be evaluated for ponding instability in accordance with Chapters 7 and 8 of ASCE 7.
|  | 1609.1 Applications. | Buildings, structures and parts thereof shall be designed to withstand the minimum wind loads prescribed herein. Decreases in wind loads shall not be made for the effect of shielding by other structures.
|  | 1609.1.1 Determination of wind loads. | Wind loads on every building or structure shall be determined in accordance with Chapters 26 to 30 of ASCE 7. The type of opening protection required, the basic design wind speed, V, and the exposure category for a site is permitted to be determined in accordance with Section 1609 or ASCE 7. Wind shall be assumed to come from any horizontal direction and wind pressures shall be assumed to act normal to the surface considered. Exceptions: 1. Subject to the limitations of Section 1609.1.1.1, the provisions of ICC 600 shall be permitted for applicable Group R-2 and R-3 buildings. 2. Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AWC WFCM. 3. Subject to the limitations of Section 1609.1.1.1, residential structures using the provisions of AISI S230. 4. Designs using NAAMM FP 1001. 5. Designs using TIA-222 for antenna-supporting structures and antennas, provided that the horizontal extent of Topographic Category 2 escarpments in Section 2.6.6.2 of TIA-222 shall be 16 times the height of the escarpment. 6. Wind tunnel tests in accordance with ASCE 49 and Sections 31.4 and 31.5 of ASCE 7. The wind speeds in Figures 1609.3(1) through 1609.3(12) are basic design wind speeds, V, and shall be converted in accordance with Section 1609.3.1 to allowable stress design wind speeds, Vasd, when the provisions of the standards referenced in Exceptions 4 and 5 are used.
1609.3 Basic design wind speed. | The basic design wind speed, V, in mph, for determining wind speed shall be that of Table 1609.3. |  |  |  | See BC16 Tables&Figures
1609.3.1 Wind speed conversion. | Where required, the basic design wind speed, V, of Table 1609.3 shall be converted to allowable stress design wind speed, Vasd, using Equation 16-40. | 1609.1.1.1 Applicability. | The provisions of ICC 600 are applicable only to buildings located within Exposure B or C as defined in Section 1609.4. The provisions of ICC 600, AWC WFCM and AISI S230 shall not apply to buildings sited on the upper half of an isolated hill, ridge or escarpment meeting all of the following conditions: |  | See BC16 Tables&Figures
1609.4 Exposure category. | For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed.
1609.4.1 Wind directions and sectors. | For each selected wind direction at which the wind loads are to be evaluated, the exposure of the building or structure shall be determined for the two upwind sectors extending 45 degrees (0.79 rad) either side of the selected wind direction. The exposures in these two sectors shall be determined in accordance with Sections 1609.4.2 and 1609.4.3 and the exposure resulting in the highest wind loads shall be used to represent winds from that direction.
1609.4.2 Surface roughness categories. | A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the categories defined below, for the purpose of assigning an exposure category as defined in Section 1609.4.3.
1609.4.3 Exposure categories. | An exposure category shall be determined in accordance with the following:
1609.5 Roof systems. | Roof systems shall be designed and constructed in accordance with Sections 1609.5.1 through 1609.5.3, as applicable.
1609.5.1 Roof deck. | The roof deck shall be designed to withstand the wind pressures determined in accordance with Section 1609.1.1 for buildings of any height. | 1609.3 Basic design wind speed. | The basic design wind speed, V, in mph, for the determination of the wind loads shall be determined by Figures 1609.3(1) through 1609.3(12). The basic design wind speed, V, for use in the design of Risk Category II buildings and structures shall be obtained from Figures 1609.3(1), 1609.3(5) and 1609.3(6). The basic design wind speed, V, for use in the design of Risk Category III buildings and structures shall be obtained from Figures 1609.3(2), 1609.3(7) and 1609.3(8). The basic design wind speed, V, for use in the design of Risk Category IV buildings and structures shall be obtained from Figures 1609.3(3), 1609.3(9) and 1609.3(10). The basic design wind speed, V, for use in the design of Risk Category I buildings and structures shall be obtained from Figures 1609.3(4), 1609.3(11) and 1609.3(12). The basic design wind speed, V, for the special wind regions indicated near mountainous terrain and near gorges shall be in accordance with local jurisdiction requirements. The basic design wind speeds, V, determined by the local jurisdiction shall be in accordance with Chapter 26 of ASCE 7.
1609.5.2 Roof coverings. | Roof coverings shall comply with Section 1609.5.1. Exceptions: 1. Rigid tile roof coverings that are air permeable and installed over a roof deck complying with Section 1609.5.1 are permitted to be designed in accordance with Section 1609.5.3. 2. Asphalt shingles installed over a roof deck complying with Section 1609.5.1 shall comply with the wind-resistance requirements of Section 1504.1.1. | 1609.3.1 Wind speed conversion. | Where required, the basic design wind speeds of Figures 1609.3(1) through 1609.3(12) shall be converted to allowable stress design wind speeds, Vasd, using Table 1609.3.1 or Equation 16-17. (Equation 16-17) where: Vasd = Allowable stress design wind speed applicable to methods specified in Exceptions 4 and 5 of Section 1609.1.1. V = Basic design wind speeds determined from Figures 1609.3(1) through 1609.3(12). |  | See BC16 Tables&Figures
1609.1.2.2 Application of ASTM E1996. | The text of Section 6.2.2 of ASTM E1996 shall be substituted as follows: | 1609.4 Exposure category. | For each wind direction considered, an exposure category that adequately reflects the characteristics of ground surface irregularities shall be determined for the site at which the building or structure is to be constructed. Account shall be taken of variations in ground surface roughness that arise from natural topography and vegetation as well as from constructed features.
1609.5.3 Rigid tile. | Wind loads on rigid tile roof coverings shall be determined in accordance with the following equation: | 1609.4.1 Wind directions and sectors. | For each selected wind direction at which the wind loads are to be evaluated, the exposure of the building or structure shall be determined for the two upwind sectors extending 45 degrees (0.79 rad) either side of the selected wind direction. The exposures in these two sectors shall be determined in accordance with Sections 1609.4.2 and 1609.4.3 and the exposure resulting in the highest wind loads shall be used to represent winds from that direction.
1609.1.2.3 Garage doors. | Garage door glazed opening protection for wind-borne debris shall meet the requirements of an approved impact-resisting standard or ANSI/DASMA 115. | 1609.4.2 Surface roughness categories. | A ground surface roughness within each 45-degree (0.79 rad) sector shall be determined for a distance upwind of the site as defined in Section 1609.4.3 from the following categories, for the purpose of assigning an exposure category as defined in Section 1609.4.3.
1609.1.3 Minimum wind loads. | The design wind pressure, p, used in the design of the main wind-force-resisting system shall not be less than 16 psf (0.766 kN/m2) multiplied by the area of the building or structure projected on a vertical plane normal to the wind direction. In the calculation of design wind pressure, p, used in the design of components and cladding for buildings, the algebraic sum of the pressures acting on opposite faces shall be taken into account. The design pressure for components and cladding of buildings shall not be less than 32 psf (1.533 kN/m2) acting in either direction normal to the surface. The design force for open buildings and other structures shall not be less than 16 psf (0.766 kN/m2) multiplied by the area Af. | 1609.4.3 Exposure categories. | An exposure category shall be determined in accordance with the following:
1609.1.4 Anchorage against overturning, uplift and sliding. | Structural members and systems and components and cladding in a building or structure shall be anchored to resist wind-induced overturning, uplift and sliding and to provide continuous load paths for these forces to the foundation. | 1609.5 Roof systems. | Roof systems shall be designed and constructed in accordance with Sections 1609.5.1 through 1609.5.3, as applicable.
1611.1 Design rain loads. | Each portion of a roof shall be designed to sustain the load of rainwater that will accumulate on it if the primary drainage system for that portion is blocked plus the uniform load caused by water that rises above the inlet of the secondary drainage system at its design flow.
1609.1.5 Wind and seismic detailing. | Lateral-force-resisting systems shall meet seismic detailing requirements and limitations prescribed in this code, even when wind code prescribed load effects are greater than seismic load effects. | 1609.5.1 Roof deck. | The roof deck shall be designed to withstand the wind pressures determined in accordance with ASCE 7.
1611.2 Ponding instability. | Susceptible bays of roofs shall be evaluated for ponding instability in accordance with Section 8.4 ASCE 7.
1609.1.6 Wind tunnel test limitations. | The lower limit on pressures for main wind-force-resisting systems and components and cladding shall be in accordance with this section. | 1609.5.2 Roof coverings. | Roof coverings shall comply with Section 1609.5.1. Exception: Rigid tile roof coverings that are air permeable and installed over a roof deck complying with Section 1609.5.1 are permitted to be designed in accordance with Section 1609.5.3. Asphalt shingles installed over a roof deck complying with Section 1609.5.1 shall comply with the wind-resistance requirements of Section 1504.2.
1611.3 Controlled drainage. | Roofs equipped with hardware to control the rate of drainage shall be equipped with a secondary drainage system at a higher elevation that limits accumulation of water on the roof above that elevation. Such roofs shall be designed to sustain the load of rainwater that will accumulate on them to the elevation of the secondary drainage system plus the uniform load caused by water that rises above the inlet of the secondary drainage system at its design flow determined from Section 1611.1. Such roofs shall also be checked for ponding instability in accordance with Section 1611.2.
1609.1.6.1 Lower limits on main wind-force-resisting system. | Base overturning moments determined from wind tunnel testing shall be limited to not less than 80 percent of the design base overturning moments determined in accordance with Section 27.2 of ASCE 7 unless the wind tunnel results and testing procedure are peer reviewed by an independent wind tunnel laboratory. In no case shall the limiting value be less than 70 percent of the design base overturning moments determined in accordance with Section 27.2 of ASCE 7. | 1609.5.3 Rigid tile. | Wind loads on rigid tile roof coverings shall be determined in accordance with the following equation:
1612.1 General. | Buildings and other structures located in whole or in part in flood hazard areas shall meet the requirements of Section 5.3 of ASCE 7 and Appendix G of this code. The structural design shall be based on the design loads stated in Section 5.4 of ASCE 7, the load combinations of Section 1605, and Appendix G of this code.
1609.1.6.2 Lower limits on components and cladding. | The design pressures for components and cladding on walls or roofs shall be selected as the greater of: (i) the wind tunnel test results; or (ii) 80 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 30.5 of ASCE 7, unless the wind tunnel results and testing procedure are peer reviewed by an independent wind tunnel laboratory. In no case shall the limiting value be less than 70 percent of the pressure obtained for Zone 4 for walls and Zone 1 for roofs, as determined in Section 30.5 of ASCE 7.
1609.1.6.3 Scope of peer review by independent wind tunnel laboratory. | When applicable, the peer reviewer of the wind tunnel test shall:
1609.2 Definitions. | For the purposes of Section 1609 and as used elsewhere in the code, the following terms are defined in Chapter 2: | 1611.1 Design rain loads. | Each portion of a roof shall be designed to sustain the load of rainwater as per the requirements of Chapter 8 of ASCE 7. The design rainfall shall be based on the 100-year 15-minute duration event, or on other rainfall rates determined from approved local weather data. Alternatively,​ a design rainfall of twice the 100-year hourly rainfall rate indicated in Figures 1611.1(1) through 1611.1(5) shall be permitted.
1609.3.2 Wind speed for serviceability design. | Table 1609.3.2 presents 3-second gust wind speeds for mean recurrence intervals (MRI) of 10, 25, 50 and 100 years. These wind speeds may be used for serviceability applications such as drift and habitability. |  |  |  | See BC16 Tables&Figures
1609.6 Simplified design procedure. | Use of the simplified design procedure shall comply with Sections 1609.6.1 through 1609.6.5. | 1611.2 Ponding instability. | Susceptible bays of roofs shall be evaluated for ponding instability in accordance with Chapters 7 and 8 of ASCE 7.
1609.6.1 Scope. | The procedures in Section 1609.6 shall be permitted to be used for determining and applying wind pressures in the design of enclosed buildings in Risk Category I and II as listed below:
1609.6.2 Main windforce-resisting systems. | Main windforce-resisting systems shall comply with the following: | 1611.3 Controlled drainage. | Roofs equipped with hardware to control the rate of drainage shall be equipped with a secondary drainage system at a higher elevation that limits accumulation of water on the roof above that elevation. Such roofs shall be designed to sustain the load of rainwater that will accumulate on them to the elevation of the secondary drainage system plus the uniform load caused by water that rises above the inlet of the secondary drainage system at its design flow determined from Section 1611.1. Such roofs shall be checked for ponding instability in accordance with Section 1611.2.
1609.6.3 Design wind load cases. | The main windforce-resisting system of buildings, whose wind loads have been determined pursuant to Section 1609.6.1, shall be designed for wind load cases as defined below:
1609.6.4 Components and cladding. | Net design wind positive and negative pressures (pressure and suction) for the components and cladding of buildings represent the net pressures (sum of internal and external) to be applied normal to each building surface. The net design wind positive and negative pressures shall not be less than 48 psf (12.30 kN/m2), except at the corners of the building with a width equivalent to 10 percent of the building’s width at its side, the net design wind negative pressure for the components and cladding shall not be less than: (i) 72 psf (3.46 kN/m2) for the portion of the building between 200 feet (60 960 mm) to 300 feet (91 440 mm) height above ground and (ii) 64 psf (3.07 kN/m2) for the portion of the building between 100 feet (30 480 mm) to 199 feet (60 656 mm) in height above ground. | 1612.1 General. | Within flood hazard areas as established in Section 1612.3, all new construction of buildings, structures and portions of buildings and structures, including substantial improvement and restoration of substantial damage to buildings and structures, shall be designed and constructed to resist the effects of flood hazards and flood loads. For buildings that are located in more than one flood hazard area, the provisions associated with the most restrictive flood hazard area shall apply.
1609.6.5 Roof. | The design pressure and suction acting over the entire roof including purlins, roofing, and other roof elements (including their fastenings) shall be not less than 48 psf (2.30 kN/m2).
1609.7 Attached canopies on buildings. | Canopies attached to buildings shall comply with Section 1609.7.1 or 1609.7.2, as applicable.
1609.7.1 Buildings with h≤60 ft. | The design wind pressure for canopies attached to walls of buildings with h≤60 ft. shall follow Chapter 30 of ASCE 7.
1609.7.2 Buildings with h>60 ft. | The design wind pressure for canopies attached to walls of buildings with h>60 ft. and hc/h< 0.5, as shown on Figure 1609.7, shall be from the following equation:
1609.8 Wind load on structures during construction. | Structures during construction shall comply with Sections 1609.8.1 and 1609.8.2.
1609.8.1 Design wind speed. | Design wind speed during construction for a construction period of less than 5 years may be reduced as follows:
1609.8.2 Frameworks without cladding. | For unenclosed frames and elements, the appropriate drag factors and wind effect on successive elements shall be accounted for per recognized standards and references, or in accordance with suitable wind tunnel testing. |  |  |  | See BC16 Tables&Figures
1610.1 General. | Foundation walls and retaining walls shall be designed to resist lateral soil loads. Soil loads specified in Table 1610.1 shall be used as the minimum design lateral soil loads unless determined otherwise by a geotechnical investigation in accordance with Section 1803. Foundation walls and other walls in which horizontal movement is restricted at the top shall be designed for at-rest pressure. Retaining walls free to move and rotate at the top shall be permitted to be designed for active pressure. Design lateral pressure from surcharge loads shall be added to the lateral earth pressure load. Design lateral pressure shall be increased if soils at the site are expansive. Foundation walls shall be designed to support the weight of the full hydrostatic pressure of undrained backfill unless a drainage system is installed in accordance with Sections 1805.4.2 and 1805.4.3. Exception: Foundation walls extending not more than 8 feet (2438.4 mm) below grade and laterally supported at the top by flexible diaphragms shall be permitted to be designed for active pressure. |  |  |  | See BC16 Tables&Figures
1612.2 Reserved.
1612.3 Reserved.
1612.4 Reserved.
1612.5 Reserved.
1613.1 Scope. | Every structure, and portion thereof, including nonstructural components that are permanently attached to structures and their supports and attachments, shall be designed and constructed to resist the effects of earthquake motions in accordance with ASCE 7, excluding Chapter 14 and Appendix 11A. The seismic design category for a structure shall be determined in accordance with either Section 1613 or ASCE 7. Exceptions: 1. One- and two-family dwellings three stories or less in height. 2. The seismic force-resisting system of wood-frame buildings that conform to the provisions of Section 2308 are not required to be analyzed as specified in this section. 3. Agricultural storage structures intended only for incidental human occupancy. 4. Structures that require special consideration of their response characteristics and environment that are not addressed by this code or ASCE 7 and for which other regulations provide seismic criteria, such as vehicular bridges, electrical transmission towers, hydraulic structures, buried utility lines and their appurtenances and nuclear reactors.
1613.2 Definitions. | The following terms are defined in Chapter 2:
1613.3 Seismic ground motion values. | Seismic ground motion values shall be determined in accordance with this section.
1613.3.1 Mapped acceleration parameters. | The mapped maximum considered earthquake spectral response acceleration at short periods (SS) shall be 0.296 g and at 1-s period (S1) shall be 0.061 g. The mapped long-period transition period (TL) shall be 6.0 seconds. Alternatively, electronic values of mapped acceleration parameters Ss and S1 and other seismic design parameters provided at the U.S. Geological Survey (USGS) website at https://doi.org/10.5066/F7NK3C76 may be used as per the guidelines of ASCE 7, Section 11.4.
1613.3.2 Site class definitions. | Based on the site soil properties, the site shall be classified as Site Class A, B, C, D, E or F in accordance with Chapter 20 of ASCE 7, and this code. Where the soil properties are not known in sufficient detail to determine the site class, Site Class D shall be used unless the commissioner or geotechnical data determines Site Class E or F soils are present at the site.
1613.3.3 Site coefficients and adjusted maximum considered earthquake spectral response acceleration parameters. | The maximum considered earthquake spectral response acceleration for short periods, SMS, and at 1-second period, SM1, adjusted for site class effects shall be determined by Equations 16-44 and 16-45, respectively: Exception: When electronic values of mapped acceleration parameters are used as per Section 1613.3.1 of this code, the site coefficients, Fa and Fv, cannot be taken from Tables 1613.3.3(1) and 1613.3.3(2) of this code. Rather, general procedures in Chapter 11 of ASCE 7 shall be followed to determine Fa and Fv.
1613.3.4 Design spectral response acceleration parameters. | Five-percent damped design spectral response acceleration at short periods, SDS, and at 1-s period, SD1, shall be determined from Equations 16-46 and 16-47, respectively:
1613.3.4.1 Site classification for seismic design. | Site classification for Site Class C, D or E shall be determined from Table 1613.3.4.1. The notations presented below apply to only materials encountered above rock meeting Class 1a, 1b, or 1c as defined in Section 1803 or rock with shear wave velocity greater than 2,500 feet per second (762 meters per second) to a maximum depth of 100 feet (30 480 mm). Profiles containing distinctly different soil and rock layers shall be subdivided into those layers designated by a number that ranges from 1 to n at the bottom where there is a total of n distinct layers in the upper 100 feet (30 480 mm). The symbol i then refers to any one of the layers between 1 and n. For situations in which site investigations, performed in accordance with Chapter 20 of ASCE 7, reveal rock conditions consistent with Site Class B, but site-specific velocity measurements are not made, the site coefficients Fa, Fv, and FPGA shall be taken as unity (1.0). |  |  |  | See BC16 Tables&Figures
1613.3.4.1.1 Steps for classifying a site. | The following steps shall be performed during the classification of a site:
1613.3.5 Determination of seismic design category. | All structures shall be assigned a seismic design category based on their risk category and the design spectral response acceleration parameters, SDS and SD1, determined in accordance with Section 1613.3.4 of this code or the site-specific procedures of ASCE 7. Each building and structure shall be assigned to the seismic design category in accordance with Table 1613.3.5 of this code, irrespective of the fundamental period of vibration of the structure, T. Exception: When electronic values of mapped acceleration parameters are used as per Section 1613.3.1, the seismic design category for Risk Category IV structures shall not differ from the values in Table 1613.3.5. | 1613.1 Scope. | Every structure, and portion thereof, including nonstructural components that are permanently attached to structures and their supports and attachments, shall be designed and constructed to resist the effects of earthquake motions in accordance with Chapters 11, 12, 13, 15, 17 and 18 of ASCE 7, as applicable. The seismic design category for a structure is permitted to be determined in accordance with Section 1613 or ASCE 7. Exceptions: 1. Detached one- and two-family dwellings, assigned to Seismic Design Category A, B or C, or located where the mapped short-period spectral response acceleration, SS, is less than 0.4 g. 2. The seismic force-resisting system of wood-frame buildings that conform to the provisions of Section 2308 are not required to be analyzed as specified in this section. 3. Agricultural storage structures intended only for incidental human occupancy. 4. Structures that require special consideration of their response characteristics and environment that are not addressed by this code or ASCE 7 and for which other regulations provide seismic criteria, such as vehicular bridges, electrical transmission towers, hydraulic structures, buried utility lines and their appurtenances and nuclear reactors. 5. References within ASCE 7 to Chapter 14 shall not apply, except as specifically required herein. |  | See BC16 Tables&Figures
1613.3.5.1 Alternative seismic design category determination. | The seismic design category is permitted to be determined from Table 11.6-1 of ASCE 7 alone, except for Risk Category IV structures for which Table 1613.3.5 of this code shall be used, when all of the following apply: |  |  | See BC11 Tables&Figures | See BC16 Tables&Figures
1613.3.5.2 Simplified design procedure. | Where the alternate simplified design procedure of ASCE 7 is used, the seismic design category shall be determined in accordance with ASCE 7.
1613.4 Structural separations. | All structures shall be separated from adjacent structures. When a structure adjoins a property line not common to a public way (typically side or rear lot lines), that structure shall also be set back from the property line by at least 1 inch (25.4 mm) for each 50 feet (15 240 mm) of height and a minimum of 1 inch (25.4 mm) for structures with heights less than 50 feet (15 240 mm). For structures in Seismic Design Category D, refer to ASCE 7 for additional requirements. Exception: Smaller separations or property line setbacks shall be permitted when justified by rational analysis based on maximum expected ground motions with a minimum separation of 1 inch (25.4 mm) along the full height of the structure.
1613.4.1 Masonry structures. | For structures adjacent to existing unreinforced masonry bearing wall structures, the structural separation shall be filed with a material with a minimum compressive strength of 25 psi (172.37 kPa) and a maximum compressive strength of 100 psi (689.74 kPa). Additionally, when the adjacent wall is a party wall, the party wall shall be made secure by the party responsible for the new construction as per Chapter 33.
1613.4.2 Covers. | The infill material shall be covered on all sides and shall meet the appropriate provisions of Chapter 26. The covering must be of adequate strength to resist the wind loads for cladding as specified in Chapter 16 and shall conform to all applicable provisions in Chapter 14.
1613.4.3 Covers wider than 5 inches (127 mm). | When a building separation wider than 5 inches (127 mm) is created pursuant to Section 1613.4, such separation, at the roof level of the proposed new building, or at the roof level of an existing adjoining building where if that building is lower than the proposed new building, shall have a horizontal cover/closure that conforms with the following: 1. The cover/closure material shall be noncombustible; and Exception: The cover/closure material used shall be permitted to be combustible material in accordance with Section 1510.9 if all the material on the appropriate roof conforms to the limitations therein, there are no masonry openings in either wall abutting the building separation, and both buildings are noncombustible. 2. The cover/closure shall be capable of withstanding the roof live load of 30 psf (1.43 kPa), securely fastened to the new building, and be of a type that would be capable of preventing unauthorized or accidental access to the space.
1613.5 ASCE 7, Table 12. | 2-1. Modify ASCE 7, Table 12.2-1 as follows:
16. Light-frame (cold-formed steel) walls sheathed with wood structural panels rated for shear resistance or steel sheets.
16. Special reinforced masonry shear walls.
1613.6 Ballasted photovoltaic panel systems. | Ballasted, roof-mounted photovoltaic panel systems need not be rigidly attached to the roof or supporting structure. Ballasted non-penetrating systems shall be designed and installed only on roofs with slopes not more than one unit vertical in 12 units horizontal. Ballasted nonpenetrating systems shall be designed to resist sliding and uplift resulting from lateral and vertical forces as required by Section 1605 of this code, using a coefficient of friction determined by acceptable engineering principles. In structures assigned to Seismic Design Category C or D, ballasted nonpenetrating systems shall be designed to accommodate seismic displacement determined by nonlinear response-history analysis or shake-table testing, using input motions consistent with ASCE 7 lateral and vertical seismic forces for nonstructural components on roofs.
1614.1 General. | Ice-sensitive structures shall be designed for atmospheric ice loads in accordance with Chapter 10 of ASCE 7.
1615.1 Definitions. | The following terms are defined in Chapter 2:
1616.1 Scope. | The intent of these provisions is to enhance structural performance under extreme event scenarios by providing additional overall system redundancy and local robustness. All structures shall be designed to satisfy the prescriptive requirements of this section. Exception: Structures in Risk Category I of Table 1604.5 and structures in Occupancy Group R-3 are exempt from the requirements of Sections 1615 through 1617. |  |  |  | See BC16 Tables&Figures
1616.2 Continuity and ties. | All structural elements shall have a minimum degree of continuity and shall be tied together horizontally and vertically as specified in Chapters 19, 21 and 22 for concrete, masonry and steel, respectively.
1616.3 Lateral bracing. | Floor and roof diaphragms or other horizontal elements shall be tied to the lateral load-resisting system.
1616.4 Vehicular impact. | Structural columns that are directly exposed to vehicular traffic shall be designed for vehicular impact. Structural columns that are adequately protected by bollards, guard walls, vehicle arrest devices or other elements do not need to be designed for vehicular impact. The load combinations for vehicular impact shall be as specified in Section 1605.5.
1616.5 Gas explosions. | In buildings with gas piping operating at pressures in excess of 15 psig (193.4 kPa gauge), all key elements and their connections within 15 feet (4572 mm) of such piping shall be designed to resist a potential gas explosion. The structure shall be designed to account for the potential loss of the affected key elements one at a time by the alternate load path method. Load combinations for the alternate load path shall be as specified in Section 1605.4. In lieu of the alternate load path method, the affected key elements shall be designed to withstand a load of 430 psf (20.6 kPa) applied using the load combinations specified in Section 1605.5. The load shall be applied along the entire length of the element, and shall be applied in the manner and direction that produces the most damaging effect.
1616.5.1 Explosion prevention and deflagration venting. | The structural design and installation of explosion prevention systems and deflagration venting shall be in accordance with the requirements of Appendices E and G of the New York City Fuel Gas Code, as well as the New York City Fire Code, and the rules and regulations of the department.
1617.1 Scope. | A key element analysis shall be performed for the following buildings:
1617.2 Load combinations. | Where specifically required by Section 1617.1, elements and components shall be designed to resist the forces calculated using the combination specified in Section 1605.4 or 1605.6 as applicable. | 1614.1 General. | Ice-sensitive structures shall be designed for atmospheric ice loads in accordance with Chapter 10 of ASCE 7.
1617.3 Seismic and wind. | When the code-prescribed seismic or wind design produces greater effects, the seismic or wind design shall govern, but the detailing requirements and limitations prescribed in this and referenced sections shall also be followed.
1617.4 Joints. | Where a structure is divided by joints that allow for movement, each portion of the structure between joints shall be considered as a separate structure.
1617.5 Key element analysis. | Where key elements are present in a structure, the structure shall be designed to account for their potential loss one at a time by the alternate load path method or by the specific local resistance method as specified in Section 1617.6.
1617.6 The specific local resistance method. | Where the specific local resistance method is used, key elements shall be designed using specific local loads as follows:
1617.7 Design criteria. | Alternate load path method and/or specific local resistance method for key elements shall conform to the appropriate design criteria as determined from Sections 1617.8 through 1617.10.
1617.8 Analysis procedures. | All structural analysis for specific local loads or alternate load paths shall be made by one of the following methods:
1617.8.1 Static elastic analysis. | For analysis of this type, dynamic effects of member loss or dynamic effects of specific local loads need not be considered. The structural demand is obtained from linear static analysis. However, structural member capacity is based on ultimate capacity of the entire cross section. The demand/capacity ratio of structural elements shall not exceed one.
1617.8.2 Dynamic inelastic analysis. | For analysis of this type, dynamic effects of member loss or specific local loads shall be considered. The structure does not need to remain elastic; however, the response ratio and rotation limits obtained from Table 1617.8.3 shall not be exceeded. |  |  |  | See BC16 Tables&Figures
1617.8.3 Energy methods. | Static inelastic analysis using energy equilibrium may also be used. The structure does not need to remain elastic; however, the response ratio and rotation limits obtained from Table 1617.8.3 shall not be exceeded. |  |  |  | See BC16 Tables&Figures
1617.9 Minimum response. | Structural response of elements determined using a dynamic inelastic analysis shall not be less than 80 percent of the structural response determined using a static elastic analysis.
1617.10 Strength reduction factors. | For structural design for specific local loads or alternate load paths, all strength reduction factors may be multiplied by 1.1.
1618.1 General. | The provisions of this section specify where structural peer review is required, how and by whom it is to be performed.
1618.2 Where required. | A structural peer review of the primary structure shall be performed and a report provided for the following buildings:
1618.3 Structural peer review. | It shall be verified that the structural design is in general conformance with the requirements of this code.
1618.4 Geotechnical peer review. | Geotechnical peer reviews are required to be performed in accordance with Section d.
1618.5 Structural peer reviewer. | The structural peer review shall be performed by a qualified independent structural engineer who has been retained by or on behalf of the owner. A structural peer reviewer shall meet the requirements of the rules of the department.
1618.5.1 Independence. | In order to satisfy the requirement that the peer reviewer be independent, the department requires that the peer reviewer must not engage in any activities that may conflict with their objective judgment and integrity, including but not limited to having a financial and/or other interest in the design, construction, installation, manufacture or maintenance of structures or components that they are reviewing.
1618.6 Extent of the structural peer review. | The structural peer review shall comply with Sections 1618.6.1 and 1618.6.2.
1618.6.1 Scope. | The structural peer reviewer shall review the plans and specifications submitted with the permit application for general compliance with the structural and foundation design provisions of this code. The reviewing engineer shall perform the following tasks at a minimum:
1618.6.2 Structural design criteria. | If the design criteria and design assumptions are not shown on the drawings or in the computations, the structural engineer of record shall provide a statement of these criteria and assumptions for the reviewer. In addition, the design engineer shall provide information and/or calculations, if requested by the peer reviewer.
1618.7 Structural peer review report. | The structural peer review report shall comply with Sections 1618.7.1 through 1618.7.3.
1618.7.1 General. | The reviewing engineer shall submit a report to the department stating whether or not the structural design shown on the plans and specifications generally conforms to the structural and foundation requirements of this code.
1618.7.2 Contents. | The report shall demonstrate, at a minimum, compliance with Items 1 through 12 of Section 1618.6.1. In addition, the report shall also include the following:
1618.7.3 Phased submission. | If an application is submitted for a permit for the construction of foundations or any other part of a building before the construction documents for the whole building have been submitted, then the structural peer review and report shall be phased. The structural peer reviewer shall be provided with sufficient information on which to make a structural peer review of the phased submission. In addition to the requirements of this section, phased submission of the report shall include any changes made to the initial structural peer review evaluation. The geotechnical peer review report need not be submitted concurrently with the structural peer review report.
1618.8 Responsibility. | The responsibilities of the engineer of record and peer reviewer shall be as laid out in Sections 1618.8.1 through 1618.8.4.
1618.8.1 Structural engineer of record. | The structural engineer of record shall retain sole responsibility for the structural design. The activities and reports of the structural peer reviewer shall not relieve the structural engineer of record of this responsibility.
1618.8.2 Structural peer reviewer. | The structural peer reviewer’s report states his or her opinion regarding the design by the engineer of record. The standard of care to which the structural peer reviewer shall be held in the performance of the structural peer review and report is that level of skill and care consistent with structural peer review services performed by professional engineers licensed in the State of New York for similar type projects. The structural peer reviewer shall not be responsible for the conclusions of the wind and geotechnical peer review reports.
1618.8.3 Revisions of design. | The structural engineer of record shall identify that a new review is required based upon changes to the design documents relevant to the scope of the peer review. The structural peer reviewer shall review the items that have been affected and shall revise the structural peer review report.
1618.8.4 Disputes. | When a dispute arises between the applicant of record and the peer reviewer regarding compliance with Section 1618 that cannot be resolved by these parties, such dispute shall be reported to the department in the form of a letter from the applicant of record. The department may make a final decision or may accept a change of the peer reviewer.
1618.9 Change to peer reviewer. | The peer reviewer cannot be changed without the express consent of the department. The current peer reviewer must submit both a written letter to the borough commissioner detailing the reason for the withdrawal request and a report of the structural peer review findings to date. If a change of peer reviewer is approved, a revised submission indicating the replacement peer reviewer shall be filed with the department.
1619.1 General. | Temporary construction installations that are required by this code to be designed by a registered design professional, and all temporary structures, shall comply with all the provisions of this code, except as described in Sections 1619.3 and 1619.4.
1619.2 Definitions. | The following terms are defined in Chapter 2:
1619.3 Temporary construction installations. | Temporary construction installations shall be subject to the requirements of this section and Chapter 33.
1619.3.1 Design drawings for temporary construction installations. | Design loads, including location and intensity of live loads, shall be indicated on the design drawings for temporary construction installations. Drawings for multilevel temporary construction installations shall indicate the maximum number of levels to be loaded simultaneously and the maximum design loads. Any temporary construction installation utilizing authorized exemptions and load reductions in the structural design shall be indicated on drawings as temporary, and all reduced loads shall be indicated on the drawings. The environmental load mitigations shall be indicated on the design drawings. The design drawings shall be maintained at the site of the temporary construction installation and be made available to the department upon request.
1619.3.2 Loads for temporary construction installations. | Temporary construction installations shall be designed and constructed to resist the loads and load combinations required by this chapter for permanent construction and Chapter 33 of the building code. Live loads shall not be less than the code prescribed value or the maximum loads for the use of a temporary construction installation as noted on the design drawings. Exceptions: 1. Load reductions may be utilized where permitted by Section 1619.3.3. 2. Derricks not permanently mounted to a building shall not be subject to the loads and load combinations of this chapter. Such derricks shall instead be subject to the requirements of Section 3319 and rules promulgated by the commissioner. However, temporary construction installations used to support such derricks shall be subject to the loads and load combinations of this chapter. 3. Mobile cranes shall not be subject to the loads and load combinations of this chapter. Mobile cranes shall instead be subject to the requirements of Section 3319 and rules promulgated by the commissioner. However, temporary construction installations used to support mobile cranes shall be subject to the loads and load combinations of this chapter.
1619.3.3 Load reductions for temporary construction installations. | Temporary construction installations shall be permitted to reduce the design environmental loads required by this chapter in accordance with the specifications below. An action plan for load reductions shall be required in accordance with Section 1619.5. 1. Seismic resistance. Temporary construction installations do not need to consider seismic design. These installations, other than supports of excavation, shall be designed for a minimum of 2 percent of the dead and live load as a service level lateral force. This load shall be used in lieu of seismic forces required by Section 1613 in load combinations including seismic forces. This load shall be distributed in proportion to the design loads, applied in any horizontal direction, and need not be combined with other environmental loads. 2. Wind. The wind design for temporary construction installations shall be computed as required by Section 1609. The basic wind speed used to design the temporary construction installation shall be permitted to be reduced by applying a factor of 0.8. Exceptions: The following are exceptions to item 2 concerning load reductions for wind design: 1. Mast climbers shall not be permitted to reduce wind loads. 2. Suspended scaffolds shall be designed for an out of service wind speed of at least 45 mph (72.4 kph), or a lower speed when so specified by the scaffold manufacturer. 3. Other environmental forces. Other environmental forces, including but not limited to snow, flood, ice, and temperature differential effects, shall be permitted to be reduced as appropriate for the limited seasonal exposure of the temporary construction installation.
1619.3.4 Permit renewal for temporary construction installations that utilize an action plan. | Where a temporary construction installation requires an action plan in accordance with Section 1619.5, the application to renew the permit for such temporary construction installation shall be accompanied by the submission of a report from a registered design professional certifying, based on an inspection of the temporary construction installation performed by the registered design professional within 30 days prior to the submittal of the permit renewal application, that the action plan:
1619.4 Temporary structures. | Temporary structures shall be subject to the requirements of Section 3103.1 and this section.
1619.4.1 Design drawings for temporary structures. | Design loads, including location and intensity of live loads, shall be indicated on the design drawings for temporary structures. Drawings for multilevel temporary structures shall indicate the maximum number of levels to be loaded simultaneously and the maximum design loads. Any temporary structure utilizing authorized exemptions and load reductions in the structural design shall be indicated on drawings as temporary, and all reduced loads shall be indicated on the drawings. The environmental load mitigations shall be indicated on the design drawings. The design drawings shall be maintained at the site of the temporary structure and be made available to the department upon request.
1619.4.2 Loads for temporary structures. | Temporary structures shall be designed and constructed to resist the loads and load combinations required by this chapter. Live loads shall not be less than the code prescribed value or the maximum loads for the use of a temporary structure as noted on the design drawings. Exception: Load reductions may be utilized where permitted by Section 1619.4.3.
1619.4.3 Load reductions for temporary structures. | Temporary structures shall be permitted to reduce the design environmental loads required by this chapter in accordance with the specifications below. An action plan for load reductions shall be required in accordance with Section 1619.5. 1. Seismic resistance. Temporary structures do not need to consider seismic design. Temporary structures shall be designed for a minimum of 2 percent of the dead and live load as a service level lateral force. This load shall be used in lieu of seismic forces required by Section 1613 in load combinations including seismic forces. This load shall be distributed in proportion to the design loads, applied in any horizontal direction, and need not be combined with other environmental loads. 2. Wind. The wind design for temporary structures shall be computed as required by Section 1609. The basic wind speed used to design the structure shall be permitted to be reduced by applying a factor of 0.8. Exception: In lieu of applying a factor of 0.8, temporary structures may be removed from service at the environmental conditions determined by the manufacturer of the temporary structure. The threshold for removal of service shall be indicated on the design drawings required by Section 1619.4.1 as well as the action plan required by Section 1619.5. 3. Other environmental forces. Other environmental forces, including but not limited to snow, flood, ice, and temperature differential effects, shall be permitted to be reduced as appropriate for the limited seasonal exposure of the temporary structure.
1619.4.4 Duration of time for temporary structures. | Temporary structures shall be erected for a limited period not exceeding ninety days in accordance with Article 111 of Title 28 of the Administrative Code. Such limited period shall be counted from the date the temporary structure is substantially completed. Exception: Where the commissioner has approved a request to extend the duration of time for a temporary structure in accordance with Section 1619.4.5.
1619.4.5 Extension of time for temporary structures. | Subject to the approval of the commissioner, the duration of time for a temporary structure may be extended by increments not to exceed ninety days. Each request to extend the time for a temporary structure shall be accompanied by the submission of a report from a registered design professional certifying the following:
1619.5 Action plan. | All temporary structures or temporary construction installations with reduced design environmental loads in accordance with Sections 1619.3.3 or 1619.4.3 shall include environmental load mitigation measures as part of an action plan to protect the public. The action plan measures shall be indicated on the design drawings required by Sections 1619.3.1 or 1619.4.1. Exception: An action plan is not required for: 1. Derricks not permanently mounted to a building. Derricks not permanently mounted to a building shall be secured in accordance with a wind action plan as specified in rules promulgated by the commissioner. 2. Mobile cranes. Mobile cranes shall be secured in accordance with a wind action plan as specified in rules promulgated by the commissioner. 3. A suspended scaffold. Suspended scaffolds shall be secured in accordance with the requirements of Section 3314; requirements for securing suspended scaffolds shall be indicated on design drawings when required by Section 3314.
1619.5.1 Implementation. | The action plan shall be such that it can be reliably implemented within one day of notice or less as appropriate for the actions.
1619.5.2 Components. | The action plan shall, at a minimum, include the following:
|  | 1602.1 Notations. | The following notations are used in this chapter:
|  | 1603.1.2 Roof live load. | The roof live load used in the design shall be indicated for roof areas (Section 1607.14).
|  | 1603.1.3 Roof snow load data. | The ground snow load, pg, shall be indicated. In areas where the ground snow load, pg, exceeds 10 pounds per square foot (psf) (0.479 kN/m2), the following additional information shall also be provided, regardless of whether snow loads govern the design of the roof:
|  | 1603.1.4 Wind design data. | The following information related to wind loads shall be shown, regardless of whether wind loads govern the design of the lateral force-resisting system of the structure:
|  | 1603.1.5 Earthquake design data. | The following information related to seismic loads shall be shown, regardless of whether seismic loads govern the design of the lateral force-resisting system of the structure:
|  | 1603.1.6 Geotechnical information. | The design load-bearing values of soils shall be shown on the construction documents.
|  | 1603.1.7 Flood design data. | For buildings located in whole or in part in flood hazard areas as established in Section 1612.3, the documentation pertaining to design, if required in Section 1612.4, shall be included and the following information, referenced to the datum on the community’s Flood Insurance Rate Map (FIRM), shall be shown, regardless of whether flood loads govern the design of the building:
|  | 1603.1.8 Special loads. | Special loads that are applicable to the design of the building, structure or portions thereof, including but not limited to the loads of machinery or equipment, and that are greater than specified floor and roof loads shall be specified by their descriptions and locations.
|  | 1603.1.8.1 Photovoltaic panel systems. | The dead load of rooftop-mounted photovoltaic panel systems, including rack support systems, shall be indicated on the construction documents.
|  | 1603.1.9 Roof rain load data. | Rain intensity, i (in/hr) (cm/hr), shall be shown regardless of whether rain loads govern the design.
|  | 1605.2 Alternative allowable stress design load combinations. | In lieu of the load combinations in ASCE 7, Section 2.4, structures and portions thereof shall be permitted to be designed for the most critical effects resulting from the following combinations. Where using these alternative allowable stress load combinations that include wind or seismic loads, allowable stresses are permitted to be increased or load combinations reduced where permitted by the material chapter of this code or the referenced standards. For load combinations that include the counteracting effects of dead and wind loads, only two-thirds of the minimum dead load likely to be in place during a design wind event shall be used. Where using these alternative load combinations to evaluate sliding, overturning and soil bearing at the soil-structure interface, the reduction of foundation overturning from Section 12.13.4 in ASCE 7 shall not be used. Where using these alternative basic load combinations for proportioning foundations for loadings, which include seismic loads, the vertical seismic load effect, Ev, in Equation 12.4-4 of ASCE 7 is permitted to be taken equal to zero. Where required by ASCE 7, Chapters 12, 13 and 15, the load combinations including overstrength of ASCE 7, Section 2.3.6 shall be used. D + L + (Lr or S or R) (Equation 16-1) D + L + 0.6W (Equation 16-2) D + L + 0.6W + S/2 (Equation 16-3) D + L + S + 0.6W/2 (Equation 16-4) D + L + S + E/1.4 (Equation 16-5) 0.9D + E/1.4 (Equation 16-6) Exceptions: 1. Crane hook loads need not be combined with roof live loads or with more than three-fourths of the snow load or one-half of the wind load. 2. Flat roof snow loads of 30 pounds per square foot (1.44 kN/m2) or less and roof live loads of 30 pounds per square foot (1.44 kN/m2) or less need not be combined with seismic loads. Where flat roof snow loads exceed 30 pounds per square foot (1.44 kN/m2), 20 percent shall be combined with seismic loads.
|  | 1606.2 Weights of materials of construction. | For purposes of design, the actual weights of materials of construction shall be used. In the absence of definite information, values used shall be subject to the approval of the building official.
|  | 1606.3 Weight of fixed service equipment. | In determining dead loads for purposes of design, the weight of fixed service equipment, including the maximum weight of the contents of fixed service equipment, shall be included. The components of fixed service equipment that are variable, such as liquid contents and movable trays, shall not be used to counteract forces causing overturning, sliding, and uplift conditions in accordance with Section 1.3.6 of ASCE 7. Exceptions: 1. Where force effects are the result of the presence of the variable components, the components are permitted to be used to counter those load effects. In such cases, the structure shall be designed for force effects with the variable components present and with them absent. 2. For the calculation of seismic force effects, the components of fixed service equipment that are variable, such as liquid contents and movable trays, need not exceed those expected during normal operation.
|  | 1606.4 Photovoltaic panel systems. | The weight of photovoltaic panel systems, their support system, and ballast shall be considered as dead load.
|  | 1606.5 Vegetative and landscaped roofs. | The weight of all landscaping and hardscaping materials for vegetative and landscaped roofs shall be considered as dead load. The weight shall be computed considering both fully saturated soil and drainage layer materials and fully dry soil and drainage layer materials to determine the most severe load effects on the structure.
|  | 1607.7 Passenger vehicle garages. | Floors in garages or portions of a building used for the storage of motor vehicles shall be designed for the uniformly distributed live loads indicated in Table 1607.1 or the following concentrated load: |  | See BC16 Tables&Figures
|  | 1607.8 Heavy vehicle loads. | Floors and other surfaces that are intended to support vehicle loads greater than a 10,000-pound (4536 kg) gross vehicle weight rating shall comply with Sections 1607.8.1 through 1607.8.5.
|  | 1607.8.1 Loads. | Where any structure does not restrict access for vehicles that exceed a 10,000-pound (4536 kg) gross vehicle weight rating, those portions of the structure subject to such loads shall be designed using the vehicular live loads, including consideration of impact and fatigue, in accordance with the codes and specifications required by the jurisdiction having authority for the design and construction of the roadways and bridges in the same location of the structure.
|  | 1607.8.2 Fire truck and emergency vehicles. | Where a structure or portions of a structure are accessed and loaded by fire department access vehicles and other similar emergency vehicles, the structure shall be designed for the greater of the following loads:
|  | 1607.8.3 Heavy vehicle garages. | Garages designed to accommodate vehicles that exceed a 10,000-pound (4536 kg) gross vehicle weight rating, shall be designed using the live loading specified by Section 1607.8.1. For garages the design for impact and fatigue is not required. Exception: The vehicular live loads and load placement are allowed to be determined using the actual vehicle weights for the vehicles allowed onto the garage floors, provided that such loads and placement are based on rational engineering principles and are approved by the building official, but shall be not less than 50 psf (2.9 kN/m2). This live load shall not be reduced.
|  | 1607.8.4 Forklifts and movable equipment. | Where a structure is intended to have forklifts or other movable equipment present, the structure shall be designed for the total vehicle or equipment load and the individual wheel loads for the anticipated vehicles as specified by the owner of the facility. These loads shall be posted in accordance with Section 1607.8.5.
|  | 1607.8.4.1 Impact and fatigue. | Impact loads and fatigue loading shall be considered in the design of the supporting structure. For the purposes of design, the vehicle and wheel loads shall be increased by 30 percent to account for impact.
|  | 1607.8.5 Posting. | The maximum weight of vehicles allowed into or on a garage or other structure shall be posted by the owner or the owner’s authorized agent in accordance with Section 106.1.
|  | 1607.9 Loads on handrails, guards, grab bars and seats. | Handrails and guards shall be designed and constructed for the structural loading conditions set forth in Section 1607.9.1. Grab bars, shower seats and accessible benches shall be designed and constructed for the structural loading conditions set forth in Section 1607.9.2.
|  | 1607.9.1 Handrails and guards. | Handrails and guards shall be designed to resist a linear load of 50 pounds per linear foot (plf) (0.73 kN/m) in accordance with Section 4.5.1.1 of ASCE 7. Glass handrail assemblies and guards shall comply with Section 2407. Exceptions: 1. For one- and two-family dwellings, only the single concentrated load required by Section 1607.9.1.1 shall be applied. 2. In Group I-3, F, H and S occupancies, for areas that are not accessible to the general public and that have an occupant load less than 50, the minimum load shall be 20 pounds per foot (0.29 kN/m).
|  | 1607.9.1.1 Concentrated load. | Handrails and guards shall be designed to resist a concentrated load of 200 pounds (0.89 kN) in accordance with Section 4.5.1 of ASCE 7.
|  | 1607.9.1.2 Guard component loads. | Balusters, panel fillers and guard infill components, including all rails except the handrail and the top rail, shall be designed to resist a concentrated load of 50 pounds (0.22 kN) in accordance with Section 4.5.1.2 of ASCE 7.
|  | 1607.9.2 Grab bars, shower seats and accessible benches. | Grab bars, shower seats and accessible benches shall be designed to resist a single concentrated load of 250 pounds (1.11 kN) applied in any direction at any point on the grab bar, shower seat, or seat of the accessible bench so as to produce the maximum load effects.
|  | 1607.10 Vehicle barriers. | Vehicle barriers for passenger vehicles shall be designed to resist a concentrated load of 6,000 pounds (26.70 kN) in accordance with Section 4.5.3 of ASCE 7. Garages accommodating trucks and buses shall be designed in accordance with an approved method that contains provisions for traffic railings.
|  | 1607.11 Impact loads. | The live loads specified in Sections 1607.3 through 1607.10 shall be assumed to include adequate allowance for ordinary impact conditions. Provisions shall be made in the structural design for uses and loads that involve unusual vibration and impact forces.
|  | 1607.11.1 Elevators. | Members, elements and components subject to dynamic loads from elevators shall be designed for impact loads and deflection limits prescribed by ASME A17.1/CSA B44.
|  | 1607.11.2 Machinery. | For the purpose of design, the weight of machinery and moving loads shall be increased as follows to allow for impact:
|  | 1607.11.3 Elements supporting hoists for façade access and building maintenance equipment. | In addition to any other applicable live loads, structural elements that support hoists for façade access and building maintenance equipment shall be designed for a live load of 2.5 times the rated load of the hoist or the stall load of the hoist, whichever is larger.
|  | 1607.11.4 Fall arrest, lifeline, and rope descent system anchorages. | In addition to any other applicable live loads, fall arrest, lifeline, and rope descent system anchorages and structural elements that support these anchorages shall be designed for a live load of not less than 3,100 pounds (13.8 kN) for each attached line, in any direction that the load can be applied.
|  | 1607.12 Reduction in uniform live loads. | Except for uniform live loads at roofs, all other minimum uniformly distributed live loads, Lo, in Table 1607.1 are permitted to be reduced in accordance with Section 1607.12.1 or 1607.12.2. Uniform live loads at roofs are permitted to be reduced in accordance with Section 1607.14.2. |  | See BC16 Tables&Figures
|  | 1607.12.1 Basic uniform live load reduction. | Subject to the limitations of Sections 1607.12.1.1 through 1607.12.1.3 and Table 1607.1, members for which a value of KLLAT is 400 square feet (37.16 m2) or more are permitted to be designed for a reduced uniformly distributed live load, L, in accordance with the following equation: |  | See BC16 Tables&Figures
|  | 1607.12.1.1 One-way slabs. | The tributary area, AT, for use in Equation 16-7 for one-way slabs shall not exceed an area defined by the slab span times a width normal to the span of 1.5 times the slab span.
|  | 1607.12.1.2 Heavy live loads. | Live loads that exceed 100 psf (4.79 kN/m2) shall not be reduced. Exceptions: 1. The live loads for members supporting two or more floors are permitted to be reduced by not greater than 20 percent, but the live load shall be not less than L as calculated in Section 1607.12.1. 2. For uses other than storage, where approved, additional live load reductions shall be permitted where shown by the registered design professional that a rational approach has been used and that such reductions are warranted.
|  | 1607.12.1.3 Passenger vehicle garages. | The live loads shall not be reduced in passenger vehicle garages. Exception: The live loads for members supporting two or more floors are permitted to be reduced by not greater than 20 percent, but the live load be shall be not less than L as calculated in Section 1607.12.1.
|  | 1607.12.2 Alternative uniform live load reduction. | As an alternative to Section 1607.12.1 and subject to the limitations of Table 1607.1, uniformly distributed live loads are permitted to be reduced in accordance with the following provisions. Such reductions shall apply to slab systems, beams, girders, columns, piers, walls and foundations. 1. A reduction shall not be permitted where the live load exceeds 100 psf (4.79 kN/m2) except that the design live load for members supporting two or more floors is permitted to be reduced by not greater than 20 percent. Exception: For uses other than storage, where approved, additional live load reductions shall be permitted where shown by the registered design professional that a rational approach has been used and that such reductions are warranted. 2. A reduction shall not be permitted in passenger vehicle parking garages except that the live loads for members supporting two or more floors are permitted to be reduced by not greater than 20 percent. 3. For live loads not exceeding 100 psf (4.79 kN/m2), the design live load for any structural member supporting 150 square feet (13.94 m2) or more is permitted to be reduced in accordance with Equation 16-8 4. For one-way slabs, the area, A, for use in Equation 16-8 shall not exceed the product of the slab span and a width normal to the span of 0.5 times the slab span. R = 0.08(A – 150) (Equation 16-8) For SI: R = 0.861(A - 13.94) Such reduction shall not exceed the smallest of: 1. 40 percent for members supporting one floor. 2. 60 percent for members supporting two or more floors. 3. R as determined by the following equation: R = 23.1(1+ D/Lo) (Equation 16-9) where: A = Area of floor supported by the member, square feet (m2). D = Dead load per square foot (m2) of area supported. Lo = Unreduced live load per square foot (m2) of area supported. R = Reduction in percent. |  | See BC16 Tables&Figures
|  | 1607.13 Distribution of floor loads. | Where uniform floor live loads are involved in the design of structural members arranged so as to create continuity, the minimum applied loads shall be the full dead loads on all spans in combination with the floor live loads on spans selected to produce the greatest load effect at each location under consideration. Floor live loads are permitted to be reduced in accordance with Section 1607.12 .
|  | 1607.14 Roof loads. | The structural supports of roofs and marquees shall be designed to resist wind and, where applicable, snow and earthquake loads, in addition to the dead load of construction and the appropriate live loads as prescribed in this section, or as set forth in Table 1607.1. The live loads acting on a sloping surface shall be assumed to act vertically on the horizontal projection of that surface. |  | See BC16 Tables&Figures
|  | 1607.14.1 Distribution of roof loads. | Where uniform roof live loads are reduced to less than 20 psf (0.96 kN/m2) in accordance with Section 1607.14.2.1 and are applied to the design of structural members arranged so as to create continuity, the reduced roof live load shall be applied to adjacent spans or to alternate spans, whichever produces the most unfavorable load effect. See Section 1607.14.2 for reductions in minimum roof live loads and Section 7.5 of ASCE 7 for partial snow loading.
|  | 1607.14.2 Reduction in uniform roof live loads. | The minimum uniformly distributed live loads of roofs and marquees, Lo, in Table 1607.1 are permitted to be reduced in accordance with Section 1607.14.2.1. |  | See BC16 Tables&Figures
|  | 1607.14.2.1 Ordinary roofs, awnings and canopies. | Ordinary flat, pitched and curved roofs, and awnings and canopies other than of fabric construction supported by a skeleton structure, are permitted to be designed for a reduced uniformly distributed roof live load, Lr, as specified in the following equations or other controlling combinations of loads as specified in Section 1605, whichever produces the greater load effect.
|  | 1607.14.2.2 Occupiable roofs. | Areas of roofs that are occupiable, such as vegetative roofs, landscaped roofs or for assembly or other similar purposes, and marquees are permitted to have their uniformly distributed live loads reduced in accordance with Section 1607.12.
|  | 1607.14.3 Awnings and canopies. | Awnings and canopies shall be designed for uniform live loads as required in Table 1607.1 as well as for snow loads and wind loads as specified in Sections 1608 and 1609. |  | See BC16 Tables&Figures
|  | 1607.14.4 Photovoltaic panel systems. | Roof structures that provide support for photovoltaic panel systems shall be designed in accordance with Sections 1607.14.4.1 through 1607.14.4.5 , as applicable.
|  | 1607.14.4.1 Roof live load. | Roof structures that support photovoltaic panel systems shall be designed to resist each of the following conditions: 1. Applicable uniform and concentrated roof loads with the photovoltaic panel system dead loads. Exception: Roof live loads need not be applied to the area covered by photovoltaic panels where the clear space between the panels and the roof surface is 24 inches (610 mm) or less. 2. Applicable uniform and concentrated roof loads without the photovoltaic panel system present.
|  | 1607.14.4.2 Photovoltaic panels or modules. | The structure of a roof that supports solar photovoltaic panels or modules shall be designed to accommodate the full solar photovoltaic panels or modules and ballast dead load, including concentrated loads from support frames in combination with the loads from Section 1607.14.4.1 and other applicable loads. Where applicable, snow drift loads created by the photovoltaic panels or modules shall be included.
|  | 1607.14.4.3 Photovoltaic panels installed on open grid roof structures. | Structures with open grid framing and without a roof deck or sheathing supporting photovoltaic panel systems shall be designed to support the uniform and concentrated roof live loads specified in Section 1607.14.4.1, except that the uniform roof live load shall be permitted to be reduced to 12 psf (0.57 kN/m2).
|  | 1607.14.4.4 Ground-mounted photovoltaic (PV) panel systems. | Ground-mounted photovoltaic (PV) panel systems that are independent structures and do not have accessible/occupied space underneath are not required to accommodate a roof photovoltaic live load. Other loads and combinations in accordance with Section 1605 shall be accommodated.
|  | 1607.14.4.5 Ballasted photovoltaic panel systems. | Roof structures that provide support for ballasted photovoltaic panel systems shall be designed, or analyzed, in accordance with Section 1604.4; checked in accordance with Section 1604.3.6 for deflections; and checked in accordance with Section 1611 for ponding.
|  | 1607.15 Crane loads. | The crane live load shall be the rated capacity of the crane. Design loads for the runway beams, including connections and support brackets, of moving bridge cranes and monorail cranes shall include the maximum wheel loads of the crane and the vertical impact, lateral and longitudinal forces induced by the moving crane.
|  | 1607.15.1 Maximum wheel load. | The maximum wheel loads shall be the wheel loads produced by the weight of the bridge, as applicable, plus the sum of the rated capacity and the weight of the trolley with the trolley positioned on its runway at the location where the resulting load effect is maximum.
|  | 1607.15.2 Vertical impact force. | The maximum wheel loads of the crane shall be increased by the following percentages to account for the effects of vertical impact or vibration:
|  | 1607.15.3 Lateral force. | The lateral force on crane runway beams with electrically powered trolleys shall be calculated as 20 percent of the sum of the rated capacity of the crane and the weight of the hoist and trolley. The lateral force shall be assumed to act horizontally at the traction surface of a runway beam, in either direction perpendicular to the beam, and shall be distributed with due regard to the lateral stiffness of the runway beam and supporting structure.
|  | 1607.15.4 Longitudinal force. | The longitudinal force on crane runway beams, except for bridge cranes with hand-geared bridges, shall be calculated as 10 percent of the maximum wheel loads of the crane. The longitudinal force shall be assumed to act horizontally at the traction surface of a runway beam, in either direction parallel to the beam.
|  | 1607.16 Interior walls and partitions. | Interior walls and partitions that exceed 6 feet (1829 mm) in height, including their finish materials, shall have adequate strength and stiffness to resist the loads to which they are subjected but not less than a horizontal load of 5 psf (0.240 kN/m2).
|  | 1607.16.1 Fabric partitions. | Fabric partitions that exceed 6 feet (1829 mm) in height, including their finish materials, shall have adequate strength and stiffness to resist the following load conditions:
|  | 1607.16.2 Fire walls. | In order to meet the structural stability requirements of Section 706.2 where the structure on either side of the wall has collapsed, fire walls and their supports shall be designed to withstand a minimum horizontal allowable stress load of 5 psf (0.240 kN/m2).
|  | 1607.17 Fixed ladders. | Fixed ladders with rungs shall be designed to resist a single concentrated load of 300 pounds (1.33 kN) in accordance with Section 4.5.4 of ASCE 7. Where rails of fixed ladders extend above a floor or platform at the top of the ladder, each side rail extension shall be designed to resist a single concentrated load of 100 pounds (0.445 kN) in accordance with Section 4.5.4 of ASCE 7. Ship’s ladders shall be designed to resist the stair loads given in Table 1607.1. |  | See BC16 Tables&Figures
|  | 1607.18 Library stack rooms. | The live loading indicated in Table 1607.1 for library stack rooms applies to stack room floors that support nonmobile, double-faced library book stacks, subject to the following limitations:
|  | 1607.19 Seating for assembly uses. | Bleachers, folding and telescopic seating and grandstands shall be designed for the loads specified in ICC 300. Stadiums and arenas with fixed seats shall be designed for the horizontal sway loads in Section 1607.19.1.
|  | 1607.19.1 Horizontal sway loads. | The design of stadiums and arenas with fixed seats shall include horizontal swaying forces applied to each row of seats as follows:
|  | 1607.20 Sidewalks, vehicular driveways, and yards subject to trucking. | The live loading indicated in Table 1607.1 for sidewalks, vehicular driveways, and yards subject to trucking shall comply with the requirements of this section.
|  | 1607.20.1 Uniform loads. | In addition to the loads indicated in Table 1607.1, other uniform loads in accordance with an approved method that contains provisions for truck loading shall be considered where appropriate.
|  | 1607.20.2 Concentrated loads. | The concentrated wheel load indicated in Table 1607.1 shall be applied on an area of 41/2 inches by 41/2 inches (114 mm by 114 mm).
|  | 1607.21 Stair treads. | The concentrated load indicated in Table 1607.1 for stair treads shall be applied on an area of 2 inches by 2 inches (51 mm by 51 mm). This load need not be assumed to act concurrently with the uniform load.
|  | 1607.22 Residential attics. | The live loads indicated in Table 1607.1 for attics in residential occupancies shall comply with the requirements of this section.
|  | 1607.22.1 Uninhabitable attics without storage. | In residential occupancies, uninhabitable attic areas without storage are those where the maximum clear height between the joists and rafters is less than 42 inches (1067 mm), or where there are not two or more adjacent trusses with web configurations capable of accommodating an assumed rectangle 42 inches (1067 mm) in height by 24 inches (610 mm) in width, or greater, within the plane of the trusses. The live load in Table 1607.1 need not be assumed to act concurrently with any other live load requirement.
|  | 1607.22.2 Uninhabitable attics with storage. | In residential occupancies, uninhabitable attic areas with storage are those where the maximum clear height between the joist and rafter is 42 inches (1067 mm) or greater, or where there are two or more adjacent trusses with web configurations capable of accommodating an assumed rectangle 42 inches (1067 mm) in height by 24 inches (610 mm) in width, or greater, within the plane of the trusses. The live load in Table 1607.1 need only be applied to those portions of the joists or truss bottom chords where both of the following conditions are met:
|  | 1607.22.3 Attics served by stairs. | Attic spaces served by stairways other than the pull-down type shall be designed to support the minimum live load specified for habitable attics and sleeping rooms.
|  | 1609.2 Protection of openings. | In windborne debris regions, glazing in buildings shall be impact resistant or protected with an impact-resistant covering meeting the requirements of an approved impact-resistant standard or ASTM E1996 referenced herein as follows: 1. Glazed openings located within 30 feet (9144 mm) of grade shall meet the requirements of the large missile test of ASTM E1996. 2. Glazed openings located more than 30 feet (9144 mm) above grade shall meet the provisions of the small missile test of ASTM E1996. Exceptions: 1. Wood structural panels with a minimum thickness of 7/16 inch (11.1 mm) and maximum panel span of 8 feet (2438 mm) shall be permitted for opening protection in buildings with a mean roof height of 33 feet (10 058 mm) or less that are classified as a Group R-3 or R-4 occupancy. Panels shall be precut so that they shall be attached to the framing surrounding the opening containing the product with the glazed opening. Panels shall be predrilled as required for the anchorage method and shall be secured with the attachment hardware provided. Attachments shall be designed to resist the components and cladding loads determined in accordance with the provisions of ASCE 7, with corrosion-resistant attachment hardware provided and anchors permanently installed on the building. Attachment in accordance with Table 1609.2 with corrosion-resistant attachment hardware provided and anchors permanently installed on the building is permitted for buildings with a mean roof height of 45 feet (13 716 mm) or less where Vasd determined in accordance with Section 1609.3.1 does not exceed 140 mph (63 m/s). 2. Glazing in Risk Category I buildings, including greenhouses that are occupied for growing plants on a production or research basis, without public access shall be permitted to be unprotected. 3. Glazing in Risk Category II, III or IV buildings located over 60 feet (18 288 mm) above the ground and over 30 feet (9144 mm) above aggregate surface roofs located within 1,500 feet (458 m) of the building shall be permitted to be unprotected.
|  | 1609.2.1 Louvers. | Louvers protecting intake and exhaust ventilation ducts not assumed to be open that are located within 30 feet (9144 mm) of grade shall meet the requirements of AMCA 540.
|  | 1609.2.2 Application of ASTM E1996. | The text of Section 6.2.2 of ASTM E1996 shall be substituted as follows:
|  | 1609.2.3 Garage doors. | Garage door glazed opening protection for windborne debris shall meet the requirements of an approved impact-resisting standard or ANSI/DASMA 115.
|  | 1610.1 Lateral pressures. | Foundation walls and retaining walls shall be designed to resist lateral soil loads from adjacent soil. Soil loads specified in Table 1610.1 shall be used as the minimum design lateral soil loads unless determined otherwise by a geotechnical investigation in accordance with Section 1803. Foundation walls and other walls in which horizontal movement is restricted at the top shall be designed for at-rest pressure. Retaining walls free to move and rotate at the top shall be permitted to be designed for active pressure. Lateral pressure from surcharge loads shall be added to the lateral soil load. Lateral pressure shall be increased if expansive soils are present at the site. Foundation walls shall be designed to support the weight of the full hydrostatic pressure of undrained backfill unless a drainage system is installed in accordance with Sections 1805.4.2 and 1805.4.3. Exception: Foundation walls extending not more than 8 feet (2438 mm) below grade and laterally supported at the top by flexible diaphragms shall be permitted to be designed for active pressure.
|  | 1610.2 Uplift loads on floor and foundations. | Basement floors, slabs on ground, foundations, and similar approximately horizontal elements below grade shall be designed to resist uplift loads where applicable. The upward pressure of water shall be taken as the full hydrostatic pressure applied over the entire area. The hydrostatic load shall be measured from the underside of the element being evaluated. The design for upward loads caused by expansive soils shall comply with Section 1808.6.
|  | 1612.2 Design and construction. | The design and construction of buildings and structures located in flood hazard areas, including coastal high hazard areas and coastal A zones, shall be in accordance with Chapter 5 of ASCE 7 and ASCE 24.
|  | 1612.3 Establishment of flood hazard areas. | To establish flood hazard areas, the applicable governing authority shall adopt a flood hazard map and supporting data. The flood hazard map shall include, at a minimum, areas of special flood hazard as identified by the Federal Emergency Management Agency in an engineering report entitled “The Flood Insurance Study for ,” dated , as amended or revised with the accompanying Flood Insurance Rate Map (FIRM) and Flood Boundary and Floodway Map (FBFM) and related supporting data along with any revisions thereto. The adopted flood hazard map and supporting data are hereby adopted by reference and declared to be part of this section.
|  | 1612.3.1 Design flood elevations. | Where design flood elevations are not included in the flood hazard areas established in Section 1612.3, or where floodways are not designated, the building official is authorized to require the applicant to do one of the following:
|  | 1612.3.2 Determination of impacts. | In riverine flood hazard areas where design flood elevations are specified but floodways have not been designated, the applicant shall provide a floodway analysis that demonstrates that the proposed work will not increase the design flood elevation more than 1 foot (305 mm) at any point within the jurisdiction of the applicable governing authority.
|  | 1612.4 Flood hazard documentation. | The following documentation shall be prepared and sealed by a registered design professional and submitted to the building official:
|  | 1613.2 Seismic ground motion values. | Seismic ground motion values shall be determined in accordance with this section.
|  | 1613.2.1 Mapped acceleration parameters. | The parameters SS and S1 shall be determined from the 0.2 and 1-second spectral response accelerations shown on Figures 1613.2.1(1) through 1613.2.1(10). Where S1 is less than or equal to 0.04 and SS is less than or equal to 0.15, the structure is permitted to be assigned Seismic Design Category A.
|  | 1613.2.2 Site class definitions. | Based on the site soil properties, the site shall be classified as Site Class A, B, C, D, E or F in accordance with Chapter 20 of ASCE 7.
|  | 1613.2.3 Site coefficients and adjusted maximum considered earthquake spectral response acceleration parameters. | The maximum considered earthquake spectral response acceleration for short periods, SMS, and at 1-second period, SM1, adjusted for site class effects shall be determined by Equations 16-20 and 16-21, respectively:
|  | 1613.2.4 Design spectral response acceleration parameters. | Five-percent damped design spectral response acceleration at short periods, SDS, and at 1-second period, SD1, shall be determined from Equations 16-22 and Equation 16-23, respectively:
|  | 1613.2.5 Determination of seismic design category. | Structures classified as Risk Category I, II or III that are located where the mapped spectral response acceleration parameter at 1-second period, S1, is greater than or equal to 0.75 shall be assigned to Seismic Design Category E. Structures classified as Risk Category IV that are located where the mapped spectral response acceleration parameter at 1-second period, S1, is greater than or equal to 0.75 shall be assigned to Seismic Design Category F. Other structures shall be assigned to a seismic design category based on their risk category and the design spectral response acceleration parameters, SDS and SD1, determined in accordance with Section 1613.2.4 or the site-specific procedures of ASCE 7. Each building and structure shall be assigned to the more severe seismic design category in accordance with Table 1613.2.5(1) or 1613.2.5(2), irrespective of the fundamental period of vibration of the structure, T.
|  | 1613.2.5.1 Alternative seismic design category determination. | Where S1 is less than 0.75, the seismic design category is permitted to be determined from Table 1613.2.5(1) alone where all of the following apply:
|  | 1613.2.5.2 Simplified design procedure. | Where the alternate simplified design procedure of ASCE 7 is used, the seismic design category shall be determined in accordance with ASCE 7.
|  | 1613.3 Ballasted photovoltaic panel systems. | Ballasted, roof-mounted photovoltaic panel systems need not be rigidly attached to the roof or supporting structure. Ballasted non-penetrating systems shall be designed and installed only on roofs with slopes not more than one unit vertical in 12 units horizontal. Ballasted nonpenetrating systems shall be designed to resist sliding and uplift resulting from lateral and vertical forces as required by Section 1605, using a coefficient of friction determined by acceptable engineering principles. In structures assigned to Seismic Design Category C, D, E or F, ballasted nonpenetrating systems shall be designed to accommodate seismic displacement determined by nonlinear response-hi story or other approved analysis or shake-table testing, using input motions consistent with ASCE 7 lateral and vertical seismic forces for nonstructural components on roofs.
|  | 1615.1 General. | The design and construction of Risk Category III and IV buildings and structures located in the Tsunami Design Zones defined in the Tsunami Design Geodatabase shall be in accordance with Chapter 6 of ASCE 7, except as modified by this code.
|  | 1616.1 General. | High-rise buildings that are assigned to Risk Category III or IV shall comply with the requirements of Section 1616.2 if they are frame structures, or Section 1616.3 if they are bearing wall structures.
|  | 1616.2 Frame structures. | Frame structures shall comply with the requirements of this section.
|  | 1616.2.1 Concrete frame structures. | Frame structures constructed primarily of reinforced or prestressed concrete, either cast-in-place or precast, or a combination of these, shall conform to the requirements of Section 4.10 of ACI 318. Where ACI 318 requires that nonprestressed reinforcing or prestressing steel pass through the region bounded by the longitudinal column reinforcement, that reinforcing or prestressing steel shall have a minimum nominal tensile strength equal to two-thirds of the required one-way vertical strength of the connection of the floor or roof system to the column in each direction of beam or slab reinforcement passing through the column. Exception: Where concrete slabs with continuous reinforcement having an area not less than 0.0015 times the concrete area in each of two orthogonal directions are present and are either monolithic with or equivalently bonded to beams, girders or columns, the longitudinal reinforcing or prestressing steel passing through the column reinforcement shall have a nominal tensile strength of one-third of the required one-way vertical strength of the connection of the floor or roof system to the column in each direction of beam or slab reinforcement passing through the column.
|  | 1616.2.2 Structural steel, open web steel joist or joist girder, or composite steel and concrete frame structures. | Frame structures constructed with a structural steel frame or a frame composed of open web steel joists, joist girders with or without other structural steel elements or a frame composed of composite steel or composite steel joists and reinforced concrete elements shall conform to the requirements of this section.
|  | 1616.2.2.1 Columns. | Each column splice shall have the minimum design strength in tension to transfer the design dead and live load tributary to the column between the splice and the splice or base immediately below.
|  | 1616.2.2.2 Beams. | End connections of all beams and girders shall have a minimum nominal axial tensile strength equal to the required vertical shear strength for allowable stress design (ASD) or two-thirds of the required shear strength for load and resistance factor design (LRFD) but not less than 10 kips (45 kN). For the purpose of this section, the shear force and the axial tensile force need not be considered to act simultaneously. Exception: Where beams, girders, open web joist and joist girders support a concrete slab or concrete slab on metal deck that is attached to the beam or girder with not less than 3/8-inch-diameter (9.5 mm) headed shear studs, at a spacing of not more than 12 inches (305 mm) on center, averaged over the length of the member, or other attachment having equivalent shear strength, and the slab contains continuous distributed reinforcement in each of two orthogonal directions with an area not less than 0.0015 times the concrete area, the nominal axial tension strength of the end connection shall be permitted to be taken as half the required vertical shear strength for ASD or one-third of the required shear strength for LRFD, but not less than 10 kips (45 kN).
|  | 1616.3 Bearing wall structures. | Bearing wall structures shall have vertical ties in all load-bearing walls and longitudinal ties, transverse ties and perimeter ties at each floor level in accordance with this section and as shown in Figure 1616.3.
|  | 1616.3.1 Concrete wall structures. | Precast bearing wall structures constructed solely of reinforced or prestressed concrete, or combinations of these shall conform to the requirements of Sections 16.2.4 and 16.2.5 of ACI 318.
|  | 1616.3.2 Other bearing wall structures. | Ties in bearing wall structures other than those covered in Section 1616.3.1 shall conform to this section.
|  | 1616.3.2.1 Longitudinal ties. | Longitudinal ties shall consist of continuous reinforcement in slabs; continuous or spliced decks or sheathing; continuous or spliced members framing to, within or across walls; or connections of continuous framing members to walls. Longitudinal ties shall extend across interior load-bearing walls and shall connect to exterior load-bearing walls and shall be spaced at not greater than 10 feet (3038 mm) on center. Ties shall have a minimum nominal tensile strength, TT, given by Equation 16-24. For ASD the minimum nominal tensile strength shall be permitted to be taken as 1.5 times the allowable tensile stress times the area of the tie.
|  | 1616.3.2.2 Transverse ties. | Transverse ties shall consist of continuous reinforcement in slabs; continuous or spliced decks or sheathing; continuous or spliced members framing to, within or across walls; or connections of continuous framing members to walls. Transverse ties shall be placed not farther apart than the spacing of load-bearing walls. Transverse ties shall have minimum nominal tensile strength TT, given by Equation 16-24. For ASD the minimum nominal tensile strength shall be permitted to be taken as 1.5 times the allowable tensile stress times the area of the tie.
|  | 1616.3.2.3 Perimeter ties. | Perimeter ties shall consist of continuous reinforcement in slabs; continuous or spliced decks or sheathing; continuous or spliced members framing to, within or across walls; or connections of continuous framing members to walls. Ties around the perimeter of each floor and roof shall be located within 4 feet (1219 mm) of the edge and shall provide a nominal strength in tension not less than Tp, given by Equation 16-25. For ASD the minimum nominal tensile strength shall be permitted to be taken as 1.5 times the allowable tensile stress times the area of the tie.
|  | 1616.3.2.4 Vertical ties. | Vertical ties shall consist of continuous or spliced reinforcing, continuous or spliced members, wall sheathing or other engineered systems. Vertical tension ties shall be provided in bearing walls and shall be continuous over the height of the building. The minimum nominal tensile strength for vertical ties within a bearing wall shall be equal to the weight of the wall within that story plus the weight of the diaphragm tributary to the wall in the story below. Not fewer than two ties shall be provided for each wall. The strength of each tie need not exceed 3,000 pounds per foot (450 kN/m) of wall tributary to the tie for walls of masonry construction or 750 pounds per foot (140 kN/m) of wall tributary to the tie for walls of cold-formed steel light-frame construction.

## BC17
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1701.1 Scope. | The provisions of this chapter shall govern the inspection of quality, workmanship and requirements for construction. Materials, inspection and testing shall conform to the applicable standards listed in this code or in the rules of the department. See Chapter 1 of Title 28 of the Administrative Code for additional provisions relating to materials, testing and inspections. | 1701.1 Scope. | The provisions of this chapter shall govern the quality, workmanship and requirements for materials covered. Materials of construction and tests shall conform to the applicable standards listed in this code.
1701.2 New materials. | See Chapter 1 of Title 28 of the Administrative Code for additional provisions.
1701.3 Used materials. | See Chapter 1 of Title 28 of the Administrative Code.
1702.1 Definitions. | The following terms are defined in Chapter 2:
1704.1 General. | Where application is made for construction as described in this section, one or more special inspection agencies meeting the requirements of Sections 28-114.1 and 28-115.1 of the Administrative Code shall be retained by the owner to provide inspections during construction on the types of work listed under Section 1705 and elsewhere in this code. These inspections are in addition to the other inspections required by Section 110, elsewhere in this code, and Section 28-116 of the Administrative Code. The special inspector shall be acceptable to the registered design professional of record. Exception: Special inspections are not required for building components unless the design involves the practice of professional engineering or architecture as defined by the Education Law of the State of New York and applicable regulations governing the professional registration and certification of engineers or architects. | 1704.1 General. | Special inspections and tests, statements of special inspections, responsibilities of contractors, submittals to the building official and structural observations shall meet the applicable requirements of this section.
1704.1.1 Responsibilities. | Special inspection responsibilities of registered design professionals of record, special inspection agencies, and permit holders shall meet the applicable requirements of this section.
1704.1.1.1 Responsibilities of the registered design professional of record. | The registered design professional of record shall have the following duties and responsibilities:
1704.1.1.2 Responsibilities of the special inspection agency. | The special inspection agency shall have the following duties and responsibilities:
1704.1.1.3 Responsibilities of the permit holder. | The permit holder shall have the following duties and responsibilities:
1704.2 Inspection of fabricators. | Where fabrication of structural members, and other regulated products is performed on the premises of a fabricator’s shop, special inspection and progress inspection of the fabricated items shall be required by this section, the New York City Construction Codes, and Chapter 1 of Title 28 of the Administrative Code.
1704.2.1 Fabrication and implementation procedures. | The special inspector shall verify that the fabricator maintains detailed fabrication and quality control procedures that provide a basis for inspection control of the workmanship and the fabricator’s ability to conform to approved construction documents and referenced standards. The special inspector shall review the procedures for completeness and adequacy relative to the code requirements for the fabricator’s scope of work. Exception: Special inspections and progress inspections as required by Section 1704.2 shall not be required where the fabricator is approved in accordance with Chapter 1 of Title 28 of the Administrative Code, except as required by Section 1704.2.2 of this code.
1704.2.2 Fabricator approval. | Work that is subject to special inspection and performed on the approved fabricator’s premises shall be inspected by the special inspection agency in accordance with Section 1704.2.2.3. Approval of fabricators shall be based upon review of the fabricator’s written procedural and quality control manuals and periodic auditing of fabrication practices by an approved agency.
1704.2.2.1 Certificate of intent to fabricate. | For all work where approval is sought based upon Section 1704.2.2, the approved fabricator shall submit a certificate of intent to fabricate such work to the department identifying the work to be performed as an approved fabricator, and that such work shall be performed in accordance with the approved construction documents, referenced standards and applicable provisions of law and for which site the work is being fabricated prior to fabricating any items for such project.
1704.2.2.2 Fabricator’s certificate of compliance. | For all fabricated items, the approved fabricator shall submit a certificate of compliance to the department stating that the work was performed in accordance with the approved construction documents, referenced standards and applicable provisions of law.
1704.2.2.3 In-plant special inspections. | The owner shall engage an approved special inspection agency to perform special inspections for the portion of the work performed in the approved fabricator’s premises. These inspections shall at a minimum include: (i) one visit to the fabricator’s premises during the course of the subject work to verify the fabricator’s compliance with the written and procedural quality control manuals; and (ii) inspection of 5 percent of the subject work to verify compliance with the approved construction documents.
1705.1 General. | Special inspections and tests of structural elements and nonstructural components of buildings and structures shall meet the applicable requirements of this section. | 1705.1 General. | Special inspections and tests of elements and nonstructural components of buildings and structures shall meet the applicable requirements of this section.
1705.1.1 Special cases. | Special inspections shall be required for proposed work that is, in the opinion of the commissioner, unusual in its nature, including, but not limited to: | 1705.1.1 Special cases. | Special inspections and tests shall be required for proposed work that is, in the opinion of the building official, unusual in its nature, such as, but not limited to, the following examples:
1705.1.1.1 Qualifications. | Where special inspections are required for proposed work in accordance with Section 1705.1.1, the special inspection shall be performed by special inspectors qualified to inspect the work to be inspected. The qualifications of the special inspector shall be acceptable to the commissioner.
1705.2 Steel construction. | The special inspections of new installations and alterations to existing installations of steel elements in buildings and structures shall be as required by this section and Table 1705.2. Where required, special inspection of steel shall also comply with Section 1711. Exceptions: 1. Special inspection of the steel fabrication process shall not be required where the fabricator does not perform any welding, thermal cutting or heating operation of any kind as part of the fabrication process. In such cases, the fabricator shall be required to submit a detailed procedure for material control that demonstrates the fabricator’s ability to maintain suitable records and procedures such that, at any time during the fabrication process, the material specification, grade and mill test reports for the main stress-carrying elements are capable of being determined. 2. When specified by the registered design professional, the special inspector shall have the option to perform periodic inspections during welding of the following items, provided the materials, welding procedures and qualifications of welders are verified prior to the start of the work; periodic inspections are made of the work in progress and a visual inspection of all welds is made prior to completion or prior to shipment of shop welding. 2.1. Single-pass fillet welds not exceeding 5/16 inch (7.9 mm) in size. 2.2. Floor and roof deck welding. 2.3. Welded studs when used for structural diaphragm. 2.4. Welded sheet steel for cold-formed steel members. 2.5. Welding of stairs and railing systems. 2.6. Welding of connections where the calculated connection strength is at least twice the required strength of the connection. Such connections shall be specifically indicated on the approved construction documents. | 1705.2 Steel construction. | The special inspections and nondestructive testing of steel construction in buildings, structures, and portions thereof shall be in accordance with this section. Exception: Special inspections of the steel fabrication process shall not be required where the fabrication process for the entire building or structure does not include any welding, thermal cutting or heating operation of any kind. In such cases, the fabricator shall be required to submit a detailed procedure for material control that demonstrates the fabricator’s ability to maintain suitable records and procedures such that, at any time during the fabrication process, the material specification and grade for the main stress-carrying elements are capable of being determined. Mill test reports shall be identifiable to the main stress-carrying elements where required by the approved construction documents.
1705.2.1 Welding. | Welding inspection and welding inspector qualification shall be in compliance with this section and the rules of the department.
1705.2.1.1 Structural steel. | Welding inspection and welding inspector qualification for structural steel shall be in accordance with AWS D1.1.
1705.2.1.2 Cold-formed steel deck. | Welding inspection and welding inspector qualification for cold-formed steel floor and roof decks shall be in accordance with SDI QA/QC.
1705.2.1.3 Reinforcing steel. | Welding inspection and welding inspector qualification for reinforcing steel shall be in accordance with AWS D1.4.
1705.2.2 Details. | The special inspector shall perform an inspection of the steel frame to verify compliance with the details shown on the approved construction documents, such as bracing, stiffening, member locations and proper application of joint details at each connection, including connections designed for seismic effects.
1705.2.3 High-strength bolts. | Installation of high-strength bolts shall be inspected in accordance with this section and AISC 360. Exception: Installation of high strength bolts in bearing type connections where the calculated connection strength is at least twice the required strength of the connection. Inspection of such connections shall be made under Section 1705.2.2. Such connections shall be clearly indicated on the approved construction documents.
1705.2.3.1 General. | While the work is in progress, the special inspector shall determine that the requirements for bolts, nuts, washers and paint; bolted parts and installation and tightening in such standards are met. For bolts requiring pretensioning, the special inspector shall observe the preinstallation testing and calibration procedures when such procedures are required by the installation method or by project plans or specifications; determine that all plies of connected materials have been drawn together and properly snugged and monitor the installation of bolts to verify that the selected procedure for installation is properly used to tighten bolts. For joints required to be tightened only to the snug-tight condition, the special inspector need only verify that the connected materials have been drawn together and properly snugged.
1705.2.3.2 Periodic inspection. | Inspection of bolt installation for pretensioning is permitted to be performed on a periodic basis when using the turn-of-nut method with matchmarking techniques, the direct tension indicator method or the alternate design fastener (twist-off bolt) method. Joints designated as snug tight need be inspected only on a periodic basis.
1705.2.3.3 Continuous inspection. | Inspection of bolt installation for pretensioning using the calibrated wrench method or the turn-of-nut method without matchmarking shall be performed on a continuous basis.
1705.2.4 Special inspection for seismic resistance. | In addition to the other special inspection requirements of this code, special inspections of structural steel seismic force resistancing systems and structural steel elements shall be performed in accordance with Section 1705.2.4.1 and 1705.2.4.2.
1705.2.4.1 Seismic force-resisting systems. | Special inspections of structural steel in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C or D shall be performed in accordance with the quality assurance requirements of AISC 341. Exception: Special inspections per Section 1705.2.4.1 are not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C that are not specifically detailed for seismic resistance, with a response modification coefficient, R, of 3 or less, excluding cantilever column systems.
1705.2.4.2 Structural steel elements. | Special inspections of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C or D other than those covered in Section 1705.2.4.1 of this code, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. Exception: Special inspections of structural steel elements per Section 1705.2.4.2 are not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C with a response modification coefficient, R, of 3 or less.
1705.2.5 Testing for seismic resistance of structural steel. | Nondestructive testing for seismic resistance shall be in accordance with Section 1705.2.5.1 or 1705.2.5.2, as applicable.
1705.2.5.1 Seismic force-resisting systems. | Nondestructive testing of structural steel in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, or D shall be performed in accordance with the quality assurance requirements of AISC 341. Exception: Nondestructive testing is not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C that are not specifically detailed for seismic resistance, with a response modification coefficient, R, of 3 or less, excluding cantilever column systems.
1705.2.5.2 Structural steel elements. | Nondestructive testing of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C or D other than those covered in Section 1705.2.5.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. Exception: Nondestructive testing of structural steel elements is not required in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B or C with a response modification coefficient, R, of 3 or less.
1705.2.6 Cold-formed steel construction. | Special inspections for prefabricated and site built cold-formed steel construction and assemblies used structurally shall be as required by this section and Table 1705.2.6.
1705.2.7 Open-web steel joists and joist girders. | Special inspections of open web steel joists and joist girders in buildings, structures, and portions thereof shall be in accordance with Table 1705.2.7.
1705.3 Concrete construction. | The special inspections and verifications for concrete construction shall be as required by this section and Table 1705.3. Exceptions: 1. Special inspection shall not be required when specifically indicated as not required on the approved construction documents for: 1.1. Nonstructural concrete slabs supported directly on the ground, including prestressed slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 Mpa). 1.2. Concrete foundation(s) for lightweight fences and recreational equipment. 1.3. Concrete patios, site furnishings, garden walls, driveways, sidewalks and similar construction. 2. Testing required by Table 1705.3, Item 6, may be waived by the registered design professional who prepared the approved structural construction documents when such waiver is specifically indicated on such construction documents in the following cases: 2.1. Where the total concrete placement on a given project is less than 50 cubic yards (38.2 m3). 2.2. Isolated spread concrete footings of R-3 buildings three stories or less above grade plan that are fully supported on earth or rock. 2.3. Continuous concrete footings supporting walls of R-3 buildings three stories or less above grade plan that are fully supported on earth or rock where the structural design of the footing is based on a specified compressive strength, f’c, no greater than 2,500 pounds per square inch (psi) (17.2 Mpa), and the compressive strength used in the footing construction is at least 4,000 psi (27.6 Mpa). | 1705.3 Concrete construction. | Special inspections and tests of concrete construction shall be performed in accordance with this section and Table 1705.3. Exceptions: Special inspections and tests shall not be required for: 1. Isolated spread concrete footings of buildings three stories or less above grade plane that are fully supported on earth or rock. 2. Continuous concrete footings supporting walls of buildings three stories or less above grade plane that are fully supported on earth or rock where: 2.1. The footings support walls of light-frame construction. 2.2. The footings are designed in accordance with Table 1809.7. 2.3. The structural design of the footing is based on a specified compressive strength, f c, not more than 2,500 pounds per square inch (psi) (17.2 MPa), regardless of the compressive strength specified in the approved construction documents or used in the footing construction. 3. Nonstructural concrete slabs supported directly on the ground, including prestressed slabs on grade, where the effective prestress in the concrete is less than 150 psi (1.03 MPa). 4. Concrete foundation walls constructed in accordance with Table 1807.1.6.2. 5. Concrete patios, driveways and sidewalks, on grade.
1705.3.1 Materials. | In the absence of sufficient data or documentation providing evidence of conformance to quality standards for materials in Chapter 3 of ACI 318, the commissioner shall require testing of materials in accordance with the appropriate standards and criteria for the material in Chapters 19 and 20 of ACI 318. Weldability of reinforcement, except that which conforms to ASTM A 706, shall be determined in accordance with the requirements of Section 1903.6.2 of this code.
1705.3.2 Concrete construction. | When the specified compressive strength of concrete in a column is greater than 1.4 times that specified for a floor system, the special inspections for concrete construction shall also comply with the requirements of Section 1908.1.4.
1705.4 Masonry construction. | Masonry construction shall be inspected and verified in accordance with the requirements of Sections 1705.4.1 through 1705.4.3, depending on the risk category of the building or structure. Exception: Special inspections shall not be required for: 1. Masonry fireplaces, masonry heaters or masonry chimneys installed or constructed in accordance with Section 2111, 2112, or 2113, respectively. 2. Alterations to existing masonry, where the quantity of replaced masonry is less than 10 square feet (0.93 m2) in any 100 square feet (9.3 m2) of wall area, when specifically exempted on the approved construction documents. | 1705.4 Masonry construction. | Special inspections and tests of masonry construction shall be performed in accordance with the quality assurance program requirements of TMS 402 and TMS 602. Exception: Special inspections and tests shall not be required for: 1. Empirically designed masonry, glass unit masonry or masonry veneer designed in accordance with Section 2109, Section 2110 or Chapter 14, respectively, where they are part of a structure classified as Risk Category I, II or III. 2. Masonry foundation walls constructed in accordance with Table 1807.1.6.3(1), 1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4). 3. Masonry fireplaces, masonry heaters or masonry chimneys installed or constructed in accordance with Section 2111, 2112 or 2113, respectively.
1705.4.1 Empirically designed masonry, glass unit masonry and masonry veneer in buildings in Risk Category IV. | The minimum inspection program for empirically designed masonry, glass unit masonry and masonry veneer designed in accordance with Section 2109, 2110, or Chapter 14 of this code, respectively, or by Chapter 5, 6 or 7 of TMS 402 as modified by Chapter 21 of this code, in structures classified as Risk Category IV, in accordance with Table 1604.5, shall comply with Table 1705.4.1 of this code.
1705.4.2 Masonry in buildings three stories or less in height in Risk Categories I, II, or III. | The minimum special inspection program for structures classified as Risk Categories I, II, or III, in accordance with Table 1604.5, which are three stories or less in height, shall comply with Table 1705.4.1.
1705.4.3 Masonry in buildings greater than three stories in height, and engineered masonry in Risk Category IV. | The minimum special inspection program for masonry designed in accordance with Section 2107 or 2108, or by chapters other than Chapters 5, 6 or 7 of TMS 402 as modified by Chapter 21 of this code, in structures classified as Risk Category IV, in accordance with Table 1604.5 of this code, and masonry in buildings greater than three stories in height, shall comply with Table 1705.4.3 of this code. Exception: Alterations to existing masonry walls where the quantity of masonry involved in any one given location does not exceed 50 contiguous square feet (4.64 m2) shall be permitted to be subject to level 1 special inspection in accordance with Table 1705.4.1 when specifically identified as such on the approved construction documents by the registered design professional of record.
1705.5 Wood construction. | Special inspections of site-built assemblies shall be in accordance with Sections 1705.5.1 through 1705.5.4. Special inspections of the fabrication process of prefabricated wood structural elements and assemblies shall be in accordance with Section 1705.10. | 1705.5 Wood construction. | Special inspections of prefabricated wood structural elements and assemblies shall be in accordance with Section 1704.2.5. Special inspections of site-built assemblies shall be in accordance with this section.
1705.5.1 High-load diaphragms. | High-load diaphragms designed in accordance with Table 2306.2(2) shall be subject to special inspections as indicated in Section 1704.1. The special inspector shall inspect the wood structural panel sheathing to ascertain whether it is of the grade and thickness shown on the approved construction documents. Additionally, the special inspector must verify the nominal size of framing members at adjoining panel edges, the nail or staple diameter and length, the number of fastener lines and that the spacing between fasteners in each line and at edge margins agrees with the approved construction documents. | 1705.5.1 High-load diaphragms. | High-load diaphragms designed in accordance with Section 2306.2 shall be installed with special inspections as indicated in Section 1704.2. The special inspector shall inspect the wood structural panel sheathing to ascertain whether it is of the grade and thickness shown on the approved construction documents. Additionally, the special inspector must verify the nominal size of framing members at adjoining panel edges, the nail or staple diameter and length, the number of fastener lines and that the spacing between fasteners in each line and at edge margins agrees with the approved construction documents.
1705.5.2 Metal-plate-connected wood trusses. | In addition to the requirements of Section 1704.1, metal-plate-connected wood trusses shall be subject to special inspection in accordance with Sections 1705.5.2.1 and 1705.5.2.2.
1705.5.2.1 Erection. | The use of all metal-plate-connected wood trusses shall be subject to special inspection for compliance with the approved construction documents, the requirements of Sections 1704.1, and the following:
1705.5.2.2 Metal-plate-connected wood trusses spanning 60 feet or greater. | Where a truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.
1705.5.3 Prefabricated wood I-joists. | The fabrication of prefabricated wood I-joists shall be subject to special inspections in accordance with Section 1704.2 and the requirements of Section 2303.1.2.
1705.5.3.1 Erection. | The erection of prefabricated wood I-joists shall be subject to special inspection for compliance with the approved construction documents, the requirements of Sections 1704.1, and the following:
1705.5.4 Other structural wood construction. | All other structural wood construction shall be subject to progress inspections for the structural frame to the extent required by Section 110.3.3.
1705.5.5 Special inspection for seismic resistance. | For the seismic force-resisting systems of structures assigned to Seismic Design Category C or D: 1. Continuous special inspection shall be required during field gluing operations of elements of the seismic force resisting system. 2. Periodic special inspection shall be required for nailing, bolting, anchoring and of other elements of the seismic force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, shear panels and hold-downs. Exception: 1. Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the seismic force-resisting system, where the fastener spacing of the sheathing is more than 4 inches (101.6 mm) on center. 2. Where adhesive anchors require continuous special inspection elsewhere in this code, continuous special inspection shall be provided.
1705.5.6 Type IV construction. | Special inspections of Type IV construction utilizing cross-laminated timber or structural composite lumber elements shall be in accordance with Table 1705.5.6.
1705.6 Subsurface conditions. | The special inspections for existing subsurface conditions, fill placement, load-bearing requirements, subsurface investigations, borings and test pits shall be performed in accordance with this section and Table 1705.6 of this code. The approved geotechnical report and construction documents, as applicable, shall be used to determine compliance. Special inspection reports of borings and/or test pits shall be in accordance with ASTM D 1586, ASTM D 1587 and Section 1803.5 of this code.
1705.7 Deep foundation elements. | Installation and testing of deep foundation elements shall be subject to special inspections as specified in Table 1705.7. The approved geotechnical report and construction documents prepared by the registered design professionals shall be used to determine compliance. A special inspector shall be present during the installation and testing of each deep foundation element. The frequency shall be in accordance with the frequency specified in Tables 1705.7, 1705.7.1, 1705.7.2 and 1705.7.3, as applicable. Submittal of records of special inspections required by this section shall be in accordance with Section 1705.7.5.
1705.7.1 Driven and vibrated deep foundation elements. | The installation and testing of driven and vibrated deep foundation elements shall be subject to special inspections as specified in Table 1705.7 and Table 1705.7.1.
1705.9 Helical pile foundations. | Special inspections shall be performed continuously during installation of helical pile foundations. The information recorded shall include installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the registered design professional of record. The approved geotechnical report and the construction documents prepared by the registered design professional and standards established by the commissioner pursuant to Section 28-113.2.2 of the Administrative Code shall be used to determine compliance. The special inspection agency shall submit to the department records of the inspection of the installation of helical piles on forms provided by the department. | 1705.9 Helical pile foundations. | Continuous special inspections shall be performed during installation of helical pile foundations. The information recorded shall include installation equipment used, pile dimensions, tip elevations, final depth, final installation torque and other pertinent installation data as required by the registered design professional in responsible charge. The approved geotechnical report and the construction documents prepared by the registered design professional shall be used to determine compliance.
1705.7.2 Drilled deep foundation elements. | The installation and testing of drilled deep foundation elements shall be subject to special inspections as specified in Table 1705.7 and Table 1705.7.2.
1705.7.3 Cast-in-place deep foundation elements. | The installation and testing of driven or drilled cast-in-place deep foundation elements shall be subject to special inspections as specified in Tables 1705.7, 1705.7.1, 1705.7.2 and 1705.7.3, as applicable.
1705.7.4 Additional inspection. | For methods of deep foundation element installation not covered in Section 1705.7, perform an additional inspection as required by the approved construction documents and record the results noting whether or not the deep foundation element installation complies with the requirements of Sections 1810, 1811, and 1812, and the construction documents. For steel deep foundation elements, perform an additional inspection in accordance with Section 1705.2. For concrete or grout deep foundation elements, and concrete or grout-filled deep foundation elements, perform an additional inspection in accordance with Section 1705.3. For concrete or grout, and concrete or grout filled deep foundation elements, perform an additional inspection in accordance with Section 1705.3.
1705.7.5 Submittal of records of special inspections. | The special inspection agency shall submit to the commissioner records of the inspection of the installation of each deep foundation element. The special inspection agency shall also submit records of testing of deep foundation elements at the request of the commissioner. The submittal shall include the following:
1705.8 Prestressed rock and soil anchors installation and testing and grout inspection. | Special inspection for the installation and testing of permanent prestressed rock and soil anchors shall be performed in accordance with Section 1705.8.1 and Table 1705.8.1. Special inspection for the installation and testing of grout inspection shall be performed in accordance with Section 1705.8.2.
1705.8.1 Prestressed rock and soil anchors. | The installation and testing of permanent prestressed rock and soil anchors shall be subject to special inspections. A special inspector shall be present during the installation of each anchor, including all drilling, grouting, tendon splicing (including corrosion protection) and placement, and installation of any accessories such as trumpets and bearing plates. The special inspector shall also be present for all required load testing and shall create a report containing a log for each element installed and for each load test performed. The special inspection agency shall submit to the commissioner records of the installation of each rock anchor, and where testing is required, the special inspection agency shall also submit records of the testing. The special inspection agency shall submit to the commissioner records of the installation and testing of each anchor.
1705.8.1.1 Records of anchor element installation. | The record of installation of each anchor element shall include, but not be limited to, the following:
1705.8.1.2 Records of testing of anchor elements. | The records of testing of anchor elements shall include, but not be limited to, the following:
1705.8.2 Grout inspection. | Grout inspection shall be in accordance with Sections 1705.3 and 1815.8.
1705.10 Reserved.
1705.11 Reserved.
1705.12 Special inspections for seismic resistance. | Special inspections for seismic resistance shall be required as specified in Sections 1705.12.1 through 1705.12.5, unless exempted by the exceptions of Section 1704.2.
1705.12.1 Designated seismic systems. | For structures assigned to Seismic Design Category C or D, the special inspector shall examine designated seismic systems requiring seismic qualification in accordance with Section 13.2.2 of ASCE 7 and verify that the label, anchorage and mounting conform to the certificate of compliance.
1705.12.2 Access floors. | Periodic special inspection is required for the anchorage of access floors in structures assigned to Seismic Design Category D.
1705.12.3 Plumbing, mechanical, fuel gas, and electrical components. | Periodic special inspection of plumbing, mechanical and electrical components shall be required for the following:
1705.12.4 Storage racks. | Periodic special inspection is required for the anchorage of storage racks that are 8 feet (2438.4 mm) or greater in height in structures assigned to Seismic Design Category D.
1705.12.5 Seismic isolation systems. | Periodic special inspection shall be provided for seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C or D during the fabrication and installation of isolator units and energy dissipation devices.
1705.13 Testing for seismic resistance. | Testing for seismic resistance shall be required as specified in Sections 1705.13.1 through 1705.13.3, unless exempted from special inspections by the exceptions of Section 1704.2.
1705.13.1 Nonstructural components. | For structures assigned to Seismic Design Category B, C, or D where the requirements of Section 13.2.1 of ASCE 7 for nonstructural components, supports or attachments are met by seismic qualification as specified in Item 2 therein, the registered design professional shall specify on the approved construction documents the requirements for seismic qualification by analysis, testing or experience data. Certificates of compliance for the seismic qualification shall be submitted to the commissioner.
1705.13.2 Designated seismic systems. | For structures assigned to Seismic Design Category C or D and with designated seismic systems that are subject to the requirements of Section 13.2.2 of ASCE 7 for certification, the registered design professional shall specify on the approved construction documents the requirements to be met by analysis, testing or experience data as specified therein. Certificates of compliance documenting that the requirements are met shall be submitted to the commissioner.
1705.13.3 Seismic isolation systems. | Seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, or D shall be tested in accordance with Section 17.8 of ASCE 7.
1705.14 Sprayed fire-resistant materials. | Special inspections for sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be in accordance with Sections 1705.14.1 through 1705.14.7. Special inspections shall be based on the fire-resistance design as designated by the approved construction documents. The tests set forth in this section shall be based on samplings from specific floor, roof and wall assemblies and structural members. Special inspections shall be performed after the rough installation of electrical, automatic sprinkler, mechanical and plumbing systems and suspension systems for ceilings, where applicable.
1705.14.1 Physical and visual tests. | The special inspections shall include the following tests and observations to demonstrate compliance with the listing and the fire-resistance rating:
1705.14.2 Structural member surface conditions. | The surfaces shall be prepared in accordance with the approved fire-resistance design and the written instructions of approved manufacturers. The prepared surface of structural members to be sprayed shall be inspected before the application of the sprayed fire-resistant material.
1705.14.3 Application. | The substrate shall have a minimum ambient temperature before and after application as specified in the written instructions of approved manufacturers. The area for application shall be ventilated during and after application as required by the written instructions of approved manufacturers.
1705.14.4 Thickness. | No more than 10 percent of the thickness measurements of the sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be less than the thickness required by the approved fire-resistance design, but in no case less than the minimum allowable thickness required by Section 1705.14.4.1.
1705.14.4.1 Minimum allowable thickness. | For design thicknesses 1 inch (25.4 mm) or greater, the minimum allowable individual thickness shall be the design thickness minus ¼ inch (6.4 mm). For design thicknesses less than 1 inch (25.4 mm), the minimum allowable individual thickness shall be the design thickness minus 25 percent. Thickness shall be determined in accordance with ASTM E 605. Samples of the sprayed fire-resistant materials shall be selected in accordance with Sections 1705.14.4.2 through 1705.14.4.9 of this code.
1705.14.4.2 Floor, roof and wall assemblies. | The thickness of the sprayed fire-resistant material applied to floor, roof and wall assemblies shall be determined in accordance with ASTM E 605, making not fewer than four measurements for each 1,000 square feet (92.9 m2) of the sprayed area in each story or portion thereof.
1705.14.4.3 Cellular decks. | Thickness measurements shall be selected from a square area, 12 inches by 12 inches (304.8 mm by 304.8 mm) in size. A minimum of four measurements shall be made, located symmetrically within the square area.
1705.14.4.4 Fluted decks. | Thickness measurements shall be selected from a square area, 12 inches by 12 inches (304.8 mm by 304.8 mm) in size. Not fewer than four measurements shall be made, located symmetrically within the square area, including one each of the following: valley, crest and sides. The average of the measurements shall be reported.
1705.14.4.5 Structural framing members. | The thickness of the sprayed fire-resistant material applied to structural members shall be determined in accordance with ASTM E 605. Thickness testing shall be performed on not less than 25 percent of the structural members on each floor.
1705.14.4.5.1 Beams and girders. | At beams and girders thickness measurements shall be made at nine locations around the beam or girder at each end of one 12-inch (304.8 mm) length.
1705.14.4.5.2 Joists and trusses. | At joists and trusses, thickness measurements shall be made at seven locations around the joist or truss at each end of one 12-inch (304.8 mm) length.
1705.14.4.5.3 Wide-flanged columns. | At wide-flanged columns, thickness measurements shall be made at 12 locations around the column at each end of one 12-inch (304.8 mm) length.
1705.14.4.5.4 Hollow structural section and pipe columns. | At hollow structural section and pipe columns, thickness measurements shall be made at not fewer than four locations around the column at each end of one 12-inch (304.8 mm) length.
1705.14.5 Density. | The density of the sprayed fire-resistant material shall not be less than the density specified in the approved fire-resistance design. Density of the sprayed fire-resistant material shall be determined in accordance with ASTM E 605. The test samples for determining the density of the sprayed fire-resistant materials shall be selected as follows:
1705.14.6 Bond strength. | The cohesive/adhesive bond strength of the cured sprayed fire-resistant material applied to floor, roof and wall assemblies and structural members shall not be less than 150 pounds per square foot (psf) (7.18 kN/m2). The cohesive/adhesive bond strength shall be determined in accordance with the field test specified in ASTM E 736 by testing in-place samples of the sprayed fire-resistant material selected in accordance with Sections 1705.14.6.1 through 1705.14.6.3 of this code. Exception: For high-rise buildings, as described in Section 403 of this code, refer to the requirements for minimum bond strength in Table 403.2.4 of this code.
1705.14.6.1 Floor, roof and wall assemblies. | The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232.3 m2) or part thereof of the sprayed area in each story. Samples shall be obtained from locations no less than 50 LF (15 240 mm) apart or 10 LF (3048 mm) from any starting edge of an application of a specific type of material.
1705.14.6.2 Structural members. | The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from beams, girders, joists, trusses, columns and other structural members at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232.3 m2) of floor area or portion thereof in each story.
1705.14.6.3 Primer, paint and encapsulant bond tests. | Bond tests to qualify a primer, paint or encapsulant shall be conducted when the sprayed fire-resistant material is applied to a primed, painted or encapsulated surface for which acceptable bond-strength performance between these coatings and the fire-resistant material has not been determined. A bonding agent approved by the SFRM manufacturer shall be applied to a primed, painted or encapsulated surface where the bond strengths are found to be less than required values.
1705.14.7 Inspection of existing sprayed fire-resistant materials during alterations in office spaces and spaces classified in Occupancy Group B. | In office spaces and spaces classified in Occupancy Group B, where an alteration exposes any required sprayed fire-resistant materials on structural members or where, pursuant to an alteration, persons are required to enter or access areas in which such sprayed fire-resistant materials are capable of being observed, the existing required sprayed fire-resistant materials shall be subject to special inspection. Such inspection shall require the special inspector to perform a visual inspection and report the existing sprayed fire-resistant materials and conditions to the registered design professional.
1705.15 Mastic and intumescent fire-resistant coatings. | Special inspections and tests for mastic and intumescent fire-resistant coatings applied to structural elements and decks shall be in accordance with AWCI 12-B. Special inspections and tests shall be based on provisions of AWCI 12-B and the fire-resistance design as designated in the approved construction documents.
1705.16 Combustible exterior wall coverings. | Special inspections shall be required for all exterior wall coverings containing combustible materials installed more than 15 feet (4572 mm) above adjacent finished grades and alterations to existing exterior wall coverings containing combustible materials installed more than 15 feet (4572 mm) above adjacent finished grades. Exterior insulation and finish system (EIFS) applications, metal composite materials (MCM), high-pressure decorative exterior-grade compact laminates (HPL) and exterior wall covering containing combustible veneers, combustible framing, combustible water-resistive barriers and foam plastic insulation installed more than 15 feet (4572 mm) above adjacent finished grades and alterations to existing installations more than 15 feet (4572 mm) above adjacent finished grades shall be inspected in accordance with Section 1705.16.1. Exceptions 1. Water-resistive barriers that are the only combustible component in the exterior wall covering satisfying the requirements of Exceptions 1 or 2 of Section 1403.5.1. 2. Type VB construction up to 40 feet (12 192 mm) or less in height above grade.
1705.16.1 Inspection program. | The special inspection shall include verification of compliance with the approved construction documents for the following: attachment to structure; component properties; thicknesses, orientation, cavity sizes and location of thermal barriers, fireblocking and cavity closures; installation of waterproofing membranes, weeps, drains, mold prevention features are as specified; and conformance with the manufacturers’ installation instructions, and NFPA 285 tested assembly design documentation. The special inspector shall verify that individual components required to be labeled in accordance with this code do bear such labels.
1705.16.2 Water-resistive barrier coating. | A water-resistive barrier coating complying with ASTM E 2570 requires special inspection of the water-resistive barrier coating when installed over a sheathing substrate. Inspection of water-resistive barrier coating must verify conformance with approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation.
1705.16.3 Thermal barrier. | The special inspector shall confirm the installation of the thermal barrier is in accordance with the approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation. Exception: Foam plastic insulation installation on one-story buildings not required to have thermal barrier complying with Section 2603.4.1.4 of this code.
1705.16.4 Fireblocking. | The special inspector shall confirm the installation of fireblocking is in accordance with Chapter 7 of this code, the approved construction documents, manufacturer’s installation instructions, and NFPA 285 tested assembly design documentation. Exception: EIFS systems and exterior wall coverings not required to have fireblocking pursuant to Section 718.2.6.1 of this code.
1705.17 Fire-resistant penetrations and joints. | Special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems, and perimeter fire barrier systems that are tested and listed in accordance with Sections 714.3.1.2, 714.4.2, 715.3 and 715.4 shall comply with Sections 1705.17.1 and 1705.17.2.
1705.17.1 Penetration firestops. | Inspections of penetration firestop systems that are tested and listed in accordance with Sections 714.3.1.2 and 714.4.2 of this code shall be conducted by an approved special inspection agency in accordance with ASTM E 2174.
1705.17.2 Joint systems. | Inspection of fire-resistant joint systems that are tested and listed in accordance with Sections 715.3 and 715.4 of this code shall be conducted by an approved special inspection agency in accordance with ASTM E 2393.
1705.18 Testing for smoke control. | Testing of smoke control systems shall be witnessed in its entirety by a special inspector in accordance with Sections 1705.18.1 and 909. Exception: Post-fire smoke purge systems that are not required to function as a smoke control system shall be permitted to be inspected pursuant to the special inspection requirements of Section 1705.21.
1705.18.1 Testing scope. | The test scope shall be as follows:
1705.19 Vertical masonry foundation elements. | Special inspection shall be performed in accordance with Section 1705.4 for vertical masonry foundation elements. Exception: Piers for support of lightweight fences, recreational equipment, site furnishings and similar construction, unless special inspection is specifically noted as required on the approved construction documents.
1705.20 Wall panels, curtain walls and veneers. | Special inspection is required for exterior architectural wall panels, curtain walls and the anchoring of veneers for the full height of the installation when any portion of the wall panel, curtain wall and veneer installation exceeds an elevation of 40 feet (12 192 mm) above grade. Special inspection of masonry veneer on such structures shall be in accordance with Section 1705.4. Special inspection of combustible exterior wall covering shall be in accordance with Section 1705.16. Exceptions: Special inspection of wall panels, curtain walls and the anchoring of veneers is not applicable to: 1. Repairs and replacement in kind of gaskets or seals; 2. Reglazing other than 4-sided structural silicone glazing for which a permit is required; or 3. Where exempted by the rules of the department.
1705.20.1 Design and installation documents. | The special inspector shall become familiar with and retain a copy of the approved construction documents, and the following items, as applicable, approved by the registered design professional of record:
1705.20.2 Inspection program. | The special inspector shall field check the site conditions at the time the structure is prepared for component installation, and periodically during component installation, to verify the following work is performed in compliance with the approved construction documents, including that:
1705.21 Special inspection for mechanical systems. | Mechanical systems that require a certificate of compliance in accordance with Section 28-116.4.1 of the Administrative Code shall be inspected for conformance with the approved construction documents.
1705.21.1 Tests for mechanical systems. | Tests of mechanical systems shall be performed in accordance with applicable sections of the code including Sections 507.6, 1011, 1108 and 1208 of the New York City Mechanical Code. The special inspector shall witness all required tests.
1705.21.2 Factory built equipment. | Listed and labeled self-contained factory-built equipment and appliances deemed by the registered design professional to meet the design, manufacture and factory test requirements of this code shall be field tested in accordance with the manufacturers’ installation and operational test standards.
1705.21.3 Special inspection of mechanical systems. | Inspections of mechanical systems shall include the following as applicable to the system:
1705.22 Special inspection for fuel storage and fuel-piping systems. | Fuel-oil storage equipment, including tanks, pumps, valves, transfer, return, fill and vent piping, hangers and bracing, fill and vent terminals, and related systems regulated by Section 1305 of the New York City Mechanical Code, shall be inspected for conformance with the approved construction documents and the manufacturers’ installation standards. Testing of fuel storage tanks and piping shall be performed in accordance with Section 1305 of the New York City Mechanical Code. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code. Exceptions: 1. Listed fuel oil storage tanks 660 gallons (2498.4 L) or less in capacity, supplied with a label or manufacturer’s certification attesting that the tank was factory tested to a testing standard indicated in Section 1308.1 of the New York City Mechanical Code. 2. Systems and equipment exempt from service equipment certificate of compliance in accordance with Section 28-116.4.1 of the Administrative Code.
1705.23 High-pressure-steam piping and high temperature hot water piping. | High-pressure-steam piping and high temperature hot water piping regulated by Section 1211 of the New York City Mechanical Code, shall be subject to special inspection in accordance with this section. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code.
1705.23.1 Welding. | The special inspector shall verify the qualifications of the welder and the quality of the welding materials and equipment prior to welding operations. The special inspector shall review the proposed welding procedures for compliance with applicable standards listed in Section 1211.2.2 of the New York City Mechanical Code.
1705.23.2 Welding operations. | The special inspector shall perform periodic inspection of the pipe joining and welding operations in accordance with the above. Radiographic testing shall be applied to connections as indicated in Section 1211.2.2 of the New York City Mechanical Code. Unacceptable connections and installations shall be rejected.
1705.23.3 Testing of high-pressure-steam systems and high temperature hot water piping systems. | Hydrostatic testing shall be performed on the completed installation of new and altered systems in accordance with Section 1211.2.3 of the New York City Mechanical Code. The special inspector shall witness all required hydrostatic tests. Exception: Testing requirements shall not apply to alteration or repairs to existing piping systems in which the integrity of the piping is not affected. Such alterations shall be visually inspected for compliance with the approved construction documents.
1705.24 High-pressure-gas piping. | High-pressure-gas piping regulated in Section 406 of the New York City Fuel Gas Code shall be subject to special inspection in accordance with this section. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code.
1705.24.1 Welding. | The special inspector shall verify the qualifications of the welder, the quality of the welding materials and equipment prior to welding operations. The special inspector shall review the proposed welding procedures for compliance with applicable standards listed in Section 406 of the New York City Fuel Gas Code.
1705.24.2 Welding operations. | The special inspector shall perform periodic special inspection for the pipe joining and welding operations in accordance with the above. Radiographic testing shall be performed to the connections as indicated in Section 406 of the New York City Fuel Gas Code.
1705.24.3 Testing of high-pressure-gas piping. | Pressure testing shall be performed on the completed installation of new and altered systems in accordance with Section 406 of the New York City Fuel Gas Code. The special inspector shall witness all required pressure tests.
1705.25 Structural stability. | Special inspection for structural stability is an inspection of a structure to verify the ability of such structural system to remain in position, or revert to the original position or another stable equilibrium position acceptable by this code, without incurring damage to the structural system from the activity or load to which it had been subjected until the completion of construction. Such special inspection shall be required for construction work as specified in this section or elsewhere in this code. Structural materials and methods of construction utilized in temporary protections shall be subject to special inspection when such materials and methods of construction would be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including but not limited to special inspections for concrete, structural steel, and deep foundation installation. The registered design professional responsible for plans for a new building, alteration, or other work requiring structural stability inspections shall identify those areas on the plans submitted to the department in accordance with Section 1704.1.1.1. The means and methods of implementing the structural stability measures shall be prepared by a registered design professional and filed with the department where required in this section and elsewhere in this code. Exception: Alterations consisting of the replacement of existing exterior lintels located less than 75 feet (22 860 mm) above curb level spanning less than 4 feet (1220 mm) and existing interior headers spanning less than 4 feet (1220 mm), provided the size of the existing span is not increased, shall be exempt from special inspection for structural stability.
1705.25.1 Alterations to existing structures. | Alterations to existing structures in which loads are transferred from one structural system of structural elements to another, such as installation of columns or girders, replacement of existing bearing walls, the creation of openings or slots in existing walls, girders or floors, alteration of arches, rigid frames, trusses in frame buildings, where the stability or integrity of a structural system is to be temporarily diminished, or where otherwise required by the commissioner, shall be subject to special inspections in accordance with Sections 1705.25.7 through 1705.25.10.
1705.25.2 Construction operations influencing adjacent structures. | Where construction operations have the potential to affect structurally the condition or occupancy of the subject structure and/or an adjacent structure, the structural stability of such structures shall be subject to special inspections in accordance with Sections 1705.25.7 through 1705.25.10.
1705.25.3 Excavations. | Methods employed to protect the sides of excavations meeting the requirements of exception 1 of Section 3304.4.1, and blasting for the purpose of excavation shall be subject to special inspections in accordance with Sections 1705.25.7 through 1705.25.10.
1705.25.3.1 Slurry. | The proportions and installation of slurry mixtures to protect the sides of excavations shall be subject to special inspection. Slurry mix proportions and installation procedures shall be provided by a registered design professional, and the special inspection agency shall verify compliance with the approved procedures.
1705.25.3.2 New foundations. | In addition to the special inspection for structural stability, any new foundation elements installed as part of support of excavation operations shall be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including, but not limited to, special inspection for concrete, structural steel, and deep foundation installation.
1705.25.3.3 Effect of blasting. | Adjoining properties shall be subject to special inspection for structural stability due to the effects of blasting when blasting is utilized for excavation.
1705.25.4 Underpinning and alternate methods of support of buildings and adjacent property. | Underpinning of structures and alternate methods of support of buildings and adjacent property shall be subject to special inspections in accordance with Sections 1705.25.7 through 1705.25.10.
1705.25.4.1 New foundations. | In addition to the special inspection for structural stability, any new foundation elements installed as part of underpinning operations shall be subject to special inspection as a permanent installation in accordance with the applicable sections of this chapter, including, but not limited to, special inspection for concrete, structural steel, and deep foundation installation.
1705.25.5 Demolition. | Demolition operations shall be subject to special inspection in accordance with Sections 1705.25.5.1 and 1705.25.5.2 as applicable to the operations.
1705.25.5.1 Mechanical means and methods of demolition. | Where mechanical demolition equipment, other than handheld devices, is to be used in the full or partial demolition of a building from within the building, or is to be used within the building to remove debris or move material, such demolition operation shall be subject to special inspection in accordance with Sections 1705.25.7 through 1705.25.10. The special inspector shall visit the site a minimum of three times: before demolition operations start, during demolition, and at the conclusion of demolition. Additionally, the special inspector shall visit the site at minimum intervals identified in the design documents and set forth in Section 1705.25.8.2.
1705.25.5.2 Other means of demolition. | Where full or partial demolition of a weakened structure as specified in Section 3306.7 or the demolition of a masonry wall with a height to thickness ratio of 16 or greater is proposed, or the demolition of a floor structure directly supported by such wall, such demolition operation shall be subject to special inspection in accordance with Sections 1705.25.7 through 1705.25.10. The special inspector shall visit the site a minimum of three times: before demolition operations start, during demolition, and at the conclusion of demolition. Additionally, the special inspector shall visit the site at minimum intervals identified in the design documents and set forth in Section 1705.25.8.2.
1705.25.6 Raising and moving of a building. | A periodic special inspection shall be required in accordance with Sections 1705.25.7 through 1705.25.10 where the lowest above-grade floor or the lowest subgrade floor of a building is to be raised, lifted, elevated or moved.
1705.25.7 Inspection program. | Prior to commencement of work requiring special inspection per Section 1705.25, the special inspector shall review the approved construction documents, related reports, and contractor’s sequence of operations and confirm that all areas of work requiring special inspection per Section 1705.25 have design documents addressing the structural stability temporary protections and sequence. A written statement shall be included in the design documents prepared in accordance with Section 1705.25.8, indicating:
1705.25.8 Design documents. | Design documents, including shop drawings, sketches and written descriptions of proposed work regarding structural stability in construction operations shall be prepared by a registered design professional in the employ of the owner or the contractor. Where required by this section or elsewhere in this code, the work associated with the structural stability protection methods shall be filed with the department. When filing of the design of protection methods is not required, such designs may be revised at any time by the registered design professional. Copies of the special inspection log book, the design documents and revisions thereof, shall be maintained at the job site, and at the office of the special inspector, available for use and review at all reasonable times, until the work subject to special inspection is complete. In the case of alteration to existing structures, the structural stability design documents shall be reviewed by the registered design professional of record.
1705.25.8.1 Monitoring. | The design documents for structural stability shall include any requirements for monitoring of the subject structure and/or adjacent structures, as determined by the registered design professional responsible for the design. The monitoring plan shall be specific to the buildings to be monitored and operations to be undertaken, and shall specify the scope and frequency of monitoring, acceptable tolerances, and reporting criteria for when tolerances are exceeded, including when the department is required to be notified. The monitoring plan shall include provisions for daily monitoring, at a minimum, until the structural stability protection methods are no longer necessary. Such monitoring can be accomplished by remote means, in-person monitoring or any combination thereof.
1705.25.8.1.1 Additional monitoring requirements for demolition. | The design documents for structural stability shall identify and specify the monitoring required for the demolition operation and be specific to all phases of the demolition operation. These specifications must be part of the requirements identified for special inspection.
1705.25.8.2 Additional requirements for design documents for demolition. | Design documents for demolition shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the demolition sequence. Building components and phases of demolition deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1.
1705.25.8.3 Additional requirements for design documents for underpinning and alternate methods of support of buildings and adjacent property. | Design documents for underpinning and alternate methods of support of buildings and adjacent property shall comply with the requirements of Section 1817. Such drawings shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the sequence of operations. Building components and phases of operations deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1. At a minimum, underpinning shall be subject to continuous special inspection for structural stability of the structure being underpinned while work is occurring.
1705.25.8.4 Additional requirements for design documents for protection of the sides of excavations and blasting. | Design documents for protection of the sides of excavations and blasting methods of support of buildings and adjacent property shall indicate a project-specific required minimum interval for special inspections. A written statement of what the special inspection must include shall be provided on the design documents. The minimum special inspection interval must be incorporated into the sequence of operations. Building components and phases of operations deemed to be structurally critical must be identified for inspection. A monitoring protocol must be provided in accordance with the requirements of Section 1705.25.8.1.1. At a minimum, protection of the sides of excavations and blasting work shall be subject to continuous special inspection for structural stability of the structure or adjacent property being affected while work is occurring.
1705.25.9 Inspection during construction operations. | The special inspector shall visit the jobsite at agreed intervals, assess the ongoing work and verify that operations conform with the design documents. Deficiencies shall be reported as required by Section 1704.1.2. In the event unsafe conditions are discovered, the commissioner and the registered design professional employed by the contractor shall be immediately notified by the special inspector.
1705.25.10 Records of special inspections. | The special inspection logbook shall be maintained at the special inspector’s office and shall contain the following information:
1705.26 Tenant protection plan compliance. | When alteration, partial demolition, or construction operations are performed at occupied multiple dwellings, the special inspector shall periodically verify compliance with a tenant protection plan as provided for in Chapter 1 of Title 28 of the Administrative Code and Section 3303.10 of this code. Special inspections for compliance with the tenant protection plan shall comply with Sections 1705.26.1 and 1705.26.2 of this code. Exceptions: Special inspection for tenant protection plan compliance is not required where the scope of the work is limited to: 1. A three-family home; 2. The interior of a single dwelling unit of an occupied multiple dwelling with no disruption to the essential services of other units, where such dwelling is owner-occupied. For a dwelling unit within a property that is owned by a condominium or held by a shareholder of a cooperative corporation under a proprietary lease, the unit must be occupied by the owners of record for such unit; or 3. The interior of a single dwelling unit of an occupied multiple dwelling three stories or less in height.
1705.26.1 Inspection frequency. | Special inspections shall be performed throughout the duration of the tenant protection plan at sufficient periodic intervals to verify compliance with the tenant protection plan throughout the course of work. At a minimum, inspections shall be performed:
1705.26.2 Reporting. | A written record of the special inspections performed for the tenant protection plan shall be maintained in a log prepared by the special inspector. The log shall include an entry for each inspection and shall indicate that the alteration or construction operation is being performed in accordance with the tenant protection plan. Copies of the special inspection log book shall be maintained at the job site, and at the office of the special inspector, and shall be available for use and review at all reasonable times, until the work subject to special inspection is complete.
1705.27 Private on-site storm water disposal systems and detention facilities. | Storm water detention and retention systems required to comply with Section 1114 of the New York City Plumbing Code, and roof detention facilities shall be inspected for compliance with the provisions of this section.
1705.27.1 Subsurface investigation special inspection. | Soil borings, testpits and soil percolation testing shall be subject to the special inspection requirements of this section.
1705.27.1.1 Soil borings and testpits. | Prior to the approval of construction documents, soil borings and testpits shall be performed in accordance with the provisions of Section 1114.2.1 of the New York City Plumbing Code. Soil borings and testpits shall be performed under the supervision of a special inspector. The results of the soil borings and testpits shall be filed on forms provided by the department.
1705.27.1.2 Soil percolation tests. | Prior to the approval of construction documents, soil percolation tests shall be performed in accordance with the provisions of Section 1114.2.2 of the New York City Plumbing Code at the site of a proposed on-site stormwater drainage and detention facility installation to determine the suitability of the soil and site. Such test shall be performed under the supervision of a special inspector. The results of the percolation tests shall be filed on forms provided by the department, stating the suitability of the site and the capacity of the subsoil for the proposed use. The registered design professional of record for the dry-well system shall be notified immediately if the results of the percolation test demonstrate that the system may not function as designed.
1705.27.2 Installation special inspection. | Private on-site stormwater disposal systems and detention facilities shall be inspected for conformance with the approved construction documents. Minor variations, based on actual site conditions, shall be acceptable at the discretion of the registered design professional of record. Verification shall include:
1705.28 Individual on-site private sewage disposal systems. | Individual on-site private sewage disposal systems shall be inspected in accordance with the rules of the department.
1705.29 Sprinkler system special inspection. | New and altered sprinkler systems shall be inspected in accordance with Sections 903 and 1705.29.1. The permit holder responsible for the sprinkler work shall perform all required acceptance tests, complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests and shall verify that all installations of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that painting of the sprinkler system required by Section 903.6 of this code has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the Department of Buildings. Seismic bracing shall be inspected in accordance with Section 1705.12. Exception: If the department witnesses a hydrostatic pressure test, it need not be witnessed by the special inspection agency.
1705.29.1 Hydrostatic pressure testing. | All new or altered sprinkler systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5 of this code, and NFPA 13. Exceptions: Modification of six or fewer sprinklers: 1. May be tested under working pressure in lieu of hydrostatic testing, or 2. Need not be witnessed by a special inspection when the hydrostatic test is performed by the licensed installing contractor.
1705.30 Standpipe system special inspection. | New and altered standpipe systems shall be inspected in accordance with Sections 905 and 1705.30.1. Fire pump tests associated with standpipe systems shall be tested in accordance with Section 1705.30.2. The permit holder responsible for the standpipe work shall perform all required acceptance tests, and complete and sign the appropriate contractor’s material and test certifications. The special inspector shall witness all required tests, verify that installation of all materials, fittings, hangers, assemblies and signage are in accordance with the approved construction documents, that painting of the standpipe system required by Section 905.11 has been performed and that the contractor has transmitted required maintenance literature and instruction to the owner. The special inspector shall verify that the material and test certification forms have been transmitted to the Fire Department and the Department of Buildings. Seismic bracing shall be inspected in accordance with Section 1705.12. Exception: The special inspection agency need not witness the hydrostatic pressure test when such test is witnessed by the department.
1705.30.1 Hydrostatic pressure testing. | All new or altered standpipe systems in buildings shall undergo successful hydrostatic pressure testing by a licensed master plumber or licensed fire suppression piping contractor in accordance with the requirements of this code, including Section 901.5, Sections 1705.30.1.1 through 1705.30.1.5 and NFPA 14. Exception: When the standpipe system is exposed to freezing conditions, a hydrostatic pressure test required by this section may be postponed until such conditions no longer exist, notwithstanding any requirement that the standpipe be maintained in a state of readiness, provided that the system undergoes an interim test with dry nitrogen or air using a compressor in accordance with NFPA 14. Any such air pressure tests shall be witnessed by the special inspector unless witnessed by the department.
1705.30.1.1 New buildings under construction. | For standpipes required to comply with Section 3303.8 of this code, an initial hydrostatic pressure test of the entire system shall be performed when the building reaches a height of 75 feet (22 860 mm) and additional successful hydrostatic pressure tests of the entire system shall be performed at 175 feet (53 340 mm), and at every 100 feet (30 480 mm) in height thereafter. The permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5.
1705.30.1.2 Enlargements or additions to existing system. | Where there is an enlargement that triggers a new standpipe system or there is an addition to an existing standpipe system, hydrostatic pressure tests of the entire system shall be performed for every 75 feet (22 860 mm) of additional height added to the system. The permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5.
1705.30.1.3 Removal of stories, including full demolitions. | Where stories are removed from a building served by an existing standpipe system, hydrostatic pressure tests of the entire system shall be performed prior to the commencement of work.
1705.30.1.4 Alterations. | For alterations not covered under Sections 1705.30.1.2 or 1705.30.1.3 above, the permit holder shall perform a final acceptance test of the completed system in accordance with the requirements of Section 901.5.
1705.30.1.5 Readiness. | No standpipe system shall be considered in readiness until there has been a successful hydrostatic pressure test.
1705.30.2 Fire pump tests. | Fire pump tests associated with standpipe systems shall be tested in accordance with Section 913.5 of this code. The special inspector shall witness all required tests and shall verify that all installations comply with NFPA 20 and are in accordance with the approved construction documents.
1705.31 Heating systems. | Special inspection shall be required for new and altered boilers and heating systems. All boilers and heating systems, including chimney connectors, shall be inspected for compliance with the approved construction documents. New heating systems shall be tested in accordance with Section 1011 of the New York City Mechanical Code. Alterations to heating systems shall be subjected to applicable tests for the altered portions of the system and to verify its satisfactory operation within the existing system. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code. Exception: Tests and inspections need not duplicate any valid tests or inspections previously certified by the commissioner or a duly authorized insurance company.
1705.32 Chimneys and vents. | New and altered chimneys and vents, replacing an existing appliance in accordance with Section 503.5.6 of the New York City Fuel Gas Code, or change in appliance in accordance with Section 507 of the New York City Fuel Gas Code and Section 807 of the New York City Mechanical Code shall be subject to special inspection. The chimney or vent shall be inspected to verify compliance with the approved construction documents, and proper clearance or isolation from adjacent combustible construction. Testing of the chimney or vent shall be performed as applicable in accordance with Section 810 of the New York City Mechanical Code and Section 503.5.6 of the New York City Fuel Gas Code. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code. Exception: A pressurized smoke test need not be performed on existing and new Listed Type B gas vents and Type L vents. Listed Type B gas vents and Type L vents shall be visually inspected for the presence of a continuous inner wall, proper installation, and no damage or deterioration via readily accessible areas of the vent system, such as the appliance, tee caps, cleanout openings, or termination. The vent system shall be inspected for proper clearances, protection and damage.
1705.32.1 Reuse of existing chimneys. | When a new heating system appliance is installed, the special inspector shall verify the condition of the existing chimney lining and breaching. Deficiencies shall be reported as required by Section 1704.1.1.2.
1705.33 Aluminum construction. | The special inspections for structural aluminum elements of buildings and structures shall be as required by Section 1705.33.1.
1705.33.1 Welding operations. | All welding operations of aluminum elements shall be subject to special inspection for compliance with this code, AA ADM and AWS D1.2. Exception: Welding operations in connections where the calculated stresses in the welds are less than 50 percent of the basic allowable values. Such connections shall be specifically indicated on the approved construction documents.
1705.34 Flood zone compliance. | Special inspection for flood zone compliance shall be as required by Appendix G of this code.
1705.35 Luminous exit path markings. | The installation of luminous exit path markings shall be subject to special inspection in accordance with the requirements of Section 1025.8. The special inspector shall verify that approved luminous exit path markings were provided and installed in accordance with Section 1704, the approved construction documents, and manufacturer’s instructions.
1705.36 Emergency and standby power systems (generators). | The installation of generators as part of emergency and standby power systems shall be subject to special inspection. The special inspector shall: perform visual inspections; verify that the installations of all materials, equipment and signage complies with the installation standards; and verify that the installation of the generator and associated connections complies with the approved construction documents. The special inspector shall witness tests that verify the automatic operation of the emergency or standby power system in accordance with NFPA 110 and NFPA 111. Deficient results shall be rejected, and deficiencies shall be corrected and successfully retested in the presence of the special inspector prior to sign-off of the emergency or standby power system special inspection. Special inspection of seismic bracing shall be performed in accordance with Section 1705.12 of this code.
1705.37 Post-installed anchors. | The installation of post-installed mechanical anchors, adhesive anchors, and screw anchors shall comply with Table 1705.37. The special inspection shall include the verification of compliance with approved construction documents and standards established by the commissioner pursuant to Section 28-113.2.2 of the Administrative Code.
1705.38 Special inspection for nonpotable water systems. | Testing and inspection of nonpotable water systems shall be in accordance with Chapter 13 of the New York City Plumbing Code. The special inspector shall witness all required tests in accordance with Chapter 13 of the New York City Plumbing Code.
1705.38.1 Tests for nonpotable water systems. | Tests of nonpotable water systems shall be performed in accordance with Sections 1705.38.1.1 through 1705.38.1.2 of this code.
1704.38.1.1 Water storage tanks. | Water storage tanks shall be tested in accordance with Sections 1302.12.2 and 1303.15.4 of the New York City Plumbing Code.
1705.38.1.2 Roofwashers. | Roofwashers shall be tested in accordance with Section 1303.15.2 of the New York City Plumbing Code.
1705.38.2 Special inspection of nonpotable water systems. | Inspections of nonpotable water systems shall include the following as applicable to the system:
1705.38.2.1 Visual inspection that components of such systems are complete in accordance with the manufacturers’ instructions and the approved construction documents;.
1705.38.2.2 Required labeling, operational instructions and safety signage properly posted.
1705.38.2.3 Inspection of vermin and insect protection. | Inlets and vents to the system shall be inspected in accordance with Sections 1302.12.5 and 1303.15.7 of the New York City Plumbing Code.
1705.39 Special inspection for exhaust and vent systems in plenums and ducts. | Chimneys, vents, and exhaust systems under positive pressure that penetrate ducts or plenums installed in accordance with exceptions 1 and 2 of Section 601.4 of the New York City Mechanical Code shall be inspected for conformance with the approved construction documents.
1705.39.1 Visual inspection. | Visual inspection shall confirm that joints, seams, and connections of covered mechanical systems are securely fastened and sealed with welds, gaskets, mastics (adhesives), mastic-plus-embedded-fabric systems, liquid sealants or tapes.
1705.39.2 Smoke test. | The special inspection shall include witnessing the system smoke test performed in accordance with Section 810 of the New York City Mechanical Code.
1706.1 Conformance to standards. | The design strengths and permissible stresses of any structural material that are identified by a manufacturer’s designation as to manufacture and grade by mill tests, or the strength and stress grade is otherwise confirmed to the satisfaction of the commissioner shall con­form to the specifications and methods of design of accepted engineering practice or the rules of the department in the absence of applicable standards. | 1706.1 Conformance to standards. | The design strengths and permissible stresses of any structural material that are identified by a manufacturer’s designation as to manufacture and grade by mill tests, or the strength and stress grade is otherwise confirmed to the satisfaction of the building official, shall conform to the specifications and methods of design of accepted engineering practice or the approved rules in the absence of applicable standards.
1706.2 New materials. | For materials that are not specifically provided for in this code, the design strengths and permissible stresses shall be established by tests as provided for in Section 1707. | 1706.2 New materials. | For materials that are not specifically provided for in this code, the design strengths and permissible stresses shall be established by tests as provided for in Section 1707.
1707.1 General. | In the absence of rules or other approved standards, and upon special application by a registered design professional the commissioner shall make, or cause to be made, the necessary tests and investigations; or the commissioner shall accept duly authenticated reports from approved agencies in respect to the quality and manner of use of new materials or assemblies as provided for in Article 113 of Chapter 1 of Title 28 of the Administrative Code. The cost of all tests and other investigations required under the provisions of this code shall be borne by the permit applicant. | 1707.1 General. | In the absence of approved rules or other approved standards, the building official shall make, or cause to be made, the necessary tests and investigations; or the building official shall accept duly authenticated reports from approved agencies in respect to the quality and manner of use of new materials or assemblies as provided for in Section 104.11. The cost of all tests and other investigations required under the provisions of this code shall be borne by the owner or the owner’s authorized agent.
1708.1 General. | Whenever there is a reasonable doubt as to the stability or load-bearing capacity of a completed building, structure or portion thereof for the expected loads, an engineering assessment shall be required. The engineering assessment shall involve either a structural analysis or an in-situ load test, or both. The structural analysis shall be based on actual material properties and other as-built conditions that affect stability or load-bearing capacity, and shall be conducted in accordance with the applicable design standard. If the structural assessment determines that the load-bearing capacity is less than that required by the code, load tests shall be conducted in accordance with Section 1708.2. If the building, structure or portion thereof is found to have inadequate stability or load-bearing capacity for the expected loads, modifications to ensure structural adequacy or the removal of the inadequate construction shall be required. | 1708.1 General. | Whenever there is a reasonable doubt as to the stability or load-bearing capacity of a completed building, structure or portion thereof for the expected loads, an engineering assessment shall be required. The engineering assessment shall involve either a structural analysis or an in-situ load test, or both. The structural analysis shall be based on actual material properties and other as-built conditions that affect stability or load-bearing capacity, and shall be conducted in accordance with the applicable design standard. The in-situ load tests shall be conducted in accordance with Section 1708.2. If the building, structure or portion thereof is found to have inadequate stability or load-bearing capacity for the expected loads, modifications to ensure structural adequacy or the removal of the inadequate construction shall be required.
1708.2 Test standards. | Structural components and assemblies shall be tested in accordance with the appropriate material stan­dards listed in Chapter 35. In the absence of a standard that contains an applicable load test procedure, the test procedure shall be developed by a registered design professional and approved. The test procedure shall simulate loads and conditions of application that the completed structure or portion thereof will be subjected to in normal use.
1708.3 In-situ load tests. | In-situ load tests shall be conducted in accordance with Section 1708.3.1 or Section 1708.3.2 and shall be supervised by a registered design professional. The test shall simulate the applicable loading conditions specified in Chapter 16 as necessary to address the concerns regarding structural stability of the building, structure or portion thereof.
1708.3.1 Load test procedure specified. | Where a standard listed in Chapter 35 contains an applicable load test procedure and acceptance criteria, the test procedure and acceptance criteria in the standard shall apply. In the absence of specific load factors or acceptance criteria, the load factors and acceptance criteria in Section 1708.3.2 shall apply.
1708.3.2 Load test procedure not specified. | In the absence of applicable load test procedures contained within a standard referenced by this code or acceptance criteria for a specific material or method of construction, such existing structure shall be subjected to a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components that are not a part of the seismic-load-resisting system, the test load shall be equal to two times the unfactored design loads. The test load shall be left in place for a period of 24 hours. The structure shall be considered to have successfully met the test requirements where the following criteria are satisfied:
1709.1 General. | In evaluating the physical properties of materials and methods of construction that are not capable of being designed by approved engineering analysis or do not comply with applicable material design standards listed in Chapter 35, the structural adequacy shall be predetermined based on the load test criteria established in this section. | 1709.1 General. | Where proposed construction is not capable of being designed by approved engineering analysis, or where proposed construction design method does not comply with the applicable material design standard, the system of construction or the structural unit and the connections shall be subjected to the tests prescribed in Section 1709. The building official shall accept certified reports of such tests conducted by an approved testing agency, provided that such tests meet the requirements of this code and approved procedures.
1709.2 Load test procedures specified. | Where specific load test procedures, load factors and acceptance criteria are included in the applicable design standards listed in Chapter 35, such test procedures, load factors and acceptance criteria shall apply. In the absence of specific test procedures, load factors or acceptance criteria, the corresponding provisions in Section 1709.3 shall apply. | 1709.2 Load test procedures specified. | Where specific load test procedures, load factors and acceptance criteria are included in the applicable referenced standards, such test procedures, load factors and acceptance criteria shall apply. In the absence of specific test procedures, load factors or acceptance criteria, the corresponding provisions in Section 1709.3 shall apply.
1709.3 Load test procedures not specified. | Where load test procedures are not specified in the applicable design standards listed in Chapter 35, the load-bearing and deformation capacity of structural components and assemblies shall be determined on the basis of a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components and assemblies that are not a part of the seismic-load-resisting system, the test shall be as specified in Section 1709.3.1. Load tests shall simulate the applicable loading conditions specified in Chapter 16. | 1709.3 Load test procedures not specified. | Where load test procedures are not specified in the applicable referenced standards, the load-bearing and deformation capacity of structural components and assemblies shall be determined on the basis of a test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components and assemblies that are not a part of the seismic force-resisting system, the test shall be as specified in Section 1709.3.1. Load tests shall simulate the applicable loading conditions specified in Chapter 16.
1709.3.1 Test procedure. | The test assembly shall be subjected to an increasing superimposed load equal to not less than two times the superimposed design load. The test load shall be left in place for a period of 24 hours. The tested assembly shall be considered to have successfully met the test requirements if the assembly recovers not less than 75 percent of the maximum deflection within 24 hours after the removal of the test load. The test assembly shall then be reloaded and subjected to an increasing superimposed load until either structural failure occurs or the superimposed load is equal to two and one-half times the load at which the deflection limitations specified in Section 1709.3.2 were reached, or the load is equal to two and one-half times the superimposed design load. In the case of structural components and assemblies for which deflection limitations are not specified in Section 1709.3.2, the test specimen shall be subjected to an increasing superimposed load until structural failure occurs or the load is equal to two and one-half times the desired superimposed design load. The allowable superimposed design load shall be taken as the lesser of: | 1709.3.1 Test procedure. | The test assembly shall be subjected to an increasing superimposed load equal to not less than two times the superimposed design load. The test load shall be left in place for a period of 24 hours. The tested assembly shall be considered to have successfully met the test requirements if the assembly recovers not less than 75 percent of the maximum deflection within 24 hours after the removal of the test load. The test assembly shall then be reloaded and subjected to an increasing superimposed load until either structural failure occurs or the superimposed load is equal to two and one-half times the load at which the deflection limitations specified in Section 1709.3.2 were reached, or the load is equal to two and one-half times the superimposed design load. In the case of structural components and assemblies for which deflection limitations are not specified in Section 1709.3.2, the test specimen shall be subjected to an increasing superimposed load until structural failure occurs or the load is equal to two and one-half times the desired superimposed design load. The allowable superimposed design load shall be taken as the least of:
1709.3.2 Deflection. | The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3. | 1709.3.2 Deflection. | The deflection of structural members under the design load shall not exceed the limitations in Section 1604.3.
1709.4 Wall and partition assemblies. | Load-bearing wall and partition assemblies shall sustain the test load both with and without window framing. The test load shall include all design load components. Wall and partition assemblies shall be tested both with and without door and window framing. | 1709.4 Wall and partition assemblies. | Load-bearing wall and partition assemblies shall sustain the test load both with and without window framing. The test load shall include all design load components. Wall and partition assemblies shall be tested both with and without door and window framing.
1709.5 Exterior window and door assemblies. | The design pressure rating of exterior windows and doors in buildings shall be determined in accordance with Section 1709.5.1 or Section 1709.5.2. Exception: Structural wind load design pressures for window units smaller than the size tested in accordance with Section 1709.5.1 or Section 1709.5.2 shall be permitted to be higher than the design value of the tested unit provided such higher pressures are determined by accepted engineering analysis. All components of the small unit shall be the same as the tested unit. Where such calculated design pressures are used, they shall be validated by an additional test of the window unit having the highest allowable design pressure. | 1709.5 Exterior window and door assemblies. | The design pressure rating of exterior windows and doors in buildings shall be determined in accordance with Section 1709.5.1 or 1709.5.2. For exterior windows and doors tested in accordance with Section 1709.5.1 or 1709.5.2, required design wind pressures determined from ASCE 7 shall be permitted to be converted to allowable stress design by multiplying by 0.6. Exception: Structural wind load design pressures for window or door assemblies other than the size tested in accordance with Section 1709.5.1 or 1709.5.2 shall be permitted to be different than the design value of the tested assembly, provided that such pressures are determined by accepted engineering analysis or validated by an additional test of the window or door assembly to the alternative allowable design pressure in accordance with Section 1709.5.2. Components of the alternate size assembly shall be the same as the tested or labeled assembly. Where engineering analysis is used, it shall be performed in accordance with the analysis procedures of AAMA 2502.
1709.5.1 Exterior windows and doors. | Exterior windows and doors shall be tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440. The label shall state the name of the manufacturer, the approved labeling agency and the product designation as specified in AAMA/WDMA/CSA 101/I.S.2/A440. Products tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440 shall not be subject to the requirements of Sections 2403.2 and 2403.3. | 1709.5.1 Exterior windows and doors. | Exterior windows and sliding doors shall be tested and labeled as conforming to AAMA/WDMA/CSA101/I.S.2/A440. The label shall state the name of the manufacturer, the approved labeling agency and the product designation as specified in AAMA/WDMA/CSA101/I.S.2/A440. Exterior side-hinged doors shall be tested and labeled as conforming to AAMA/WDMA/CSA101/I.S.2/A440 or comply with Section 1709.5.2. Products tested and labeled as conforming to AAMA/WDMA/CSA 101/I.S.2/A440 shall not be subject to the requirements of Sections 2403.2 and 2403.3.
1709.5.2 Exterior windows and door assemblies not provided for in Section 1709. | 5.1. Exterior window and door assemblies shall be tested in accordance with ASTM E 330. Structural performance of garage doors shall be determined in accordance with either ASTM E 330 or ANSI/DASMA 108, and shall meet the acceptance criteria of ANSI/DASMA 108. Exterior window and door assemblies containing glass shall comply with Section 2403 of this code. The design pressure for testing shall be calculated in accordance with Chapter 16 of this code. Each assembly shall be tested for 10 seconds at a load equal to 1.5 times the design pressure. | 1709.5.2 Exterior windows and door assemblies not provided for in Section 1709. | 5.1. Exterior window and door assemblies shall be tested in accordance with ASTM E330. Exterior window and door assemblies containing glass shall comply with Section 2403. The design pressure for testing shall be calculated in accordance with Chapter 16. Each assembly shall be tested for 10 seconds at a load equal to 1.5 times the design pressure.
1709.6 Skylights and sloped glazing. | Skylights and sloped glazing shall comply with the requirements of Chapter 24. | 1709.6 Skylights and sloped glazing. | Skylights and sloped glazing shall comply with the requirements of Chapter 24.
1709.7 Test specimens. | Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on repre­sentative samples of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency. | 1709.7 Test specimens. | Test specimens and construction shall be representative of the materials, workmanship and details normally used in practice. The properties of the materials used to construct the test assembly shall be determined on the basis of tests on samples taken from the load assembly or on representative samples of the materials used to construct the load test assembly. Required tests shall be conducted or witnessed by an approved agency.
1710.1 Where required. | Where proposed construction is not capable of being designed by approved engineering analysis, or where proposed construction design method does not com­ply with the applicable material design standard, the system of construction or the structural unit and the connections shall be subjected to the tests prescribed in Section 1711. The commissioner shall accept certified reports of such tests conducted by an approved testing agency, provided that such tests meet the requirements of this code and approved procedures.
1711.1 Test standards for joist hangers and connectors. | Test standards for joist handlers and connectors shall be in accordance with Sections 1711.1.1 through 1711.2.2.
1711.1.1 Test standards for joist hangers. | The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers shall be determined in accordance with ASTM D 1761, using lumber having a specific gravity of 0.49 or greater, but not greater than 0.55, as determined in accordance with AF&PA NDS for the joist and headers. Exception: The joist length shall not be required to exceed 24 inches ( 609.6 mm).
1711.1.2 Vertical load capacity for joist hangers. | The vertical load capacity for the joist hanger shall be determined by testing a minimum of three joist hanger assemblies as specified in ASTM D 1761. If the ultimate vertical load for any one of the tests varies more than 20 percent from the average ultimate vertical load, at least three additional tests shall be conducted. The allowable vertical load of the joist hanger shall be the lowest value determined from the following:
1711.1.3 Torsional moment capacity for joist hangers. | The torsional moment capacity for the joist hanger shall be determined by testing at least three joist hanger assemblies as specified in ASTM D 1761. The allowable torsional moment of the joist hanger shall be the average torsional moment at which the lateral movement of the top or bottom of the joist with respect to the original position of the joist is 0.125 inch (3.2 mm).
1711.1.4 Design value modifications for joist hangers. | Allowable design values for joist hangers that are determined by Item 4 or 5 in Section 1711.1.2 shall be permitted to be modified by the appropriate duration of loading factors as specified in AF&PA NDS but shall not exceed the direct loads as determined by Item 1, 2 or 3 in Section 1711.1.2. Allowable design values determined by Item 1, 2 or 3 in Section 1711.1.2 shall not be modified by dura­tion of loading factors.
1711.2 Concrete and clay roof tiles. | Concrete and clay roof tiles shall be tested in accordance with Sections 1711.2.1 and 1711.2.2.
1711.2.1 Overturning resistance. | Concrete and clay roof tiles shall be tested to determine their resistance to overturning due to wind in accordance with ICC SBCCI SSTD 11 and Chapter 15.
1711.2.2 Wind tunnel testing. | When roof tiles do not satisfy the limitations in Chapter 16 for rigid tile, a wind tunnel test shall be used to determine the wind characteristics of the concrete or clay tile roof covering in accordance with ICC SBCCI SSTD 11 and Chapter 15.
|  | 1702.1 General. | New building materials, equipment, appliances, systems or methods of construction not provided for in this code, and any material of questioned suitability proposed for use in the construction of a building or structure, shall be subjected to the tests prescribed in this chapter and in the approved rules to determine character, quality and limitations of use.
|  | 1703.1 Approved agency. | An approved agency shall provide all information as necessary for the building official to determine that the agency meets the applicable requirements specified in Sections 1703.1.1 through 1703.1.3.
|  | 1703.1.1 Independence. | An approved agency shall be objective, competent and independent from the contractor responsible for the work being inspected. The agency shall disclose to the building official and the registered design professional in responsible charge possible conflicts of interest so that objectivity can be confirmed.
|  | 1703.1.2 Equipment. | An approved agency shall have adequate equipment to perform required tests. The equipment shall be periodically calibrated.
|  | 1703.1.3 Personnel. | An approved agency shall employ experienced personnel educated in conducting, supervising and evaluating tests and special inspections.
|  | 1703.2 Written approval. | Any material, appliance, equipment, system or method of construction meeting the requirements of this code shall be approved in writing after satisfactory completion of the required tests and submission of required test reports.
|  | 1703.3 Record of approval. | For any material, appliance, equipment, system or method of construction that has been approved, a record of such approval, including the conditions and limitations of the approval, shall be kept on file in the building official’s office and shall be available for public review at appropriate times.
|  | 1703.4 Performance. | Specific information consisting of test reports conducted by an approved agency in accordance with the appropriate referenced standards, or other such information as necessary, shall be provided for the building official to determine that the product, material or assembly meets the applicable code requirements.
|  | 1703.4.1 Research and investigation. | Sufficient technical data shall be submitted to the building official to substantiate the proposed use of any product, material or assembly. If it is determined that the evidence submitted is satisfactory proof of performance for the use intended, the building official shall approve the use of the product, material or assembly subject to the requirements of this code. The costs, reports and investigations required under these provisions shall be paid by the owner or the owner’s authorized agent.
|  | 1703.4.2 Research reports. | Supporting data, where necessary to assist in the approval of products, materials or assemblies not specifically provided for in this code, shall consist of valid research reports from approved sources.
|  | 1703.5 Labeling. | Products, materials or assemblies required to be labeled shall be labeled in accordance with the procedures set forth in Sections 1703.5.1 through 1703.5.4.
|  | 1703.5.1 Testing. | An approved agency shall test a representative sample of the product, material or assembly being labeled to the relevant standard or standards. The approved agency shall maintain a record of the tests performed. The record shall provide sufficient detail to verify compliance with the test standard.
|  | 1703.5.2 Inspection and identification. | The approved agency shall periodically perform an inspection, which shall be in-plant if necessary, of the product or material that is to be labeled. The inspection shall verify that the labeled product, material or assembly is representative of the product, material or assembly tested.
|  | 1703.5.3 Label information. | The label shall contain the manufacturer’s identification, model number, serial number or definitive information describing the performance characteristics of the product, material or assembly and the approved agency’s identification.
|  | 1703.5.4 Method of labeling. | Information required to be permanently identified on the product, material or assembly shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed.
|  | 1703.6 Evaluation and follow-up inspection services. | Where structural components or other items regulated by this code are not visible for inspection after completion of a prefabricated assembly, the owner or the owner’s authorized agent shall submit a report of each prefabricated assembly. The report shall indicate the complete details of the assembly, including a description of the assembly and its components, the basis upon which the assembly is being evaluated, test results and similar information and other data as necessary for the building official to determine conformance to this code. Such a report shall be approved by the building official.
|  | 1703.6.1 Follow-up inspection. | The owner or the owner’s authorized agent shall provide for special inspections of fabricated items in accordance with Section 1704.2.5.
|  | 1703.6.2 Test and inspection records. | Copies of necessary test and special inspection records shall be filed with the building official.
|  | 1704.2 Special inspections and tests. | Where application is made to the building official for construction as specified in Section 105, the owner or the owner’s authorized agent, other than the contractor, shall employ one or more approved agencies to provide special inspections and tests during construction on the types of work specified in Section 1705 and identify the approved agencies to the building official. These special inspections and tests are in addition to the inspections by the building official that are identified in Section 110. Exceptions: 1. Special inspections and tests are not required for construction of a minor nature or as warranted by conditions in the jurisdiction as approved by the building official. 2. Unless otherwise required by the building official, special inspections and tests are not required for Group U occupancies that are accessory to a residential occupancy including, but not limited to, those listed in Section 312.1. 3. Special inspections and tests are not required for portions of structures designed and constructed in accordance with the cold-formed steel light-frame construction provisions of Section 2211.1.2 or the conventional light-frame construction provisions of Section 2308. 4. The contractor is permitted to employ the approved agencies where the contractor is also the owner.
|  | 1704.2.1 Special inspector qualifications. | Prior to the start of the construction, the approved agencies shall provide written documentation to the building official demonstrating the competence and relevant experience or training of the special inspectors who will perform the special inspections and tests during construction. Experience or training shall be considered to be relevant where the documented experience or training is related in complexity to the same type of special inspection or testing activities for projects of similar complexity and material qualities. These qualifications are in addition to qualifications specified in other sections of this code.
|  | 1704.2.2 Access for special inspection. | The construction or work for which special inspection or testing is required shall remain accessible and exposed for special inspection or testing purposes until completion of the required special inspections or tests.
|  | 1704.2.3 Statement of special inspections. | The applicant shall submit a statement of special inspections in accordance with Section 107.1 as a condition for permit issuance. This statement shall be in accordance with Section 1704.3. Exception: A statement of special inspections is not required for portions of structures designed and constructed in accordance with the cold-formed steel light-frame construction provisions of Section 2211.1.2 or the conventional light-frame construction provisions of Section 2308.
|  | 1704.2.4 Report requirement. | Approved agencies shall keep records of special inspections and tests. The approved agency shall submit reports of special inspections and tests to the building official and to the registered design professional in responsible charge. Reports shall indicate that work inspected or tested was or was not completed in conformance to approved construction documents. Discrepancies shall be brought to the immediate attention of the contractor for correction. If they are not corrected, the discrepancies shall be brought to the attention of the building official and to the registered design professional in responsible charge prior to the completion of that phase of the work. A final report documenting required special inspections and tests, and correction of any discrepancies noted in the inspections or tests, shall be submitted at a point in time agreed upon prior to the start of work by the owner or the owner’s authorized agent to the building official.
|  | 1704.2.5 Special inspection of fabricated items. | Where fabrication of structural, load-bearing or lateral load-resisting members or assemblies is being conducted on the premises of a fabricator’s shop, special inspections of the fabricated items shall be performed during fabrication, except where the fabricator has been approved to perform work without special inspections in accordance with Section 1704.2.5.1.
|  | 1704.2.5.1 Fabricator approval. | Special inspections during fabrication are not required where the work is done on the premises of a fabricator approved to perform such work without special inspection. Approval shall be based on review of the fabricator’s written fabrication procedures and quality control manuals that provide a basis for control of materials and workmanship, with periodic auditing of fabrication and quality control practices by an approved agency or the building official. At completion of fabrication, the approved fabricator shall submit a certificate of compliance to the owner or the owner’s authorized agent for submittal to the building official as specified in Section 1704.5 stating that the work was performed in accordance with the approved construction documents.
|  | 1704.3 Statement of special inspections. | Where special inspections or tests are required by Section 1705, the registered design professional in responsible charge shall prepare a statement of special inspections in accordance with Section 1704.3.1 for submittal by the applicant in accordance with Section 1704.2.3. Exception: The statement of special inspections is permitted to be prepared by a qualified person approved by the building official for construction not designed by a registered design professional.
|  | 1704.3.1 Content of statement of special inspections. | The statement of special inspections shall identify the following:
|  | 1704.3.2 Seismic requirements in the statement of special inspections. | Where Section 1705.13 or 1705.14 specifies special inspections or tests for seismic resistance, the statement of special inspections shall identify the designated seismic systems and seismic force-resisting systems that are subject to the special inspections or tests.
|  | 1704.3.3 Wind requirements in the statement of special inspections. | Where Section 1705.12 specifies special inspection for wind resistance, the statement of special inspections shall identify the main windforce-resisting systems and wind-resisting components that are subject to special inspections.
|  | 1704.4 Contractor responsibility. | Each contractor responsible for the construction of a main wind- or seismic force-resisting system, designated seismic system or a wind- or seismic force-resisting component listed in the statement of special inspections shall submit a written statement of responsibility to the building official and the owner or the owner’s authorized agent prior to the commencement of work on the system or component. The contractor’s statement of responsibility shall contain acknowledgement of awareness of the special requirements contained in the statement of special inspections.
|  | 1704.5 Submittals to the building official. | In addition to the submittal of reports of special inspections and tests in accordance with Section 1704.2.4, reports and certificates shall be submitted by the owner or the owner’s authorized agent to the building official for each of the following:
|  | 1704.6 Structural observations. | Where required by the provisions of Section 1704.6.1, the owner or the owner’s authorized agent shall employ a registered design professional to perform structural observations. The structural observer shall visually observe representative locations of structural systems, details and load paths for general conformance to the approved construction documents. Structural observation does not include or waive the responsibility for the inspections in Section 110 or the special inspections in Section 1705 or other sections of this code. Prior to the commencement of observations, the structural observer shall submit to the building official a written statement identifying the frequency and extent of structural observations. At the conclusion of the work included in the permit, the structural observer shall submit to the building official a written statement that the site visits have been made and identify any reported deficiencies that, to the best of the structural observer’s knowledge, have not been resolved.
|  | 1704.6.1 Structural observations for structures. | Structural observations shall be provided for those structures where one or more of the following conditions exist:
|  | 1705.2.1 Structural steel. | Special inspections and nondestructive testing of structural steel elements in buildings, structures and portions thereof shall be in accordance with the quality assurance inspection requirements of AISC 360. Exception: Special inspection of railing systems composed of structural steel elements shall be limited to welding inspection of welds at the base of cantilevered rail posts.
|  | 1705.2.2 Cold-formed steel deck. | Special inspections and qualification of welding special inspectors for cold-formed steel floor and roof deck shall be in accordance with the quality assurance inspection requirements of SDI QA/QC.
|  | 1705.2.3 Open-web steel joists and joist girders. | Special inspections of open-web steel joists and joist girders in buildings, structures and portions thereof shall be in accordance with Table 1705.2.3.
|  | 1705.2.4 Cold-formed steel trusses spanning 60 feet or greater. | Where a cold-formed steel truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.
|  | 1705.3.1 Welding of reinforcing bars. | Special inspections of welding and qualifications of special inspectors for reinforcing bars shall be in accordance with the requirements of AWS D1.4 for special inspection and of AWS D1.4 for special inspector qualification.
|  | 1705.3.2 Material tests. | In the absence of sufficient data or documentation providing evidence of conformance to quality standards for materials in Chapters 19 and 20 of ACI 318, the building official shall require testing of materials in accordance with the appropriate standards and criteria for the material in Chapters 19 and 20 of ACI 318.
|  | 1705.4.1 Glass unit masonry and masonry veneer in Risk Category IV. | Special inspections and tests for glass unit masonry or masonry veneer designed in accordance with Section 2110 or Chapter 14, respectively, where they are part of a structure classified as Risk Category IV shall be performed in accordance with TMS 602 Level 2.
|  | 1705.4.2 Vertical masonry foundation elements. | Special inspections and tests of vertical masonry foundation elements shall be performed in accordance with Section 1705.4.
|  | 1705.5.2 Metal-plate-connected wood trusses spanning 60 feet or greater. | Where a truss clear span is 60 feet (18 288 mm) or greater, the special inspector shall verify that the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing are installed in accordance with the approved truss submittal package.
|  | 1705.5.3 Mass timber construction. | Special inspections of mass timber elements in Types IV-A, IV-B and IV-C construction shall be in accordance with Table 1705.5.3.
|  | 1705.6 Soils. | Special inspections and tests of existing site soil conditions, fill placement and load-bearing requirements shall be performed in accordance with this section and Table 1705.6. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance. Exception: Where Section 1803 does not require reporting of materials and procedures for fill placement, the special inspector shall verify that the in-place dry density of the compacted fill is not less than 90 percent of the maximum dry density at optimum moisture content determined in accordance with ASTM D1557.
|  | 1705.7 Driven deep foundations. | Special inspections and tests shall be performed during installation of driven deep foundation elements as specified in Table 1705.7. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance.
|  | 1705.8 Cast-in-place deep foundations. | Special inspections and tests shall be performed during installation of cast-in-place deep foundation elements as specified in Table 1705.8. The approved geotechnical report and the construction documents prepared by the registered design professionals shall be used to determine compliance.
|  | 1705.10 Structural integrity of deep foundation elements. | Whenever there is a reasonable doubt as to the structural integrity of a deep foundation element, an engineering assessment shall be required. The engineering assessment shall include tests for defects performed in accordance with ASTM D4945, ASTM D5882, ASTM D6760 or ASTM D7949, or other approved method.
|  | 1705.11 Fabricated items. | Special inspections of fabricated items shall be performed in accordance with Section 1704.2.5.
|  | 1705.12 Special inspections for wind resistance. | Special inspections for wind resistance specified in Sections 1705.12.1 through 1705.12.3, unless exempted by the exceptions to Section 1704.2, are required for buildings and structures constructed in the following areas:
|  | 1705.12.1 Structural wood. | Continuous special inspection is required during field gluing operations of elements of the main windforce-resisting system. Periodic special inspection is required for nailing, bolting, anchoring and other fastening of elements of the main windforce-resisting system, including wood shear walls, wood diaphragms, drag struts, braces and hold-downs. Exception: Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the main windforce-resisting system, where the lateral resistance is provided by structural sheathing and the specified fastener spacing at panel edges is more than 4 inches (102 mm) on center.
|  | 1705.12.2 Cold-formed steel light-frame construction. | Periodic special inspection is required for welding operations of elements of the main windforce-resisting system. Periodic special inspection is required for screw attachment, bolting, anchoring and other fastening of elements of the main windforce-resisting system, including shear walls, braces, diaphragms, collectors (drag struts) and hold-downs. Exception: Special inspections are not required for cold-formed steel light-frame shear walls and diaphragms, including screwing, bolting, anchoring and other fastening to components of the windforce-resisting system, where either of the following applies: 1. The sheathing is gypsum board or fiberboard. 2. The sheathing is wood structural panel or steel sheets on only one side of the shear wall, shear panel or diaphragm assembly and the specified fastener spacing at the panel or sheet edges is more than 4 inches (102 mm) on center (o.c.).
|  | 1705.12.3 Wind-resisting components. | Periodic special inspection is required for fastening of the following systems and components:
|  | 1705.13 Special inspections for seismic resistance. | Special inspections for seismic resistance shall be required as specified in Sections 1705.13.1 through 1705.13.9, unless exempted by the exceptions of Section 1704.2. Exception: The special inspections specified in Sections 1705.13.1 through 1705.13.9 are not required for structures designed and constructed in accordance with one of the following: 1. The structure consists of light-frame construction; the design spectral response acceleration at short periods, SDS, as determined in Section 1613.2.4, does not exceed 0.5; and the building height of the structure does not exceed 35 feet (10 668 mm). 2. The seismic force-resisting system of the structure consists of reinforced masonry or reinforced concrete; the design spectral response acceleration at short periods, SDS, as determined in Section 1613.2.4, does not exceed 0.5; and the building height of the structure does not exceed 25 feet (7620 mm). 3. The structure is a detached one- or two-family dwelling not exceeding two stories above grade plane and does not have any of the following horizontal or vertical irregularities in accordance with Section 12.3 of ASCE 7: 3.1. Torsional or extreme torsional irregularity. 3.2. Nonparallel systems irregularity. 3.3. Stiffness-soft story or stiffness-extreme soft story irregularity. 3.4. Discontinuity in lateral strength-weak story irregularity.
|  | 1705.13.1 Structural steel. | Special inspections for seismic resistance shall be in accordance with Section 1705.13.1.1 or 1705.13.1.2, as applicable.
|  | 1705.13.1.1 Seismic force-resisting systems. | Special inspections of structural steel in the seismic force-resisting systems in buildings and structures assigned to Seismic Design Category B, C, D, E or F shall be performed in accordance with the quality assurance requirements of AISC 341. Exceptions: 1. In buildings and structures assigned to Seismic Design Category B or C, special inspections are not required for structural steel seismic force-resisting systems where the response modification coefficient, R, designated for “Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems” in ASCE 7, Table 12.2-1, has been used for design and detailing. 2. In structures assigned to Seismic Design Category D, E, or F, special inspections are not required for structural steel seismic force-resisting systems where design and detailing in accordance with AISC 360 is permitted by ASCE 7, Table 15.4-1.
|  | 1705.13.1.2 Structural steel elements. | Special inspections of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, D, E or F other than those covered in Section 1705.13.1.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. Exceptions: 1. In buildings and structures assigned to Seismic Design Category B or C, special inspections of structural steel elements are not required for seismic force-resisting systems with a response modification coefficient, R, of 3 or less. 2. In structures assigned to Seismic Design Category D, E, or F, special inspections of structural steel elements are not required for seismic force-resisting systems where design and detailing other than AISC 341 is permitted by ASCE 7, Table 15.4-1. Special inspection shall be in accordance with the applicable referenced standard listed in ASCE 7, Table 15.4-1.
|  | 1705.13.2 Structural wood. | For the seismic force-resisting systems of structures assigned to Seismic Design Category C, D, E or F: 1. Continuous special inspection shall be required during field gluing operations of elements of the seismic force-resisting system. 2. Periodic special inspection shall be required for nailing, bolting, anchoring and other fastening of elements of the seismic force-resisting system, including wood shear walls, wood diaphragms, drag struts, braces, shear panels and hold-downs. Exception: Special inspections are not required for wood shear walls, shear panels and diaphragms, including nailing, bolting, anchoring and other fastening to other elements of the seismic force-resisting system, where the lateral resistance is provided by structural sheathing, and the specified fastener spacing at the panel edges is more than 4 inches (102 mm) on center.
|  | 1705.13.3 Cold-formed steel light-frame construction. | For the seismic force-resisting systems of structures assigned to Seismic Design Category C, D, E or F, periodic special inspection shall be required for both: 1. Welding operations of elements of the seismic force-resisting system. 2. Screw attachment, bolting, anchoring and other fastening of elements of the seismic force-resisting system, including shear walls, braces, diaphragms, collectors (drag struts) and hold-downs. Exception: Special inspections are not required for cold-formed steel light-frame shear walls and diaphragms, including screw installation, bolting, anchoring and other fastening to components of the seismic force-resisting system, where either of the following applies: 1. The sheathing is gypsum board or fiberboard. 2. The sheathing is wood structural panel or steel sheets on only one side of the shear wall, shear panel or diaphragm assembly and the specified fastener spacing at the panel or sheet edge is more than 4 inches (102 mm) on center.
|  | 1705.13.4 Designated seismic systems. | For structures assigned to Seismic Design Category C, D, E or F, the special inspector shall examine designated seismic systems requiring seismic qualification in accordance with Section 13.2.2 of ASCE 7 and verify that the label, anchorage and mounting conform to the certificate of compliance.
|  | 1705.13.5 Architectural components. | Periodic special inspection is required for the erection and fastening of exterior cladding, interior and exterior nonbearing walls and interior and exterior veneer in structures assigned to Seismic Design Category D, E or F. Exception: Periodic special inspection is not required for the following: 1. Exterior cladding, interior and exterior nonbearing walls and interior and exterior veneer 30 feet (9144 mm) or less in height above grade or walking surface. 2. Exterior cladding and interior and exterior veneer weighing 5 psf (0.24 kN/m2) or less. 3. Interior nonbearing walls weighing 15 psf (0.72 kN/m2) or less.
|  | 1705.13.5.1 Access floors. | Periodic special inspection is required for the anchorage of access floors in structures assigned to Seismic Design Category D, E or F.
|  | 1705.13.6 Plumbing, mechanical and electrical components. | Periodic special inspection of plumbing, mechanical and electrical components shall be required for the following:
|  | 1705.13.7 Storage racks. | Steel storage racks and steel cantilevered storage racks that are 8 feet (2438 mm) in height or greater and assigned to Seismic Design Category D, E or F shall be provided with periodic special inspection as required by Table 1705.13.7.
|  | 1705.13.8 Seismic isolation systems. | Periodic special inspection shall be provided for seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, D, E or F during the fabrication and installation of isolator units and energy dissipation devices.
|  | 1705.13.9 Cold-formed steel special bolted moment frames. | Periodic special inspection shall be provided for the installation of cold-formed steel special bolted moment frames in the seismic force-resisting systems of structures assigned to Seismic Design Category D, E or F.
|  | 1705.14 Testing for seismic resistance. | Testing for seismic resistance shall be required as specified in Sections 1705.14.1 through 1705.14.4, unless exempted from special inspections by the exceptions of Section 1704.2.
|  | 1705.14.1 Structural steel. | Nondestructive testing for seismic resistance shall be in accordance with Section 1705.14.1.1 or 1705.14.1.2, as applicable.
|  | 1705.14.1.1 Seismic force-resisting systems. | Nondestructive testing of structural steel in the seismic force-resisting systems in buildings and structures assigned to Seismic Design Category B, C, D, E or F shall be performed in accordance with the quality assurance requirements of AISC 341. Exceptions: 1. In buildings and structures assigned to Seismic Design Category B or C, nondestructive testing is not required for structural steel seismic force-resisting systems where the response modification coefficient, R, designated for “Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems” in ASCE 7, Table 12.2-1, has been used for design and detailing. 2. In structures assigned to Seismic Design Category D, E, or F, nondestructive testing is not required for structural steel seismic force-resisting systems where design and detailing in accordance with AISC 360 is permitted by ASCE 7, Table 15.4-1.
|  | 1705.14.1.2 Structural steel elements. | Nondestructive testing of structural steel elements in the seismic force-resisting systems of buildings and structures assigned to Seismic Design Category B, C, D, E or F other than those covered in Section 1705.14.1.1, including struts, collectors, chords and foundation elements, shall be performed in accordance with the quality assurance requirements of AISC 341. Exceptions: 1. In buildings and structures assigned to Seismic Design Category B or C, nondestructive testing of structural steel elements is not required for seismic force-resisting systems with a response modification coefficient, R, of 3 or less. 2. In structures assigned to Seismic Design Category D, E or F, nondestructive testing of structural steel elements is not required for seismic force-resisting systems where design and detailing other than AISC 341 is permitted by ASCE 7, Table 15.4-1. Nondestructive testing of structural steel elements shall be in accordance with the applicable referenced standard listed in ASCE 7, Table 15.4-1.
|  | 1705.14.2 Nonstructural components. | For structures assigned to Seismic Design Category B, C, D, E or F, where the requirements of Section 13.2.1 of ASCE 7 for nonstructural components, supports or attachments are met by seismic qualification as specified in Item 2 therein, the registered design professional shall specify on the approved construction documents the requirements for seismic qualification by analysis, testing or experience data. Certificates of compliance for the seismic qualification shall be submitted to the building official as specified in Section 1704.5.
|  | 1705.14.3 Designated seismic systems. | For structures assigned to Seismic Design Category C, D, E or F and with designated seismic systems that are subject to the requirements of Section 13.2.2 of ASCE 7 for certification, the registered design professional shall specify on the approved construction documents the requirements to be met by analysis, testing or experience data as specified therein. Certificates of compliance documenting that the requirements are met shall be submitted to the building official as specified in Section 1704.5.
|  | 1705.14.4 Seismic isolation systems. | Seismic isolation systems in seismically isolated structures assigned to Seismic Design Category B, C, D, E or F shall be tested in accordance with Section 17.8 of ASCE 7.
|  | 1705.15 Sprayed fire-resistant materials. | Special inspections and tests of sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be performed in accordance with Sections 1705.15.1 through 1705.15.6. Special inspections shall be based on the fire-resistance design as designated in the approved construction documents. The tests set forth in this section shall be based on samplings from specific floor, roof and wall assemblies and structural members. Special inspections and tests shall be performed during construction with an additional visual inspection after the rough installation of electrical, automatic sprinkler, mechanical and plumbing systems and suspension systems for ceilings, and before concealment where applicable. The required sample size shall not exceed 110 percent of that specified by the referenced standards in Sections 1705.15.4.1 through 1705.15.4.9.
|  | 1705.15.1 Physical and visual tests. | The special inspections and tests shall include the following to demonstrate compliance with the listing and the fire-resistance rating:
|  | 1705.15.2 Structural member surface conditions. | The surfaces shall be prepared in accordance with the approved fire-resistance design and the written instructions of approved manufacturers. The prepared surface of structural members to be sprayed shall be inspected by the special inspector before the application of the sprayed fire-resistant material.
|  | 1705.15.3 Application. | The substrate shall have a minimum ambient temperature before and after application as specified in the written instructions of approved manufacturers. The area for application shall be ventilated during and after application as required by the written instructions of approved manufacturers.
|  | 1705.15.4 Thickness. | Not more than 10 percent of the thickness measurements of the sprayed fire-resistant materials applied to floor, roof and wall assemblies and structural members shall be less than the thickness required by the approved fire-resistance design, and none shall be less than the minimum allowable thickness required by Section 1705.15.4.1.
|  | 1705.15.4.1 Minimum allowable thickness. | For design thicknesses 1 inch (25 mm) or greater, the minimum allowable individual thickness shall be the design thickness minus 1/4 inch (6.4 mm). For design thicknesses less than 1 inch (25 mm), the minimum allowable individual thickness shall be the design thickness minus 25 percent. Thickness shall be determined in accordance with ASTM E605. Samples of the sprayed fire-resistant materials shall be selected in accordance with Sections 1705.15.4.2 and 1705.15.4.3.
|  | 1705.15.4.2 Floor, roof and wall assemblies. | The thickness of the sprayed fire-resistant material applied to floor, roof and wall assemblies shall be determined in accordance with ASTM E605, making not less than four measurements for each 1,000 square feet (93 m2) of the sprayed area, or portion thereof, in each story.
|  | 1705.15.4.3 Cellular decks. | Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. Not fewer than four measurements shall be made, located symmetrically within the square area.
|  | 1705.15.4.4 Fluted decks. | Thickness measurements shall be selected from a square area, 12 inches by 12 inches (305 mm by 305 mm) in size. Not fewer than four measurements shall be made, located symmetrically within the square area, including one each of the following: valley, crest and sides. The average of the measurements shall be reported.
|  | 1705.15.4.5 Structural members. | The thickness of the sprayed fire-resistant material applied to structural members shall be determined in accordance with ASTM E605. Thickness testing shall be performed on not less than 25 percent of the structural members on each floor.
|  | 1705.15.4.6 Beams and girders. | At beams and girders thickness measurements shall be made at nine locations around the beam or girder at each end of a 12-inch (305 mm) length.
|  | 1705.15.4.7 Joists and trusses. | At joists and trusses, thickness measurements shall be made at seven locations around the joist or truss at each end of a 12-inch (305 mm) length.
|  | 1705.15.4.8 Wide-flanged columns. | At wide-flanged columns, thickness measurements shall be made at 12 locations around the column at each end of a 12-inch (305 mm) length.
|  | 1705.15.4.9 Hollow structural section and pipe columns. | At hollow structural section and pipe columns, thickness measurements shall be made at not fewer than four locations around the column at each end of a 12-inch (305 mm) length.
|  | 1705.15.5 Density. | The density of the sprayed fire-resistant material shall be not less than the density specified in the approved fire-resistance design. Density of the sprayed fire-resistant material shall be determined in accordance with ASTM E605. The test samples for determining the density of the sprayed fire-resistant materials shall be selected as follows:
|  | 1705.15.6 Bond strength. | The cohesive/adhesive bond strength of the cured sprayed fire-resistant material applied to floor, roof and wall assemblies and structural members shall be not less than 150 pounds per square foot (psf) (7.18 kN/m2). The cohesive/adhesive bond strength shall be determined in accordance with the field test specified in ASTM E736 by testing in-place samples of the sprayed fire-resistant material selected in accordance with Sections 1705.15.6.1 through 1705.15.6.3.
|  | 1705.15.6.1 Floor, roof and wall assemblies. | The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from each floor, roof and wall assembly at the rate of not less than one sample for every 2,500 square feet (232 m2) of the sprayed area, or portion thereof, in each story.
|  | 1705.15.6.2 Structural members. | The test samples for determining the cohesive/adhesive bond strength of the sprayed fire-resistant materials shall be selected from beams, girders, trusses, columns and other structural members at the rate of not less than one sample for each type of structural member for each 2,500 square feet (232 m2) of floor area or portion thereof in each story.
|  | 1705.15.6.3 Primer, paint and encapsulant bond tests. | Bond tests to qualify a primer, paint or encapsulant shall be conducted where the sprayed fire-resistant material is applied to a primed, painted or encapsulated surface for which acceptable bond-strength performance between these coatings and the fire-resistant material has not been determined. A bonding agent approved by the SFRM manufacturer shall be applied to a primed, painted or encapsulated surface where the bond strengths are found to be less than required values.
|  | 1705.16 Mastic and intumescent fire-resistant coatings. | Special inspections and tests for mastic and intumescent fire-resistant coatings applied to structural elements and decks shall be performed in accordance with AWCI 12-B. Special inspections and tests shall be based on the fire-resistance design as designated in the approved construction documents. Special inspections and tests shall be performed during construction. Additional visual inspection shall be performed after the rough installation and, where applicable, prior to the concealment of electrical, automatic sprinkler, mechanical and plumbing systems.
|  | 1705.17 Exterior insulation and finish systems (EIFS). | Special inspections shall be required for all EIFS applications. 1. Special inspections shall not be required for EIFS applications installed over a water-resistive barrier with a means of draining moisture to the exterior. 2. Special inspections shall not be required for EIFS applications installed over masonry or concrete walls.
|  | 1705.17.1 Water-resistive barrier coating. | A water-resistive barrier coating complying with ASTM E2570 requires special inspection of the water-resistive barrier coating where installed over a sheathing substrate.
|  | 1705.18 Fire-resistant penetrations and joints. | In high-rise buildings, in buildings assigned to Risk Category III or IV, or in fire areas containing Group R occupancies with an occupant load greater than 250, special inspections for through-penetrations, membrane penetration firestops, fire-resistant joint systems and perimeter fire containment systems that are tested and listed in accordance with Sections 714.4.1.2, 714.5.1.2, 715.3.1 and 715.4 shall be in accordance with Section 1705.18.1 or 1705.18.2.
|  | 1705.18.1 Penetration firestops. | Inspections of penetration firestop systems that are tested and listed in accordance with Sections 714.4.1.2 and 714.5.1.2 shall be conducted by an approved agency in accordance with ASTM E2174.
|  | 1705.18.2 Fire-resistant joint systems. | Inspection of fire-resistant joint systems that are tested and listed in accordance with Sections 715.3.1 and 715.4 shall be conducted by an approved agency in accordance with ASTM E2393.
|  | 1705.19 Testing for smoke control. | Smoke control systems shall be tested by a special inspector.
|  | 1705.19.1 Testing scope. | The test scope shall be as follows:
|  | 1705.19.2 Qualifications. | Approved agencies for smoke control testing shall have expertise in fire protection engineering, mechanical engineering and certification as air balancers.
|  | 1705.20 Sealing of mass timber. | Periodic special inspections of sealants or adhesives shall be conducted where sealant or adhesive required by Section 703.7 is applied to mass timber building elements as designated in the approved construction documents.
|  | 1708.2 In-situ load tests. | In-situ load tests shall be conducted in accordance with Section 1708.2.1 or 1708.2.2 and shall be supervised by a registered design professional. The test shall simulate the applicable loading conditions specified in Chapter 16 as necessary to address the concerns regarding structural stability of the building, structure or portion thereof.
|  | 1708.2.1 Load test procedure specified. | Where a referenced material standard contains an applicable load test procedure and acceptance criteria, the test procedure and acceptance criteria in the standard shall apply. In the absence of specific load factors or acceptance criteria, the load factors and acceptance criteria in Section 1708.2.2 shall apply.
|  | 1708.2.2 Load test procedure not specified. | In the absence of applicable load test procedures contained within a material standard referenced by this code or acceptance criteria for a specific material or method of construction, such existing structure shall be subjected to an approved test procedure developed by a registered design professional that simulates applicable loading and deformation conditions. For components that are not a part of the seismic force-resisting system, at a minimum the test load shall be equal to the specified factored design loads. For materials such as wood that have strengths that are dependent on load duration, the test load shall be adjusted to account for the difference in load duration of the test compared to the expected duration of the design loads being considered. For statically loaded components, the test load shall be left in place for a period of 24 hours. For components that carry dynamic loads (for example, machine supports or fall arrest anchors), the load shall be left in place for a period consistent with the component’s actual function. The structure shall be considered to have successfully met the test requirements where the following criteria are satisfied:
|  | 1709.5.2.1 Garage doors and rolling doors. | Garage doors and rolling doors shall be tested in accordance with either ASTM E330 or ANSI/DASMA 108, and shall meet the pass/fail criteria of ANSI/DASMA 108. Garage doors and rolling doors shall be labeled with a permanent label identifying the door manufacturer, the door model/series number, the positive and negative design wind pressure rating, the installation instruction drawing reference number, and the applicable test standard.
|  | 1709.5.3 Windborne debris protection. | Protection of exterior glazed openings in buildings located in windborne debris regions shall be in accordance with Section 1609.2.
|  | 1709.5.3.1 Impact protective systems testing and labeling. | Impact protective systems shall be tested for impact resistance by an approved independent laboratory for compliance with ASTM E1886 and ASTM E1996 and for design wind pressure for compliance with ASTM E330. Required design wind pressures shall be determined in accordance with ASCE 7, and for the purposes of this section, multiplied by 0.6 to convert to allowable stress design.

## BC18
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1801.1 Scope. | The provisions of this chapter shall apply to building and foundation systems in those areas not subject to scour or water pressure by wind and wave action. Buildings and foundations subject to such scour or water pressure loads shall be designed in accordance with Chapter 16 and Appendix G. | 1801.1 Scope. | The provisions of this chapter shall apply to building and foundation systems.
1801.2 Design. | Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in Section 1605.3. The quality and design of materials used structurally in excavations and foundations shall comply with the requirements specified in Chapters 16, 19, 21, 22 and 23. Excavations and fills shall also comply with Chapter 33.
1802.1 General. | The following terms are defined in Chapter 2: | 1802.1 General. | Allowable bearing pressures, allowable stresses and design formulas provided in this chapter shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2. The quality and design of materials used structurally in excavations and foundations shall comply with the requirements specified in Chapters 16, 19, 21, 22 and 23. Excavations and fills shall comply with Chapter 33.
1801.2.1 Foundation design for seismic overturning. | Where foundations are proportioned using the load combinations of Sections 1605.2 or 1605.3.1 and the computation of seismic overturning effects is by equivalent lateral force or modal analysis, the proportioning shall be in accordance with Section 12.13.4 of ASCE 7.
1803.1 General. | Geotechnical investigations shall be subject to special inspections in accordance with Sections 1705.6, 1705.7 and 1705.19 and be conducted in accordance with Sections 1803.2 through 1803.7. An engineer shall scope, supervise and approve the subsurface investigation and the classification of the soil and rock encountered. | 1803.1 General. | Geotechnical investigations shall be conducted in accordance with Section 1803.2 and reported in accordance with Section 1803.6. Where required by the building official or where geotechnical investigations involve in-situ testing, laboratory testing or engineering calculations, such investigations shall be conducted by a registered design professional.
1803.2 Where required. | A geotechnical investigation shall be performed and report shall be prepared for:
1803.2.1 Seismic Design Category C. | For structures assigned to Seismic Design Category C in accordance with Section 1613, the geotechnical investigation shall include an evaluation of the following potential geologic and seismic hazards:
1803.2.2 Seismic Design Category D. | For structures assigned to Seismic Design Category D in accordance with Section 1613, the geotechnical investigation shall meet the requirements of Section 1803.2.1 and the following as applicable:
1803.3 Material classification. | Soil and rock classification shall be based on materials disclosed by borings, test pits or other subsurface exploration methods. Soil classifications shall be determined in accordance with ASTM D2487 (refer to Table 1803.3) and the supplemental definitions contained herein. Rock classifications shall be determined in accordance with generally accepted engineering practice and the supplemental definitions contained herein. Laboratory tests shall be conducted to ascertain these classifications where deemed necessary by the engineer responsible for the geotechnical investigation or the commissioner.
1803.4 Investigation. | An engineer shall scope and supervise the geotechnical investigation. The geotechnical investigation shall be sufficient for evaluating soil and rock conditions including, but not limited to, material classification, stratigraphy, groundwater, slope stability, soil and rock strength, adequacy of load-bearing soils and rock, the effect of moisture variation on soil-bearing capacity, compressibility, liquefaction and expansiveness. The investigation shall comply with Sections 1803.4.1 through 1803.4.4.
1803.4.1 Scope of investigation. | The scope of the geotechnical investigation, including the number, types and depths of borings, the number of test pits or the number of alternative test methods; the equipment used to drill and sample; the in-situ testing; and the laboratory testing program shall be determined by the engineer responsible for the investigation, subject to the requirements of this chapter. 1. Borings shall be uniformly distributed under the structure or distributed in accordance with load patterns imposed by the structure. 2. At a minimum, investigations for structures shall include: 2.1. One exploratory boring for built-over areas up to and including 750 square feet (69.7 m2). 2.2. Two exploratory borings for built-over areas greater than 750 square feet (69.7 m2) but less than 5,000 square feet (464.5 m2), and at least one additional boring for each additional 2,500 square feet (232.3 m2), or part thereof, of built-over areas up to 20,000 square feet (1858.1 m2). 2.3. At least one boring for each additional 5,000 square feet (464.5 m2), or part thereof, of built-over areas in excess of 20,000 square feet (1858.1 m2). 3. At a minimum, investigations for retaining walls greater than 10 feet (3048 mm) in height shall include one exploratory boring for every 50 linear feet (15 240 mm) of wall. 4. Borings shall be taken into bedrock, or to an adequate depth below the top of the load-bearing strata to demonstrate that the foundation loads have been sufficiently dissipated and to evaluate global stability of retaining walls. 5. For structures having an average area load (dead plus live) of 1,000 pounds per square foot (47.9 kN/m2) or more, at least one boring for every 10,000 square feet (929 m2) of footprint area shall penetrate at least 100 feet (30 480 mm) below the curb grade or 5 feet (1524 mm) into bedrock of Class 1c or better, whichever is less. 6. At least one-half of the borings satisfying this requirement shall be located within the limits of the built-up area and the remainder shall be within 25 feet (7620 mm) of the built-up area limits. 7. For structures to be supported on deep foundations, the required number of borings shall be not less than two borings, and based on a minimum of one boring per 2,000 square feet (184.8 m2) for the first 20,000 square feet (1858.1 m2) and one boring per every additional 4,000 square feet (371.6 m2) thereafter. 8. All boring, sampling, and in-situ testing operations shall be subject to special inspection in accordance with Table 1705.6. Exception: Test pits may be substituted for borings for one and two-story structures. The registered design professional shall submit a test pit observation report to the commissioner.
1803.4.2 Existing data. | Suitable borings, test pits, probings, and the logs and records that were obtained as part of earlier exploration programs by an engineer other than the engineer performing the geotechnical investigation and that meet the requirements of this section may only be used as partial fulfillment of the requirements of Section 1803.4.1. Additional boring(s) shall be made to fulfill the requirements of Section 1803.4.1, with a minimum of one additional boring required.
1803.4.3 Groundwater table. | The geotechnical investigation shall determine the existing groundwater table.
1803.4.4 Compressible soils. | In areas containing compressible soils, the geotechnical investigation shall determine the extent of these soils in the plan area of the structure and shall be subject to the requirements of Section 1803.3.
1803.5 Soil and rock sampling. | The soil boring and sampling procedures and apparatus shall be in accordance with ASTM D1586 and ASTM D1587 and generally accepted engineering practice. The rock coring, sampling procedure and apparatus shall be in accordance with ASTM D2113 and generally accepted engineering practice. Rock cores shall be obtained with a double-tube core barrel with a minimum outside diameter of 2⅞ inches (73 mm). With the approval of the engineer responsible for the geotechnical investigation, smaller-diameter double-tube core barrels may be used under special circumstances such as telescoping casing to penetrate boulders, or space limitations requiring the use of drill rigs incapable of obtaining large-diameter cores.
1803.5.1 Bedrock support. | Where the foundation design relies on rock to support footings, deep foundations or caisson sockets, or permanent prestressed rock anchors, a sufficient number of rock corings shall be drilled to sufficient depths to assess the competency of the rock and its load-bearing capacity, but no less than 10 feet (3048 mm) below the lowest level of bearing.
1803.5.2 Alternative investigative methods. | The engineer responsible for the geotechnical investigation may engage specialized technicians to conduct alternative investigative methods such as cone penetrometer testing (CPT) performed in accordance with ASTM D3441 or ASTM D5778. Data from these investigations may be used to (i) supplement soil boring and rock coring information, provided there is a demonstrated correlation between the findings, and (ii) determine material properties for static and seismic or liquefaction analyses. CPTs may replace borings on a one to one basis, but in no case shall there be fewer than half the required standard borings as per Section 1803.4.1, and no less than two standard borings. The boring depth requirements of Section 1803.4.1 shall be accomplished with borings. The alternative investigative methods must be capable of extending to the depths of the required borings. Other in-situ testing methods, such as geophysical, vane shear, and pressuremeter, may be used to determine engineering design parameters, but may not be used as a substitute for the required number of borings.
1803.5.3 Material disposition. | Soil and rock samples shall be maintained in an accessible location by the permit holder or owner and made available to the engineer responsible for the geotechnical investigation and to the department, until the foundation work has been completed and accepted, or until 1 year after the investigation is complete, whichever is longer.
1803.6 Geotechnical reports. | A geotechnical engineering report shall be prepared for all sites and submitted to the commissioner. Exception: One- and two-family dwellings no more than three stories in height shall not require a geotechnical report except where any of the following exist: 1. Shallow foundations are used that bear on or above compressible soils (see Section 1803.4.4), uncontrolled fill (see Section 1806.2.3), or artificially treated soils (see Section 1806.2.4); 2. Underpinning is required; 3. The structure is within the special flood hazard area; 4. Dewatering is required; 5. Test pits are implemented in lieu of borings as per Section 1803.4.1; or 6. As required by the commissioner.
1803.6.1 Information required in geotechnical reports. | The geotechnical report shall be prepared by the engineer responsible for the geotechnical investigation and shall be signed and sealed. The geotechnical report submitted to the commissioner shall include the foundation system shown on the drawings submitted to the department. The report shall include, but need not be limited to, the following information:
1803.7 Construction documents. | Construction documents shall be prepared in accordance with Section 106.7.1.
1804.1 Excavations near foundations. | Excavations for any purpose shall not reduce vertical or lateral support for any foundation without first evaluating if underpinning or protecting the foundation against detrimental lateral or vertical movement, or both, is required. Where required, underpinning or shoring shall be provided in accordance with Section 1817.
1804.2 Placement of backfill. | The excavation outside the foundation shall be backfilled with soil that is free of organic material, construction debris, or boulders. A controlled low-strength material (CLSM) can be used as backfill in lieu of soil. Soil backfill shall be placed in lifts and compacted in a manner that does not damage the foundation or the waterproofing or dampproofing material. Exception: Controlled low-strength material need not be compacted.
1804.3 Surcharge. | No fill or other surcharge loads shall be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or the surcharge. Exception: Grading for landscaping purposes shall be permitted where done with walk-behind equipment where the grade is not increased more than one foot (304.8 mm) from original design grade, or where approved by the commissioner.
1804.4 Site grading. | The ground immediately adjacent to the foundation shall be sloped away from the structure as needed, or an approved alternate method of diverting water away from the foundation shall be used, where surface water would detrimentally affect the foundation material (soil and/or rock). Grading shall not be detrimental to the bearing material of adjacent structures. Site grading shall also comply with Section 1101.11 of the New York City Plumbing Code. | 1804.4 Site grading. | The ground immediately adjacent to the foundation shall be sloped away from the building at a slope of not less than 1 unit vertical in 20 units horizontal (5-percent slope) for a minimum distance of 10 feet (3048 mm) measured perpendicular to the face of the wall. If physical obstructions or lot lines prohibit 10 feet (3048 mm) of horizontal distance, a 5-percent slope shall be provided to an approved alternative method of diverting water away from the foundation. Swales used for this purpose shall be sloped not less than 2 percent where located within 10 feet (3048 mm) of the building foundation. Impervious surfaces within 10 feet (3048 mm) of the building foundation shall be sloped not less than 2 percent away from the building. Exceptions: 1. Where climatic or soil conditions warrant, the slope of the ground away from the building foundation shall be permitted to be reduced to not less than 1 unit vertical in 48 units horizontal (2-percent slope). 2. Impervious surfaces shall be permitted to be sloped less than 2 percent where the surface is a door landing or ramp that is required to comply with Section 1010.1.4, 1012.3 or 1012.6.1. The procedure used to establish the final ground level adjacent to the foundation shall account for additional settlement of the backfill.
1804.4.1 Seepage. | In an excavation where soil and groundwater conditions are such that an inward or upward seepage might be produced in materials intended to provide vertical or lateral support for foundation elements or for adjacent foundations, excavating methods shall control or prevent the inflow of ground water to prevent disturbance of the soil material in the excavation or beneath existing buildings. No foundation shall be placed on soil that has been disturbed by seepage unless remedial measures have been taken.
1804.5 Grading and filling in flood hazard areas. | Grading and/or filling in areas of special flood hazard shall not be permitted except as permitted in Appendix G.
1804.6 Compacted fill material. | Where foundations will bear on compacted fill material, the compacted fill shall comply with the provisions of a geotechnical report prepared, signed and sealed by the engineer, which shall contain the following: | 1804.6 Compacted fill material. | Where shallow foundations will bear on compacted fill material, the compacted fill shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803. Exception: Compacted fill material 12 inches (305 mm) in depth or less need not comply with an approved report, provided that the in-place dry density is not less than 90 percent of the maximum dry density at optimum moisture content determined in accordance with ASTM D1557. The compaction shall be verified by special inspection in accordance with Section 1705.6.
1804.7 Controlled low-strength material (CLSM). | Where footings will bear on controlled low-strength material (CLSM), the CLSM shall comply with the provisions of a geotechnical report prepared, signed and sealed by the engineer, which shall contain the following: | 1804.7 Controlled low-strength material (CLSM). | Where shallow foundations will bear on controlled low-strength material (CLSM), the CLSM shall comply with the provisions of an approved geotechnical report, as set forth in Section 1803.
1805.1 Where required. | Walls or portions thereof that retain soil or rock and enclose interior spaces and floors below grade shall be waterproofed or dampproofed in accordance with this section, with the exception of those spaces containing occupancy groups other than residential and institutional where such omission is not detrimental to the building or occupancy. Ventilation for crawl spaces shall comply with Section 1203.3.
1805.1.1 Flood hazard areas. | Buildings and structures in areas of special flood hazard shall comply with Appendix G.
1805.2 Dampproofing required. | Where hydrostatic pressure will not occur as determined by Section 1803, floors and walls for other than wood foundation systems shall be dampproofed in accordance with this section. Wood foundation systems shall be constructed in accordance with AWC TR7.
1805.2.1 Floors. | Dampproofing materials for floors shall be installed between: (i) the floor and (ii) the base course required by Section 1805.4.1 or the sub-floor. Subgrade for the dampproofing material shall be prepared in accordance with manufacturer’s recommendations. Dampproofing material shall be installed in accordance with manufacturer’s recommendations and protected after placement. Any damaged areas and punctures must be repaired prior to placement of slab. All penetrations shall be sealed as per manufacturer’s recommendations. | 1805.2.1 Floors. | Dampproofing materials for floors shall be installed between the floor and the base course required by Section 1805.4.1, except where a separate floor is provided above a concrete slab.
1805.2.2 Walls. | Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level as determined by the registered design professional and shall be installed in accordance with manufacturer’s recommendations. Dampproofing at walls shall overlap or extend past the slab dampproofing such that there are no gaps or breaches in the dampproofing system. | 1805.2.2 Walls. | Dampproofing materials for walls shall be installed on the exterior surface of the wall, and shall extend from the top of the footing to above ground level.
1805.3 Waterproofing required. | Where the geotechnical investigation required by Section 1803 indicates that a hydrostatic pressure condition exists, walls and floors shall be waterproofed in accordance with this section.
1805.3.1 Floors. | Floors required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected. Waterproofing shall be accomplished by creating a continuous water seal below the floor using appropriate waterproofing materials. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations. Floor waterproofing must be transitioned to accomplish a complete tie-in with the foundation wall waterproofing. | 1805.3.1 Floors. | Floors required to be waterproofed shall be of concrete and designed and constructed to withstand the hydrostatic pressures to which the floors will be subjected.
1805.3.2 Walls. | Walls required to be waterproofed shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected. Waterproofing shall be applied from the bottom of the wall to not less than 12 inches (304.8 mm) above the maximum elevation of the groundwater table or as directed by the registered design professional. The remainder of the wall shall be dampproofed in accordance with Section 1805.2.2. Joints, penetrations and other interruptions shall be sealed in accordance with manufacturer’s recommendations. | 1805.3.2 Walls. | Walls required to be waterproofed shall be of concrete or masonry and shall be designed and constructed to withstand the hydrostatic pressures and other lateral loads to which the walls will be subjected.
1805.3.3 Joints and penetrations. | Joints in or between walls and floors, and penetrations of walls and floors shall be sealed utilizing methods and materials approved by the registered design professional. Joints, penetrations and other interruptions shall be sealed in accordance with the manufacturer’s recommendations. | 1805.3.3 Joints and penetrations. | Joints in walls and floors, joints between the wall and floor and penetrations of the wall and floor shall be made watertight utilizing approved methods and materials.
1805.4 Subsoil drainage system. | Where it is determined that there is a potential for infiltration or seepage, a subsoil drainage system shall be permitted to be used to control this inflow, provided that: | 1805.4 Subsoil drainage system. | Where a hydrostatic pressure condition does not exist, dampproofing shall be provided and a base shall be installed under the floor and a drain installed around the foundation perimeter. A subsoil drainage system designed and constructed in accordance with Section 1805.1.3 shall be deemed adequate for lowering the ground-water table.
1805.4.1 Drainage course. | A drainage course shall consist of washed gravel, crushed natural stone or other suitable drainage medium acceptable to the engineer. Recycled concrete aggregate is not acceptable for use in a drainage course where a subsoil drainage system is used.
1805.4.2 Foundation drain. | A foundation drain shall be installed where required by the registered design professional. The foundation drain, including layout, materials, and cleanouts, shall be designed by the registered design professional. | 1805.4.2 Foundation drain. | A drain shall be placed around the perimeter of a foundation that consists of gravel or crushed stone containing not more than 10-percent material that passes through a No. 4 (4.75 mm) sieve. The drain shall extend not less than 12 inches (305 mm) beyond the outside edge of the footing. The thickness shall be such that the bottom of the drain is not higher than the bottom of the base under the floor, and that the top of the drain is not less than 6 inches (152 mm) above the top of the footing. The top of the drain shall be covered with an approved filter membrane material. Where a drain tile or perforated pipe is used, the invert of the pipe or tile shall not be higher than the floor elevation. The top of joints or the top of perforations shall be protected with an approved filter membrane material. The pipe or tile shall be placed on not less than 2 inches (51 mm) of gravel or crushed stone complying with Section 1805.4.1, and shall be covered with not less than 6 inches (152 mm) of the same material.
1805.4.3 Drainage discharge. | The drainage course and foundation drain shall discharge by gravity or mechani­cal means into an approved drainage system that complies with the New York City Plumbing Code and any other laws or requirements of agencies having jurisdiction. | 1805.4.3 Drainage discharge. | The floor base and foundation perimeter drain shall discharge by gravity or mechanical means into an approved drainage system that complies with the International Plumbing Code. Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a dedicated drainage system is not required.
1805.5 In situ walls. | In situ walls (such as slurry walls, tangent pile walls, and secant pile walls) with joints sealed by grouting or other methods acceptable to the engineer shall not require waterproofing or dampproofing unless required by the engineer.
1806.1 Design. | The allowable bearing pressures provided in Table 1806.1 shall be used with the allowable stress design load combinations specified in Section 1605.3.
1806.2 Allowable bearing pressure. | The allowable bearing pressure for supporting soil and rock shall not exceed the values specified in Table 1806.1, unless data to substantiate the use of a higher value are developed and contained in the engineer’s geotechnical report, and the commissioner approves such value. Allowable bearing pressure shall be considered to be the pressure at the base of a foundation in excess of the effective stress existing at the same level prior to construction operations.
1806.2.1 Nominally unsatisfactory bearing material. | Organic silts, organic clays, peats, soft clays, loose granular soils, loose silts, and varved silts shall be considered nominally unsatisfactory bearing material. The allowable bearing pressure shall be determined independently of Table 1806.1 subject to the following:
1806.2.2 Controlled fills. | Fills shall be considered as satisfactory bearing material of the applicable class when placed in accordance with the following procedures and subject to the special inspection provisions of Chapter 17:
1806.2.2.1 Allowable bearing pressure of controlled fills. | Provided the capacity of the underlying soil is not exceeded, the allowable bearing pressure of controlled fill shall be limited to:
1806.2.3 Uncontrolled fills. | Fills other than controlled fill may be considered as satisfactory bearing material of applicable class, subject to the following:
1806.2.4 Artificially treated soils. | Nominally unsatisfactory soil materials that are artificially compacted, cemented, or preconsolidated may be used for the support of buildings, and nominally satisfactory soil materials that are similarly treated may be used to resist soil bearing pressures in excess of those indicated in Table 1806.1. The engineer shall develop treatment plans and procedures and post-treatment performance and testing requirements, and submit such plans, procedures, and requirements to the commissioner for approval. After treatment, a sufficient amount of sampling and/or in-situ tests shall be performed in the treated soil to demonstrate the efficacy of the treatment for the increased bearing pressure.
1807.1 General. | Retaining walls shall be designed in accordance with Section 1807.2.
1807.2 Design. | Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and the effects of water pressure, including uplift. Where a keyway is extended below the wall base with the intent to engage passive pressure and enhance sliding stability, lateral soil pressures on both sides of the keyway shall be considered in the sliding analysis.
1807.2.1 Design lateral soil loads. | Retaining walls shall be designed for the lateral soil loads set forth in Section 1605. Exception: Where the structural design of a retaining wall is based on load factor design, the load factors in Section 1605.2 may be modified as follows: where water can freely flow over the top of the wall, the wall may be designed for a water pressure equal to that caused by a groundwater table elevation at the top of the wall. For this condition, the load factor for the groundwater pressure may be reduced to 1.2. The load factor for the lateral earth pressure shall remain at 1.6.
1807.2.2 Safety factor. | Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605 shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall. Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.
1807.3 Temporary retaining structures. | Structural members for temporary retaining structures may be designed with a 20 percent increase in the allowable bending stress only.
1809.1 General. | Shallow foundations shall be designed and constructed in accordance with Sections 1809.1 through 1809.6. Shallow foundations shall be constructed on suitable bearing materials established in accordance with the requirements of Sections 1804 and 1806. | 1809.1 General. | Shallow foundations shall be designed and constructed in accordance with Sections 1809.2 through 1809.13.
1809.2 Stepped footings. | The top surface of footings shall be level. The bottom surface of footings shall be permitted to have a slope not exceeding one unit vertical in 10 units horizontal (10-percent slope). Footings shall be stepped where necessary to change the elevation of the top surface of the footing or where the surface of the ground slopes more than one unit vertical in 10 units horizontal (10-percent slope).
1809.3 Depth of footings. | The minimum depth of shallow foundations below the undisturbed ground surface shall be 12 inches (304.8 mm). Where applicable, the depth of shallow foundations shall also conform to Section 1809.3.1.
1809.3.1 Frost protection. | Except where otherwise protected from frost, shallow foundations, pile caps, and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods: 1. Extending a minimum of 4 feet (1220 mm) below the lowest adjacent permanent exposed grade; Exception: Grade beams shall be embedded a minimum of 18 inches (457.2 mm) below the lowest adjacent permanent exposed grade. 2. Constructing in accordance with ASCE 32; or 3. Erecting on solid rock. Exception: Free-standing buildings meeting all of the following conditions shall not be required to be frost protected: 1. Classified in Structural Occupancy Category I (see Table 1604.5); 2. Area of 400 square feet (37.1 m2) or less; and 3. Eave height of 10 feet (3048 mm) or less.
1809.3.2 Foundations on frozen soil. | Shallow foundations shall not bear on frozen soil. Exception: Temporary structures may bear on frozen soil if the soil is maintained in a frozen condition throughout the service life of the temporary structures being supported. The method of maintaining the soil in a frozen condition shall be approved by the commissioner.
1809.4 Shallow foundations at different levels. | Where shallow foundations are supported at different levels, or are at different levels from the shallow foundations of adjacent structures, the influence of the pressures under the higher foundation on the stability of the lower foundations shall be considered in the design. The design shall consider the requirements for lateral support of the material supporting the higher foundation, the additional load imposed on the lower foundations, and assessment of the effects of dragdown on deep foundations supporting adjacent buildings or compression of soils supporting adjacent buildings.
1809.5 Shallow foundations. | Shallow foundations shall be designed and constructed in accordance with Sections 1809.5.1 through 1809.5.8.
1809.5.1 Design. | Shallow foundations shall be designed so that the allowable bearing capacity of the soil is not exceeded, and that differential settlements are within the allowable limits for the structure. The minimum width of shallow foundations shall be 18 inches (457.2 mm).
1809.5.1.1 Design loads. | Shallow foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 1605.3. The dead load shall include the weight of shallow foundations and overlying fill. Reduced live loads, as specified in Section 1607.11, are permitted to be used in the design of shallow foundations.
1809.5.1.2 Vibratory loads. | Where machinery opera­tions or other vibrations are transmitted through the shallow foundations, consideration shall be given in the shallow foundation design to prevent detrimental disturbances of the soil.
1809.5.1.3 Shifting or moving soils. | When the possibility of shifting or moving soil exists, the short and long term impact of such soils shall be considered in the design of shallow foundations.
1809.5.2 Concrete shallow foundations. | The design, materials and construction of concrete shallow foundations shall comply with Sections 1809.5.2.1 through 1809.5.2.5 and the provisions of Chapter 19.
1809.5.2.1 Concrete strength. | Concrete in shallow foundations shall have a specified compressive strength (f’c) of not less than 2,500 pounds per square inch (psi) (17.24 MPa) at 28 days.
1809.5.2.2 Footing seismic ties. | Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, individual spread footings founded on soil defined in Section 1613.3.2 as Site Class E or F shall be interconnected by ties. Ties shall be capable of carrying, in tension or compression, a force equal to the product of the larger footing load times the seismic coefficient SDS divided by 10 unless it is demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade or reinforced concrete slabs on grade.
1809.5.2.3 Plain concrete footings. | The thickness of plain concrete footings supporting walls of other than light-frame construction shall not be less than 8 inches (203.2 mm) where placed on soil. Exception: For plain concrete footings supporting Group R-3 occupancies, the thickness is permitted to be 6 inches (152.4 mm), provided that the footing does not extend beyond a distance greater than the thickness of the footing on either side of the supported wall.
1809.5.2.4 Placement of concrete. | Concrete shallow foundations shall not be placed through water unless a tremie or other method approved by the commissioner is used. Where placed under or in the presence of water, the concrete shall be deposited by approved means to ensure minimum segregation of the mix and negligible turbulence of the water.
1809.5.2.5 Protection of concrete. | No shallow foundation shall be placed on frozen soils unless the soils are maintained in frozen condition throughout the service life of the structure being supported. No foundation shall be placed in freezing weather unless provision is made to maintain the underlying soil free of frost. Concrete shallow foundations shall be protected from freezing during depositing and for a period of not less than five days thereafter. Water shall not be allowed to flow through the deposited concrete.
1809.5.3 Masonry-unit footings. | The design, materials and construction of masonry-unit footings shall comply with the provisions of Chapter 21.
1809.5.4 Steel grillage footings. | Grillage footings of structural steel elements shall be separated with approved steel spacers and be entirely encased in concrete with at least 6 inches (152.4 mm) on the bottom and at least 4 inches (101.6 mm) at all other points. The spaces between the elements shall be completely filled with concrete or cement grout.
1809.5.5 Timber footings. | Refer to Chapter 23.
1809.5.6 Wood foundations. | Refer to Chapter 23.
1809.5.7 Pier foundations. | The design, materials, and construction of pier foundations shall conform to the requirements of Sections 1809.5.2, 1809.5.3, and 1809.5.7.1 through 1809.5.7.6. Exception: Piers shall be load tested as a deep foundation in accordance with the applicable portions of Section 1810 when the bearing stratum is not physically available for inspection during construction as required by Chapter 17.
1809.5.7.1 Dimensions and height. | The minimum horizontal dimension of piers shall be 2 feet (609.6 mm), and the height shall not exceed 12 times the least horizontal dimension.
1809.5.7.2 Concrete design. | Where adequate lateral support is furnished by the surrounding materials defined in Section 1810.7 of this code, piers may be constructed of plain or reinforced concrete and the requirements of ACI 318 shall apply. Exception: Where adequate lateral support is not provided, and the ratio of unsupported height to least horizontal dimension does not exceed three, piers of plain concrete shall be designed and constructed as pedestals in accordance with ACI 318. Where the unsupported height to least horizontal dimension exceeds three, piers shall be constructed of reinforced concrete, and shall conform to the requirements for columns in ACI 318.
1809.5.7.3 Reinforcement placement. | Reinforcement shall be tied and placed as a unit in the pier prior to placement of concrete. Exception: Steel dowels embedded 5 feet (1524 mm) or less in the pier may be placed individually. Reinforcement is permitted to be wet set and the concrete cover that is otherwise required to measure a minimum of 2½ inches (63.5 mm) may be reduced to 2 inches (50.8 mm) for Groups R-3 and U occupancies not exceeding two stories of light-frame construction, provided the construction method is approved by the commissioner.
1809.5.7.4 Concrete placement. | Concrete shall be placed in such a manner as to ensure the exclusion of any foreign matter and to fill the full lateral dimensions of each pier. Concrete shall not be placed through water except where a tremie or other approved method is used. When depositing concrete from the top of the pier, the concrete shall not be chuted directly into the pier but shall be poured in a rapid and continuous operation through a funnel hopper centered at the top of the pier.
1809.5.7.5 Steel shell. | Where concrete piers are entirely encased within a circular steel shell, and the area of the shell steel is considered reinforcing steel, the steel shall be protected under the conditions specified in Section 1810.2.12. Horizontal joints in the shell shall be spliced to comply with Section 1810.2.11.
1809.5.7.6 Dewatering. | Where piers are carried to depths below the groundwater level, the piers shall be constructed by a method that will provide accurate preparation and inspection of the subgrade in dry conditions.
1809.5.8 Foundation walls. | Concrete and masonry foundation walls shall be designed in accordance with Chapter 19 or 21, respectively.
1809.5.8.1 Foundation wall thickness. | The minimum thickness of concrete and masonry foundation walls shall comply with Section 1809.5.8.1.1.
1809.5.8.1.1 Thickness based on walls supported. | The thickness of foundation walls shall not be less than the thickness of the wall supported, except that foundation walls of at least 8 inch (203.2 mm) nominal width are permitted to support brick-veneered frame walls and 10 inch wide (254 mm) cavity walls.
1809.5.8.2 Foundation wall drainage. | Foundation walls shall be designed to support the weight of the full hydrostatic pressure of undrained backfill unless a drainage system is installed in accordance with Sections 1805.4.2 and 1805.4.3.
1809.6 Seismic requirements. | For structures assigned to Seismic Design Category C or D, provisions of ACI 318 18.13, as modified by Section 1908 of this code, shall apply when not in conflict with the provisions of Section 1809 of this code. Concrete shall have a specified compressive strength of not less than 3,000 psi (20.68 MPa) at 28 days. Exceptions: 1. Group R or U occupancies of light-framed construction and two stories or fewer in height are permitted to use concrete with a specified compressive strength of not less than 2,500 psi (17.2 MPa) at 28 days. 2. One and two-family dwellings not more than three stories in height are not required to comply with the provisions of ACI 318, Section 18.11, as modified by Section 1908 of this code.
1810.1 Scope. | Deep foundation elements, including but not limited to timber piles, precast concrete piles, structural steel piles, cast-in-place concrete piles, caisson piles, drilled displacement piles, composite piles, and helical piles, shall comply with Section 1810; driven piles shall comply with Section 1811; cast-in-place concrete piles shall comply with Section 1812; composite piles shall comply with Section 1813; and helical piles shall comply with Section 1814.
1810.2 Deep foundations—general requirements.
1810.2.1 General. | Deep foundations shall be designed and installed in accordance with the requirements of the geotechnical investigation and report required by Section 1803 and Sections 1810 through 1814.
1810.2.2 Additional geotechnical investigation and report requirements. | Where deep foundations are used, the geotechnical investigation and report provisions of Section 1803 shall be expanded to include, but not be limited to, consideration of the following:
1810.2.3 Special inspection. | Special inspections for deep foundations shall be performed by an engineer in accordance with Sections 1705.7 and 1705.19.
1810.2.4 Pile caps. | Pile caps shall be of reinforced concrete, and shall include all elements to which deep foundations are connected, including grade beams and mats. The soil immediately below the pile cap shall not be considered as carrying any vertical load. The tops of deep foundations shall be embedded not fewer than 3 inches (76.2 mm) into pile caps and the caps shall extend at least 4 inches (101.6 mm) beyond the outermost edges of the deep foundation elements. The tops of deep foundations shall be cut back to sound material before capping. Pile caps shall be protected from the effects of frost in accordance with Section 1809.3.1.
1810.2.5 More than one type, capacity or method of installation for deep foundations. | In the conditions described below, the several parts of the building supported on the different types or different capacities of deep foundations shall be separated by suitable joints providing for differential movement, or analysis shall be prepared by the engineer, establishing to the satisfaction of the commissioner that the proposed construction is adequate and safe, and showing that the probable settlements and differential settlements to be expected will be tolerable to the structure and not result in instability of the building.
1810.2.6 Settlement analysis. | The settlement of an individual deep foundation or groups of deep foundations shall be estimated based on approved methods of analysis. The predicted settlement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any stresses to exceed allowable values.
1810.2.7 Use of existing deep foundations. | Deep foundations left in place where a structure has been demolished shall not be used for the support of new construction unless the existing deep foundations are load tested in accordance with Section 1810.4, original installation and testing records of the existing deep foundations are available, or the new loads are no more than half the calculated previous loads on the existing deep foundations. The engineer shall determine and certify that the existing deep foundations are sound and meet the requirements of this code.
1810.2.8 Special types of deep foundations. | The use of types of deep foundations not specifically mentioned herein is permitted, subject to the approval of the commissioner, upon the submission of acceptable test data, calculations and other information relating to the structural properties and load capacity of such deep foundations. The allowable stresses shall not in any case exceed the limitations specified herein.
1810.2.9 Minimum spacing of deep foundations. | Minimum spacing of deep foundations shall: (i) provide for adequate distribution of the load on the deep foundation group into the supporting soil or rock, (ii) account for installation effects, and (iii) be in accordance with the recommendations of Section 1810.2.2.
1810.2.10 Deep foundations located near a lot line. | Deep foundations located near a lot line shall be designed on the assumption that the adjacent lot will be excavated to a depth of 10 feet (3048 mm) below the nearest legally established curb level. Where such excavation would reduce the embedded length of the deep foundation, the portion of the deep foundation exposed shall be deemed to provide no lateral or vertical support, and the load-carrying determination shall discount the resistance offered by the soil that is subject to potential excavation.
1810.2.11 Splices. | Splices shall be constructed so as to provide and maintain true alignment and position of the component parts of the deep foundation element during installation and thereafter and shall be of adequate strength to transmit the vertical and lateral loads (including tensions) and the moments occurring in the deep foundation section at the location of the splice without exceeding the allowable stresses for such materials as established in Table 1810.8. In all cases, splices shall develop at least 50 percent of the bending capacity of the deep foundation. In all cases, splices situated in the upper 10 feet (3048 mm) of the deep foundation shall be capable of resisting (at allowable working stresses) the applied moments and shears. For individual deep foundation elements or groups comprised of two deep foundation elements, splices in the upper 10 feet (3048 mm) also shall be capable of resisting the moment and shear that would result from an assumed eccentricity of the load on the deep foundation of 3 inches (76.2 mm). For deep foundations located near a lot line, the applied moment and shears of such deep foundations shall be determined on the basis that the adjacent site will be excavated to a depth of 10 feet (3048 mm) below the nearest established curb level as required in Section 1810.2.10. Exception: For caissons core beams, the splice shall develop the lesser of 50 percent of the capacity of the core in bending or twice the design bending moment carried by the core at the location of the splice, provided that the core splice is not within two caisson diameters of any splice in the casing.
1810.2.12 Protective treatment of deep foundation materials. | Where boring records or site conditions indicate possible deleterious action on deep foundation elements because of soil constituents or other aggressive environmental factors (such as chemical seepage, the presence of salt water, electrical current, changing water levels or other factors), the deep foundation elements shall be adequately protected by materials, methods or processes approved by the engineer. Protective materials shall be applied to the deep foundations so as not to be rendered ineffective by driving. The effectiveness of such protective measures for the particular purpose shall have been thoroughly established by satisfactory service records or other evidence.
1810.2.13 Minimum concrete cover. | The minimum concrete cover for cast-in-place and precast concrete piles shall be as shown in Table 1810.2.13.
1810.3 Allowable deep foundation loads. | Allowable deep foundation loads shall be determined in accordance with Sections 1810.3.1 through 1810.3.5.
1810.3.1 Determination of allowable individual axial compressive loads. | The allowable individual axial compressive loads on deep foundations shall be the lesser of the allowable structural capacity of the element or the allowable geotechnical capacity of the element. This allowable load shall be determined by an engineer experienced in geotechnical engineering and shall be approved by the commissioner as described below: 1. The allowable structural capacity of the deep foundation shall be determined in accordance with Sections 1810 through 1816. 2. The allowable geotechnical capacity of the deep foundation shall be calculated using a recognized method of analysis and a minimum factor of safety of 2 with respect to failure. 3. The allowable geotechnical capacity shall be demonstrated by load tests. Exceptions: 1. Allowable loads for deep foundations installed by jacking shall be determined in accordance with Section 1810.3.2. 2. Caisson piles socketed into Class 1a through 1c material as defined in Table 1806.1. 3. Driven deep foundations with allowable loads less than or equal to 40 tons (392.7 kN) (30 tons (294.2 kN) for timber piles). 4. Micropiles with allowable loads less than or equal to 20 tons (196.1 kN), provided all of the following criteria are satisfied: 4.1. The maximum allowable bond stress between the soil and the grout is less than or equal to 4 psi (27.6 kPa). 4.2. The minimum bond zone diameter is greater than or equal to 9 inches (228.6 mm). 4.3. The bond zone is formed entirely in Class 3b or better soils.
1810.3.1.1 Group effects. | The allowable load determined in Section 1810.3.1 shall account for group effects on deep foundations. The analysis of group effects shall be performed by an engineer experienced in geotechnical engineering and calculated using recognized methods of analysis. This analysis shall include a bearing capacity and settlement analysis of the anticipated group(s) of deep foundations and shall consider the presence of weaker soil strata that may be present below the deep foundation element.
1810.3.1.2 Down-drag. | Where deep foundations are installed through subsiding fills or other subsiding strata and derive support from underlying firmer materials, consideration shall be given to the downward frictional forces that may be imposed on the deep foundations by the subsiding upper strata.
1810.3.1.3 Bearing stratum. | The plans for the proposed work shall establish, in accordance with the requirements relating to allowable bearing pressure, the bearing stratum to which the deep foundations in the various sections of the building must penetrate and the approximate elevations of the top of such bearing stratum. Where penetration of a given distance into the bearing strata is required for adequate distribution of the loads, such penetration shall be shown on the plans. The indicated elevations of the top of the bearing strata shall be modified by such additional data as may be obtained during construction. All deep foundations shall penetrate to or into the designated bearing stratum.
1810.3.2 Deep foundations installed by jacking or other static forces. | The allowable capacity of a deep foundation installed by jacking or other static forces shall be not more than 50 percent of the load or force used to install the deep foundation to the required penetration, except for deep foundations jacked into position for underpinning. The allowable capacity of each deep foundation used for permanent underpinning shall not exceed the larger of the following values: ⅔ of the total jacking force used to obtain the required penetration if the load is held constant for 7 hours without measurable settlement; or ½ of the total jacking force at final penetration if the load is held for a period of 1 hour without measurable settlement. The jacking resistance used to determine the working load shall not include the resistance offered by nonbearing soils, soils which are to be excavated or soils where support will dissipate with time.
1810.3.3 Helical piles. | The allowable axial compressive load for helical piles shall be in accordance with the requirements of Section 1814.
1810.3.4 Allowable uplift load. | Where required by the design, the allowable uplift load for a single deep foundation shall be determined in accordance with accepted engineering practices based on a minimum factor of safety of three or by uplift load tests performed in accordance with Section 1810.4.2.1. Where uplift load tests are performed, the maximum allowable uplift load shall not exceed the ultimate load capacity divided by a factor of safety of two. The allowable uplift load for a deep foundation group shall not exceed the sum of the allowable uplift loads of the individual deep foundations in the group, nor the uplift capacity calculating the group action of the deep foundation in accordance with accepted engineering practice where the calculated ultimate group capacity is divided by a safety factor of 2.5.
1810.3.5 Allowable lateral load. | The allowable lateral load of a single deep foundation element or a group thereof shall be determined by an approved method of analysis in accordance with accepted engineering practice. The maximum allowable lateral load of a deep foundation shall be 1 ton (8.9 kN), unless verified by lateral load test. Load testing, where required, shall be in accordance with Section 1810.4.3. See Sections 1810.4.3.1 and 1810.4.3.2 for determining the allowable lateral load from the results of lateral load tests.
1810.3.5.1 Group effects. | Lateral capacities for deep foundation groups shall be modified to account for group effects in accordance with accepted engineering practice.
1810.4 Load tests. | Where required, deep foundations shall be load tested in accordance with the requirements of Sections 1810.4.1 through 1810.4.3.
1810.4.1 Compressive load tests. | Where load tests are required per Section 1810.3 or 1810.4.1.1.1, the deep foundations shall be load tested in accordance with the applicable section.
1810.4.1.1 Required number of load tests. | Where load tests are required, at least one test shall be performed in each area of the foundation site within which the subsurface soil conditions are “substantially similar” in character, as determined by the engineer, and at least one test shall be performed for each deep foundation type for the entire foundation installation of the building or group of buildings on a site occupying a total area of 5,000 square feet (464.5 m2) or less. Where load tests are required, at least two load tests shall be performed for a site having a footprint between 5,000 square feet (464.5 m2) and 30,000 square feet (2787.1 m2), and one additional load test shall be performed for each 20,000 square feet (1868.1 m2) of added footprint area. For conditions where multiple deep foundation types or capacities are used, refer to Section 1810.2.5.
1810.4.1.1.1 Additional load tests. | Where load bearing capacities of the installed deep foundations are in doubt, are considered non-conforming by the engineer, or where required by the commissioner, additional deep foundation elements shall be load tested to establish the allowable capacity. For friction-based deep foundations where the actual production deep foundation lengths vary more than 25 percent from that of the deep foundations initially installed and load tested, the engineer shall determine if additional load tests are required to establish the allowable capacity of the deep foundation. The number of additional load tests shall be determined by the engineer or commissioner.
1810.4.1.2 Load test apparatus and inspection requirements. | The apparatus and structure to be used in making the load test shall be designed by an engineer. Load tests shall be performed under the observation of the special inspector. A complete record of such tests shall be filed with the commissioner.
1810.4.1.3 Compressive load test procedures. | Compressive load tests shall be conducted in accordance with ASTM D1143 standard procedures and the following conditions: 1. Dial extensometer gages shall provide readings to the nearest 0.001 inch (0.025 mm). Electrical transducers may be used to make settlement observations, provided that backup measurements are made utilizing dial extensometers as described herein at sufficient times to validate the transducer readings. 2. If the allowable axial compressive load is less than or equal to the Basic Maximum Allowable Loads on Deep Foundations in Table 1810.4.1.3, the total test load shall remain in place for a minimum of 12 hours, and shall be held until the average rate of settlement as measured over a 12-hour period does not exceed 0.001 inches (0.025 mm) per hour. The total load shall be removed in decrements not exceeding 25 percent of the total load at 1 hour intervals or longer. For cases where the allowable load on the deep foundation is greater than the values prescribed in Table 1810.4.1.3, refer to Section 1810.4.1.5. 3. In addition to observations required by ASTM D1143, settlement observations shall be performed 24 hours after the entire test load has been removed. Exception: A static load test for drilled deep foundations using an embedding load transfer mechanism shall be considered acceptable, provided that the test is performed in general accordance with ASTM D1143 – Quick Load Test Method. The deep foundation shall be suitably instrumented to evaluate the load transfer through soil or rock at multiple locations along the shaft. 4. Any temporary supporting capacity that the soil might provide to the deep foundation during a load test, but which would be dissipated with time, shall be eliminated by casing off or by other suitable means, such as increasing the total test load to account for such temporary capacity.
1810.4.1.4 High strain, dynamic compressive test methods. | High strain, dynamic compressive test methods performed in accordance with ASTM D4945 shall be permitted to be used where two or more load tests are required and subject to the approval of the commissioner. In such case, at least one high strain dynamic test shall be performed as a calibration on a static load tested deep foundation or nearby deep foundation driven to comparable resistance. No more than one-half of the required number of load tests may be performed by high strain dynamic methods. High strain dynamic tests shall be performed under the supervision of an engineer experienced in the methods used. The number of high strain dynamic tests shall be at least twice the number of replaced static load tests.
1810.4.1.5 Acceptance criteria. | The allowable load of a deep foundation shall be the lesser of the two values computed as follows:
1810.4.1.5.1 Substantiation of higher allowable loads. | The basic maximum allowable loads of deep foundations tabulated in Table 1810.4.1.3 may be exceeded where a higher value can be substantiated on the basis of load tests and analysis, except for the loads for timber and helical piles. The provisions of Section 1810.4.1 shall be supplemented, as follows: the final load increment shall remain in place for a total of not less than 24 hours; single tested deep foundations shall be subjected to cyclical loading in accordance with ASTM D1143 or suitably instrumented with telltales and strain gauges so that the movements of the tip and butt of the deep foundation may be independently determined and load transfer to the soil evaluated. A complete record demonstrating satisfactory performance of the test shall be submitted to the commissioner.
1810.4.2 Uplift load test. | Where uplift load tests are required, one uplift load test shall be conducted in each area of substantially similar subsurface conditions up to 5,000 square feet (465 m2) of building footprint where deep foundations are subjected to uplift, and not less than two uplift load tests shall be conducted for each area of building footprint where deep foundations are subjected to uplift between 5,000 square feet (465 m2) and 30,000 square feet (2787.1 m2) and for such area one additional uplift load test shall be conducted for each 20,000 square feet (1858.1 m2) of additional area of building footprint where deep foundations are subject to uplift. For conditions where multiple types or capacities of deep foundations are used, refer to Section 1810.2.5.
1810.4.2.1 Uplift load test procedures. | Uplift load tests shall be conducted in accordance with ASTM D3689 standard procedures and the following conditions:
1810.4.2.2 Uplift load test apparatus and inspection requirements. | The apparatus and structure to be used in making the load test shall be designed by an engineer. Load tests shall be performed under the observation of the special inspector. A complete record of such tests shall be filed with the commissioner.
1810.4.3 Lateral load tests. | Where testing is required, lateral load tests shall be performed in accordance with ASTM D3966. A minimum of two deep foundations shall be tested for every area of similar subsurface conditions. For conditions where multiple types or capacities of deep foundations are used, refer to Section 1810.2.5.
1810.4.3.1 Free headed deep foundations. | For deep foundations whose heads are to be designed to be free to rotate in the final structure, the maximum test load shall be at least twice the proposed design working load. In the absence of specific project requirements as determined by the engineer, the resulting allowable load shall not be more than one-half of that test load that produces a gross lateral movement of 1 inch (25.4 mm) of the deep foundation at the ground surface.
1810.4.3.2 Fixed headed deep foundations. | For deep foundations whose heads are designed to be fixed in the final structure, the results of the load test shall be used to verify the input parameters used in the lateral load analysis. In the absence of specific project requirements as determined by the engineer, the allowable load shall be the load that produces a gross lateral movement of ⅜ inch (9.5 mm) of the deep foundation at the ground surface in the lateral load analysis.
1810.4.3.3 Lateral load test procedures. | Lateral load tests shall be conducted in accordance with ASTM D3966 standard procedures. In addition, dial extensometer gages shall provide readings to the nearest 0.001 inch (0.025 mm). Electrical transducers may be used to make deflection observations, provided that backup measurements are made utilizing dial extensometers as described herein at sufficient times to validate the transducer readings.
1810.4.3.4 Load test apparatus and inspection requirements. | The apparatus and structure to be used in making the load test shall be designed by an engineer. Lateral load tests shall be performed under the observation of the special inspector. A complete record of such tests shall be filed with the commissioner.
1810.5 Installation. | Installation of deep foundations shall be subject to the requirements of Sections 1810.5.1 through 1810.5.8.
1810.5.1 Protection of deep foundations during installation. | Deep foundations shall be handled and installed to the required penetration and resistance by methods that leave the deep foundations’ strength unimpaired and that develop and retain the deep foundations’ required load-bearing resistance. Any damaged deep foundation shall be satisfactorily repaired or the deep foundation shall be rejected. As an alternative and subject to the approval by the commissioner, deep foundations that are damaged, misaligned, or do not reach their design tip elevation may be used at a reduced fraction of the design load based on an analysis by the engineer.
1810.5.2 Equipment. | Equipment and methods of installation shall be such that deep foundations are installed in their proper position and alignment without damage. Equipment shall be maintained in good working order.
1810.5.3 Preexcavation. | The use of jetting, augering or other methods of preexcavation shall be subject to the approval of the commissioner. Where permitted, preexcavation shall be carried out in the same manner as used for deep foundation elements subject to load tests and in such a manner that will not impair the carrying capacity of the deep foundation elements already in place or damage adjacent structures. The element tips of deep foundations shall be advanced below the preexcavated depth until the required resistance or penetration is obtained.
1810.5.4 Minimum penetration of deep foundations. | Deep foundations shall penetrate the minimum distance required to develop the required load capacity of the deep foundation as established by the required penetration resistance and load tests as applicable.
1810.5.5 Damage to adjacent structures or deep foundations. | Deep foundations shall be installed in such a manner and sequence as to prevent distortion or damage that affects the structural integrity of the deep foundations being installed, or previously installed adjacent deep foundations. The sequence of the installation shall avoid compacting the surrounding soil to the extent that other deep foundations cannot be installed properly, and shall prevent ground movements that are capable of damaging adjacent structures. Deep foundations shall be installed with adequate provision for the protection of adjacent buildings and property.
1810.5.6 Identification. | All deep foundation elements shipped or delivered to the job site shall be identified for conformity to the specified grade and this identification shall be maintained continuously from the point of manufacture to the point of installation. Such shipment or delivery shall be accompanied by a certification from the material supplier or manufacturer indicating conformance with the construction documents. Such certification shall be made available to the engineer of record and the department. In the absence of adequate data, deep foundation elements shall be tested by an approved agency to determine conformity to the specified grade. The approved agency shall furnish a certification of compliance to the engineer of record, or upon request to the commissioner.
1810.5.7 Deep foundation location plan. | A plan showing the location and designation of deep foundations by an identification system shall be filed with the commissioner prior to installation of such deep foundations. Detailed records for individual deep foundations shall bear an identification corresponding to that shown on the plan.
1810.5.8 Installation of deep foundations. | Deep foundations within the area of influence of a given, satisfactorily tested deep foundation shall be installed to the same installation criteria as the satisfactorily tested deep foundation. The same equipment that was used to install the satisfactorily tested deep foundation, identically operated in all aspects, shall be used to install the deep foundation. All deep foundation shall be of the same type, size and shape as the satisfactorily tested deep foundation. All deep foundations within the area of influence as represented by a given satisfactorily tested deep foundation shall bear in, or on, the same bearing stratum as the satisfactorily tested deep foundation.
1810.6 Tolerances. | Tolerances for deep foundations shall be in accordance with the requirements of Sections 1810.6.1 through 1810.6.4.
1810.6.1 Tolerance in the location of the head of the deep foundation. | A tolerance of 3 inches (76.2 mm) from the designed location shall be permitted in the installation of each deep foundation as measured from its head, without reduction in load capacity of the deep foundation group unless otherwise noted on the foundation plans. When deep foundations are installed outside of this tolerance, the true loading on such deep foundations shall be analytically determined from a survey that defines the actual location of the deep foundations as installed and using the actual eccentricity in the deep foundation group with respect to the line of action of the applied load.
1810.6.2 Out of plumb tolerance. | If the axis of any deep foundation is installed out of plumb or deviates from the specified batter by more than 4 percent, the design of the foundation shall be modified to resist the resulting vertical and lateral forces. In types of deep foundations for which subsurface inspection is not possible, this determination shall be made on the exposed section of the deep foundation, which at the time of checking axial alignment, shall not be less than 2 feet (609.6 mm) in length. In deep foundations that can be checked for axial alignment below the ground surface, the sweep of the deep foundation axis shall not exceed 4 percent of the embedded length.
1810.6.3 Deep foundations that are bent during installation. | The load-bearing capacity of deep foundations discovered to have a sharp or sweeping bend shall be determined using an approved method of analysis by the engineer responsible for the deep foundation design in accordance with accepted engineering practice or by load testing a representative deep foundation.
1810.6.4 Deep foundations that are mislocated during installation. | The maximum compressive load on any deep foundation due to mislocation shall not exceed 110 percent of the allowable design load. If the total load on any deep foundation, so determined, is in excess of 110 percent of the allowable load-bearing capacity, correction shall be made by installing additional deep foundations or by other methods of load distribution as required to reduce the maximum load to 110 percent of the allowable deep foundation capacity.
1810.7 Lateral support. | Lateral support for deep foundation elements shall be in accordance with the requirements of Sections 1810.7.1 through 1810.7.4.
1810.7.1 Buckling of deep foundations. | Any soil other than soil with no shear strength shall be deemed to afford sufficient lateral support to the deep foundation to prevent buckling and to permit the design of the deep foundation in accordance with accepted engineering practice and the applicable provisions of this code.
1810.7.2 Unbraced deep foundations. | Deep foundation elements standing unbraced in air, water or soils with no shear strength shall be designed as columns in accordance with the provisions of this code. Such deep foundations driven into firm ground can be considered fixed and laterally supported at 5 feet (1524 mm) below the ground surface and in soft material at 10 feet (3048 mm) below the ground surface unless otherwise prescribed by the engineer.
1810.7.3 Bracing at tops of deep foundations. | Deep foundations shall be braced to provide lateral stability and resist eccentric loads and moments in all directions. Three or more deep foundations connected by a rigid cap shall be considered braced, provided that the deep foundations are located in radial directions from the centroid of the group not less than 60 degrees (1 rad) apart. A group of two deep foundation elements in a rigid cap shall be considered to be braced along the axis connecting the two deep foundations. Methods used to brace deep foundations shall be subject to the approval of the commissioner.
1810.7.4 Bracing of short deep foundations. | All pile caps supported by deep foundations that penetrate less than 10 feet (3048 mm) below cutoff level or less than 10 feet (3048 mm) below ground level shall be braced against lateral movement. Such bracing may consist of connection to other pile caps that encompass deep foundations embedded more than 10 feet (3048 mm) below those levels. The heads of the deep foundations shall be fixed in the cap. In no case shall more than fifty percent of the deep foundations in the foundation of any building penetrate less than 10 feet (3048 mm) below cut-off level or less than 10 feet (3048 mm) below ground level. Exception: The requirements of this section shall not apply to caisson piles.
1810.7.4.1 Deep foundations located near a lot line. | Where the embedded length of deep foundations located near a lot line would be reduced to less than 10 feet (3048 mm) by excavation of the adjacent site to a depth of 10 feet (3048 mm) below the nearest established curb level, the provisions of Section 1810.7.4 shall apply.
1810.8 Allowable stresses. | Allowable stresses for deep foundations shall be as listed in Table 1810.8. Exception: Allowable stresses greater than those specified in Table 1810.8 in Sections 1811 and 1812 shall be permitted where supporting data justifying such higher stresses are filed and approved by the commissioner.
1810.9 Seismic design of deep foundations. | Seismic design of deep foundation elements for structures assigned to Seismic Design Categories C & D shall be performed in accordance with Sections 1810.9.1 and 1810.9.2.
1810.9.1 Seismic Design Category C. | Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, individual pile caps or deep foundations shall be interconnected by ties. Ties shall be capable of carrying, in tension and compression, a force equal to the lesser of: (i) the product of the larger of the pile cap or column design gravity load times the seismic coefficient, SDS, divided by 10, or (ii) 25 percent of the smaller of the deep foundation or column design gravity load, unless it can be demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade, reinforced concrete slabs on grade, or confinement by competent rock, hard cohesive soils or very dense granular soils.
1810.9.1.1 Connection to pile cap. | For structures assigned to Seismic Design Category C or D in accordance with Section 1613, deep foundation elements consisting of concrete shall be connected to the pile cap by embedding the element reinforcement or field-placed dowels anchored in the element into the pile cap for a distance equal to their development length in accordance with ACI 318. It shall be permitted to connect precast, prestressed deep foundations to the pile cap by developing the element prestressing strands into the pile cap, provided the connection is ductile. For deformed bars, the development length is the full development length for compression, or tension in the case of uplift, without reduction for excess reinforcement in accordance with Section 25.4.10 of ACI 318. Alternative measures for laterally confining concrete and maintaining toughness and ductile-like behavior at the top of the element shall be permitted, provided the design is such that any hinging occurs in the confined region. The minimum transverse steel ratio for confinement shall not be less than one-half of that required for columns. For resistance to uplift forces, anchorage of steel pipes, tubes or H-piles to the pile cap shall be made by means other than concrete bond to the bare steel section. Concrete-filled steel pipes or tubes shall have reinforcement of not less than 0.01 times the cross sectional area of the concrete fill, developed into the cap and extending into the concrete fill a length equal to two times the required cap embedment, but not less than the development length in tension of the reinforcement. Exception: Anchorage of concrete-filled steel pipe piles is permitted to be accomplished using deformed bars developed into the concrete portion of the deep foundation. Splices of deep foundation segments shall develop the full strength of the deep foundation, but the splice need not develop the nominal strength of the deep foundation in tension, shear and bending when the splice has been designed to resist axial and shear forces and moments from the load combinations of Section 12.4 of ASCE 7.
1810.9.1.2 Design details. | Moments, shears and lateral deflections used for design of deep foundations shall be established considering the nonlinear interaction of the shaft and soil, as recommended by the engineer. Where the ratio of the depth of embedment of the center-to-center diameter or width of deep foundations is less than or equal to six, the deep foundation may be assumed to be rigid. Group effects from soil on lateral deep foundation nominal strength shall be included where deep foundation center-to-center spacing in the direction of lateral force is less than eight diameters. Group effects on vertical nominal strength of deep foundations shall be included where deep foundation center-to-center spacing is less than three diameters. The uplift soil nominal strength of deep foundations shall be taken as the uplift strength as limited by the frictional force developed between the soil and the deep foundation.
1810.9.2 Seismic Design Category D. | Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, the requirements for Seismic Design Category C given in Section 1810.9.1 shall be met. Provisions of ACI 318, Section 18.13.4, shall also apply when not in conflict with the provisions of Sections 1810 through 1816. Concrete shall have a specified compressive strength of not less than 3,000 psi (20.68 MPa) at 28 days. Exceptions: 1. Group R or U occupancies of light-framed construction and two stories or less in height are permitted to use concrete with a specified compressive strength of not less than 2,500 psi (17.2 MPa) at 28 days. 2. Detached one and two-family dwellings of light-frame construction and two stories or less in height are not required to comply with the provisions of ACI 318, Section 18.13.4. 3. Section 18.13.4.4(a) of ACI 318 shall not apply to concrete piles.
1810.9.2.1 Design details for deep foundations and grade beams. | Design details for deep foundations and grade beams shall comply with the following:
1810.9.2.2 Connection to pile cap. | For deep foundations required to resist uplift forces or provide rotational restraint, design of anchorage of deep foundations into the pile cap shall be provided considering the combined effect of axial forces due to uplift and bending moments due to fixity to the pile cap. Anchorage into the pile cap shall be capable of developing the following:
1810.9.2.3 Flexural strength. | Where the vertical, lateral-force-resisting elements are columns, the grade beam or pile cap flexural strengths shall exceed the column flexural strength.
1810.9.2.4 Battered deep foundations. | The connection between deep foundations that are battered and grade beams or pile caps shall be designed to resist the nominal strength of the deep foundation acting as a short column. Battered deep foundations and their connections shall be capable of resisting forces and moments from the load combinations of Section 12.4 of ASCE 7.
1811.1 General. | Driven deep foundations shall be designed and installed in accordance with Sections 1810 and 1811.2 through 1811.7. Driven deep foundation elements shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.
1811.2 Equipment. | Equipment and methods of installation shall be such that deep foundations are installed in their proper position and alignment, without damage. Equipment shall be maintained in good working order.
1811.2.1 Driving hammer for deep foundations. | The hammer to be used to drive deep foundations shall deliver a maximum energy consistent with the size, strength and weight of the driven deep foundations. The hammer shall travel freely in the leads. The hammer shall deliver its rated energy, and measurements shall be made of the fall of the ram or other suitable data shall be obtained at intervals necessary to verify the actual energy delivered during the final 20 blows of the hammer.
1811.2.2 Cushion or cap block. | The cushion or cap block shall be a solid block of hardwood with its grains parallel to the axis of the deep foundation and enclosed in a tight-fitting steel housing, or other accepted equivalent assembly. If laminated materials are used, their type and construction shall be such that their strength is equal to or greater than hardwood. Wood chips, pieces of rope, hose, shavings, automobile tires or similar materials shall not be used. Cap block cushions shall be replaced if burned, crushed, or otherwise damaged. Other cushion materials may be used subject to the approval of the engineer. The introduction of fresh hammer cushion or pile-driving cushion material just prior to final penetration is not permitted.
1811.2.3 Followers. | Followers shall not be used unless permitted in writing by the engineer responsible for the driving operation of the deep foundation. The required driving resistance shall account for the losses of driving energy transmitted to the deep foundation because of the follower. The follower shall be a single length section, be provided with a socket or hood carefully fitted to the top of the deep foundation to minimize loss of energy and to prevent damage to the deep foundation, and have sufficient rigidity to prevent “whip” during driving.
1811.3 Driving criteria. | The allowable compressive load on steel and concrete piles, where determined solely by the application of an approved wave equation analyses approved by the engineer, shall not exceed 40 tons (392.3 kN). The allowable compressive loads on timber piles, where determined solely by the wave equation analyses approved by the engineer, shall not exceed 30 tons (294.2 kN). For allowable loads greater than these values, the wave equation method of analysis may be used to establish initial driving criteria, but final driving criteria and the allowable load shall be verified by load tests in accordance with Section 1810.4. Minimum driving resistance and hammer energy may be determined in accordance with Tables 1811.3(a) and 1811.3(b).
1811.3.1 Capacity as indicated by resistance to penetration. | Where subsurface investigation and general experience in the area indicate that the soil that must be penetrated by the deep foundation consists of glacial deposits containing boulders, or fills containing rip-rap, excavated detritus, masonry, concrete or other obstructions in sufficient numbers to present a hazard to the installation of the deep foundations, the selection of type of deep foundation and penetration criteria shall be subject to the approval of the commissioner, but in no case shall the minimum penetration resistance be less than that stated in Tables 1811.3(a) and 1811.3(b).
1811.4 Installation of driven deep foundations. | Driven deep foundations shall be installed in accordance with Section 1810.2 and Sections 1811.4.1 through 1811.4.3.
1811.4.1 Driving near fresh concrete. | Deep foundations shall not be driven adjacent to fresh concrete that is less than 3 days old without approval by the engineer.
1811.4.2 Heaved deep foundations. | Deep foundations that have heaved during the driving of adjacent deep foundations shall be redriven as necessary to develop the required capacity and penetration, or the capacity of the deep foundation shall be verified by load tests in accordance with Section 1810.4.
1811.4.3 Use of vibratory drivers. | Vibratory drivers shall only be used to install deep foundation elements where the deep foundation is subsequently seated by an impact hammer to the final driving criteria established in accordance with Section 1811.3.
1811.5 Timber piles. | Timber piles shall be designed in accordance with the AWC NDS.
1811.5.1 Materials. | Round timber piles shall conform to ASTM D 25. Sawn timber piles shall conform to DOC PS-20.
1811.5.2 Preservative treatment. | Timber piles used to support permanent structures shall be treated in accordance with this section unless it is established that the tops of the untreated timber piles will be below the lowest groundwater level assumed to exist during the life of the structure as specified in Section 1810.2.12. Preservative and minimum final retention shall be in accordance with AWPA U1 (Commodity Specification E, Use Category 4C) for round timber piles and AWPA U1 (Commodity Specification A, Use Category 4B) for sawn timber piles. Preservative-treated timber piles shall be subject to a quality control program administered by an approved agency. Cuts to timber piles shall be treated in accordance with AWPA M4.
1811.5.3 Defective timber piles. | Any sudden decrease in driving resistance of a timber pile shall be investigated for possible damage. If the sudden decrease in driving resistance cannot be correlated to load-bearing data, the timber pile shall be removed for inspectionor rejected.
1811.5.4 Sizes of timber piles. | Timber piles shall be of adequate size to resist the applied loads without creating stresses in the timber pile material in excess of 1,200 psi (8.27 MPa) for piles of southern pine, Douglas fir, oak, or other wood of comparable strength; or 800 psi (5.52 MPa) for timber piles of cedar, Norway pine, spruce or other wood of comparable strength. Timber piles of 25 tons (222.5 kN) of capacity or more shall have a minimum 8-inch tip (203.2 mm) with uniform taper. Timber piles of less than 25 tons (222.5 kN) of capacity shall have a minimum 6-inch (152.4 mm) tip with uniform taper. All timber piles, regardless of capacity, driven to end bearing on bedrock of Classes 1a to 1d and compact gravels and sands of Class 2a shall have a minimum 8-inch (203.2 mm) tip and a uniform taper. Any species of wood may be used for timber piles that conforms to ASTM D 25 and that will stand the driving stresses.
1811.5.5 Lagged or inverted timber piles. | The use of lagged or inverted timber piles is permitted. Double lagging shall be adequately connected to the basic timber pile material to transfer the full load from the basic timber pile material to the lagging without exceeding values of allowable stress as established in Chapter 23. The connection for single lagging shall be proportioned for half the timber pile load. The diameter of any inverted timber pile at any section shall be adequate to resist the applied load without exceeding the stresses specified in Section 1811.5.4, but in no case shall it be less than 8 inches (203.2 mm).
1811.6 Precast concrete piles.
1811.6.1 General. | The materials, reinforcement and installation of precast concrete piles shall conform to Sections 1811.6.1.1 through 1811.6.1.3.
1811.6.1.1 Minimum dimension. | The minimum horizontal dimension shall be 8 inches (203.2 mm). Corners of square precast concrete piles shall be chamfered.
1811.6.1.2 Reinforcement. | Longitudinal steel shall be arranged in a symmetrical pattern and be laterally tied with steel ties or wire spiral spaced not more than 4 inches (101.6 mm) apart, center to center, for a distance of 2 feet (609.6 mm) from the ends of the precast concrete pile; and not more than 6 inches (152.4 mm) elsewhere except that at the ends of each precast concrete pile, the first five ties or spirals shall be spaced 1 inch (25.4 mm) center to center. The gage of ties and spirals shall be as follows:
1811.6.1.3 Installation. | Precast concrete piles shall be handled and driven so as not to cause injury or overstressing in a manner that affects durability or strength. A precast concrete pile shall not be driven before the concrete has attained a compressive strength of at least 75 percent of the 28-day specified compressive strength (f’c), and not less than the strength sufficient to withstand handling and driving forces.
1811.6.2 Precast nonprestressed concrete piles. | Precast nonprestressed concrete piles shall conform to Sections 1811.6.2.1 through 1811.6.2.4.
1811.6.2.1 Materials. | Concrete shall have a 28-day specified compressive strength (f’c) of not less than 3,000 psi (20.68 MPa).
1811.6.2.2 Minimum reinforcement. | The minimum amount of longitudinal reinforcement shall be 0.8 percent of the concrete section and consist of at least four bars.
1811.6.2.2.1 Seismic reinforcement in Seismic Design Category C. | Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, longitudinal reinforcement with a minimum steel ratio of 0.01 shall be provided throughout the length of precast concrete piles. Within a distance equivalent to three times the diameter of the deep foundation element of the bottom of the pile cap, the longitudinal reinforcement shall be confined with closed ties or spirals of a minimum ⅜-inch (9.5 mm) diameter. Ties or spirals shall be provided at a maximum spacing of eight times the diameter of the smallest longitudinal bar, not to exceed 6 inches (152.4 mm). Throughout the remainder of the precast nonprestressed concrete pile, the closed ties or spirals shall have a maximum spacing of 16 times the smallest longitudinal-bar diameter, not to exceed 6 inches (152.4 mm).
1811.6.2.2.2 Seismic reinforcement in Seismic Design Category D. | Where a structure is assigned to Seismic Design Category D in accordance with Section 1613, the requirements of Seismic Design Category C shall apply, except that transverse reinforcement shall comply with requirements of Section 1812.1.2.5.
1811.6.2.3 Allowable stresses. | For allowable stresses, see Table 1810.8.
1811.6.2.4 Concrete cover. | For concrete cover requirements, see Table 1810.2.13.
1811.6.3 Precast prestressed concrete piles. | Precast prestressed concrete piles shall conform to the requirements of Sections 1811.6.3.1 through 1811.6.3.4.
1811.6.3.1 Materials. | Prestressing steel shall conform to ASTM A 416. Concrete shall have a 28-day specified compressive strength (f’c) of not less than 5,000 psi (34.48 MPa).
1811.6.3.2 Design. | Precast prestressed concrete piles shall be designed to resist stresses induced by handling and driving as well as by loads. The effective prestress shall not be less than 400 psi (2.76 MPa) for precast prestressed concrete piles less than 30 feet (9144 mm) in length, 550 psi (3.79 MPa) for precast prestressed concrete piles between 30 and 50 feet (9144 mm and 15 240 mm) in length and 700 psi (4.83 MPa) for precast prestressed concrete piles greater than 50 feet (15 240 mm) in length. Effective prestress shall be based on an assumed loss of 30,000 psi (207 MPa) in the prestressing steel. The tensile stress in the prestressing steel shall not exceed the values specified in ACI 318.
1811.6.3.2.1 Design in Seismic Design Category C. | Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, precast prestressed concrete piles shall have transverse reinforcement in accordance with this section. The minimum volumetric ratio of spiral reinforcement shall not be less than the amount required by the following formula for the upper 20 feet (6096 mm) of the precast prestressed concrete pile. Exception: The minimum spiral reinforcement index required by Equation 18-1 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 and the applicable overstrength factor, Ω0. In such cases, minimum spiral reinforcement index shall be as specified in Section 1811.6.1.2 of this code.
1811.6.3.2.2 Design in Seismic Design Category D. | Where a structure is assigned to Seismic Design Category D in accordance with Section 1613.3.5, the requirements for Seismic Design Category C in Section 1811.6.3.2.1 shall be met, in addition to the following: This required amount of spiral reinforcement is permitted to be obtained by providing an inner and outer spiral. Exception: The minimum spiral reinforcement required by Equation 18-2 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 and the applicable overstrength factor, Ω0. In such cases, minimum spiral reinforcement index shall be as specified in Section 1811.6.1.2.
1811.6.3.3 Allowable stresses. | For allowable stresses, see Table 1810.8.
1811.6.3.4 Concrete cover. | For concrete cover requirements, see Table 1810.2.13.
1811.7 Structural steel piles. | Structural steel piles shall conform to the requirements of Sections 1811.7.1 through 1811.7.6.
1811.7.1 Materials. | Structural steel H-piles and structural steel sheet piling shall conform to the material requirements in ASTM A6. Steel pipe piles shall conform to the material requirements in ASTM A252. Welded built-up steel piles shall be fabricated from plates that conform to the material requirements in ASTM A 36, ASTM A283, ASTM A572, ASTM A588 or ASTM A690.
1811.7.1.1 Structural steel pipe piles to be welded. | Structural steel pipe piles to be fabricated or spliced by welding shall be subject to qualification requirements of AWS D1.1 for unlisted base metals. Structural steel pipe piles to be welded shall have a carbon equivalency (CE) not exceeding 0.45 as defined by AWS D1.1 and a sulfur content not exceeding 0.05%. Carbon equivalency and sulfur content shall be determined by mill certificates or by chemical analysis, for a minimum of two samples per 1,000 linear feet (304 800 mm) of pipe or part thereof, where mill certificates are unavailable.
1811.7.1.2 High strength pipe. | High strength pipe meeting the strength requirements of API 5L (N80) and API 5CT (N80) shall be permitted for use as structural steel pipe piles. All such pipe and casing shall meet the minimum tensile requirements of ASTM A252, Grade 3 with a minimum elongation of 15 percent, except that the yield strength shall be a minimum of 80 ksi (551.6 MPa). The following requirements shall also apply:
1811.7.2 Allowable stresses. | For the allowable stresses for materials used in structural steel piles see Table 1810.8.
1811.7.3 Dimensions of Structural Steel H-piles. | Sections of structural steel H-piles shall comply with the requirements for HP shapes in ASTM A6 or the following:
1811.7.4 Dimensions of structural steel pipe piles. | Structural steel pipe piles driven open ended shall have a nominal outside diameter of not less than 8 inches (203.2 mm). The pipe shall have a minimum of 0.34 square inches (219.4 mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 N×m) of energy from the hammer used to install deep foundation elements or the equivalent strength for steels having a yield strength greater than 35,000 psi (241.3 MPa), or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the structural steel pipe pile section is appropriate for the selected hammer. Where pipe wall thickness less than 0.188 inch (4.8 mm) is driven open ended, a suitable cutting shoe shall be provided.
1811.7.5 Built-up structural steel piles fabricated from plates. | Built-up sections of steel piles fabricated from welded plates shall comply with the following:
1811.7.6 Structural steel sheet piling. | Individual sections of structural steel sheet piling shall conform to the profile indicated by the manufacturer, and shall conform to the general requirements specified by ASTM A6.
1812.1 General. | The materials, reinforcement and installation of cast-in-place concrete piles shall conform to Sections 1812.1.1 through 1812.1.3.
1812.1.1 Materials. | Concrete or grout shall have a 28-day specified compressive strength (f’c) of not less than 2,500 psi (17.24 MPa), except in micropiles and caisson piles where the minimum compressive strength shall be 4,000 psi (27.58 MPa). Where concrete is placed through a funnel hopper at the top of the cast-in-place concrete pile, the concrete mix shall be designed and proportioned so as to produce a cohesive workable mix having a slump of not less than 4 inches (101.6 mm) and not more than 6 inches (152.4 mm). Where concrete is to be pumped, the mix design shall be such that material produced is suitable for pumping.
1812.1.1.1 Concrete sampling and testing. | Sampling and testing of concrete shall be in accordance with Chapter 19.
1812.1.1.2 Grout sampling and testing. | Sampling and testing of grout shall be in accordance with Sections 1812.1.1.2.1 through 1812.1.1.2.3.
1812.1.1.2.1 Interval. | Grout samples shall be collected and testing shall be performed for the lesser of the following conditions:
1812.1.1.2.2 Compressive strength. | Compressive strength tests shall be performed using cylinders having a maximum diameter of 3 inches (72.3 mm). Grout shall be tested in accordance with ASTM C39. A minimum of six (6) samples shall be prepared for each test group.
1812.1.1.2.3 Specific gravity. | Specific gravity testing shall be performed using the American Petroleum Institute (API) Recommended Practice 13B-1 or in accordance with ASTM C138.
1812.1.2 Placement of reinforcement. | Reinforcement, where required, shall be placed in accordance with Section 1812.3.4 and shall be assembled, tied together, and placed in the cast-in-place concrete pile as a unit before concrete or grout is placed. Exceptions: Where approved by the engineer, reinforcement may be placed after the cast-in-place concrete piles are filled with concrete or grout under the following situations: 1. Tied reinforcement in augered uncased cast-in-place concrete piles, while the concrete or grout is still in a semifluid state. 2. Tied reinforcement in cast-in-place concrete piles filled with grout, while the grout is in a semifluid state. 3. Steel dowels embedded 5 feet (1524 mm) or less in the cast-in-place concrete pile while the concrete or grout is still in a semifluid state.
1812.1.2.1 Design cracking moment. | The design cracking moment (ØMn) for a cast-in-place deep foundation element not enclosed by a structural steel pipe or tube shall be determined using the following equation:
1812.1.2.2 Required reinforcement. | Where subject to uplift, or where the required moment strength determined using the load combinations of Section 1605.2 exceeds the design cracking moment determined in accordance with Section 1812.1.2.1, cast-in-place concrete piles not enclosed by a structural steel pipe or tube shall be reinforced.
1812.1.2.3 Reinforcement in Seismic Design Categories C & D. | Where a structure is assigned to Seismic Design Category C in accordance with Section 1613, reinforcement shall be provided in accordance with Section 1812.1.2.4. Where a structure is assigned to Seismic Design Category D, reinforcement shall be provided in accordance with Section 1812.1.2.5.
1812.1.2.4 Seismic reinforcement in Seismic Design Category C. | For structures assigned to Seismic Design Category C in accordance with Section 1613, cast-in-place concrete pile elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. A minimum of four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.0025, shall be provided throughout the minimum reinforced length of the element as defined below starting at the top of the element. The minimum reinforced length of the element shall be the greatest of the following: 1. One-third of the element length; 2. A distance of 10 feet (3048 mm); 3. Three times the least element dimension; or 4. The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1812.1.2.1 exceeds the required moment strength determined using the load combinations of Section 1605.2. Transverse reinforcement shall consist of closed ties or spirals with a minimum diameter of ⅜ inch (9.5 mm). Spacing of transverse reinforcement shall not exceed the smaller of 6 inches (152.4 mm) or 8-longitudinal-bar diameters, within a distance of three times the least element dimension from the bottom of the pile cap. Spacing of transverse reinforcement shall not exceed 16 longitudinal bar diameters throughout the remainder of the reinforced length. Exceptions: 1. The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes. 2. A spiral-welded metal casing of a thickness not less than manufacturer’s standard No. 14 gage (0.068 inch) (1.73 mm) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.
1812.1.2.5 Seismic reinforcement in Seismic Design Category D. | For structures assigned to Seismic Design Category D in accordance with Section 1613, cast-in-place concrete pile elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. A minimum of four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.005, shall be provided throughout the minimum reinforced length of the element as defined below starting at the top of the element. The minimum reinforced length of the element shall be the greatest of the following: 1. One-half of the element length; 2. A distance of 10 feet (3048 mm); 3. Three times the least element dimension; or 4. The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1812.1.2.1 exceeds the required moment strength determined using the load combinations of Section 1605.2. Transverse reinforcement shall consist of closed ties or spirals no smaller than No. 3 bars for elements with a least dimension of up to 20 inches (508 mm), and No. 4 bars for larger elements. Throughout the remainder of the reinforced length outside the regions with transverse confinement reinforcement, as specified in Section 1812.1.2.5.1 or 1812.1.2.5.2, the spacing of transverse reinforcement shall not exceed the least of the following: 1. 12 longitudinal bar diameters; 2. One-half the least dimension of the element; or 3. 12 inches (304.8 mm). Exceptions: 1. The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes. 2. A spiral-welded metal casing of a thickness not less than manufacturer’s standard No. 14 gage (0.068 inch) (1.73 mm) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.
1812.1.2.5.1 Site Classes A through D. | For Site Class A, B, C and D, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, through 18.7.5.4 of ACI 318 within three times the least element dimension of the bottom of the pile cap. A transverse spiral reinforcement ratio of not less than one-half of that required in Section 18.7.5.4(a) of ACI 318 shall be permitted.
1812.1.2.5.2 Site Classes E and F. | For Site Class E or F, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2 through 18.7.5.4 of ACI 318 within seven times the least element dimension of the pile cap and within seven times the least element dimension of the interfaces of strata of Class 4b or better and strata that are liquefiable or are composed of material meeting Class 4c or 6.
1812.1.3 Concrete or grout placement. | Concrete or grout shall be placed in such a manner as to ensure the exclusion of any foreign matter and to secure a full-sized shaft. Concrete or grout shall not be placed through water except where a tremie or other approved method is used. When depositing concrete from the top of the cast-in-place concrete pile, the concrete shall not be chuted directly into the cast-in-place concrete pile but shall be poured in a rapid and continuous operation through a funnel hopper centered at the top of the cast-in-place concrete pile. Grout for auger cast piles shall be pumped through a hollow stem auger and shall be maintained as fluid throughout placement.
1812.2 Enlarged base piles. | Enlarged base piles shall conform to the requirements of Sections 1812.2.1 through 1812.2.5.
1812.2.1 Materials. | The maximum size of coarse aggregate for concrete shall be ¾ inch (19.1 mm). Concrete to be compacted shall have a zero slump.
1812.2.2 Allowable stresses. | For allowable stresses, see Table 1810.8.
1812.2.3 Installation. | Enlarged bases formed either by compacting concrete or driving a precast base shall be formed in or driven into granular soils. Enlarged base piles shall be constructed in the same manner as successful enlarged base test piles installed for the project. Enlarged base pile shafts extending through peat or other organic soil shall be encased in a permanent steel casing. Where a cased shaft is used, the shaft shall be adequately reinforced to resist column action or the annular space around the enlarged base pile shaft shall be filled sufficiently to re-establish lateral support by the soil. Where heave of an enlarged base pile or other deep foundation occurs, the enlarged base pile or other deep foundation, shall be replaced unless it is demonstrated that the enlarged base pile or other deep foundation is undamaged and capable of carrying twice its design load.
1812.2.4 Load-bearing capacity. | The load-bearing capacity of enlarged base piles shall be verified by load tests in accordance with Section 1810.4.
1812.2.5 Concrete and grout cover. | For minimum concrete and grout cover requirements, see Table 1803.13.
1812.3 Drilled, drilled displacement, or augered uncased piles. | Drilled, drilled displacement, or augered uncased piles shall conform to Sections 1812.3.1 through 1812.3.5.
1812.3.1 Allowable stresses. | For allowable stresses, see Table 1810.8.
1812.3.2 Dimensions. | The minimum diameter of drilled or drilled displacement piles shall be 8 inches (203.2 mm). The minimum diameter of augered uncased piles shall be 12 inches (304.8 mm).
1812.3.3 Installation. | Where shafts for drilled piles are formed through unstable soils and concrete is placed in an open-drilled hole, a steel liner shall be inserted in the hole prior to placing the concrete. Where the steel liner is withdrawn during concreting, the level of concrete shall be maintained above the bottom of the liner at a sufficient height to offset any hydrostatic or lateral soil pressure.
1812.3.4 Reinforcement. | For drilled piles installed with a hollow-stem auger, where full-length longitudinal steel reinforcement is placed without lateral ties, the reinforcement shall be placed through ducts in the auger prior to filling the drilled pile with concrete. Concrete cover for reinforcement of the drilled pile shall be in accordance with Table 1810.2.13. Exception: Where physical constraints do not allow the placement of the longitudinal reinforcement prior to filling the drilled pile with concrete or where partial-length longitudinal reinforcement is placed without lateral ties, the reinforcement is allowed to be placed after the drilled piles are completely concreted but while concrete is still in a semifluid state.
1812.3.5 Reinforcement in Seismic Design Category C or D. | Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the corresponding requirements of Sections 1812.1.2.3 through 1812.1.2.5 shall be met.
1812.4 Driven uncased piles. | Driven uncased piles shall not be permitted.
1812.5 Steel-cased piles. | Steel-cased piles shall comply with the requirements of Sections 1812.5.1 through 1812.5.4.
1812.5.1 Materials. | Shells or casings for steel cased piles shall be of steel and be sufficiently strong to resist collapse and sufficiently water tight to exclude any foreign materials during the placing of concrete. Steel shells shall have a sealed tip with a diameter of not less than 8 inches (203.2 mm).
1812.5.2 Allowable stresses. | For allowable stresses, see Table 1810.8.
1812.5.2.1 Shell thickness. | The thickness of the steel shell shall not be less than manufacturer’s standard No. 14 gage (0.068 inch) (1.75 mm) minimum.
1812.5.2.2 Shell type. | The shell shall be seamless or provided with seams of strength equal to the basic material and be of a configuration that will provide confinement to the cast-in-place concrete.
1812.5.2.3 Strength. | The ratio of steel yield strength (fy) to 28-day specified compressive strength (f’c) shall not be less than six.
1812.5.2.4 Diameter. | The nominal diameter of steel cased piles shall not be greater than 16 inches (406.4 mm).
1812.5.3 Installation. | Steel shells shall be mandrel driven for their full length in contact with the surrounding soil. The steel shells shall be driven in such order and with such pacing as to ensure against distortion of or injury to steel cased piles already in place. A steel cased pile shall not be driven within four and one-half average diameters of a steel cased pile filled with concrete less than 24 hours old unless approved by the commissioner. Concrete shall not be placed in steel shells within heave range of driving.
1812.5.4 Reinforcement. | Reinforcing shall be required for unsupported lengths of steel cased piles or where the steel cased pile is designed to resist uplift or unbalanced lateral loads. For minimum concrete cover requirements, see Table 1810.2.13.
1812.5.4.1 Seismic reinforcement. | Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the reinforcement requirements of Sections 1812.1.2.3 through 1812.1.2.5 shall be met.
1812.6 Concrete-filled steel pipe and tube piles. | Concrete-filled steel pipe and tube piles shall conform to the requirements of Sections 1812.6.1 through 1812.6.5.
1812.6.1 Materials. | Steel pipe and tube sections used for concrete-filled steel pipe and tube piles shall conform to ASTM A252 or ASTM A283. Concrete shall conform to Section 1812.1.1. The maximum coarse aggregate size shall be ¾ inch (19.1 mm).
1812.6.2 Allowable stresses. | For allowable stresses, see Table 1810.8.
1812.6.3 Minimum dimensions. | Concrete-filled steel pipe and tube piles shall have a nominal outside diameter of not less than 8 inches (203.2 mm) and a minimum wall thickness in accordance with Section 1811.7.4. For concrete-filled steel pipe and tube piles driven with a mandrel, the minimum wall thickness shall be 1/10 inch (2.5 mm).
1812.6.4 Reinforcement. | Reinforcement steel shall conform to Section 1812.1.2. For minimum concrete cover requirements see Table 1810.2.13.
1812.6.4.1 Seismic reinforcement. | Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, minimum reinforcement no less than 0.01 times the cross-sectional area of the concrete within the concrete-filled steel pipe and tube piles shall be provided in the top of the concrete-filled steel pipe and tube piles with an embedment length equal to two times the required cap embedment anchorage into the pile cap, but not less than the tension development length of the reinforcement. The wall thickness of the steel pipe shall not be less than 3/16 inch (4.8 mm).
1812.6.5 Placing concrete. | The placement of concrete shall conform to Section 1812.1.3.
1812.7 Caisson piles. | Caisson piles shall conform to the requirements of Sections 1812.7.1 through 1812.7.7.
1812.7.1 Construction. | Caisson piles shall consist of a shaft section of concrete or grout-filled pipe, extending to bedrock, with an uncased socket drilled into bedrock of Class 1c or better and filled with concrete or grout. The caisson pile shall have a full-length structural steel core, full length steel reinforcing, or a stub core or steel reinforcing installed in the rock socket and extending into the pipe portion a distance equal to the socket depth. The minimum outside diameter of the caisson pile shall be 7 inches (177.8 mm), and the diameter of the rock socket shall be approximately equal to the inside diameter of the caisson pile.
1812.7.1.1 Drilling with air. | Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.
1812.7.2 Materials. | Pipe and steel cores for caisson piles shall conform to the material requirements in Section 1811.7. Pipes shall have a minimum wall thickness of ⅜ inch (9.5 mm) and shall be fitted with a suitable steel-driving shoe or cutting teeth welded to the bottom of the pipe. Concrete or grout shall have a 28-day specified compressive strength (f’c) of not less than 4,000 psi (27.58 MPa).
1812.7.2.1 Reinforcing bars. | For the purposes of Section 1812.7, threaded bars conforming to ASTM A615 and ASTM A722 shall be considered the same as deformed reinforcing bars.
1812.7.3 Rock socket design. | The depth of the rock socket in Class 1c rock or better shall be sufficient to develop the full load-bearing capacity of the caisson pile based upon the sum of the allowable bearing pressure on the bottom of the socket in accordance with Table 1806.1 plus an allowable bond stress of 200 psi (1379 kPa) on the sides of the socket. The depth of the socket in Class 1c rock or better below the bottom of the pipe shall not be less than 3 feet (914.4 mm) or the outside diameter of the pipe.
1812.7.3.1 Increased allowable bond stress. | Load tests, with instrumentation in the rock socket to demonstrate the transfer of force to the rock, shall be performed to justify the use of bond stresses above 200 psi (1379 kPa). A minimum factor of safety of 2 shall be applied to the ultimate test load where an increase in allowable bond stress is sought. A report summarizing the methods and results of the load test shall be submitted to the commissioner for approval.
1812.7.3.2 Minimum number of load tests. | In each area of the foundation site within which the subsurface soil and rock conditions are “substantially similar” in character, as determined by the engineer, at least one load test shall be performed for the largest caisson pile diameter used on a site occupying a total area of 80,000 square feet (7432.2 m2) or less. For sites greater than 80,000 square feet (7432.2 m2), an additional load test shall be performed for every 80,000 square feet (7432.2 m2) of added footprint area.
1812.7.4 Structural core and steel reinforcing. | The gross cross-sectional area of the structural steel core or bundled center reinforcing shall not exceed 30 percent of the gross area of the caisson pile. For reinforcing placed at the perimeter of the caisson pile, the area of the reinforcing shall not exceed 8 percent of the area inside the casing. Minimum concrete cover shall be in accordance with Table 1810.2.13.
1812.7.4.1 Splicing of steel reinforcing. | Steel reinforcing shall be spliced in accordance with the requirements of ACI 318.
1812.7.4.2 Seismic reinforcement. | Where a structure is assigned to Seismic Design Category C or D in accordance with Section 1613, the reinforcement requirements of Section 1812.6.4.1 shall be met.
1812.7.5 Allowable stresses. | For allowable stresses, see Table 1810.8.
1812.7.6 Installation. | The rock socket and steel pipe shall be thoroughly cleaned of foreign materials before filling with concrete or grout. Steel cores shall be set within 6 inches (152.4 mm) above the base of the rock socket. Concrete shall not be placed through water except where a tremie or other method approved by the commissioner is used.
1812.7.6.1 Drilling with air. | Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.
1812.7.7 Rock socket inspection. | Caisson pile rock sockets shall be subject to special inspection in accordance with Section 1705.19. All caisson pile rock sockets shall be inspected to verify rock quality. Inspection may be accomplished by direct observation, by video methods or by a core boring performed prior to the drilling of the socket.
1812.8 Micropiles. | Micropiles shall conform to Sections 1812.8.1 through 1812.8.6.
1812.8.1 Materials. | Reinforcement shall consist of deformed reinforcing bars in accordance with ASTM A615 Grade 60 or 75 or ASTM A722 Grade 150. The steel pipe or casing shall have a minimum yield strength of 45,000 psi (310.3 MPa) and a minimum elongation of 15 percent as shown by mill certifications or two coupon test samples per 40,000 pounds (18 143.7 kg) of pipe or casing.
1812.8.2 Dimensions. | Micropiles shall have an outside diameter of between 5 and 14 inches (127 and 355.6 mm). The steel pipe shall have a minimum wall thickness of 3/16 inch (4.8 mm).
1812.8.3 Design. | Micropiles shall develop their load-carrying capacity by means of a bond zone in soil. The design of micropiles shall not consider end bearing. Micropiles shall be grouted and have either a steel pipe or steel reinforcement at every section along the length. It shall be permitted to transition compression loads from the steel pipe to the deformed reinforcing bars by extending the bars into the pipe section by at least their development length in tension, in accordance with ACI 318.
1812.8.3.1 Reinforcement. | For micropiles or portions thereof grouted inside a temporary or permanent casing or a hole drilled with grout, the steel pipe or steel reinforcement shall be designed to carry at least 40 percent of the design compression load. Micropiles or portions thereof grouted in an open hole in soil without temporary or permanent casing and without suitable means of verifying the hole diameter during grouting shall be designed to carry the entire compression load in the reinforcing steel. Where a steel pipe is used for reinforcement, the portion of the grout enclosed within the pipe is permitted to be included in the determination of the allowable stress in the grout.
1812.8.3.2 Seismic reinforcement. | For structures assigned to Seismic Design Category C, a permanent steel casing shall be provided from the top of the micropile down to the point of zero curvature. For structures assigned to Seismic Design Category D, the micropile shall be approved by the commissioner in accordance with Section 28-113.2 of the Administrative Code. The alternative system design, supporting documentation and test data shall be submitted to the commissioner for review and approval.
1812.8.4 Splices. | Splices in reinforcing bars shall be made in accordance with ACI 318. Splices in the steel pipe or casing shall be made by use of flush threaded joints, or by welded joints. Reductions for the structural capacity of the threaded joint casing at splice locations shall be accounted for in the design.
1812.8.5 Installation. | Micropile elements shall be permitted to be formed in holes advanced by rotary or percussive drilling methods, with or without casing. The elements shall be grouted with a fluid cement grout. The grout shall be pumped through a tremie pipe extending to the bottom of the element until grout of suitable quality returns at the top of the element. The following requirements apply to specific installation methods:
1812.8.5.1 Drilling with air. | Where existing structures may be affected by subsurface disturbances, air drilling shall be prohibited.
1812.8.6 Pressure grouted bond zone. | Micropiles shall be installed with a pressure grouted bond zone. The bond zone shall be formed entirely in soil of Class 4 or better and the grout shall be placed under pressure exceeding 1.5 times the existing total stress at the midpoint of the bond zone. The bond zone shall be formed by extending the casing to the bottom of the bond zone and withdrawing the casing while the grout is being pumped under pressure. The casing above the bond zone shall remain in place permanently. Reinforcing to the bond zone shall be placed in the casing to the depth of the bond zone prior to placing grout.
1813.1 General. | Composite piles shall conform to the requirements of Sections 1813.2 through 1813.5.
1813.2 Design. | Composite piles consisting of two or more approved types of deep foundations shall be designed to meet the conditions of installation.
1813.3 Limitation of load. | The maximum allowable load shall be limited by the capacity of the weakest section incorporated in the composite pile.
1813.4 Splices. | Splices between concrete and steel or wood sections shall be designed to prevent separation both before and after the concrete portion has set, and to ensure the align­ment and transmission of the total load on the composite pile. Splices shall be designed to resist uplift caused by upheaval during driving of adjacent deep foundations, and shall develop the full compressive strength and not less than 50 percent of the tension and bending strength of the weaker section.
1813.5 Seismic reinforcement. | Where a structure is assigned to Seismic Design Category C or D, in accordance with Section 1613 and where concrete and steel are used as part of the composite pile assembly, the concrete reinforcement shall comply with Sections 1812.1.2.3 and 1812.1.2.5 and the steel section shall comply with Section 1811.7.4 or Section 1812.6.4.1.
1814.1 General. | Helical piles may be used to support axial compression, or resist axial tension and lateral loads. All helical pile foundation systems shall be approved by the commissioner in accordance with Section 28-113.2 of the Administrative Code.
1814.2 Design. | Design of helical pile foundations shall be based on a geotechnical investigation in accordance with Sections 1803 and 1810.2 with the following additional conditions stated in Sections 1814.2.1 and 1814.2.2. Exception: For the repair of residential porches, stoops and slab on grades, helical test probes may be used to substitute for test borings, provided the helical pile has a torque to capacity ratio approved in accordance with Section 28-113.2.1 of the Administrative Code.
1814.2.1 Corrosion testing requirements. | Tests shall be performed in each soil layer for soil resistivity, soil pH, organic content and sulphate concentration. The device or system shall not be used in conditions that are indicative of a potential helical pile corrosion situation, as defined by soil resistivity less than 1,000 ohm-cm, pH less than 5.5, soils with high organic content, sulfate concentrations greater than 1,000 ppm, landfills, or mine waste.
1814.2.2 Protective treatment. | In addition to the protective treatment requirements of Section 1810.2.12, helical pile design shall consider the abrasive action inherent in the installation process when protective exterior treatment is specified as helical pile protection.
1814.3 Determination of allowable loads. | The allowable load of helical piles shall be in accordance with the applicable provisions of Section 1810.3. In addition, the requirements of this section shall apply.
1814.3.1 Allowable axial tension and compression. | The allowable axial tension and compression load shall not exceed 30 tons (267 kN).
1814.3.2 Allowable lateral load. | The allowable lateral load resisted by a helical pile shall not exceed 3 tons (29.4 kN).
1814.4 Load tests. | Load tests shall be in accordance with Sections 1810.4 and 1814.4.1 through 1814.4.4.
1814.4.1 Compression load test procedures. | The allowable axial compression load of a helical pile shall be verified by load tests in accordance with the requirements of Section 1810.4, except that ASTM D1143 may be conducted using the Quick Load Test Loading Procedure. Following each compression load test, the helical pile being tested shall be removed by unscrewing and inspected for any deformations to the helices to verify the structural integrity of the shaft and its connections.
1814.4.1.1 Required number of axial compression load tests. | The number of axial compression load tests shall satisfy Section 1810.4. Exception: Load tests on helical piles shall not be required, provided the following conditions are satisfied: 1. The helical pile has a torque to capacity ratio approved in accordance with Section 28-113.2.1 of the Administrative Code; 2. The torque correlation shall demonstrate a factor of safety (FS) of 2.5 on the allowable load; and 3. The maximum allowable axial compression load on the helical pile shall be 10 tons 98 kN).
1814.4.1.2 Acceptance criteria. | The allowable load on the helical pile shall be computed in accordance with Section 1810.4.1.5.
1814.4.2 Axial tension load test procedures. | The allowable axial tension load of a helical pile shall be verified by load testing in accordance with Section 1810.4 of this code; however, it shall be permitted to use the Quick Load Test Loading Procedure of ASTM D3689. Following the tension load test, the helical pile shall be removed by unscrewing, and shall be inspected for any deformations to the helices and to verify the structural integrity of the shaft and connections.
1814.4.2.1 Required number of axial tension load tests. | The number of axial tension load tests shall satisfy Section 1810.4, but with a minimum of one test.
1814.4.3 Lateral load test procedures. | The allowable lateral load of a helical pile shall be verified with load testing in accordance with Section 1810.4. Following the lateral load test, the helical pile shall be removed by unscrewing and inspected for any deformations to the helices to verify the structural integrity of the shaft and connections.
1814.4.3.1 Required number of lateral load tests. | The number of lateral load tests shall satisfy Section 1810.4, but shall not be fewer than one test.
1814.4.3.2 Acceptance criteria. | The allowable lateral load on the helical pile shall be computed in accordance with Sections 1810.4.3.1 and 1810.4.3.2.
1814.4.4 Additional load tests. | Additional axial compression, axial tension and lateral load tests shall be performed for questionable construction as required by Section 1810.4.1.1.1.
1814.5 Minimum installation torque. | Where load tests are required, the helical pile being tested shall be used to determine the minimum required site-specific torque for installation of production helical piles. For each helical pile, the special inspector shall measure and log the installation torque for each foot of depth and the final torque in the helice’s soil-bearing zone. The shaft advancement shall equal or exceed 85 percent of helix pitch per revolution at time of final torque measurement. Where load tests are not required, installation torque shall be in accordance with the exception defined under Section 1814.4.3.
1814.6 Internal stability of helical piles to resist overturning and translation. | Where bracket assemblies or structural eccentric forces cause bending, the resulting moment design of the helical pile shall ensure stability in accordance with Section 1810.2.5 and general engineering practice. Where side-mount brackets are used and a stability analysis indicates that there is insufficient internal stability to resist overturning and translation, helical piles shall be installed staggered or other means shall be designed to provide stability and prevent rotation of the foundation.
1814.7 Buckling. | When helical piles are embedded in soils of Classes 6 and 7, a buckling analysis shall be performed by a recognized method. The allowable axial compressive load shall be not more than two-thirds of the calculated load-causing buckling. The additional bending moments due to bracket assemblies, structural eccentric forces and coupling rigidity shall be appropriately included in the buckling analysis.
1814.8 Shaft flexural capacity. | Where a moment is transmitted to a single helical pile, a structural analysis shall be conducted to verify that the shaft is capable of resisting the moment with acceptable deflection.
1814.9 Side-mount bracket assembly test. | Where side-mount brackets are used, each bracket assembly shall be proof-tested to a minimum 110 percent of allowable load to demonstrate that the bracket assembly is capable of transferring the loads to the helical pile. The load shall be applied in six equal increments. The 110 percent test load shall be held for a minimum 30 minutes without bracket assembly distortion or deformation. Side-mount brackets for permanent applications shall be encased in concrete with a minimum embedment of 3 inches (76.2 mm). Concrete used to encase side-mount brackets shall meet the requirements of Sections 1903, 1904, 1905 and 1906.
1814.10 Minimum spacing of helical piles. | Minimum spacing between the center lines of helical piles shall be four times the largest helix plate diameter.
1814.11 Installation. | Equipment used for the installation of helical piles shall be as recommended by the helical pile manufacturer.
1814.12 Special inspection. | The installation of helical piles shall be subject to the special inspection requirements in Section 1705.7 and the following requirements:
1815.1 General. | Rock and soil anchors discussed in this document are cement grouted, prestressed tendons (bars or strands) that are installed in soil or rock. Permanent prestressed rock and soil anchors shall be designed and constructed in accordance with Sections 1815.2 through 1815.8 and PTI DC35.1.
1815.2 Additional geotechnical investigation and report requirements. | Where prestressed rock and soil anchors are used, the geotechnical investigation and report provisions of Section 1803.6 shall be expanded to include, but not be limited to, consideration of the following:
1815.3 Materials. | Materials used in prestressed rock and soil anchors shall conform to the following:
1815.4 Design. | Anchors shall be designed in accordance with Sections 1815.4.1 through 1815.4.5.
1815.4.1 Ultimate bond strength. | The average ultimate bond strength along the interface between anchor grout and the ground shall be determined by a generally accepted means of analysis and confirmed by load testing performed in accordance with Section 1815.5.
1815.4.2 Applicable strata. | The bonded zone of anchors shall not be formed in soils designated as Class 6 or Class 7.
1815.4.3 Bonded zone. | The bonded zone of anchors shall be fully located within materials of similar character and strength.
1815.4.4 Group capacity. | Group capacity of anchors shall be determined by a generally accepted means of analysis and shall:
1815.4.5 Structural aspects.
1815.5 Load testing. | Load testing shall be in accordance with PTI DC35.1. Extended creep tests shall be performed for any anchors designed with bonded zones located within materials designated as Class 1d, Class 4 or Class 5.
1815.6 Installation. | Installation procedures shall comply with the following:
1815.7 Grout sampling and testing. | Sampling and testing of grout shall be performed in accordance with Section 1812.1.1.2.
1815.8 Special inspection. | The installation and testing of prestressed rock and soil anchors shall be subject to special inspection in accordance with the requirements of Section 1705.19.
1816.1 General. | An assessment of the liquefaction potential shall be determined for each building site except Structural Occupancy/Risk Category I structures. The evaluation of liquefaction potential shall include the following considerations:
1816.2 Site-specific analyses. | In evaluating liquefaction potential, the analysis shall consider the following parameters: peak ground acceleration, earthquake magnitude, magnitude scaling factor, effective stress, hammer energy, cone penetration resistance (where applicable), and fines content. If a site response analysis is conducted, bedrock acceleration time histories and a shear wave velocity profile based on in-situ measurements may be utilized. These analyses may consider the results of laboratory cyclic shear tests. Where borings are drilled for the purpose of site-specific analyses and for the purpose of evaluating liquefaction potential, the drilling and sampling procedures and apparatus shall be in accordance with ASTM D6066.
1816.2.1 Peak ground acceleration. | Peak ground acceleration shall be determined based on either (i) a site-specific study taking into account soil amplification effects as specified in Section 11.4.8 of ASCE 7 or (ii) the Maximum Considered Geometric Mean peak ground acceleration adjusted for site class effects PGAM as provided in Table 1816.2.1 without adjustment for targeted risk.
1816.3 Foundation design analysis. | The foundation design analysis shall consider an assessment of the potential consequences of any liquefaction and soil strength loss, including an estimation of total and differential settlement, lateral movement or reduction in foundation soil-bearing capacity, and may incorporate the potential benefits of any proposed mitigation measures. Such measures may be given consideration in the design of the structure and may include, but are not limited to, ground improvement, pore pressure dissipation, selection of appropriate foundation type and depths, selection of appropriate structural systems to accommodate anticipated displacements, or any combination of these measures.
1816.4 Design considerations. | Where liquefaction is determined to be probable, the following considerations shall be addressed in the design:
1817.1 General. | Where the proposed work may disturb, displace or otherwise affect the lateral or vertical support of property or buildings, an engineer shall evaluate the need for and methods to maintain the stability and integrity of the building(s), utilities or soil adjacent to such activity.
1817.2 Minimum requirements for undeveloped adjacent property. | The minimum requirements for construction documents for support of adjacent property which does not contain a building, such as, but not limited to, empty lots, court yards, front yards, or rear yards, shall include the following information:
1817.3 Evaluation of adjacent buildings for suitable method of support. | At the time of foundation plan approval, an engineer shall submit an evaluation report to the department assessing the condition of the existing building and the subsurface conditions of the construction site and adjacent property. The report shall also identify acceptable method(s) of support, including underpinning or alternate methods of support, for the building. This evaluation shall be performed in accordance with the requirements of Section 1817.3.1 through 1817.3.6.
1817.3.1 Assessment of the building and the subsurface conditions: The engineer shall assess the condition of the existing building, and the subsurface conditions of the construction site and adjacent property, to an extent sufficient for determining acceptable method(s) of support, including underpinning or alternate methods of support. | As necessary, the assessment shall be based on visual observations, calculations, review of the geotechnical report prepared for the project in accordance with Section 1803.6 and review of other available documentation. The investigation shall include, as necessary, but need not be limited to, the following items:
1817.3.2 Additional requirements for buildings with rubble foundation elements. | For buildings with rubble foundation elements, an assessment of the condition of the rubble element shall be performed. If the rubble foundation elements are in poor condition, recommendations for addressing the poor conditions shall be provided.
1817.3.3 Additional requirements for unreinforced masonry buildings. | Where the building being supported is of unreinforced masonry construction, the lateral stability of the masonry walls and their ability to resist the loads imposed shall be verified. Exception: If it is not possible to verify the lateral stability of the masonry walls, lateral support shall be provided at the floor levels of the adjacent building prior to installation of the underpinning or alternate method of support. Such lateral support shall be shown on the construction documents.
1817.3.4 Additional requirements for use of rock support. | Where in situ Class 1a, 1b, or 1c rock is proposed for use in place of constructed methods of support, a subsurface investigation shall be conducted to assess the properties of the rock. Site-specific data shall be obtained to determine the predominant strike and dip of the joints, foliation, and/or other discontinuities in the rock. Recommendations for any rock stabilization necessary for the proposed work shall be provided.
1817.3.5 Evaluation report. | The evaluation report shall include the following items:
1817.3.6 Responsibility for the report. | If more than one engineer participates in performing the required assessments of the building and subsurface conditions, and the author of the evaluation report is relying on the work of these additional engineer(s) in preparing the evaluation report, the findings of the additional engineer(s) shall be included as signed and sealed appendices to the evaluation report.
1817.4 Suitable Methods of Support. | Where a method of support for an existing building is required, such underpinning or alternate method of support shall be designed as a permanent structural element specific to the building using the methods described in Sections 1817.4.1 through 1817.4.3. The underpinning or alternate method of support shall be installed in accordance with provisions of this chapter and Chapter 33 and shall be inspected in accordance with the provisions of Chapter 17.
1817.4.1 Underpinning. | If the foundation loads are to be transferred to a lower bearing level, underpinning consisting of concrete piers, drilled piles, jacked piles, bracket piles, or similar engineered systems to transfer the existing building loads below the bottom of the proposed excavation shall be installed.
1817.4.2 Alternate methods of support. | In lieu of underpinning, an excavation support system and/or lateral bracing designed to restrict the movements of the adjacent buildings within the established threshold levels may be installed. Such excavation support systems may consist of secant piles, slurry walls, tangent pile walls, jet grouting, pressed-in continuous sheeting, or similar engineered system.
1817.4.3 Use of rock support. | Existing structures founded at a level above the level of adjacent new construction may be supported on Class 1a, 1b, and 1c rock in lieu of underpinning, provided the requirements of Section 1817.3.4 are satisfied.
1817.5 Design requirements. | The underpinning or alternate method of support for adjacent buildings shall be designed by an engineer and plans filed with the department for approval prior to the commencement of the work.
1817.5.1 New construction. | Materials and design shall be in accordance with the requirements of this code for new construction.
1817.5.2 Incorporation of the evaluation report. | The design shall incorporate the findings of the evaluation report and any additional evaluation and investigation deemed necessary by the engineer performing the design. If the evaluation report did not conclusively demonstrate the suitability of an underpinning or alternate method of support, such method of support shall not be used.
1817.5.3 Deviations from the evaluation report. | The engineer designing the method of support may be an engineer other than the engineer who submitted the evaluation report. If the engineer designing the method of support does not accept the evaluation report or finds it insufficient, a new evaluation report shall be submitted to the department. Similarly, if a method of support other than one(s) determined to be suitable in the evaluation report is proposed for use, an additional evaluation report shall be submitted to the department justifying the suitability of the method of support now proposed. The revised report may be submitted along with the construction documents for the design of the method of support. Alternatively, minor exceptions to the report may be incorporated into the design documents if explicitly indicated on the design documents along with the engineer’s reason for override.
1817.5.4 Design loads and load combinations. | Underpinning, alternate methods of support and any associated lateral support system, shall be designed for the loads and load combinations listed in Sections 1817.5.4.1 and 1817.5.4.2.
1817.5.4.1 Loads from the existing building. | A computation shall be performed to establish the vertical and lateral loads on the elements of the method of support from the existing building. Loads and load combinations shall be computed in accordance with the requirements of Chapter 16 or where permitted for loads of prior codes for prior code buildings.
1817.5.4.1.1 Unconfirmed load path. | Where the evaluation of Section 1817.3 is unable to visually confirm the load path from the existing building, pit-pier underpinning where all horizontal loads are transferred directly to a raker or tension anchor bracing system that braces every pit-pier is permissible. Exception: Raker bracing or tension anchors need not be installed where it is demonstrated by calculation, according to data provided by the investigation per Section 1817.3.1, that the underpinning system, analyzed independently as a retaining wall that supports the soil and water behind it, calculated both (i) with and (ii) without accounting for vertical loads from the structure above, has satisfactory bearing pressures and is stable with a 1.5 factor of safety against overturning and sliding. This exception shall not be utilized in unreinforced masonry buildings in which access to verify the lateral stability of masonry walls is not possible as per Section 1817.3.3.
1817.5.4.2 Soil and water pressures. | The design shall include at rest soil pressures, water pressures, and any surcharge pressures that arise from the adjacent portions of the building being underpinned or supported by an alternate method of support.
1817.5.5 Anticipated deflection. | A calculation shall be performed for the anticipated deflection of the method of support system and its effect on the supported building.
1817.5.6 Factor of safety. | Methods of support shall be designed to provide a minimum factor of safety of 1.5 for sliding and overturning for all loads and all anticipated interim conditions.
1817.5.7 Sequence. | The design of the method of support shall account for the means and methods of installation, sequence of operations, and all the load transfers and associated support conditions for all phases of the work.
1817.6 Minimum requirements for construction documents. | Construction documents for methods of support of adjacent buildings shall include the following information:
1817.7 Additional requirements for pit-pier underpinning. | When the method of support selected is pit-pier underpinning, the design shall meet the following minimum criteria:
1817.7.1 Pit-pier excavation. | Pit-pier excavation shall be subject to the requirements of Section 1817.7.1.1 through 1817.7.1.8.
1817.7.1.1 Excavation Methods. | Pit-pier excavations shall be performed using hand held tools. Excavation using backhoes or other mechanical means to excavate the pit-piers is prohibited.
1817.7.1.2 Clear distance between open pits. | Clear distance between open pits shall be determined by the evaluation report and shall not be less than 12 feet (3657.6 mm).
1817.7.1.3 Pit Excavation below the lowest installed lagging board. | Lagging boards shall be installed as the excavation proceeds to limit soil loss. In no case shall excavation proceed more than 2 feet (609.6 mm) below the lowest installed lagging board. At completion of pit excavation, the pit shall be fully lagged.
1817.7.1.4 Backpacking. | Backpacking of any voids shall be performed at each excavation lift.
1817.7.1.5 Excavation below the water table. | Pit excavation shall not proceed below the water table. If the depth of the underpinning requires excavation below the existing water table, a dewatering system shall be installed prior to the start of the excavation. The dewatering system shall be tested via test pit or piezometer to confirm that the water table has been sufficiently drawn down prior to the start of the pit underpinning work.
1817.7.1.6 Variable depth pits. | Where construction requires adjacent pits to be excavated to differing depths, the deeper pit-pier shall be constructed first.
1817.7.1.7 Multi-tier pit-pier underpinning. | Where multi-tier pit-pier underpinning is utilized, the upper piers shall be braced prior to the excavation of the lower pier and the installation of upper and lower piers staggered, unless the design per Section 1817.5 and drawings include explicit methods that will ensure that the installation of lower tiers shall not displace the tiers above.
1817.7.1.8 Use of tension anchors. | When tension anchors are utilized, the effects of vertical and horizontal force components shall be accounted for including any potential additional displacements.
1817.8 Additional requirements for deep foundation elements used in underpinning. | Where the method of support includes deep foundation systems such as pile supported underpinning or tie anchors, the requirements of Chapter 18 and Sections 1817.8.1 through 1817.8.5 shall be met.
1817.8.1 Pile design. | Piles used for underpinning shall be designed in accordance with Sections 1810.3 and 1810.4.
1817.8.2 Load testing of underpinning piles. | Piles used for underpinning are subject to the load testing criteria of Section 1810.4.
1817.8.3 Eccentric pile loads. | Piles used for underpinning shall be designed to sustain all moments that are generated due to any eccentricities of the load on the pile.
1817.8.4 Spanning between piles. | Unless new grade beams are provided, calculations shall be performed to confirm that the existing foundation can support the required loads spanning between the pile supports.
1817.8.5 Piles used as excavation support elements. | If underpinning piles are to be used as excavation support elements, a calculation of the anticipated pile deflection shall be performed and its impacts on the supported building shall be assessed by the engineer.
1817.9 Monitoring. | When excavation, foundation construction, underpinning, or an alternate method of support is required, adjacent structures and properties shall be monitored in accordance with a plan prepared by the engineer. The engineer shall develop the scope of the monitoring program, including location and type of instruments, frequency and duration of readings, frequency of reporting, maximum allowable time to report readings (timely reporting), reporting requirements, and permissible movement and vibration criteria. This scope shall take into account the buildings or property to be monitored and the conditions thereof. The monitoring program shall include necessary actions to address exceedances. These actions shall include notification of the commissioner. Monitoring of historic and landmarked structures shall be subject to special requirements as determined by the department. Where the building to be monitored is subject to underpinning or alternate methods of support, the monitoring plan shall be determined by the engineer designing such work.
1817.10 Special Inspection. | Special inspection shall be conducted in accordance with Chapter 17.
1818.1 General. | The provisions of this section specify where geotechnical peer review is required, how and by whom it is to be performed.
1818.2 Where required. | A geotechnical peer review shall be performed and a report shall be required in the following instances:
1818.3 Geotechnical peer review qualifications: The geotechnical peer review shall be performed by a qualified independent geotechnical engineer who has been retained by or on behalf of the owner. | A geotechnical peer reviewer shall meet the requirements of the rules of the department.
1818.3.1 Independence. | In order to satisfy the requirement that the peer reviewer be independent, the department requires that the peer reviewer must not engage in any activities that may conflict with their objective judgment and integrity, including but not limited to having a financial and/or other interest in the design, construction, installation, manufacture or maintenance of structures or components that they are reviewing.
1818.4 Extent of Geotechnical Peer Review. | The extent of the geotechnical peer review shall be performed in accordance with Section 1818.4.1.
1818.4.1 Scope. | The geotechnical peer reviewer shall review the plans and specifications submitted with the permit application for general compliance with the foundation design provisions of this code. The reviewing engineer shall perform the following tasks at a minimum:
1818.5 Geotechnical peer review report. | The geotechnical peer review report shall comply with Section 1818.5.1 through 1818.5.3.
1818.5.1 General. | The reviewing engineer shall submit a report to the department stating whether or not the geotechnical design shown on the plans, reports and specifications generally conforms to the requirements of this code.
1818.5.2 Contents. | The report shall demonstrate, at a minimum, compliance with Items 1 through 8 of Section 1818.4.1. In addition, the report shall also include the following:
1818.5.3 Phased submission. | If an application is submitted for a permit for the construction of foundations or any other part of a building before the construction documents for the whole building have been submitted, then the geotechnical peer review and report shall be phased. The geotechnical peer reviewer shall be provided with sufficient information on which to make a geotechnical peer review of the phased submission. In addition to the requirements of this section, phased submission of the report shall include any changes made to the initial geotechnical peer review evaluation. The geotechnical peer review report need not be submitted concurrently with the structural peer review report.
1818.6 Responsibility. | Responsibility shall be as provided for in Section 1818.6.1 through 1818.6.4.
1818.6.1 Engineer of record. | The engineer of record for the foundation design shall retain sole responsibility for the geotechnical design. The activities and reports of the geotechnical peer reviewer shall not relieve the engineer of record for the foundation design of this responsibility.
1818.6.2 Geotechnical peer reviewer. | The geotechnical peer reviewer’s report states his or her opinion regarding the design by the engineer of record for the foundation design. The standard of care to which the geotechnical peer reviewer shall be held in the performance of the geotechnical peer review and report is that level of skill and care are consistent with geotechnical peer review services performed by professional engineers licensed in the State of New York for similar type projects. The geotechnical peer reviewer shall not be responsible for the accuracy of the subsurface investigation data or the conclusions of the structural peer review reports.
1818.6.3 Revisions of design. | The engineer of record for the foundation design shall identify that a new review is required based upon changes to the design documents relevant to the scope of the peer review. The geotechnical peer reviewer shall review the items that have been affected and shall revise the geotechnical peer review report.
1818.6.4 Disputes. | When a dispute arises between the applicant of record and the peer reviewer regarding compliance with Section 1818 that cannot be resolved by these parties, such dispute shall be reported to the department in the form of a letter from the applicant of record. The department may make a final decision or may accept a change of the peer reviewer.
1818.7 Change to peer reviewer. | The peer reviewer cannot be changed without the express consent of the department. The current peer reviewer must submit both a written letter to the borough commissioner detailing the reason for the withdrawal request and a report of the geotechnical peer review findings to date. If a change of peer reviewer is approved, a revised PW1 must be submitted indicating the replacement peer reviewer.
|  | 1803.2 Investigations required. | Geotechnical investigations shall be conducted in accordance with Sections 1803.3 through 1803.5. Exception: The building official shall be permitted to waive the requirement for a geotechnical investigation where satisfactory data from adjacent areas is available that demonstrates an investigation is not necessary for any of the conditions in Sections 1803.5.1 through 1803.5.6 and Sections 1803.5.10 and 1803.5.11.
|  | 1803.3 Basis of investigation. | Soil classification shall be based on observation and any necessary tests of the materials disclosed by borings, test pits or other subsurface exploration made in appropriate locations. Additional studies shall be made as necessary to evaluate slope stability, soil strength, position and adequacy of load-bearing soils, the effect of moisture variation on soil-bearing capacity, compressibility, liquefaction and expansiveness.
|  | 1803.3.1 Scope of investigation. | The scope of the geotechnical investigation including the number and types of borings or soundings, the equipment used to drill or sample, the in-situ testing equipment and the laboratory testing program shall be determined by a registered design professional.
|  | 1803.4 Qualified representative. | The investigation procedure and apparatus shall be in accordance with generally accepted engineering practice. The registered design professional shall have a fully qualified representative on site during all boring or sampling operations.
|  | 1803.5 Investigated conditions. | Geotechnical investigations shall be conducted as indicated in Sections 1803.5.1 through 1803.5.12.
|  | 1803.5.1 Classification. | Soil materials shall be classified in accordance with ASTM D2487.
|  | 1803.5.2 Questionable soil. | Where the classification, strength or compressibility of the soil is in doubt or where a load-bearing value superior to that specified in this code is claimed, the building official shall be permitted to require that a geotechnical investigation be conducted.
|  | 1803.5.3 Expansive soil. | In areas likely to have expansive soil, the building official shall require soil tests to determine where such soils do exist.
|  | 1803.5.4 Ground-water table. | A subsurface soil investigation shall be performed to determine whether the existing ground-water table is above or within 5 feet (1524 mm) below the elevation of the lowest floor level where such floor is located below the finished ground level adjacent to the foundation. Exception: A subsurface soil investigation to determine the location of the ground-water table shall not be required where waterproofing is provided in accordance with Section 1805.
|  | 1803.5.5 Deep foundations. | Where deep foundations will be used, a geotechnical investigation shall be conducted and shall include all of the following, unless sufficient data on which to base the design and installation is otherwise available:
|  | 1803.5.6 Rock strata. | Where subsurface explorations at the project site indicate variations in the structure of rock on which foundations are to be constructed, a sufficient number of borings shall be drilled to sufficient depths to assess the competency of the rock and its load-bearing capacity.
|  | 1803.5.7 Excavation near foundations. | Where excavation will reduce support from any foundation, a registered design professional shall prepare an assessment of the structure as determined from examination of the structure, available design documents, available subsurface data, and, if necessary, excavation of test pits. The registered design professional shall determine the requirements for support and protection of any existing foundation and prepare site-specific plans, details and sequence of work for submission. Such support shall be provided by underpinning, bracing, excavation retention systems, or by other means acceptable to the building official.
|  | 1803.5.8 Compacted fill material. | Where shallow foundations will bear on compacted fill material more than 12 inches (305 mm) in depth, a geotechnical investigation shall be conducted and shall include all of the following:
|  | 1803.5.9 Controlled low-strength material (CLSM). | Where shallow foundations will bear on controlled low-strength material (CLSM), a geotechnical investigation shall be conducted and shall include all of the following:
|  | 1803.5.10 Alternate setback and clearance. | Where setbacks or clearances other than those required in Section 1808.7 are desired, the building official shall be permitted to require a geotechnical investigation by a registered design professional to demonstrate that the intent of Section 1808.7 would be satisfied. Such an investigation shall include consideration of material, height of slope, slope gradient, load intensity and erosion characteristics of slope material.
|  | 1803.5.11 Seismic Design Categories C through F. | For structures assigned to Seismic Design Category C, D, E or F, a geotechnical investigation shall be conducted, and shall include an evaluation of all of the following potential geologic and seismic hazards:
|  | 1803.5.12 Seismic Design Categories D through F. | For structures assigned to Seismic Design Category D, E or F, the geotechnical investigation required by Section 1803.5.11 shall include all of the following as applicable:
|  | 1803.6 Reporting. | Where geotechnical investigations are required, a written report of the investigations shall be submitted to the building official by the permit applicant at the time of permit application. This geotechnical report shall include, but need not be limited to, the following information:
|  | 1804.1 Excavation near foundations. | Excavation for any purpose shall not reduce vertical or lateral support for any foundation or adjacent foundation without first underpinning or protecting the foundation against detrimental lateral or vertical movement, or both, in accordance with Section 1803.5.7.
|  | 1804.2 Underpinning. | Where underpinning is chosen to provide the protection or support of adjacent structures, the underpinning system shall be designed and installed in accordance with provisions of this chapter and Chapter 33.
|  | 1804.2.1 Underpinning sequencing. | Underpinning shall be installed in a sequential manner that protects the neighboring structure and the working construction site. The sequence of installation shall be identified in the approved construction documents.
|  | 1804.3 Placement of backfill. | The excavation outside the foundation shall be backfilled with soil that is free of organic material, construction debris, cobbles and boulders or with a controlled low-strength material (CLSM). The backfill shall be placed in lifts and compacted in a manner that does not damage the foundation or the waterproofing or dampproofing material. Exception: CLSM need not be compacted.
|  | 1804.5 Grading and fill in flood hazard areas. | In flood hazard areas established in Section 1612.3, grading, fill, or both, shall not be approved:
|  | 1805.1 General. | Walls or portions thereof that retain earth and enclose interior spaces and floors below grade shall be waterproofed and dampproofed in accordance with this section, with the exception of those spaces containing groups other than residential and institutional where such omission is not detrimental to the building or occupancy.
|  | 1805.1.1 Story above grade plane. | Where a basement is considered a story above grade plane and the finished ground level adjacent to the basement wall is below the basement floor elevation for 25 percent or more of the perimeter, the floor and walls shall be dampproofed in accordance with Section 1805.2 and a foundation drain shall be installed in accordance with Section 1805.4.2. The foundation drain shall be installed around the portion of the perimeter where the basement floor is below ground level. The provisions of Sections 1803.5.4, 1805.3 and 1805.4.1 shall not apply in this case.
|  | 1805.1.2 Under-floor space. | The finished ground level of an under-floor space such as a crawl space shall not be located below the bottom of the footings. Where there is evidence that the ground-water table rises to within 6 inches (152 mm) of the ground level at the outside building perimeter, or that the surface water does not readily drain from the building site, the ground level of the under-floor space shall be as high as the outside finished ground level, unless an approved drainage system is provided. The provisions of Sections 1803.5.4, 1805.2, 1805.3 and 1805.4 shall not apply in this case.
|  | 1805.1.2.1 Flood hazard areas. | For buildings and structures in flood hazard areas as established in Section 1612.3, the finished ground level of an under-floor space such as a crawl space shall be equal to or higher than the outside finished ground level on one side or more. Exception: Under-floor spaces of Group R-3 buildings that meet the requirements of FEMA TB 11.
|  | 1805.1.3 Ground-water control. | Where the ground-water table is lowered and maintained at an elevation not less than 6 inches (152 mm) below the bottom of the lowest floor, the floor and walls shall be dampproofed in accordance with Section 1805.2. The design of the system to lower the ground-water table shall be based on accepted principles of engineering that shall consider, but not necessarily be limited to, permeability of the soil, rate at which water enters the drainage system, rated capacity of pumps, head against which pumps are to operate and the rated capacity of the disposal area of the system.
|  | 1805.2 Dampproofing. | Where hydrostatic pressure will not occur as determined by Section 1803.5.4, floors and walls for other than wood foundation systems shall be dampproofed in accordance with this section. Wood foundation systems shall be constructed in accordance with AWC PWF.
|  | 1805.2.2.1 Surface preparation of walls. | Prior to application of dampproofing materials on concrete walls, holes and recesses resulting from the removal of form ties shall be sealed with a bituminous material or other approved methods or materials. Unit masonry walls shall be parged on the exterior surface below ground level with not less than 3/8 inch (9.5 mm) of Portland cement mortar. The parging shall be coved at the footing. Exception: Parging of unit masonry walls is not required where a material is approved for direct application to the masonry.
|  | 1805.3 Waterproofing. | Where the ground-water investigation required by Section 1803.5.4 indicates that a hydrostatic pressure condition exists, and the design does not include a ground-water control system as described in Section 1805.1.3, walls and floors shall be waterproofed in accordance with this section.
|  | 1805.3.2.1 Surface preparation of walls. | Prior to the application of waterproofing materials on concrete or masonry walls, the walls shall be prepared in accordance with Section 1805.2.2.1.
|  | 1805.4.1 Floor base course. | Floors of basements, except as provided for in Section 1805.1.1, shall be placed over a floor base course not less than 4 inches (102 mm) in thickness that consists of gravel or crushed stone containing not more than 10 percent of material that passes through a No. 4 (4.75 mm) sieve. Exception: Where a site is located in well-drained gravel or sand/gravel mixture soils, a floor base course is not required.
|  | 1806.1 Load combinations. | The presumptive load-bearing values provided in Table 1806.2 shall be used with the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2. The values of vertical foundation pressure and lateral bearing pressure given in Table 1806.2 shall be permitted to be increased by one-third where used with the alternative allowable stress design load combinations of Section 1605.2 that include wind or earthquake loads.
|  | 1806.2 Presumptive load-bearing values. | The load-bearing values used in design for supporting soils near the surface shall not exceed the values specified in Table 1806.2 unless data to substantiate the use of higher values are submitted and approved. Where the building official has reason to doubt the classification, strength or compressibility of the soil, the requirements of Section 1803.5.2 shall be satisfied. Presumptive load-bearing values shall apply to materials with similar physical characteristics and dispositions. Mud, organic silt, organic clays, peat or unprepared fill shall not be assumed to have a presumptive load-bearing capacity unless data to substantiate the use of such a value are submitted. Exception: A presumptive load-bearing capacity shall be permitted to be used where the building official deems the load-bearing capacity of mud, organic silt or unprepared fill is adequate for the support of lightweight or temporary structures
|  | 1806.3 Lateral load resistance. | Where the presumptive values of Table 1806.2 are used to determine resistance to lateral loads, the calculations shall be in accordance with Sections 1806.3.1 through 1806.3.4.
|  | 1806.3.1 Combined resistance. | The total resistance to lateral loads shall be permitted to be determined by combining the values derived from the lateral bearing pressure and the lateral sliding resistance specified in Table 1806.2.
|  | 1806.3.2 Lateral sliding resistance limit. | For clay, sandy clay, silty clay, clayey silt, silt and sandy silt, the lateral sliding resistance shall not exceed one-half the dead load.
|  | 1806.3.3 Increase for depth. | The lateral bearing pressures specified in Table 1806.2 shall be permitted to be increased by the tabular value for each additional foot (305 mm) of depth to a value that is not greater than 15 times the tabular value.
|  | 1806.3.4 Increase for poles. | Isolated poles for uses such as flagpoles or signs and poles used to support buildings that are not adversely affected by a 1/2-inch (12.7 mm) motion at the ground surface due to short-term lateral loads shall be permitted to be designed using lateral bearing pressures equal to two times the tabular values.
|  | 1807.1 Foundation walls. | Foundation walls shall be designed and constructed in accordance with Sections 1807.1.1 through 1807.1.6. Foundation walls shall be supported by foundations designed in accordance with Section 1808.
|  | 1807.1.1 Design lateral soil loads. | Foundation walls shall be designed for the lateral soil loads set forth in Section 1610.
|  | 1807.1.2 Unbalanced backfill height. | Unbalanced backfill height is the difference in height between the exterior finish ground level and the lower of the top of the concrete footing that supports the foundation wall or the interior finish ground level. Where an interior concrete slab on grade is provided and is in contact with the interior surface of the foundation wall, the unbalanced backfill height shall be permitted to be measured from the exterior finish ground level to the top of the interior concrete slab.
|  | 1807.1.3 Rubble stone foundation walls. | Foundation walls of rough or random rubble stone shall be not less than 16 inches (406 mm) thick. Rubble stone shall not be used for foundation walls of structures assigned to Seismic Design Category C, D, E or F.
|  | 1807.1.4 Permanent wood foundation systems. | Permanent wood foundation systems shall be designed and installed in accordance with AWC PWF. Lumber and plywood shall be preservative treated in accordance with AWPA U1 (Commodity Specification A, Special Requirement 4.2) and shall be identified in accordance with Section 2303.1.9.1.
|  | 1807.1.5 Concrete and masonry foundation walls. | Concrete and masonry foundation walls shall be designed in accordance with Chapter 19 or 21, as applicable. Exception: Concrete and masonry foundation walls shall be permitted to be designed and constructed in accordance with Section 1807.1.6.
|  | 1807.1.6 Prescriptive design of concrete and masonry foundation walls. | Concrete and masonry foundation walls that are laterally supported at the top and bottom shall be permitted to be designed and constructed in accordance with this section.
|  | 1807.1.6.1 Foundation wall thickness. | The thickness of prescriptively designed foundation walls shall be not less than the thickness of the wall supported, except that foundation walls of not less than 8-inch (203 mm) nominal width shall be permitted to support brick-veneered frame walls and 10-inch-wide (254 mm) cavity walls provided that the requirements of Section 1807.1.6.2 or 1807.1.6.3 are met.
|  | 1807.1.6.2 Concrete foundation walls. | Concrete foundation walls shall comply with the following:
|  | 1807.1.6.2.1 Seismic requirements. | Based on the seismic design category assigned to the structure in accordance with Section 1613, concrete foundation walls designed using Table 1807.1.6.2 shall be subject to the following limitations:
|  | 1807.1.6.3 Masonry foundation walls. | Masonry foundation walls shall comply with the following:
|  | 1807.1.6.3.1 Alternative foundation wall reinforcement. | In lieu of the reinforcement provisions for masonry foundation walls in Table 1807.1.6.3(2), 1807.1.6.3(3) or 1807.1.6.3(4), alternative reinforcing bar sizes and spacings having an equivalent cross-sectional area of reinforcement per linear foot (mm) of wall shall be permitted to be used, provided that the spacing of reinforcement does not exceed 72 inches (1829 mm) and reinforcing bar sizes do not exceed No. 11.
|  | 1807.1.6.3.2 Seismic requirements. | Based on the seismic design category assigned to the structure in accordance with Section 1613, masonry foundation walls designed using Tables 1807.1.6.3(1) through 1807.1.6.3(4) shall be subject to the following limitations:
|  | 1807.2 Retaining walls. | Retaining walls shall be designed in accordance with Sections 1807.2.1 through 1807.2.4.
|  | 1807.2.1 General. | Retaining walls shall be designed to ensure stability against overturning, sliding, excessive foundation pressure and water uplift.
|  | 1807.2.2 Design lateral soil loads. | Retaining walls shall be designed for the lateral soil loads set forth in Section 1610. For structures assigned to Seismic Design Category D, E, or F, the design of retaining walls supporting more than 6 feet (1829 mm) of backfill height shall incorporate the additional seismic lateral earth pressure in accordance with the geotechnical investigation where required in Section 1803.2.
|  | 1807.2.3 Safety factor. | Retaining walls shall be designed to resist the lateral action of soil to produce sliding and overturning with a minimum safety factor of 1.5 in each case. The load combinations of Section 1605 shall not apply to this requirement. Instead, design shall be based on 0.7 times nominal earthquake loads, 1.0 times other nominal loads, and investigation with one or more of the variable loads set to zero. The safety factor against lateral sliding shall be taken as the available soil resistance at the base of the retaining wall foundation divided by the net lateral force applied to the retaining wall. Exception: Where earthquake loads are included, the minimum safety factor for retaining wall sliding and overturning shall be 1.1.
|  | 1807.2.4 Segmental retaining walls. | Dry-cast concrete units used in the construction of segmental retaining walls shall comply with ASTM C1372.
|  | 1807.3 Embedded posts and poles. | Designs to resist both axial and lateral loads employing posts or poles as columns embedded in earth or in concrete footings in earth shall be in accordance with Sections 1807.3.1 through 1807.3.3.
|  | 1807.3.1 Limitations. | The design procedures outlined in this section are subject to the following limitations:
|  | 1807.3.2 Design criteria. | The depth to resist lateral loads shall be determined using the design criteria established in Sections 1807.3.2.1 through 1807.3.2.3, or by other methods approved by the building official.
|  | 1807.3.2.1 Nonconstrained. | The following formula shall be used in determining the depth of embedment required to resist lateral loads where lateral constraint is not provided at the ground surface, such as by a rigid floor or rigid ground surface pavement, and where lateral constraint is not provided above the ground surface, such as by a structural diaphragm.
|  | 1807.3.2.2 Constrained. | The following formula shall be used to determine the depth of embedment required to resist lateral loads where lateral constraint is provided at the ground surface, such as by a rigid floor or pavement.
|  | 1807.3.2.3 Vertical load. | The resistance to vertical loads shall be determined using the vertical foundation pressure set forth in Table 1806.2.
|  | 1807.3.3 Backfill. | The backfill in the annular space around columns not embedded in poured footings shall be by one of the following methods:
|  | 1808.1 General. | Foundations shall be designed and constructed in accordance with Sections 1808.2 through 1808.9. Shallow foundations shall satisfy the requirements of Section 1809. Deep foundations shall satisfy the requirements of Section 1810.
|  | 1808.2 Design for capacity and settlement. | Foundations shall be so designed that the allowable bearing capacity of the soil is not exceeded, and that differential settlement is minimized. Foundations in areas with expansive soils shall be designed in accordance with the provisions of Section 1808.6.
|  | 1808.3 Design loads. | Foundations shall be designed for the most unfavorable effects due to the combinations of loads specified in Section 2.3 or 2.4 of ASCE 7 or the alternative allowable stress design load combinations of Section 1605.2. The dead load is permitted to include the weight of foundations and overlying fill. Reduced live loads, as specified in Sections 1607.12 and 1607.14, shall be permitted to be used in the design of foundations.
|  | 1808.3.1 Seismic overturning. | Where foundations are proportioned using the load combinations of Section 2.3 or 2.4 of ASCE 7 and the computation of seismic overturning effects is by equivalent lateral force analysis or modal analysis, the proportioning shall be in accordance with Section 12.13.4 of ASCE 7.
|  | 1808.3.2 Surcharge. | Fill or other surcharge loads shall not be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or the surcharge. Existing footings or foundations that will be affected by any excavation shall be underpinned or otherwise protected against settlement and shall be protected against detrimental lateral or vertical movement or both. Exception: Minor grading for landscaping purposes shall be permitted where done with walk-behind equipment, where the grade is not increased more than 1 foot (305 mm) from original design grade or where approved by the building official.
|  | 1808.4 Vibratory loads. | Where machinery operations or other vibrations are transmitted through the foundation, consideration shall be given in the foundation design to prevent detrimental disturbances of the soil.
|  | 1808.5 Shifting or moving soils. | Where it is known that the shallow subsoils are of a shifting or moving character, foundations shall be carried to a sufficient depth to ensure stability.
|  | 1808.6 Design for expansive soils. | Foundations for buildings and structures founded on expansive soils shall be designed in accordance with Section 1808.6.1 or 1808.6.2. Exceptions: Foundation design need not comply with Section 1808.6.1 or 1808.6.2 where one of the following conditions is satisfied: 1. The soil is removed in accordance with Section 1808.6.3. 2. The building official approves stabilization of the soil in accordance with Section 1808.6.4.
|  | 1808.6.1 Foundations. | Foundations placed on or within the active zone of expansive soils shall be designed to resist differential volume changes and to prevent structural damage to the supported structure. Deflection and racking of the supported structure shall be limited to that which will not interfere with the usability and serviceability of the structure.
|  | 1808.6.2 Slab-on-ground foundations. | Moments, shears and deflections for use in designing slab-on-ground, mat or raft foundations on expansive soils shall be determined in accordance with WRI/CRSI Design of Slab-on-Ground Foundations or PTI DC 10.5. Using the moments, shears and deflections determined above, nonprestressed slabs-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with WRI/CRSI Design of Slab-on-Ground Foundations and post-tensioned slab-on-ground, mat or raft foundations on expansive soils shall be designed in accordance with PTI DC 10.5. It shall be permitted to analyze and design such slabs by other methods that account for soil-structure interaction, the deformed shape of the soil support, the plate or stiffened plate action of the slab as well as both center lift and edge lift conditions. Such alternative methods shall be rational and the basis for all aspects and parameters of the method shall be available for peer review.
|  | 1808.6.3 Removal of expansive soil. | Where expansive soil is removed in lieu of designing foundations in accordance with Section 1808.6.1 or 1808.6.2, the soil shall be removed to a depth sufficient to ensure a constant moisture content in the remaining soil. Fill material shall not contain expansive soils and shall comply with Section 1804.5 or 1804.6. Exception: Expansive soil need not be removed to the depth of constant moisture, provided that the confining pressure in the expansive soil created by the fill and supported structure exceeds the swell pressure.
|  | 1808.6.4 Stabilization. | Where the active zone of expansive soils is stabilized in lieu of designing foundations in accordance with Section 1808.6.1 or 1808.6.2, the soil shall be stabilized by chemical, dewatering, presaturation or equivalent techniques.
|  | 1808.7 Foundations on or adjacent to slopes. | The placement of buildings and structures on or adjacent to slopes steeper than one unit vertical in three units horizontal (33.3-percent slope) shall comply with Sections 1808.7.1 through 1808.7.5.
|  | 1808.7.1 Building clearance from ascending slopes. | In general, buildings below slopes shall be set a sufficient distance from the slope to provide protection from slope drainage, erosion and shallow failures. Except as provided in Section 1808.7.5 and Figure 1808.7.1, the following criteria will be assumed to provide this protection. Where the existing slope is steeper than one unit vertical in one unit horizontal (100-percent slope), the toe of the slope shall be assumed to be at the intersection of a horizontal plane drawn from the top of the foundation and a plane drawn tangent to the slope at an angle of 45 degrees (0.79 rad) to the horizontal. Where a retaining wall is constructed at the toe of the slope, the height of the slope shall be measured from the top of the wall to the top of the slope.
|  | 1808.7.2 Foundation setback from descending slope surface. | Foundations on or adjacent to slope surfaces shall be founded in firm material with an embedment and set back from the slope surface sufficient to provide vertical and lateral support for the foundation without detrimental settlement. Except as provided for in Section 1808.7.5 and Figure 1808.7.1, the following setback is deemed adequate to meet the criteria. Where the slope is steeper than 1 unit vertical in 1 unit horizontal (100-percent slope), the required setback shall be measured from an imaginary plane 45 degrees (0.79 rad) to the horizontal, projected upward from the toe of the slope.
|  | 1808.7.3 Pools. | The setback between pools regulated by this code and slopes shall be equal to one-half the building footing setback distance required by this section. That portion of the pool wall within a horizontal distance of 7 feet (2134 mm) from the top of the slope shall be capable of supporting the water in the pool without soil support.
|  | 1808.7.4 Foundation elevation. | On graded sites, the top of any exterior foundation shall extend above the elevation of the street gutter at point of discharge or the inlet of an approved drainage device not less than 12 inches (305 mm) plus 2 percent. Alternate elevations are permitted subject to the approval of the building official, provided that it can be demonstrated that required drainage to the point of discharge and away from the structure is provided at all locations on the site.
|  | 1808.7.5 Alternate setback and clearance. | Alternate setbacks and clearances are permitted, subject to the approval of the building official. The building official shall be permitted to require a geotechnical investigation as set forth in Section 1803.5.10.
|  | 1808.8 Concrete foundations. | The design, materials and construction of concrete foundations shall comply with Sections 1808.8.1 through 1808.8.6 and the provisions of Chapter 19. Exception: Where concrete footings supporting walls of light-frame construction are designed in accordance with Table 1809.7, a specific design in accordance with Chapter 19 is not required.
|  | 1808.8.1 Concrete or grout strength and mix proportioning. | Concrete or grout in foundations shall have a specified compressive strength (f ′c) not less than the largest applicable value indicated in Table 1808.8.1.
|  | 1808.8.2 Concrete cover. | The concrete cover provided for prestressed and nonprestressed reinforcement in foundations shall be not less than the largest applicable value specified in Table 1808.8.2. Longitudinal bars spaced less than 11/2 inches (38 mm) clear distance apart shall be considered to be bundled bars for which the concrete cover provided shall be not less than that required by Section 20.6.1.3.4 of ACI 318. Concrete cover shall be measured from the concrete surface to the outermost surface of the steel to which the cover requirement applies. Where concrete is placed in a temporary or permanent casing or a mandrel, the inside face of the casing or mandrel shall be considered to be the concrete surface.
|  | 1808.8.3 Placement of concrete. | Concrete shall be placed in such a manner as to ensure the exclusion of any foreign matter and to secure a full-size foundation. Concrete shall not be placed through water unless a tremie or other method approved by the building official is used. Where placed under or in the presence of water, the concrete shall be deposited by approved means to ensure minimum segregation of the mix and negligible turbulence of the water. Where depositing concrete from the top of a deep foundation element, the concrete shall be chuted directly into smooth-sided pipes or tubes or placed in a rapid and continuous operation through a funnel hopper centered at the top of the element.
|  | 1808.8.4 Protection of concrete. | Concrete foundations shall be protected from freezing during depositing and for a period of not less than 5 days thereafter. Water shall not be allowed to flow through the deposited concrete.
|  | 1808.8.5 Forming of concrete. | Concrete foundations are permitted to be cast against the earth where, in the opinion of the building official, soil conditions do not require formwork. Where formwork is required, it shall be in accordance with Section 26.11 of ACI 318.
|  | 1808.8.6 Seismic requirements. | See Section 1905 for additional requirements for foundations of structures assigned to Seismic Design Category C, D, E or F. For structures assigned to Seismic Design Category D, E or F, provisions of Section 18.13 of ACI 318 shall apply where not in conflict with the provisions of Sections 1808 through 1810. Exceptions: 1. Detached one- and two-family dwellings of light-frame construction and two stories or less above grade plane are not required to comply with the provisions of Section 18.13 of ACI 318. 2. Section 18.13.4.3(a) of ACI 318 shall not apply.
|  | 1808.9 Vertical masonry foundation elements. | Vertical masonry foundation elements that are not foundation piers as defined in Section 202 shall be designed as piers, walls or columns, as applicable, in accordance with TMS 402.
|  | 1809.2 Supporting soils. | Shallow foundations shall be built on undisturbed soil, compacted fill material or controlled low-strength material (CLSM). Compacted fill material shall be placed in accordance with Section 1804.5. CLSM shall be placed in accordance with Section 1804.6.
|  | 1809.3 Stepped footings. | The top surface of footings shall be level. The bottom surface of footings shall be permitted to have a slope not exceeding 1 unit vertical in 10 units horizontal (10-percent slope). Footings shall be stepped where it is necessary to change the elevation of the top surface of the footing or where the surface of the ground slopes more than 1 unit vertical in 10 units horizontal (10-percent slope).
|  | 1809.4 Depth and width of footings. | The minimum depth of footings below the undisturbed ground surface shall be 12 inches (305 mm). Where applicable, the requirements of Section 1809.5 shall be satisfied. The minimum width of footings shall be 12 inches (305 mm).
|  | 1809.5 Frost protection. | Except where otherwise protected from frost, foundations and other permanent supports of buildings and structures shall be protected from frost by one or more of the following methods: 1. Extending below the frost line of the locality. 2. Constructing in accordance with ASCE 32. 3. Erecting on solid rock. Exception: Free-standing buildings meeting all of the following conditions shall not be required to be protected: 1. Assigned to Risk Category I. 2. Area of 600 square feet (56 m2) or less for light-frame construction or 400 square feet (37 m2) or less for other than light-frame construction. 3. Eave height of 10 feet (3048 mm) or less. Shallow foundations shall not bear on frozen soil unless such frozen condition is of a permanent character.
|  | 1809.5.1 Frost protection at required exits. | Frost protection shall be provided at exterior landings for all required exits with outward-swinging doors. Frost protection shall only be required to the extent necessary to ensure the unobstructed opening of the required exit doors.
|  | 1809.6 Location of footings. | Footings on granular soil shall be so located that the line drawn between the lower edges of adjoining footings shall not have a slope steeper than 30 degrees (0.52 rad) with the horizontal, unless the material supporting the higher footing is braced or retained or otherwise laterally supported in an approved manner or a greater slope has been properly established by engineering analysis.
|  | 1809.7 Prescriptive footings for light-frame construction. | Where a specific design is not provided, concrete or masonry-unit footings supporting walls of light-frame construction shall be permitted to be designed in accordance with Table 1809.7.
|  | 1809.8 Plain concrete footings. | The edge thickness of plain concrete footings supporting walls of other than light-frame construction shall be not less than 8 inches (203 mm) where placed on soil or rock. Exception: For plain concrete footings supporting Group R-3 occupancies, the edge thickness is permitted to be 6 inches (152 mm), provided that the footing does not extend beyond a distance greater than the thickness of the footing on either side of the supported wall.
|  | 1809.9 Masonry-unit footings. | The design, materials and construction of masonry-unit footings shall comply with Sections 1809.9.1 and 1809.9.2, and the provisions of Chapter 21. Exception: Where a specific design is not provided, masonry-unit footings supporting walls of light-frame construction shall be permitted to be designed in accordance with Table 1809.7.
|  | 1809.9.1 Dimensions. | Masonry-unit footings shall be laid in Type M or S mortar complying with Section 2103.2.1 and the depth shall be not less than twice the projection beyond the wall, pier or column. The width shall be not less than 8 inches (203 mm) wider than the wall supported thereon.
|  | 1809.9.2 Offsets. | The maximum offset of each course in brick foundation walls stepped up from the footings shall be 11/2 inches (38 mm) where laid in single courses, and 3 inches (76 mm) where laid in double courses.
|  | 1809.10 Pier and curtain wall foundations. | Except in Seismic Design Categories D, E and F, pier and curtain wall foundations shall be permitted to be used to support light-frame construction not more than two stories above grade plane, provided that the following requirements are met: 1. All load-bearing walls shall be placed on continuous concrete footings bonded integrally with the exterior wall footings. 2. The minimum actual thickness of a load-bearing masonry wall shall be not less than 4 inches (102 mm) nominal or 35/8 inches (92 mm) actual thickness, and shall be bonded integrally with piers spaced 6 feet (1829 mm) on center (o.c.). 3. Piers shall be constructed in accordance with Chapter 21 and the following: 3.1. The unsupported height of the masonry piers shall not exceed 10 times their least dimension. 3.2. Where structural clay tile or hollow concrete masonry units are used for piers supporting beams and girders, the cellular spaces shall be filled solidly with concrete or Type M or S mortar. Exception: Unfilled hollow piers shall be permitted where the unsupported height of the pier is not more than four times its least dimension. 3.3. Hollow piers shall be capped with 4 inches (102 mm) of solid masonry or concrete or the cavities of the top course shall be filled with concrete or grout. 4. The maximum height of a 4-inch (102 mm) load-bearing masonry foundation wall supporting wood frame walls and floors shall not be more than 4 feet (1219 mm) in height. 5. The unbalanced fill for 4-inch (102 mm) foundation walls shall not exceed 24 inches (610 mm) for solid masonry, nor 12 inches (305 mm) for hollow masonry.
|  | 1809.11 Steel grillage footings. | Grillage footings of structural steel elements shall be separated with approved steel spacers and be entirely encased in concrete with not less than 6 inches (152 mm) on the bottom and not less than 4 inches (102 mm) at all other points. The spaces between the shapes shall be completely filled with concrete or cement grout.
|  | 1809.12 Timber footings. | Timber footings shall be permitted for buildings of Type V construction and as otherwise approved by the building official. Such footings shall be treated in accordance with AWPA U1 (Commodity Specification A, Use Category 4B). Treated timbers are not required where placed entirely below permanent water level, or where used as capping for wood piles that project above the water level over submerged or marsh lands. The compressive stresses perpendicular to grain in untreated timber footings supported on treated piles shall not exceed 70 percent of the allowable stresses for the species and grade of timber as specified in the ANSI/AWC NDS.
|  | 1809.13 Footing seismic ties. | Where a structure is assigned to Seismic Design Category D, E or F, individual spread footings founded on soil defined in Chapter 20 of ASCE 7 as Site Class E or F shall be interconnected by ties. Unless it is demonstrated that equivalent restraint is provided by reinforced concrete beams within slabs on grade or reinforced concrete slabs on grade, ties shall be capable of carrying, in tension or compression, a force equal to the lesser of the product of the larger footing design gravity load times the seismic coefficient, SDS, divided by 10 and 25 percent of the smaller footing design gravity load.
|  | 1810.1 General. | Deep foundations shall be analyzed, designed, detailed and installed in accordance with Sections 1810.1 through 1810.4.
|  | 1810.1.1 Geotechnical investigation. | Deep foundations shall be designed and installed on the basis of a geotechnical investigation as set forth in Section 1803.
|  | 1810.1.2 Use of existing deep foundation elements. | Deep foundation elements left in place where a structure has been demolished shall not be used for the support of new construction unless satisfactory evidence is submitted to the building official, which indicates that the elements are sound and meet the requirements of this code. Such elements shall be load tested or redriven to verify their capacities. The design load applied to such elements shall be the lowest allowable load as determined by tests or redriving data.
|  | 1810.1.3 Deep foundation elements classified as columns. | Deep foundation elements standing unbraced in air, water or fluid soils shall be classified as columns and designed as such in accordance with the provisions of this code from their top down to the point where adequate lateral support is provided in accordance with Section 1810.2.1. Exception: Where the unsupported height to least horizontal dimension of a cast-in-place deep foundation element does not exceed three, it shall be permitted to design and construct such an element as a pedestal in accordance with ACI 318.
|  | 1810.1.4 Special types of deep foundations. | The use of types of deep foundation elements not specifically mentioned herein is permitted, subject to the approval of the building official, upon the submission of acceptable test data, calculations and other information relating to the structural properties and load capacity of such elements. The allowable stresses for materials shall not in any case exceed the limitations specified herein.
|  | 1810.2 Analysis. | The analysis of deep foundations for design shall be in accordance with Sections 1810.2.1 through 1810.2.5.
|  | 1810.2.1 Lateral support. | Any soil other than fluid soil shall be deemed to afford sufficient lateral support to prevent buckling of deep foundation elements and to permit the design of the elements in accordance with accepted engineering practice and the applicable provisions of this code.
|  | 1810.2.2 Stability. | Deep foundation elements shall be braced to provide lateral stability in all directions. Three or more elements connected by a rigid cap shall be considered to be braced, provided that the elements are located in radial directions from the centroid of the group not less than 60 degrees (1 rad) apart. A two-element group in a rigid cap shall be considered to be braced along the axis connecting the two elements. Methods used to brace deep foundation elements shall be subject to the approval of the building official. Deep foundation elements supporting walls shall be placed alternately in lines spaced not less than 1 foot (305 mm) apart and located symmetrically under the center of gravity of the wall load carried, unless effective measures are taken to provide for eccentricity and lateral forces, or the foundation elements are adequately braced to provide for lateral stability. Exceptions: 1. Isolated cast-in-place deep foundation elements without lateral bracing shall be permitted where the least horizontal dimension is not less than 2 feet (610 mm), adequate lateral support in accordance with Section 1810.2.1 is provided for the entire height and the height does not exceed 12 times the least horizontal dimension. 2. A single row of deep foundation elements without lateral bracing is permitted for one- and two-family dwellings and lightweight construction not exceeding two stories above grade plane or 35 feet (10 668 mm) in building height, provided that the centers of the elements are located within the width of the supported wall.
|  | 1810.2.3 Settlement. | The settlement of a single deep foundation element or group thereof shall be estimated based on approved methods of analysis. The predicted settlement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity.
|  | 1810.2.4 Lateral loads. | The moments, shears and lateral deflections used for design of deep foundation elements shall be established considering the nonlinear interaction of the shaft and soil, as determined by a registered design professional. Where the ratio of the depth of embedment of the element to its least horizontal dimension is less than or equal to six, it shall be permitted to assume the element is rigid.
|  | 1810.2.4.1 Seismic Design Categories D through F. | For structures assigned to Seismic Design Category D, E or F, deep foundation elements on Site Class E or F sites, as determined in Section 1613.2.2, shall be designed and constructed to withstand maximum imposed curvatures from earthquake ground motions and structure response. Curvatures shall include free-field soil strains modified for soil-foundation-structure interaction coupled with foundation element deformations associated with earthquake loads imparted to the foundation by the structure. Exception: Deep foundation elements that satisfy the following additional detailing requirements shall be deemed to comply with the curvature capacity requirements of this section. 1. Precast prestressed concrete piles detailed in accordance with Section 1810.3.8. 2. Cast-in-place deep foundation elements with a minimum longitudinal reinforcement ratio of 0.005 extending the full length of the element and detailed in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 as required by Section 1810.3.9.4.2.2.
|  | 1810.2.5 Group effects. | The analysis shall include group effects on lateral behavior where the center-to-center spacing of deep foundation elements in the direction of lateral force is less than eight times the least horizontal dimension of an element. The analysis shall include group effects on axial behavior where the center-to-center spacing of deep foundation elements is less than three times the least horizontal dimension of an element. Group effects shall be evaluated using a generally accepted method of analysis; the analysis for uplift of grouped elements with center-to-center spacing less than three times the least horizontal dimension of an element shall be evaluated in accordance with Section 1810.3.3.1.6.
|  | 1810.3 Design and detailing. | Deep foundations shall be designed and detailed in accordance with Sections 1810.3.1 through 1810.3.13.
|  | 1810.3.1 Design conditions. | Design of deep foundations shall include the design conditions specified in Sections 1810.3.1.1 through 1810.3.1.6, as applicable.
|  | 1810.3.1.1 Design methods for concrete elements. | Where concrete deep foundations are laterally supported in accordance with Section 1810.2.1 for the entire height and applied forces cause bending moments not greater than those resulting from accidental eccentricities, structural design of the element using the allowable stress design load combinations specified in ASCE 7, Section 2.4 or the alternative allowable stress design load combinations of Section 1605.2 and the allowable stresses specified in this chapter shall be permitted. Otherwise, the structural design of concrete deep foundation elements shall use the strength load combinations specified in ASCE 7, Section 2.3 and approved strength design methods.
|  | 1810.3.1.2 Composite elements. | Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section of the composite assembly shall satisfy the applicable requirements of this code, and the maximum allowable load in each section shall be limited by the structural capacity of that section.
|  | 1810.3.1.3 Mislocation. | The foundation or superstructure shall be designed to resist the effects of the mislocation of any deep foundation element by not less than 3 inches (76 mm). To resist the effects of mislocation, compressive overload of deep foundation elements to 110 percent of the allowable design load shall be permitted.
|  | 1810.3.1.4 Driven piles. | Driven piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by handling, driving and service loads.
|  | 1810.3.1.5 Helical piles. | Helical piles shall be designed and manufactured in accordance with accepted engineering practice to resist all stresses induced by installation into the ground and service loads.
|  | 1810.3.1.6 Casings. | Temporary and permanent casings shall be of steel and shall be sufficiently strong to resist collapse and sufficiently watertight to exclude any foreign materials during the placing of concrete. Where a permanent casing is considered reinforcing steel, the steel shall be protected under the conditions specified in Section 1810.3.2.5. Horizontal joints in the casing shall be spliced in accordance with Section 1810.3.6.
|  | 1810.3.2 Materials. | The materials used in deep foundation elements shall satisfy the requirements of Sections 1810.3.2.1 through 1810.3.2.8, as applicable.
|  | 1810.3.2.1 Concrete. | Where concrete is cast in a steel pipe or where an enlarged base is formed by compacting concrete, the maximum size for coarse aggregate shall be 3/4 inch (19.1 mm). Concrete to be compacted shall have a zero slump.
|  | 1810.3.2.1.1 Seismic hooks. | For structures assigned to Seismic Design Category C, D, E or F, the ends of hoops, spirals and ties used in concrete deep foundation elements shall be terminated with seismic hooks, as defined in ACI 318, and shall be turned into the confined concrete core.
|  | 1810.3.2.1.2 ACI 318 Equation (25. | 7.3.3). Where this chapter requires detailing of concrete deep foundation elements in accordance with Section 18.7.5.4 of ACI 318, compliance with Equation (25.7.3.3) of ACI 318 shall not be required.
|  | 1810.3.2.2 Prestressing steel. | Prestressing steel shall conform to ASTM A416.
|  | 1810.3.2.3 Steel. | Structural steel H-piles and structural steel sheet piling shall conform to the material requirements in ASTM A6. Steel pipe piles shall conform to the material requirements in ASTM A252. Fully welded steel piles shall be fabricated from plates that conform to the material requirements in ASTM A36, ASTM A283, ASTM A572, ASTM A588 or ASTM A690.
|  | 1810.3.2.4 Timber. | Timber deep foundation elements shall be designed as piles or poles in accordance with ANSI/AWC NDS. Round timber elements shall conform to ASTM D25. Sawn timber elements shall conform to DOC PS-20.
|  | 1810.3.2.4.1 Preservative treatment. | Timber deep foundation elements used to support permanent structures shall be treated in accordance with this section unless it is established that the tops of the untreated timber elements will be below the lowest ground-water level assumed to exist during the life of the structure. Preservative and minimum final retention shall be in accordance with AWPA U1 (Commodity Specification E, Use Category 4C) for round timber elements and AWPA U1 (Commodity Specification A, Use Category 4B) for sawn timber elements. Preservative-treated timber elements shall be subject to a quality control program administered by an approved agency. Element cutoffs shall be treated in accordance with AWPA M4.
|  | 1810.3.2.5 Protection of materials. | Where boring records or site conditions indicate possible deleterious action on the materials used in deep foundation elements because of soil constituents, changing water levels or other factors, the elements shall be adequately protected by materials, methods or processes approved by the building official. Protective materials shall be applied to the elements so as not to be rendered ineffective by installation. The effectiveness of such protective measures for the particular purpose shall have been thoroughly established by satisfactory service records or other evidence.
|  | 1810.3.2.6 Allowable stresses. | The allowable stresses for materials used in deep foundation elements shall not exceed those specified in Table 1810.3.2.6.
|  | 1810.3.2.7 Increased allowable compressive stress for cased mandrell-driven cast-in-place elements. | The allowable compressive stress in the concrete shall be permitted to be increased as specified in Table 1810.3.2.6 for those portions of permanently cased cast-in-place elements that satisfy all of the following conditions:
|  | 1810.3.2.8 Justification of higher allowable stresses. | Use of allowable stresses greater than those specified in Section 1810.3.2.6 shall be permitted where supporting data justifying such higher stresses is filed with the building official. Such substantiating data shall include the following:
|  | 1810.3.3 Determination of allowable loads. | The allowable axial and lateral loads on deep foundation elements shall be determined by an approved formula, load tests or method of analysis.
|  | 1810.3.3.1 Allowable axial load. | The allowable axial load on a deep foundation element shall be determined in accordance with Sections 1810.3.3.1.1 through 1810.3.3.1.9. Exception: Where approved by the building official, load testing is not required.
|  | 1810.3.3.1.1 Driving criteria. | The allowable compressive load on any driven deep foundation element where determined by the application of an approved driving formula shall not exceed 40 tons (356 kN). For allowable loads above 40 tons (356 kN), the wave equation method of analysis shall be used to estimate driveability for both driving stresses and net displacement per blow at the ultimate load. Allowable loads shall be verified by load tests in accordance with Section 1810.3.3.1.2. The formula or wave equation load shall be determined for gravity-drop or power-actuated hammers and the hammer energy used shall be the maximum consistent with the size, strength and weight of the driven elements. The use of a follower is permitted only with the approval of the building official. The introduction of fresh hammer cushion or pile cushion material just prior to final penetration is not permitted.
|  | 1810.3.3.1.2 Load tests. | Where design compressive loads are greater than those determined using the allowable stresses specified in Section 1810.3.2.6, where the design load for any deep foundation element is in doubt, or where cast-in-place deep foundation elements have an enlarged base formed either by compacting concrete or by driving a precast base, control test elements shall be tested in accordance with ASTM D1143 or ASTM D4945. One element or more shall be load tested in each area of uniform subsoil conditions. Where required by the building official, additional elements shall be load tested where necessary to establish the safe design capacity. The resulting allowable loads shall not be more than one-half of the ultimate axial load capacity of the test element as assessed by one of the published methods listed in Section 1810.3.3.1.3 with consideration for the test type, duration and subsoil. The ultimate axial load capacity shall be determined by a registered design professional with consideration given to tolerable total and differential settlements at design load in accordance with Section 1810.2.3. In subsequent installation of the balance of deep foundation elements, all elements shall be deemed to have a supporting capacity equal to that of the control element where such elements are of the same type, size and relative length as the test element; are installed using the same or comparable methods and equipment as the test element; are installed in similar subsoil conditions as the test element; and, for driven elements, where the rate of penetration (for example, net displacement per blow) of such elements is equal to or less than that of the test element driven with the same hammer through a comparable driving distance.
|  | 1810.3.3.1.3 Load test evaluation methods. | It shall be permitted to evaluate load tests of deep foundation elements using any of the following methods:
|  | 1810.3.3.1.4 Allowable shaft resistance. | The assumed shaft resistance developed by any uncased cast-in-place deep foundation element shall not exceed one-sixth of the bearing value of the soil material at minimum depth as set forth in Table 1806.2, up to 500 psf (24 kPa), unless a greater value is allowed by the building official on the basis of a geotechnical investigation as specified in Section 1803 or a greater value is substantiated by a load test in accordance with Section 1810.3.3.1.2. Shaft resistance and end-bearing resistance shall not be assumed to act simultaneously unless determined by a geotechnical investigation in accordance with Section 1803.
|  | 1810.3.3.1.5 Uplift capacity of a single deep foundation element. | Where required by the design, the uplift capacity of a single deep foundation element shall be determined by an approved method of analysis based on a minimum factor of safety of three or by load tests conducted in accordance with ASTM D3689. The maximum allowable uplift load shall not exceed the ultimate load capacity as determined in Section 1810.3.3.1.2, using the results of load tests conducted in accordance with ASTM D3689, divided by a factor of safety of two. Exception: Where uplift is due to wind or seismic loading, the minimum factor of safety shall be two where capacity is determined by an analysis and one and one-half where capacity is determined by load tests.
|  | 1810.3.3.1.6 Allowable uplift load of grouped deep foundation elements. | For grouped deep foundation elements subjected to uplift, the allowable uplift load for the group shall be calculated by a generally accepted method of analysis. Where the deep foundation elements in the group are placed at a center-to-center spacing less than three times the least horizontal dimension of the largest single element, the allowable uplift load for the group is permitted to be calculated as the lesser of:
|  | 1810.3.3.1.7 Load-bearing capacity. | Deep foundation elements shall develop ultimate load capacities of not less than twice the design working loads in the designated load-bearing layers. Analysis shall show that soil layers underlying the designated load-bearing layers do not cause the load-bearing capacity safety factor to be less than two.
|  | 1810.3.3.1.8 Bent deep foundation elements. | The load-bearing capacity of deep foundation elements discovered to have a sharp or sweeping bend shall be determined by an approved method of analysis or by load testing a representative element.
|  | 1810.3.3.1.9 Helical piles. | The allowable axial design load, Pa, of helical piles shall be determined as follows:
|  | 1810.3.3.2 Allowable lateral load. | Where required by the design, the lateral load capacity of a single deep foundation element or a group thereof shall be determined by an approved method of analysis or by lateral load tests to not less than twice the proposed design working load. The resulting allowable load shall not be more than one-half of the load that produces a gross lateral movement of 1 inch (25 mm) at the lower of the top of foundation element and the ground surface, unless it can be shown that the predicted lateral movement shall cause neither harmful distortion of, nor instability in, the structure, nor cause any element to be loaded beyond its capacity.
|  | 1810.3.4 Subsiding soils or strata. | Where deep foundation elements are installed through subsiding soils or other subsiding strata and derive support from underlying firmer materials, consideration shall be given to the downward frictional forces potentially imposed on the elements by the subsiding upper strata.
|  | 1810.3.5 Dimensions of deep foundation elements. | The dimensions of deep foundation elements shall be in accordance with Sections 1810.3.5.1 through 1810.3.5.3, as applicable.
|  | 1810.3.5.1 Precast. | The minimum lateral dimension of precast concrete deep foundation elements shall be 8 inches (203 mm). Corners of square elements shall be chamfered.
|  | 1810.3.5.2 Cast-in-place or grouted-in-place. | Cast-in-place and grouted-in-place deep foundation elements shall satisfy the requirements of this section.
|  | 1810.3.5.2.1 Cased. | Cast-in-place or grouted-in-place deep foundation elements with a permanent casing shall have a nominal outside diameter of not less than 8 inches (203 mm).
|  | 1810.3.5.2.2 Uncased. | Cast-in-place or grouted-in-place deep foundation elements without a permanent casing shall have a specified diameter of not less than 12 inches (305 mm). The element length shall not exceed 30 times the specified diameter. Exception: The length of the element is permitted to exceed 30 times the specified diameter, provided that the design and installation of the deep foundations are under the direct supervision of a registered design professional knowledgeable in the field of soil mechanics and deep foundations. The registered design professional shall submit a report to the building official stating that the elements were installed in compliance with the approved construction documents.
|  | 1810.3.5.2.3 Micropiles. | Micropiles shall have a nominal diameter of 12 inches (305 mm) or less. The minimum diameter set forth elsewhere in Section 1810.3.5 shall not apply to micropiles.
|  | 1810.3.5.3 Steel. | Steel deep foundation elements shall satisfy the requirements of this section.
|  | 1810.3.5.3.1 Structural steel H-piles. | Sections of structural steel H-piles shall comply with the requirements for HP shapes in ASTM A6, or the following:
|  | 1810.3.5.3.2 Fully welded steel piles fabricated from plates. | Sections of fully welded steel piles fabricated from plates shall comply with the following:
|  | 1810.3.5.3.3 Structural steel sheet piling. | Individual sections of structural steel sheet piling shall conform to the profile indicated by the manufacturer, and shall conform to the general requirements specified by ASTM A6.
|  | 1810.3.5.3.4 Steel pipes and tubes. | Steel pipes and tubes used as deep foundation elements shall have a nominal outside diameter of not less than 8 inches (203 mm). Where steel pipes or tubes are driven open ended, they shall have not less than 0.34 square inch (219 mm2) of steel in cross section to resist each 1,000 foot-pounds (1356 Nm) of pile hammer energy, or shall have the equivalent strength for steels having a yield strength greater than 35,000 psi (241 MPa) or the wave equation analysis shall be permitted to be used to assess compression stresses induced by driving to evaluate if the pile section is appropriate for the selected hammer. Where a pipe or tube with wall thickness less than 0.179 inch (4.6 mm) is driven open ended, a suitable cutting shoe shall be provided. Concrete-filled steel pipes or tubes in structures assigned to Seismic Design Category C, D, E or F shall have a wall thickness of not less than 3/16 inch (5 mm). The pipe or tube casing for socketed drilled shafts shall have a nominal outside diameter of not less than 18 inches (457 mm), a wall thickness of not less than 3/8 inch (9.5 mm) and a suitable steel driving shoe welded to the bottom; the diameter of the rock socket shall be approximately equal to the inside diameter of the casing. Exceptions: 1. There is no minimum diameter for steel pipes or tubes used in micropiles. 2. For mandrel-driven pipes or tubes, the minimum wall thickness shall be 1/10 inch (2.5 mm).
|  | 1810.3.5.3.5 Helical piles. | Dimensions of the central shaft and the number, size and thickness of helical bearing plates shall be sufficient to support the design loads.
|  | 1810.3.6 Splices. | Splices shall be constructed so as to provide and maintain true alignment and position of the component parts of the deep foundation element during installation and subsequent thereto and shall be designed to resist the axial and shear forces and moments occurring at the location of the splice during driving and for design load combinations. Where deep foundation elements of the same type are being spliced, splices shall develop not less than 50 percent of the bending strength of the weaker section. Where deep foundation elements of different materials or different types are being spliced, splices shall develop the full compressive strength and not less than 50 percent of the tension and bending strength of the weaker section. Where structural steel cores are to be spliced, the ends shall be milled or ground to provide full contact and shall be full-depth welded. Exception: For buildings assigned to Seismic Design Category A or B, splices need not comply with the 50-percent tension and bending strength requirements where justified by supporting data.
|  | 1810.3.6.1 Seismic Design Categories C through F. | For structures assigned to Seismic Design Category C, D, E or F splices of deep foundation elements shall develop the lesser of the following:
|  | 1810.3.7 Top of element detailing at cutoffs. | Where a minimum length for reinforcement or the extent of closely spaced confinement reinforcement is specified at the top of a deep foundation element, provisions shall be made so that those specified lengths or extents are maintained after cutoff.
|  | 1810.3.8 Precast concrete piles. | Precast concrete piles shall be designed and detailed in accordance with ACI 318. Exceptions: 1. For precast prestressed piles in Seismic Design Category C, the minimum volumetric ratio of spirals or circular hoops required by Section 18.13.5.10.4 of ACI 318 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 or Section 2.4.5 and the applicable overstrength factor, Ω0. In such cases, minimum transverse reinforcement index shall be as specified in Section 13.4.5.6 of ACI 318. 2. For precast prestressed piles in Seismic Design Categories D through F, the minimum volumetric ratio of spirals or circular hoops required by Section 18.13.5.10.5(c) of ACI 318 shall not apply in cases where the design includes full consideration of load combinations specified in ASCE 7, Section 2.3.6 or Section 2.4.5 and the applicable overstrength factor, Ω0. In such cases, minimum transverse reinforcement shall be as specified in Section 13.4.5.6 of ACI 318.
|  | 1810.3.9 Cast-in-place deep foundations. | Cast-in-place deep foundation elements shall be designed and detailed in accordance with Sections 1810.3.9.1 through 1810.3.9.6.
|  | 1810.3.9.1 Design cracking moment. | The design cracking moment (fMn) for a cast-in-place deep foundation element not enclosed by a structural steel pipe or tube shall be determined using the following equation:
|  | 1810.3.9.2 Required reinforcement. | Where subject to uplift or where the required moment strength determined using the load combinations of ASCE 7, Section 2.3 exceeds the design cracking moment determined in accordance with Section 1810.3.9.1 , cast-in-place deep foundations not enclosed by a structural steel pipe or tube shall be reinforced.
|  | 1810.3.9.3 Placement of reinforcement. | Reinforcement where required shall be assembled and tied together and shall be placed in the deep foundation element as a unit before the reinforced portion of the element is filled with concrete. Exceptions: 1. Steel dowels embedded 5 feet (1524 mm) or less shall be permitted to be placed after concreting, while the concrete is still in a semifluid state. 2. For deep foundation elements installed with a hollow-stem auger, tied reinforcement shall be placed after elements are concreted, while the concrete is still in a semifluid state. Longitudinal reinforcement without lateral ties shall be placed either through the hollow stem of the auger prior to concreting or after concreting, while the concrete is still in a semifluid state. 3. For Group R-3 and U occupancies not exceeding two stories of light-frame construction, reinforcement is permitted to be placed after concreting, while the concrete is still in a semifluid state, and the concrete cover requirement is permitted to be reduced to 2 inches (51 mm), provided that the construction method can be demonstrated to the satisfaction of the building official.
|  | 1810.3.9.4 Seismic reinforcement. | Where a structure is assigned to Seismic Design Category C, reinforcement shall be provided in accordance with Section 1810.3.9.4.1. Where a structure is assigned to Seismic Design Category D, E or F, reinforcement shall be provided in accordance with Section 1810.3.9.4.2. Exceptions: 1. Isolated deep foundation elements supporting posts of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where detailed so the element is not subject to lateral loads and the soil provides adequate lateral support in accordance with Section 1810.2.1 . 2. Isolated deep foundation elements supporting posts and bracing from decks and patios appurtenant to Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than one No. 4 bar, without ties or spirals, where the lateral load, E, to the top of the element does not exceed 200 pounds (890 N) and the soil provides adequate lateral support in accordance with Section 1810.2.1. 3. Deep foundation elements supporting the concrete foundation wall of Group R-3 and U occupancies not exceeding two stories of light-frame construction shall be permitted to be reinforced as required by rational analysis but with not less than two No. 4 bars, without ties or spirals, where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations with overstrength factor in Section 2.3.6 or 2.4.5 of ASCE 7 and the soil provides adequate lateral support in accordance with Section 1810.2.1. 4. Closed ties or spirals where required by Section 1810.3.9.4.2 shall be permitted to be limited to the top 3 feet (914 mm) of deep foundation elements 10 feet (3048 mm) or less in depth supporting Group R-3 and U occupancies of Seismic Design Category D, not exceeding two stories of light-frame construction.
|  | 1810.3.9.4.1 Seismic reinforcement in Seismic Design Category C. | For structures assigned to Seismic Design Category C, cast-in-place deep foundation elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. Not fewer than four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.0025, shall be provided throughout the minimum reinforced length of the element as defined in this section starting at the top of the element. The minimum reinforced length of the element shall be taken as the greatest of the following: 1. One-third of the element length. 2. A distance of 10 feet (3048 mm). 3. Three times the least element dimension. 4. The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations of ASCE 7, Section 2.3. Transverse reinforcement shall consist of closed ties or spirals with a minimum 3/8 inch (9.5 mm) diameter. Spacing of transverse reinforcement shall not exceed the smaller of 6 inches (152 mm) or 8-longitudinal-bar diameters, within a distance of three times the least element dimension from the bottom of the pile cap. Spacing of transverse reinforcement shall not exceed 16 longitudinal bar diameters throughout the remainder of the reinforced length. Exceptions: 1. The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes. 2. A spiral-welded metal casing of a thickness not less than the manufacturer’s standard No. 14 gage (0.068 inch) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.
|  | 1810.3.9.4.2 Seismic reinforcement in Seismic Design Categories D through F. | For structures assigned to Seismic Design Category D, E or F, cast-in-place deep foundation elements shall be reinforced as specified in this section. Reinforcement shall be provided where required by analysis. Not fewer than four longitudinal bars, with a minimum longitudinal reinforcement ratio of 0.005, shall be provided throughout the minimum reinforced length of the element as defined in this section starting at the top of the element. The minimum reinforced length of the element shall be taken as the greatest of the following: 1. One-half of the element length. 2. A distance of 10 feet (3048 mm). 3. Three times the least element dimension. 4. The distance from the top of the element to the point where the design cracking moment determined in accordance with Section 1810.3.9.1 exceeds the required moment strength determined using the load combinations of ASCE 7, Section 2.3. Transverse reinforcement shall consist of closed ties or spirals not smaller than No. 3 bars for elements with a least dimension up to 20 inches (508 mm), and No. 4 bars for larger elements. Throughout the remainder of the reinforced length outside the regions with transverse confinement reinforcement, as specified in Section 1810.3.9.4.2.1 or 1810.3.9.4.2.2, the spacing of transverse reinforcement shall not exceed the least of the following: 1. 12 longitudinal bar diameters. 2. One-half the least dimension of the element. 3. 12 inches (305 mm). Exceptions: 1. The requirements of this section shall not apply to concrete cast in structural steel pipes or tubes. 2. A spiral-welded metal casing of a thickness not less than manufacturer’s standard No. 14 gage (0.068 inch) is permitted to provide concrete confinement in lieu of the closed ties or spirals. Where used as such, the metal casing shall be protected against possible deleterious action due to soil constituents, changing water levels or other factors indicated by boring records of site conditions.
|  | 1810.3.9.4.2.1 Site Classes A through D. | For Site Class A, B, C or D sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within three times the least element dimension of the bottom of the pile cap. A transverse spiral reinforcement ratio of not less than one-half of that required in Table 18.10.6.4(g) of ACI 318 shall be permitted.
|  | 1810.3.9.4.2.2 Site Classes E and F. | For Site Class E or F sites, transverse confinement reinforcement shall be provided in the element in accordance with Sections 18.7.5.2, 18.7.5.3 and 18.7.5.4 of ACI 318 within seven times the least element dimension of the pile cap and within seven times the least element dimension of the interfaces of strata that are hard or stiff and strata that are liquefiable or are composed of soft- to medium-stiff clay.
|  | 1810.3.9.5 Belled drilled shafts. | Where drilled shafts are belled at the bottom, the edge thickness of the bell shall be not less than that required for the edge of footings. Where the sides of the bell slope at an angle less than 60 degrees (1 rad) from the horizontal, the effects of vertical shear shall be considered.
|  | 1810.3.9.6 Socketed drilled shafts. | Socketed drilled shafts shall have a permanent pipe or tube casing that extends down to bedrock and an uncased socket drilled into the bedrock, both filled with concrete. Socketed drilled shafts shall have reinforcement or a structural steel core for the length as indicated by an approved method of analysis.
|  | 1810.3.10 Micropiles. | Micropiles shall be designed and detailed in accordance with Sections 1810.3.10.1 through 1810.3.10.4.
|  | 1810.3.10.1 Construction. | Micropiles shall develop their load-carrying capacity by means of a bond zone in soil, bedrock or a combination of soil and bedrock. Micropiles shall be grouted and have either a steel pipe or tube or steel reinforcement at every section along the length. It shall be permitted to transition from deformed reinforcing bars to steel pipe or tube reinforcement by extending the bars into the pipe or tube section by not less than their development length in tension in accordance with ACI 318.
|  | 1810.3.10.2 Materials. | Reinforcement shall consist of deformed reinforcing bars in accordance with ASTM A615 Grade 60 or 75 or ASTM A722 Grade 150.
|  | 1810.3.10.3 Reinforcement. | For micropiles or portions thereof grouted inside a temporary or permanent casing or inside a hole drilled into bedrock or a hole drilled with grout, the steel pipe or tube or steel reinforcement shall be designed to carry not less than 40 percent of the design compression load. Micropiles or portions thereof grouted in an open hole in soil without temporary or permanent casing and without suitable means of verifying the hole diameter during grouting shall be designed to carry the entire compression load in the reinforcing steel. Where a steel pipe or tube is used for reinforcement, the portion of the grout enclosed within the pipe is permitted to be included in the determination of the allowable stress in the grout.
|  | 1810.3.10.4 Seismic reinforcement. | For structures assigned to Seismic Design Category C, a permanent steel casing shall be provided from the top of the micropile down to the point of zero curvature. For structures assigned to Seismic Design Category D, E or F, the micropile shall be considered as an alternative system in accordance with Section 104.11. The alternative system design, supporting documentation and test data shall be submitted to the building official for review and approval.
|  | 1810.3.11 Pile caps. | Pile caps shall conform with ACI 318 and this section. Pile caps shall be of reinforced concrete, and shall include all elements to which vertical deep foundation elements are connected, including grade beams and mats. The soil immediately below the pile cap shall not be considered as carrying any vertical load, with the exception of a combined pile raft. The tops of vertical deep foundation elements shall be embedded not less than 3 inches (76 mm) into pile caps and the caps shall extend not less than 4 inches (102 mm) beyond the edges of the elements. The tops of elements shall be cut or chipped back to sound material before capping.
|  | 1810.3.11.1 Seismic Design Categories C through F. | For structures assigned to Seismic Design Category C, D, E or F, concrete deep foundation elements shall be connected to the pile cap in accordance with ACI 318.
|  | 1810.3.11.2 Seismic Design Categories D through F. | For structures assigned to Seismic Design Category D, E or F, deep foundation element resistance to uplift forces or rotational restraint shall be provided by anchorage into the pile cap, designed considering the combined effect of axial forces due to uplift and bending moments due to fixity to the pile cap. Anchorage shall develop not less than 25 percent of the strength of the element in tension. Anchorage into the pile cap shall comply with the following: 1. In the case of uplift, the anchorage shall be capable of developing the least of the following: 1.1. The nominal tensile strength of the longitudinal reinforcement in a concrete element. 1.2. The nominal tensile strength of a steel element. 1.3. The frictional force developed between the element and the soil multiplied by 1.3. Exception: The anchorage is permitted to be designed to resist the axial tension force resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7. 2. In the case of rotational restraint, the anchorage shall be designed to resist the axial and shear forces, and moments resulting from the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7 or the anchorage shall be capable of developing the full axial, bending and shear nominal strength of the element. 3. The connection between the pile cap and the steel H-piles or unfilled steel pipe piles in structures assigned to Seismic Design Category D, E or F shall be designed for a tensile force of not less than 10 percent of the pile compression capacity. Exceptions: 1. Connection tensile capacity need not exceed the strength required to resist seismic load effects including overstrength of ASCE 7 Section 12.4.3 or 12.14.3.2. 2. Connections need not be provided where the foundation or supported structure does not rely on the tensile capacity of the piles for stability under the design seismic force. Where the vertical lateral-force-resisting elements are columns, the pile cap flexural strengths shall exceed the column flexural strength. The connection between batter piles and pile caps shall be designed to resist the nominal strength of the pile acting as a short column. Batter piles and their connection shall be designed to resist forces and moments that result from the application of seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.
|  | 1810.3.12 Grade beams. | Grade beams shall comply with the provisions of ACI 318. Exception: Grade beams designed to resist the seismic load effects including overstrength factor in accordance with Section 2.3.6 or 2.4.5 of ASCE 7.
|  | 1810.3.13 Seismic ties. | Seismic ties shall comply with the provisions of ACI 318. Exception: In Group R-3 and U occupancies of light-frame construction, deep foundation elements supporting foundation walls, isolated interior posts detailed so the element is not subject to lateral loads or exterior decks and patios are not subject to interconnection where the soils are of adequate stiffness, subject to the approval of the building official.
|  | 1810.4 Installation. | Deep foundations shall be installed in accordance with Section 1810.4. Where a single deep foundation element comprises two or more sections of different materials or different types spliced together, each section shall satisfy the applicable conditions of installation.
|  | 1810.4.1 Structural integrity. | Deep foundation elements shall be installed in such a manner and sequence as to prevent distortion or damage that would adversely affect the structural integrity of adjacent structures or of foundation elements being installed or already in place and as to avoid compacting the surrounding soil to the extent that other foundation elements cannot be installed properly.
|  | 1810.4.1.1 Compressive strength of precast concrete piles. | A precast concrete pile shall not be driven before the concrete has attained a compressive strength of not less than 75 percent of the specified compressive strength (f ′c), but not less than the strength sufficient to withstand handling and driving forces.
|  | 1810.4.1.2 Shafts in unstable soils. | Where cast-in-place deep foundation elements are formed through unstable soils, the open hole shall be stabilized by a casing, slurry, or other approved method prior to placing the concrete. Where the casing is withdrawn during concreting, the level of concrete shall be maintained above the bottom of the casing at a sufficient height to offset any hydrostatic or lateral soil pressure. Driven casings shall be mandrel driven their full length in contact with the surrounding soil.
|  | 1810.4.1.3 Driving near uncased concrete. | Deep foundation elements shall not be driven within six element diameters center to center in granular soils or within one-half the element length in cohesive soils of an uncased element filled with concrete less than 48 hours old unless approved by the building official. If driving near uncased concrete elements causes the concrete surface in any completed element to rise or drop significantly or bleed additional water, the completed element shall be replaced.
|  | 1810.4.1.4 Driving near cased concrete. | Deep foundation elements shall not be driven within four and one-half average diameters of a cased element filled with concrete less than 24 hours old unless approved by the building official. Concrete shall not be placed in casings within heave range of driving.
|  | 1810.4.1.5 Defective timber piles. | Any substantial sudden change in rate of penetration of a timber pile shall be investigated for possible damage. If the sudden change in rate of penetration cannot be correlated to soil strata, the pile shall be removed for inspection or rejected.
|  | 1810.4.2 Identification. | Deep foundation materials shall be identified for conformity to the specified grade with this identity maintained continuously from the point of manufacture to the point of installation or shall be tested by an approved agency to determine conformity to the specified grade. The approved agency shall furnish an affidavit of compliance to the building official.
|  | 1810.4.3 Location plan. | A plan showing the location and designation of deep foundation elements by an identification system shall be filed with the building official prior to installation of such elements. Detailed records for elements shall bear an identification corresponding to that shown on the plan.
|  | 1810.4.4 Preexcavation. | The use of jetting, augering or other methods of preexcavation shall be subject to the approval of the building official. Where permitted, preexcavation shall be carried out in the same manner as used for deep foundation elements subject to load tests and in such a manner that will not impair the carrying capacity of the elements already in place or damage adjacent structures. Element tips shall be advanced below the preexcavated depth until the required resistance or penetration is obtained.
|  | 1810.4.5 Vibratory driving. | Vibratory drivers shall only be used to install deep foundation elements where the element load capacity is verified by load tests in accordance with Section 1810.3.3.1.2. The installation of production elements shall be controlled according to power consumption, rate of penetration or other approved means that ensure element capacities equal or exceed those of the test elements. Exceptions: 1. The pile installation is completed by driving with an impact hammer in accordance with Section 1810.3.3.1.1. 2. The pile is to be used only for lateral resistance.
|  | 1810.4.6 Heaved elements. | Deep foundation elements that have heaved during the driving of adjacent elements shall be redriven as necessary to develop the required capacity and penetration, or the capacity of the element shall be verified by load tests in accordance with Section 1810.3.3.1.2.
|  | 1810.4.7 Enlarged base cast-in-place elements. | Enlarged bases for cast-in-place deep foundation elements formed by compacting concrete or by driving a precast base shall be formed in or driven into granular soils. Such elements shall be constructed in the same manner as successful prototype test elements driven for the project. Shafts extending through peat or other organic soil shall be encased in a permanent steel casing. Where a cased shaft is used, the shaft shall be adequately reinforced to resist column action or the annular space around the shaft shall be filled sufficiently to reestablish lateral support by the soil. Where heave occurs, the element shall be replaced unless it is demonstrated that the element is undamaged and capable of carrying twice its design load.
|  | 1810.4.8 Hollow-stem augered, cast-in-place elements. | Where concrete or grout is placed by pumping through a hollow-stem auger, the auger shall be permitted to rotate in a clockwise direction during withdrawal. As the auger is withdrawn at a steady rate or in increments not to exceed 1 foot (305 mm), concreting or grouting pumping pressures shall be measured and maintained high enough at all times to offset hydrostatic and lateral earth pressures. Concrete or grout volumes shall be measured to ensure that the volume of concrete or grout placed in each element is equal to or greater than the theoretical volume of the hole created by the auger. Where the installation process of any element is interrupted or a loss of concreting or grouting pressure occurs, the element shall be redrilled to 5 feet (1524 mm) below the elevation of the tip of the auger when the installation was interrupted or concrete or grout pressure was lost and reformed. Augered cast-in-place elements shall not be installed within six diameters center to center of an element filled with concrete or grout less than 12 hours old, unless approved by the building official. If the concrete or grout level in any completed element drops due to installation of an adjacent element, the element shall be replaced.
|  | 1810.4.9 Socketed drilled shafts. | The rock socket and pipe or tube casing of socketed drilled shafts shall be thoroughly cleaned of foreign materials before filling with concrete. Steel cores shall be bedded in cement grout at the base of the rock socket.
|  | 1810.4.10 Micropiles. | Micropile deep foundation elements shall be permitted to be formed in holes advanced by rotary or percussive drilling methods, with or without casing. The elements shall be grouted with a fluid cement grout. The grout shall be pumped through a tremie pipe extending to the bottom of the element until grout of suitable quality returns at the top of the element. The following requirements apply to specific installation methods:
|  | 1810.4.11 Helical piles. | Helical piles shall be installed to specified embedment depth and torsional resistance criteria as determined by a registered design professional. The torque applied during installation shall not exceed the manufacturer’s rated maximum installation torque resistance of the helical pile.
|  | 1810.4.12 Special inspection. | Special inspections in accordance with Sections 1705.7 and 1705.8 shall be provided for driven and cast-in-place deep foundation elements, respectively. Special inspections in accordance with Section 1705.9 shall be provided for helical piles.

## BC19
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
1901.1 Scope. | The provisions of this chapter shall govern the materials, quality control, design and construction of concrete used in structures. | 1901.1 Scope. | The provisions of this chapter shall govern the materials, quality control, design and construction of concrete used in structures.
1901.1.1 Referenced standards. | Where this code makes reference to the nationally recognized standard ACI 318, such standard shall be as modified for New York City in accordance with Section 1908 of this code. Where sections within ACI 318 are referenced in other chapters and appendices of ACI 318, the provisions of this chapter shall apply.
1901.2 Plain and reinforced concrete. | Structural concrete shall be designed and constructed in accordance with the requirements of this chapter and ACI 318 as amended in Section 1908 of this code. Except for the provisions of Sections 1904 and 1910, the design and construction of slabs on grade shall not be governed by this chapter unless they transmit vertical loads or lateral forces from other parts of the structure to the soil. Precast concrete diaphragms in buildings assigned to Seismic Design Category C or D shall be designed in accordance with the requirements of ASCE 7, Section 14.2.4. | 1901.2 Plain and reinforced concrete. | Structural concrete shall be designed and constructed in accordance with the requirements of this chapter and ACI 318 as amended in Section 1905 of this code. Except for the provisions of Sections 1904 and 1907, the design and construction of slabs on grade shall not be governed by this chapter unless they transmit vertical loads or lateral forces from other parts of the structure to the soil.
1901.3 Anchoring to concrete. | Anchoring to concrete shall be in accordance with ACI 318 as amended in Section 1908, and applies to cast-in (headed bolts, headed studs and hooked J- or L-bolts), post-installed expansion (torque-controlled and displacement-controlled), undercut and adhesive anchors. | 1901.3 Anchoring to concrete. | Anchoring to concrete shall be in accordance with ACI 318 as amended in Section 1905, and applies to cast-in (headed bolts, headed studs and hooked J- or L-bolts), post-installed expansion (torque-controlled and displacement-controlled), undercut, screw, and adhesive anchors.
1901.4 Composite structural steel and concrete structures. | Systems of structural steel acting compositely with reinforced concrete shall be designed in accordance with Section 2206. | 1901.4 Composite structural steel and concrete structures. | Systems of structural steel acting compositely with reinforced concrete shall be designed in accordance with Section 2206 of this code.
1901.5 Construction documents. | The construction documents for structural concrete construction shall include: | 1901.5 Construction documents. | The construction documents for structural concrete construction shall include:
1901.6 Special inspections and tests. | Special inspections and tests of concrete elements of buildings and structures, and concreting operations, shall be as required by Chapter 17. | 1901.6 Special inspections and tests. | Special inspections and tests of concrete elements of buildings and structures and concreting operations shall be as required by Chapter 17.
1902.1 Definitions. | The following term is defined in Chapter 2:
1903.1 General. | Materials used to produce concrete, concrete itself and testing thereof shall comply with the applicable standards listed in ACI 318 and this section. | 1903.1 General. | Materials used to produce concrete, concrete itself and testing thereof shall comply with the applicable standards listed in ACI 318.
1903.2 Special inspections. | Where required, special inspections and tests shall be in accordance with Chapter 17. | 1903.2 Special inspections. | Where required, special inspections and tests shall be in accordance with Chapter 17.
1903.3 Glass fiber-reinforced concrete. | Glass fiber-reinforced concrete (GFRC) and the materials used in such concrete shall be in accordance with the PCI MNL 128 standard. | 1903.3 Glass fiber-reinforced concrete. | Glass fiber-reinforced concrete (GFRC) and the materials used in such concrete shall be in accordance with the PCI MNL 128 standard.
1903.4 Flat wall insulating concrete form (ICF) systems. | Insulating concrete form material used for forming flat concrete walls shall conform to ASTM E 2634. | 1903.4 Flat wall insulating concrete form (ICF) systems. | Insulating concrete form material used for forming flat concrete walls shall conform to ASTM E2634.
1903.5 Water. | Water used in mixing concrete shall be clean and free from injurious amounts of oils, acids, alkalis, salts, organic materials or other substances that are deleterious to concrete or steel reinforcement and shall comply with ACI 318, Section 26.4.1.3.
1903.6 Steel reinforcement. | Reinforcement and welding of reinforcement to be placed in concrete construction shall conform to the requirements of ACI 318, Chapter 20, and this section.
1903.6.1 Reinforcement type. | Steel reinforcement used in concrete construction shall comply with ACI 318, Chapter 20.
1903.6.2 Welding. | Welding of reinforcing bars shall conform to AWS D1.4 and ACI 318, Section 26.6.4. Type and location of welded splices and other required welding of reinforcing bars shall be indicated on the construction documents or in the project specifications. The ASTM reinforcing bar specifications, except for ASTM A 706, shall be supplemented to require a report of material properties necessary to conform to the requirements in AWS D1.4. A written welding procedure shall be provided to the registered design professional of record for approval prior to any welding. All welding shall be subject to special inspection by a special inspection agency.
1903.7 Admixtures. | Admixtures to be used in concrete shall be subject to prior approval by the registered design professional of record and shall comply with ACI 318, Section 26.4.1.4. Admixtures shall be included in the concrete design mix submittals.
1903.8 Storage of materials. | The storage of materials for use in concrete shall comply with ACI 318, Section 26.5.1, and the provisions of Sections 1903.8.1 and 1903.8.2 of this chapter.
1903.8.1 Manner of storage. | Cementitious materials and aggregates shall be stored in such a manner as to prevent deterioration or intrusion of foreign matter.
1905.1 General. | The required strength and durability of concrete shall be governed by compliance with the proportioning, testing, mixing and placing provisions of Sections 1905.1.1 through 1905.13 of this code and ACI 318. | 1905.1 General. | The text of ACI 318 shall be modified as indicated in Sections 1905.1.1 through 1905.1.8.
1903.8.2 Unacceptable material. | Any material that has deteriorated or has been contaminated shall not be used for concrete.
1904.1 General. | Concrete shall be designed and proportioned to comply with the durability, strength, exposure, and other requirements as specified in ACI 318 and Sections 1904.2 through 1904.5 of this chapter.
1904.2 Exposure categories and classes. | Concrete shall be assigned to exposure classes in accordance with ACI 318, Section 19.3.1, based on:
1904.3 Concrete properties. | Concrete mixtures shall conform to the most restrictive requirements of ACI 318, Section 19.3.2, based on the exposure classes assigned in Section 1904.2 of this chapter. Exception: For occupancies and appurtenances thereto in Group R occupancies that are in buildings less than four stories above grade plane, normal-weight aggregate concrete is permitted to comply with the requirements of Table 1904.3 of this chapter in lieu of the requirements of ACI 318, Table 19.3.2.1.
1904.4 Freezing and thawing exposures. | Concrete that will be exposed to freezing and thawing, in the presence of moisture, with or without deicing chemicals being present, shall comply with ACI 318, Section 19.3.3, and Sections 1904.4.1 and 1904.4.2 of this code.
1904.4.1 Air entrainment. | Concrete exposed to freezing and thawing while moist shall be air entrained in accordance with ACI 318, Sections 19.3.3.1 and 19.3.3.3.
1904.4.2 Deicing chemicals. | For concrete exposed to freezing and thawing in the presence of moisture and deicing chemicals, the maximum weight of fly ash, other pozzolans, silica fume or slag that is included in the concrete shall not exceed the percentages of the total weight of cementitious materials permitted by Table 1904.4.2.
1904.5 Alternative cementitious materials for sulfate exposure. | Combinations of cementitious materials for use in sulfate-resistant concrete that are alternative to those listed in ACI 318, Table 19.3.2.1, shall be permitted in accordance with ACI 318, Section 26.4.2.2.
1905.1.1 Strength. | Concrete shall be proportioned to provide an average compressive strength in accordance with Section 1905.3, and shall satisfy the durability criteria of Section 1904. Concrete shall be produced to minimize the frequency of strengths below f’c in compliance with Section 1905.6.3.3. For concrete designed and constructed in accordance with this chapter, f’c shall not be less than 2,500 psi (17.22 MPa). No maximum specified compressive strength shall apply unless restricted by a specific provision of this code or ACI 318.
1905.1.2 Cylinder tests. | Requirements for f’c shall be based on tests of cylinders made and tested in accordance with Section 1905.6.3.
1905.1.3 Basis of f’c . | Unless otherwise specified, f’c shall be based on 28-day tests. If other than 28 days, test age for f’c shall be as indicated in construction documents. If at any time during the concrete operations, the concrete is not in conformance with ASTM C 94 or is otherwise compro­mised, it shall be rejected. If it is placed, the location of the load shall be recorded and a pair of cylinders shall be molded from the load per ASTM C 31 and included in the average f’c.
1905.1.4 Lightweight aggregate concrete. | Where design criteria in ACI 318, Section 19.2.4, provides for use of a splitting tensile strength value of concrete (f’ct), laboratory tests shall be made in accordance with ASTM C 330 to establish the value of f’ct corresponding to the specified value of f’c.
1905.1.5 Field acceptance. | Splitting tensile strength tests shall not be used as a basis for field acceptance of concrete.
1905.2 Selection of concrete proportions. | Concrete proportions shall be determined in accordance with ACI 318 and the provisions of Sections 1905.2.1 through 1905.2.4 of this code.
1905.2.1 General. | Proportions of materials for concrete shall be established to provide:
1905.2.2 Different materials. | Where different materials are to be used for different portions of proposed work, each combination shall be evaluated.
1905.2.3 Basis of proportions. | Concrete proportions shall be established in accordance with Section 1905.3 or Section 1905.4, and shall comply with the applicable requirements of Section 1904.
1905.2.4 Mass concrete. | For areas of high-strength mass concrete, including but not limited to, 8,000 psi (55 158 kPa) or greater and the least dimension being equal to or greater than 36 inches (914 mm), as indicated on the construction documents, a thermal control plan complying with ACI 301, Section 8.1 and acceptable to the registered design professional of record shall be submitted by the contractor.
1905.3 Proportioning on the basis of field experience and/or trial mixtures. | Concrete proportioning determined on the basis of field experience or trial mixtures shall be done in accordance with ACI 318, Sections 26.4.3 and 26.4.4, and Sections 1905.3.1 through 1905.3.5 of this chapter.
1905.3.1 Required Strength. | If the required f’cr is obtained for trial batch mixes prior to the date specified, the trial mix design may be approved by the registered design professional of record for the structural design.
1905.3.2 Performance and approval. | Concrete mix designs shall be performed by an approved agency or by a concrete producer approved by the department as an approved fabricator in accordance with Section 1704.2.2, and approved in accordance with the requirements of Sections 1905.3.2.1 through 1905.3.2.3.
1905.3.2.1 Certification. | All mix designs submitted for review and approval in accordance with Section 1905.3.2.2 shall be certified by the director of the approved agency or the quality control manager of the approved concrete producer that performed the tests used to substantiate the mix design. In addition, all mix designs shall be signed by an owner or officer of the concrete production facility.
1905.3.2.2 Review and approval. | All mixes shall be approved by the registered design professional of record and filed with the department prior to use in construction.
1905.3.2.3 Distribution. | Copies of the approved mix design(s) shall be maintained at the construction site by the contractor and made available to the department upon request. A copy of the approved mix design(s) shall be provided by the contractor to the licensed concrete testing laboratory performing the acceptance testing of the concrete at the construction site.
1905.3.3. Test records and trial mixtures. | Field strength test records or trial mixtures used to determine f’cr shall not be more than 24 months old measured from the date of batching, provided the materials are the same as those proposed for use and the concrete producer provides a written statement confirming the materials are the same as those proposed for use. Exceptions: 1. Coarse aggregates may be acquired from an alternative source provided the nominal maximum size and the volume of coarse aggregate used remain unchanged. 2. Fine aggregates may be acquired from an alternative source provided the volume of fine aggregate used remains unchanged.
1905.3.4 Materials. | The type and source of the materials used in the concrete shall be identified in the proposed concrete mix design. In order for materials in field strength test records or trial mixtures to be considered the same as those proposed for use, the materials shall, at a minimum, comply with the following: 1. Cementitious materials. Cementitious materials shall be used in the same quantities for each individual component and shall be of the same type and shall be from the same source and mill. Upon request, the concrete producer shall provide mill certificates for the cementitious materials proposed for use and cementitious materials represented by the field strength test records or trial mixtures to the registered design professional of record and the department. 2. Aggregates. Coarse and fine aggregates shall be the same nominal maximum size and shall be used in the same volume for each individual component. The aggregate supplier shall attest that the aggregates proposed are not alkali-silica reactive. The aggregate supplier is permitted to rely on New York State Department of Transportation approval of the supplier’s aggregate source. 3. Admixtures. Admixtures shall meet the requirements of the same admixture type in accordance with ASTM C 494 or ASTM C 260 and there shall be no change in air content or water content from the previously specified mix. Exception: Addition or removal of retarding or accelerating admixtures as described in Section 1905.3.5 is acceptable. 4. Additional testing. Differences or changes in materials that are proposed for use, not meeting the requirements of Items 1 through 3 above, shall require new testing demonstrated by either field strength test records or trial mixtures. Exception: Field changes to concrete proportions specified in Section 1905.3.5.
1905.3.5 Field changes to concrete proportions. | Based on test data and observations during the course of construction, the following changes described in Sections 1905.3.5.1 and 1905.3.5.2 are permitted without requiring additional trial mixtures or field strength test records, provided:
1905.3.5.1 Changes that do not require prior approval of the registered design professional of record for the structure. | The following admixture modifications to concrete proportions can be made without requiring prior acceptance by the registered design professional of record:
1905.3.5.2 Changes that require prior approval of the registered design professional of record for the structure. | The following modifications to concrete proportions can be made only with prior acceptance by the registered design professional of record. Any added materials and the final mix proportions shall be indicated in a revised mix design submitted to the registered design professional of record prior to use: 1. Retarding and accelerating admixtures. Retarding and accelerating admixtures may be added to concrete mixtures or the dosage may be modified as needed to maintain practical set times. 2. Pigment. Pigment dosage may be adjusted to maintain uniform concrete color. 3. Fibers. Synthetic, glass or natural fibers may be added to the mix within the manufacturer recommended range. Any loss in workability shall be compensated with a water reducer. Exception: Steel fibers may not be added to a concrete mixture without the performance of a new mix design. 4. Corrosion inhibitor. Corrosion inhibiting admixtures may be added, provided the corresponding adjustment of mix water remains within the limits of the required water/cementitious material ratio. The added materials and the revised design mix shall be submitted for review by the registered design professional of record for the structure prior to use. 5. Cementitious content and water-cementitious material ratio (w/cm). The cementitious content may be increased by a maximum of 12 percent, or the w/cm ratio may be decreased while maintaining the same cementitious content, but the w/cm and air content shall not be increased. Aggregate quantities shall be adjusted, as required, to maintain the mix proportion and yield. 6. Hydration control. Admixture may be added for the purpose of delaying hydration and maintaining a workable mix. 7. Source of aggregate. Change to the source of aggregate may be approved by the registered design professional of record without providing additional test data only when the original aggregate source is no longer producing the required aggregates or the quality of the aggregates produced no longer meets the requirements of ASTM C 33 or the New York State Department of Transportation, provided: 7.1. The new aggregate source is approved by the New York State Department of Transportation; 7.2. A modulus of elasticity is not specified; 7.3. The volume of both the fine and coarse aggregates remains the same and the nominal maximum size of coarse aggregates is unchanged; 7.4. Lightweight aggregate shall not be substituted for dense, nor dense aggregate for lightweight, where lightweight aggregates are defined as having a specific gravity less than 2.5; and 7.5. The registered design professional of record is informed of the reason necessitating the change of aggregate. 8. Cementitious materials. Any change to cementitious materials shall require an additional laboratory testing trial batch. The new cementitious material shall maintain the same air and water cementitious ratio (w/cm) as the original mix and meet the strength requirements of ACI 301, Table 4.2.3.3 b. Approval of the registered design professional of record and submittal of data from either a three- or seven-day compressive strength test shall be required prior to the placement of concrete.
1905.4 Proportioning without field experience or trial mixtures. | Concrete proportioning determined without field experience or trial mixtures shall be done in accordance with ACI 318, Section 26.4.4.1(b). This method of proportioning shall not be permitted for:
1905.5 Average strength reduction. | As data becomes available during construction, it is permissible to reduce the amount by which the average compressive strength (f ‘ c) is required to exceed the specified value of f’ c in accordance with ACI 318, Section 26.4.4.1(c). A new mix design shall be submitted to the registered design professional of record for approval prior to use.
1905.6 Evaluation and acceptance of concrete. | The criteria for evaluation and acceptance of concrete shall be as specified in ACI 318, Sections 26.12 and 26.13, and Sections 1905.6.1 through 1905.6.5 of this code.
1905.6.1 Acceptance testing. | Concrete shall be tested in accordance with the requirements in Sections 1905.6.2 through 1905.6.5. Concrete sampling and testing for acceptance shall be deemed a special inspection performed by a licensed concrete testing laboratory as an approved agency. An approved agency shall perform tests on fresh concrete at the job site, prepare specimens required for curing under field conditions, prepare specimens required for testing in the laboratory and record the temperature of the fresh concrete when preparing specimens for strength tests. All field sampling and testing, including the testing of aggregates, concrete mixes, and strength testing of specimens, shall be subject to special inspection by an approved agency. All testing laboratories shall be approved agencies and shall employ qualified special inspectors to perform all required field and laboratory tests. Test results shall be promptly distributed by the testing laboratory to the registered design professional of record, concrete producer, owner and contractor to allow for corrective action where the concrete is found to be noncompliant with the mix design or noncompliant with the requirements otherwise specified in this code. Unless more prompt action is required, test results shall be reported no more than 7 business days after the date the respective tests were performed.
1905.6.2 Frequency of testing. | The frequency of conducting strength tests of concrete shall be as specified in Sections 1905.6.2.1 through 1905.6.2.4.
1905.6.2.1 Minimum frequency. | For the first 250 cubic yards of each class of concrete placed each day, samples for strength tests of each such class shall be taken: (i) not less than once a day; (ii) not less than once for each 50 cubic yards (38 m3) of concrete; and (iii) not less than once for each 5,000 square feet (465 m2) of surface area for slabs or walls. After the first 250 cubic yards (191 m3), samples for strength tests of each class of concrete placed each day shall be taken once for each additional 150 cubic yards (115 m3). For structural concrete exposed to exposure class C2, additional field testing of the concrete for water content per AASHTO T 318 shall be required. At the discretion of the registered design professional of record, the frequency of testing may be reduced, but not less than once for each 150 cubic yards (115 m3).
1905.6.2.2 Minimum number. | On a given project, if the total volume of concrete is such that the frequency of testing required by Section 1905.6.2.1 would provide less than five strength tests for a given class of concrete, tests shall be made from at least five randomly selected batches or from each batch if fewer than five batches are used.
1905.6.2.3 Small volume. | When the total volume of concrete is less than 50 cubic yards (38 m3) on a given project, testing may be waived by the registered design professional of record.
1905.6.2.4 Strength test. | A strength test shall be the average of the strengths of two 6 inch by 12 inch (152 mm by 3048 mm) or two 4 inch by 8 inch (102 mm by 203mm) cylinders made from the same sample of concrete and tested at 28 days or at the test age designated for the determination of f’c. Consideration shall be given specifying an f’c at 56 days or later for concrete utilizing pozzolans in the mix proportions. At the discretion of the registered design professional of record or the approved agency performing the testing, additional pairs of test cylinders may be taken at the time of sampling for testing at a later date. The additional cylinders may be tested at a later date should the strength at the specified date not meet the required f’c.
1905.6.3 Standard-cured specimens. | Standard-cured specimens shall comply with the provisions of Sections 1905.6.3.1 through 1905.6.3.9.
1905.6.3.1 Mix Design. | The special inspector shall verify that the proportions indicated on the batch ticket for the concrete delivered to the construction site are as per the approved concrete mix design prior to concrete placement (see Table 1705.3 of this code). Concrete that does not meet the requirements of the approved concrete mix design shall be rejected.
1905.6.3.2 Sampling. | Samples for strength tests shall be taken in accordance with ASTM C 172.
1905.6.3.3 Cylinders. | Cylinders for strength tests shall be molded and standard-cured in accordance with ASTM C 31.
1905.6.3.3.1 On-site curing. | The contractor shall be responsible for providing the specified field storage curing facility and for monitoring the temperature of the cylinders as defined in ASTM C 31.
1905.6.3.3.2 Final curing. | Cylinders shall be placed in final curing conditions meeting the requirements of ASTM C 511. Cylinders shall be transported to final curing conditions by the licensed concrete testing laboratory within 48 hours of casting the cylinders.
1905.6.3.3.3 Compressive strength testing. | The cylinders shall be tested in accordance with ASTM C 39.
1905.6.3.4 Evaluation of results. | The strength level of an individual class of concrete shall be considered satisfactory if both of the following requirements are met:
1905.6.3.5 Correction. | If either of the requirements of Section 1905.6.3.4 is not met, steps shall be taken to increase the average of subsequent strength test results. The requirements of Section 1905.6.5 shall govern if the requirement of Section 1905.6.3.4, Item 2, is not met.
1905.6.3.6 Field testing. | Each time concrete is sampled for strength testing, the tests set forth in Items 1 through 5 shall be performed by the approved agency:
1905.6.3.7 Mass concrete. | For mass concrete sections identified as requiring monitoring, install temperature devices that are capable of measuring the temperature of the concrete continuously and record temperature data in increments that do not exceed 30 minutes for a minimum period of seven days per ACI 301, Section 8.3 or as otherwise directed by the registered design professional of record. In lieu of monitoring a concrete placement for core and outside face temperatures, a computer simulated thermal study may be substituted, if approved by the registered design professional of record. The computer simulated thermal study shall be of the largest section placed for a specific concrete mix proportion and reflect the thermal properties for the specific cementitious materials and quantities in the mix. The thermal study shall include the maximum temperature at which concrete may be placed and the ambient temperature range for concrete placement.
1905.6.3.8 Results of field tests. | The approved agency shall immediately report the results of field tests performed to the contractor and concrete truck driver, or other representative of the concrete producer. If at any time during the concrete operations, the concrete is not in conformance with ASTM C 94, this code, or is otherwise compromised, it shall be rejected. If it is placed, the location of the load shall be recorded and a pair of cylinders shall be molded from the load per ASTM C 31 and included in the average f’c. The approved agency shall keep a written record of all field tests at the construction site and make the records available upon request. These results need not be used in calculating the arithmetic average of consecutive test results required by Section 1905.6.3.4.
1905.6.3.9 Reporting requirements. | Field sampling and testing shall be deemed a special inspection, and the approved agency performing the field sampling and testing of concrete at the construction site shall be subject to the requirements of Section 1704.1.1.2 regarding reporting of deficiencies.
1905.6.4 Field-cured specimens. | Field-cured specimens shall comply with the provisions of Sections 1905.6.4.1 through 1905.6.4.4.
1905.6.4.1 When required. | Where required by the commissioner, the results of strength tests of cylinders cured under field conditions shall be provided to the department.
1905.6.4.2 Curing. | Field-cured cylinders shall be cured under field conditions in accordance with ASTM C 31.
1905.6.4.3 Sampling. | Field-cured test cylinders shall be molded at the same time and from the same samples as laboratory-cured test cylinders.
1905.6.4.4 Correction. | Procedures for protecting and curing concrete shall be improved when the strength of field-cured cylinders at the test age designated for determination of f’ c is less than 85 percent of that of companion laboratory-cured cylinders. The 85-percent limitation shall not apply if the field-cured strength exceeds f ‘ c by more than 500 psi (3.45 MPa).
1905.6.5 Low-strength test results. | The investigation of low-strength test results shall be in accordance with the provisions of Sections 1905.6.5.1 through 1905.6.5.5.
1905.6.5.1 Precaution. | If any strength test of laboratory-cured cylinders performed in accordance with Section 1905.6.2.4 falls below the specified value of f’c by more than the values given in Section 1905.6.3.4, Item 2, or if tests of field-cured cylinders performed in accordance with Section 1905.6.4 indicate deficiencies in protection and curing, steps shall be taken to assure that the load-carrying capacity of the structure is not jeopardized.
1905.6.5.2 Core tests. | Where calculations indicate that load-carrying capacity is significantly reduced, tests of cores drilled from the area in question in accordance with ASTM C 42 shall be permitted. In such cases, three cores shall be taken for each strength test that falls below the values given in Section 1905.6.3.4, Item 2.
1905.6.5.3 Condition of cores. | Cores shall be prepared for transport and storage by wiping drilling water from their surfaces and placing the cores in water-tight bags or containers immediately after drilling. Cores shall be tested not earlier than 48 hours nor later than seven days after coring unless approved by the registered design professional of record.
1905.6.5.4 Test results. | Concrete in an area represented by core tests shall be considered structurally adequate if the average of three cores is equal to at least 85 percent of f’c and if no single core is less than 75 percent of f’c. Additional testing of cores extracted from locations represented by erratic core strength results is permitted.
1905.6.5.5 Strength evaluation. | If the criteria of Section 1905.6.5.4 are not met and the structural adequacy remains in doubt, the commissioner may order a strength evaluation in accordance with ACI 318, Chapter 27, for the questionable portion of the structure, or take other appropriate action. The registered design professional of record shall present to the commissioner a complete analysis showing the final safe load-carrying capacity of the questionable portion of the structure including any proposed remedial actions necessary for review and approval.
1905.6.6 Steel fiber-reinforced concrete. | Steel fiber-reinforced concrete used in beams shall be subject to the requirements of ACI 318, Section 26.12.5. The required testing and inspection of steel fiber-reinforced concrete shall be deemed a special inspection. Steel fibers shall not be used in place of required reinforcing bars.
1905.7 Preparation of equipment and place of deposit. | Preparation before concrete placement shall include the following:
1905.8 Mixing. | Mixing of concrete shall be performed in accordance with Sections 1905.8.1 through 1905.8.3.
1905.8.1 General. | Concrete shall be mixed until there is a uniform distribution of materials and shall be discharged completely before the mixer is recharged. Concrete delivered shall be proportioned in accordance with Section 1905.2.3. Modification to the approved concrete proportions shall be based upon standards acceptable to the commissioner.
1905.8.2 Ready-mixed concrete. | Ready-mixed concrete shall be mixed and delivered in accordance with the requirements of ASTM C 94 or ASTM C 685.
1905.8.2.1 Concrete plants. | Concrete plants shall be certified by the National Ready Mixed Concrete Association (NRMCA), the Concrete Industry Board Concrete Producer Certification Program, or other program acceptable to the department, and shall comply with the rules of the department. Concrete producers shall have their plants inspected quarterly and have their scales and trucks certified. In fulfilling this certification requirement, the concrete producer may present certification by either a New York City government agency, or by the New York State Department of Transportation subject to the approval of the commissioner.
1905.8.2.2 Delivery personnel. | Concrete ready-mix truck drivers shall be certified by the NRMCA and shall comply with the rules of the department.
1905.8.2.3 Batch tickets. | Batch tickets shall accompany every load of concrete delivered to a site. The batch ticket shall contain the information specified in Items 1 through 7:
1905.8.2.3.1 Copies of batch tickets. | A copy of each batch ticket shall be given to the licensed concrete testing laboratory special inspector performing the acceptance testing at the delivery of each load. The licensed laboratory shall maintain copies of the batch tickets along with other inspection reports required by Section 1704.1, and make them available to the department upon request.
1905.8.3 Job-mixed concrete. | Job-mixed concrete shall comply with ACI 318, Section 26.5.
1905.9 Conveying. | The method and equipment for conveying concrete to the place of deposit shall comply with Sections 1905.9.1 and 1905.9.2.
1905.9.1 Method of conveyance. | Concrete shall be conveyed from the mixer to the place of final deposit by methods that will prevent separation or loss of materials that may alter the properties of the concrete delivered. Cylinders shall be made to determine the quality of concrete. Such cylinders shall be made at the truck or at the point of placement of the concrete as determined by the special inspection agency or the registered design professional of record.
1905.9.2 Conveying equipment. | The conveying equipment shall be capable of providing a supply of concrete at the site of placement without separation of ingredients and without interruptions sufficient to permit the loss of plasticity between successive increments.
1905.10 Depositing. | The depositing of concrete shall comply with the provisions of Sections 1905.10.1 through 1905.10.8.
1905.10.1 Segregation. | Concrete shall be deposited as nearly as practicable to its final position to avoid segregation due to rehandling or flowing.
1905.10.2 Placement timing. | Concreting operations shall be carried on at such a rate that the concrete is at all times plastic and flows readily into spaces between reinforcement.
1905.10.3 Unacceptable concrete. | Concrete that has partially hardened or been contaminated by foreign materials shall not be deposited in the structure.
1905.10.4 Retempering. | Retempered concrete or concrete that has been remixed after initial set shall not be used.
1905.10.5 Continuous operation. | After concreting has started, it shall be carried on as a continuous operation until placing of a panel or section, as defined by its boundaries or predetermined joints, is completed, except as permitted or prohibited by Section 1906.4.
1905.10.6 Placement in vertical lifts. | The top surfaces of vertically formed lifts shall be generally level.
1905.10.7 Construction joints. | When construction joints are required, they shall be made in accordance with Section 1906.4.
1905.10.8 Consolidation. | Concrete shall be thoroughly consolidated by suitable means during placement and shall be thoroughly worked around reinforcement and embedded fixtures and into corners of the forms.
1905.11 Curing. | The curing of concrete shall be in accordance with Sections 1905.11.1 through 1905.11.3.
1905.11.1 Regular. | Concrete (other than high early strength) shall be maintained above 50°F (10°C) and in a moist condition for at least the first seven days after placement, except when cured in accordance with Section 1905.11.3.
1905.11.2 High-early-strength. | High-early-strength concrete shall be maintained above 50°F (10°C) and in a moist condition for at least the first three days, except when cured in accordance with Section 1905.11.3.
1905.11.3 Accelerated curing. | Accelerated curing of concrete shall comply with ACI 318, Section 26.5.3.2(c), but concrete temperature shall not exceed 160°F (71°C).
1905.12 Cold weather requirements. | Concrete that is to be placed during freezing or near-freezing weather shall comply with the following:
1905.13 Hot weather requirements. | During hot weather, proper attention shall be given to ingredients, production methods, handling, placing, protection and curing to prevent excessive concrete temperatures or water evaporation that could impair the required strength or serviceability of the member or structure.
1906.1 Formwork. | The design, fabrication and erection of forms shall comply with the requirements of ACI 318, Section 26.11 and Section 3305.3 of this code.
1906.2 Removal of forms, shores and reshores. | The removal of forms and shores, including slabs and beams (except where cast on the ground), and the installation of reshores shall comply with ACI 318, Section 26.11.2 and Section 3305.3 of this code.
1906.3 Conduits and pipes embedded in concrete. | Conduits, pipes and sleeves of any material not harmful to concrete and within the limitations of ACI 318, Section 20.7, are permitted to be embedded in concrete with approval of the registered design professional of record.
1906.4 Construction joints. | Construction joints, including their location, shall comply with the provisions of ACI 318, Section 26.5.6. Construction joints, including their location, shall be approved by the registered design professional of record prior to installation.
1907.1 Hooks. | Standard hooks on reinforcing bars used in concrete construction shall comply with ACI 318, Section 25.3.
1907.2 Minimum bend diameters. | Minimum reinforcement bend diameters utilized in concrete construction shall comply with ACI 318, Section 25.3.2.
1907.3 Bending. | The bending of reinforcement shall comply with Sections 1907.3.1 and 1907.3.2.
1907.3.1 Cold bending. | Reinforcement shall be bent cold, unless otherwise permitted by the registered design professional of record.
1907.3.2 Embedded reinforcement. | Reinforcement partially embedded in concrete shall not be field bent, except as shown on the construction documents or permitted by the registered design professional of record.
1907.4 Surface conditions of reinforcement. | The surface conditions of reinforcement shall comply with the provisions of Sections 1907.4.1 through 1907.4.3.
1907.4.1 Coatings. | At the time concrete is placed, reinforcement shall be free from mud, oil or other nonmetallic coatings that decrease bond. Zinc and epoxy-coating of steel reinforcement in accordance with ACI 318, Section 20.6.2 shall be permitted.
1907.4.2 Rust or mill scale. | Except for prestressing reinforcement, steel reinforcement with rust, mill scale or a combination of both, shall be permitted, provided the minimum dimensions, including height of deformations and weight of a hand-wire-brushed test specimen, comply with applicable ASTM specifications specified in Section 1903.6.
1907.4.3 Prestressing reinforcement. | Prestressing reinforcement shall be clean and free of oil, dirt, scale, pitting and excessive rust. A light coating of rust is permitted.
1907.5 Placing reinforcement. | The placement of concrete reinforcement shall comply with the provisions of Sections 1907.5.1 through 1907.5.4.
1907.5.1 Support. | Reinforcement, including tendons, and posttensioning ducts shall be accurately placed and adequately supported before concrete is placed, and shall be secured against displacement within tolerances permitted in Section 1907.5.2. Where approved by the registered design professional of record, embedded items (such as dowels or inserts) that either protrude from precast concrete members or remain exposed for inspection are permitted to be embedded while the concrete is in a plastic state, provided the following conditions are met:
1907.5.2 Tolerances. | Unless otherwise specified by the registered design professional of record, reinforcement, including tendons, and posttensioning ducts shall be placed within the tolerances specified in Sections 1907.5.2.1 and 1907.5.2.2.
1907.5.2.1 d and cover. | Tolerance for d and concrete cover shall be as required in ACI 318, Section 26.6.2.1(a).
1907.5.2.2 Bends and ends. | Tolerance for longitudinal location of bends and ends of reinforcement shall be as required by ACI 318, Section 26.6.2.1(b).
1907.5.3 Welded wire reinforcement. | Welded wire reinforcement with wire size not greater than W5 or D5 used in slabs not exceeding 10 feet (3048 mm) in span is permitted to be curved from a point near the top of the slab over the support to a point near the bottom of the slab at midspan, provided such reinforcement is either continuous over, or securely anchored at support.
1907.5.4 Welding. | Welding of crossing bars shall not be permitted for assembly of reinforcement unless authorized by the registered design professional of record.
1907.6 Minimum spacing of reinforcement. | The clear distance between reinforcing bars, bundled bars, tendons and ducts shall comply with ACI 318, Section 25.2.
1907.7 Concrete protection for reinforcement. | The minimum concrete cover for reinforcement shall comply with Sections 1907.7.1 through 1907.7.8.
1907.7.1 Cast-in-place concrete (nonprestressed). | Minimum specified concrete cover shall be provided for reinforcement in nonprestressed cast-in-place concrete construction in accordance with ACI 318, Section 20.6.1.3.1, but shall not be less than required by Sections 1907.7.6 and 1907.7.8 of this code.
1907.7.2 Cast-in-place concrete (prestressed). | The minimum specified concrete cover for prestressed and nonprestressed reinforcement, ducts and end fittings in cast-in-place prestressed concrete shall comply with ACI 318, Section 20.6.1.3.2.
1907.7.3 Precast concrete (manufactured under plant control conditions). | The minimum specified concrete cover for prestressed and nonprestressed reinforcement, ducts and end fittings in precast concrete manufactured under plant control conditions shall comply with ACI 318, Section 20.6.1.3.3.
1907.7.4 Bundled bars. | The minimum specified concrete cover for bundled bars shall comply with ACI 318, Section 20.6.1.3.4.
1907.7.5 Headed shear stud reinforcement. | For headed shear stud reinforcement, the minimum specified concrete cover shall comply with ACI 318, Section 20.6.1.3.5.
1907.7.6 Corrosive environments. | In corrosive environments or other severe exposure conditions, prestressed and nonprestressed reinforcement shall be provided with additional protection in accordance with ACI 318, Section 20.6.1.4.
1907.7.7 Future extensions. | Exposed reinforcement, inserts and plates intended for bonding with future extensions shall be protected from corrosion.
1907.7.8 Fire protection. | When this code requires a thickness of cover for fire protection greater than the minimum concrete cover in Section 1907.7, such greater thickness shall be specified on the construction documents.
1907.8 Special reinforcement details for columns. | Offset bent longitudinal bars in columns and load transfer in structural steel cores of composite compression members shall comply with the provisions of ACI 318, Section 10.7.4.
1907.9 Connections. | Connections between concrete framing members shall comply with the provisions of ACI 318, Chapters 15 and 16.
1907.10 Transverse reinforcement for compression members. | Transverse reinforcement for compression members shall comply with the provisions of ACI 318, Section 25.7.2.
1907.11 Transverse reinforcement for flexural members. | Transverse reinforcement for compression reinforcement in flexural members shall comply with the provisions of ACI 318, Section 25.7.1.
1907.12 Shrinkage and temperature reinforcement. | Reinforcement for shrinkage and temperature stresses in concrete members shall comply with the provisions of ACI 318, Section 24.4.
1907.13 Requirements for structural integrity. | The detailing of reinforcement and connections between concrete members shall comply with the provisions of ACI 318, Section 4.10 and Section 1912 of this code.
1908.1 General. | The text of ACI 318 shall be modified as indicated in Sections 1908.1.1 through 1908.1.10. | 1908.1 General. | Shotcrete shall be in accordance with the requirements of ACI 318.
1908.1.1 ACI 318, Section 2. | 3. Modify existing definitions and add the following definitions to ACI 318, Section 2.3.
1908.1.2 ACI 318, Section 8. | 7.2. Modify ACI 318, Section 8.7.2.3 and 8.7.2.4, and add new sections 8.7.2.5 and 8.7.2.6 to read as follows:
1908.1.3 ACI 318, Section 14. | 1.4. Delete ACI 318, Section 14.1.4 and replace with the following: 14.1.4 – Plain concrete in structures assigned to Seismic Design Category C or D. 14.1.4.1 – Structures assigned to Seismic Design Category C or D shall not have elements of structural plain concrete, except as follows: (a) Structural plain concrete basement, foundation or other walls below the base, as defined in ASCE 7, are permitted in detached one- and two-family dwellings three stories or less in height constructed with stud-bearing walls. In dwellings assigned to Seismic Design Category D, the height of the wall shall not exceed 8 feet (2438 mm), the thickness shall be not less than 7½ inches (190 mm), and the wall shall retain no more than 4 feet (1219 mm) of unbalanced fill. Walls shall have reinforcement in accordance with 14.6.1. (b) Isolated footings of plain concrete supporting pedestals or columns are permitted, provided the projection of the footing beyond the face of the supported member does not exceed the footing thickness. Exception: In detached one- and two-family dwellings three stories or less in height, the projection of the footing beyond the face of the supported member is permitted to exceed the footing thickness. (c) Plain concrete footings supporting walls are permitted, provided the footings have at least two continuous longitudinal reinforcing bars. Bars shall not be smaller than No. 4 and shall have a total area of not less than 0.002 times the gross cross-sectional area of the footing. For footings that exceed 8 inches (203 mm) in thickness, a minimum of one bar shall be provided at the top and bottom of the footing. Continuity of reinforcement shall be provided at corners and intersections. Exceptions: 1. In Seismic Design Categories A, B and C, detached one- and two-family dwellings three stories or less in height constructed with stud-bearing walls are permitted to have plain concrete footings without longitudinal reinforcement. 2. For foundation systems consisting of a plain concrete footing and a plain concrete stemwall, a minimum of one bar shall be provided at the top of the stem wall and at the bottom of the footing. 3. Where a slab on ground is cast monolithically with the footing, one No. 5 bar is permitted to be located at either the top of the slab or bottom of the footing.
1908.1.4 ACI 318, Section 14. | 6. Modify ACI 318, Section 14.6 by adding new Section 14.6.2 to read as follows:
1908.1.5 ACI 318, Section 15. | 3. Modify ACI 318 by adding Section 15.3.2 to read as follows:
1908.1.6 ACI 318, Section 17. | 2.3. Modify ACI 318 Sections 17.2.3.4.2, 17.2.3.4.3(d) and 17.2.3.5.2 to read as follows: 17.2.3.4.2 – Where the tensile component of the strength-level earthquake force applied to anchors exceeds 20 percent of the total factored anchor tensile force associated with the same load combination, anchors and their attachments shall be designed in accordance with 17.2.3.4.3. The anchor design tensile strength shall be determined in accordance with 17.2.3.4.4. Exception: Anchors designed to resist wall out-of-plane forces with design strengths equal to or greater than the force determined in accordance with ASCE 7 Equation 12.11-1 or 12.14-10 shall be deemed to satisfy Section 17.2.3.4.3(d). 17.2.3.4.3(d) – The anchor or group of anchors shall be designed for the maximum tension obtained from design load combinations that include E, with E increased by Ω0. The anchor design tensile strength shall be calculated from 17.2.3.4.4. 17.2.3.5.2 – Where the shear component of the strength-level earthquake force applied to anchors exceeds 20 percent of the total factored anchor shear force associated with the same load combination, anchors and their attachments shall be designed in accordance with 17.2.3.5.3. The anchor design shear strength for resisting earthquake forces shall be determined in accordance with 17.5. Exceptions: 1. For the calculation of the in-plane shear strength of anchor bolts attaching wood sill plates of bearing or nonbearing walls of light-frame wood structures to foundations or foundation stem walls, the in-plane shear strength in accordance with 17.5.2 and 17.5.3 need not be computed and 17.2.3.5.3 shall be deemed to be satisfied provided all of the following are met: 1.1. The allowable in-plane shear strength of the anchor is determined in accordance with AWC NDS Table 12E for lateral design values parallel to grain. 1.2. The maximum anchor nominal diameter is ⅝ inch (16 mm). 1.3. Anchor bolts are embedded into concrete a minimum of 7 inches (178 mm). 1.4. Anchor bolts are located a minimum of 1¾ inches (45 mm) from the edge of the concrete parallel to the length of the wood sill plate. 1.5. Anchor bolts are located a minimum of 15 anchor diameters from the edge of the concrete perpendicular to the length of the wood sill plate. 1.6. The sill plate is 2-inch (51 mm) or 3-inch (76 mm) nominal thickness. 2. For the calculation of the in-plane shear strength of anchor bolts attaching cold-formed steel track of bearing or nonbearing walls of light-frame construction to foundations or foundation stem walls, the in-plane shear strength in accordance with 17.5.2 and 17.5.3 need not be computed and 17.2.3.5.3 shall be deemed to be satisfied provided all of the following are met: 2.1. The maximum anchor nominal diameter is ⅝ inch (16 mm). 2.2. Anchors are embedded into concrete a minimum of 7 inches (178 mm). 2.3. Anchors are located a minimum of 1¾ inches (45 mm) from the edge of the concrete parallel to the length of the track. 2.4. Anchors are located a minimum of 15 anchor diameters from the edge of the concrete perpendicular to the length of the track. 2.5. The track is 33 to 68 mil (0.84 mm to 1.73 mm) designation thickness. Allowable in-plane shear strength of exempt anchors, parallel to the edge of concrete, shall be permitted to be determined in accordance with AISI S100, Section J3.3.1. 3. In light-frame construction bearing or non-bearing walls, shear strength of concrete anchors less than or equal to 1 inch (25 mm) in diameter attaching sill plate or track to foundation or foundation stem wall need not satisfy 17.2.3.5.3(a) through (c) when the design strength of the anchors is determined in accordance with 17.5.2.1(c).
1908.1.7 ACI 318, Section 18. | 2.1. Modify ACI 318 Sections 18.2.1.2 and 18.2.1.6 to read as follows:
1908.1.8 ACI 318, Section 18. | 5. Modify ACI 318, Section 18.5, by adding new Section 18.5.2.2 and renumbering existing Sections 18.5.2.2 and 18.5.2.3 to become 18.5.2.3 and 18.5.2.4, respectively.
1908.1.9 ACI 318, Section 18. | 11. Modify ACI 318, Section 18.11.2 to read as follows:
1908.1.10 ACI 318, Section 18. | 13.1.1. Modify ACI 318, Section 18.13.1.1, to read as follows:
1908.1.11 ACI 318, Section 24. | 2.3.5. Add the following to Section 24.2.3.5:
1909.1 Scope. | The design and construction of structural plain concrete, both cast-in-place and precast, shall comply with the minimum requirements of ACI 318, as modified by Section 1908 of this chapter. Exception: For Group R-3 occupancies and buildings of other occupancies less than two stories above grade plane of light-frame construction, the required footing thickness of ACI 318 is permitted to be reduced to 6 inches (152 mm), provided that the footing does not extend more than 4 inches (102 mm) on either side of the supported wall.
1910.1 General. | The thickness of concrete floor slabs supported directly on the ground shall not be less than 3½ inches (89 mm). A 6-mil (0.006 inch; 0.15 mm) polyethylene vapor retarder with joints lapped not less than 6 inches (152 mm) shall be placed between the base course or subgrade and the concrete floor slab, or other approved equivalent methods or materials shall be used to retard vapor transmission through the floor slab. Exception: A vapor retarder is not required: 1. For detached structures accessory to occupancies in Group R-3, such as garages, utility buildings or other unheated facilities. 2. For unheated storage rooms having an area of less than 70 square feet (6.5 m2) and carports attached to occupancies in Group R-3. 3. For buildings of other occupancies where migration of moisture through the slab from below will not be detrimental to the intended occupancy of the building. 4. For drive ways, walks, patios and other flat work that will not be enclosed at a later date. 5. Where approved based on local site conditions.
1911.1 General. | Shotcrete is mortar or concrete that is pneumatically projected at high velocity onto a surface. Except as specified in this section, shotcrete shall conform to the requirements of this chapter for plain or reinforced concrete.
1911.1.1 Qualifications. | Nozzlemen shall be ACI certified.
1911.2 Proportions and materials. | Shotcrete proportions shall be selected that allow suitable placement procedures using the delivery equipment selected and shall result in finished in-place hardened shotcrete meeting the strength requirements of this code. Prior to using shotcrete, the mix design for shotcrete shall be performed by the contractor and shall be approved by the registered design professional of record. The approved mix design shall be filed with the department based upon preconstruction tests performed in accordance with Section 1911.5.
1911.3 Aggregate. | Coarse aggregate, if used, shall not exceed ¾ inch (19.1 mm).
1911.4 Reinforcement. | Reinforcement used in shotcrete construction shall comply with the provisions of Sections 1911.4.1 through 1911.4.4.
1911.4.1 Size. | The maximum size of reinforcement shall be No. 5 bars unless it is demonstrated by preconstruction tests that adequate encasement of larger bars will be achieved.
1911.4.2 Clearance. | When No. 5 or smaller bars are used, there shall be a minimum clearance between parallel reinforcement bars of 2½ inches (64 mm). When bars larger than No. 5 are permitted, there shall be a minimum clearance between parallel bars equal to six diameters of the bars used. When two curtains of steel are provided, the curtain nearer the nozzle shall have a minimum spacing equal to 12 bar diameters and the remaining curtain shall have a minimum spacing of six bar diameters. Exception: Subject to the approval of the commissioner, required clearances shall be reduced where it is demonstrated by preconstruction tests that adequate encasement of the bars used in the design will be achieved.
1911.4.3 Splices. | Lap splices of reinforcing bars shall utilize the noncontact lap splice method with a minimum clearance of 2 inches (51 mm) between bars. The use of contact lap splices necessary for support of the reinforcing is permitted when approved by the commissioner, based on satisfactory preconstruction tests that show that adequate encasement of the bars will be achieved, and provided that the splice is oriented so that a plane through the center of the spliced bars is perpendicular to the surface of the shotcrete.
1911.4.4 Spirally tied columns. | Shotcrete shall not be applied to spirally tied columns.
1911.5 Preconstruction tests. | A test panel shall be shot by each nozzleman and then, cured, cored or sawn, examined and tested prior to commencement of the project. The sample panel shall be representative of the project and simulate job conditions as closely as possible. The panel thickness and reinforcing shall reproduce the thickest and most congested area specified in the structural design. It shall be shot for each proposed concrete mix, at the proposed angles. The equipment used in preconstruction testing shall be the same equipment used in the work requiring such testing, unless substitute equipment is approved by the commissioner. Cores taken from the test panel shall be used to demonstrate that the proposed mix design meets the requirements of the construction documents and this code. All sampling and testing of shotcrete shall be performed by a licensed concrete testing laboratory. Construction of the test panels shall be witnessed by the special inspection agency responsible for the shotcrete construction.
1911.5.1 Sampling and testing. | Six core samples shall be obtained from each preconstruction test panel:
1911.5.2 Compressive strength testing. | The licensed concrete testing laboratory that sampled the preconstruction test panels shall test the core specimens with no reinforcing in accordance with ASTM C 39.
1911.5.3 Evaluation of strength tests. | The shotcrete test panel strength shall be deemed acceptable if the mean compressive strength of the set of three cores shall equal or exceed f’c with no individual core less than 0.75 f’c.
1911.5.4 Visual grading of cores. | Core samples and/or test panels shall be cut with reinforcing steel and shall be visually evaluated by the registered design professional of record for the structural design, or a registered design professional acceptable to the registered design professional of record for the structural design. The nozzleman shall not proceed with work if cores and/or sections cut show the rebar not to be encapsulated with concrete to the satisfaction of the registered design professional of record for the structural design.
1911.6 Rebound. | Any rebound or accumulated loose aggregate shall be removed from the surfaces to be covered prior to placing the initial or any succeeding layers of shotcrete. Rebound shall not be used as aggregate.
1911.7 Joints. | Except where permitted herein, unfinished work shall not be allowed to stand for more than 30 minutes unless edges are sloped to a thin edge. For structural elements that will be under compression and for construction joints shown on the approved construction documents, square joints are permitted. Before placing additional material adjacent to previously applied work, sloping and square edges shall be cleaned and wetted.
1911.8 Damage. | In-place shotcrete that exhibits sags, sloughs, segregation, honeycombing, sand pockets or other obvious defects shall be removed and replaced. Shotcrete above sags and sloughs shall be removed and replaced while still plastic.
1911.9 Curing. | During the curing periods specified herein, shotcrete shall be maintained above 40°F (4°C) and in moist condition.
1911.9.1 Initial curing. | Shotcrete shall be kept continuously moist for 24 hours after shotcreting is complete or shall be sealed with an approved curing compound.
1911.9.2 Final curing. | Final curing shall continue for seven days after shotcreting, or for three days if high-early-strength cement is used, or until the specified strength is obtained. Final curing shall consist of the initial curing process or the shotcrete shall be covered with an approved moisture-retaining cover.
1911.9.3 Natural curing. | Natural curing shall not be used in lieu of that specified in this section unless the relative humidity remains at or above 85 percent, and is authorized by the registered design professional of record and approved by the commissioner.
1911.10 Strength tests. | Strength tests for shotcrete shall be made by an approved agency on specimens that are representative of the work, and that are sampled and prepared in accordance with ASTM C 42.
1911.10.1 Sampling. | Specimens shall be taken from the in-place work or from test panels, and shall be taken at least once each shift, but not less than three cores for each 50 cubic yards (38.2 m3) of shotcrete. With the approval of the registered design professional of record, when in-place cores are not feasible due to rebar spacing, test panels shall be shot in the same position as the work represented. One panel shall be cast for each 50 cubic yards (38.2 m3) of concrete and 3 cores shall be taken per ASTM C 42.
1911.10.2 Panel criteria. | When the maximum-size aggregate is larger than ⅜ inch (9.5 mm), the test panels shall have minimum dimensions of 18 inches by 18 inches (457 mm by 457 mm). When the maximum-size aggregate is ⅜ inch (9.5 mm) or smaller, the test panels shall have minimum dimensions of 12 inches by 12 inches (305 mm by 305 mm). Panels shall be shot in the same position as the work, during the course of the work and by the nozzlemen doing the work. The conditions under which the panels are cured shall be the same as the work.
1911.10.3 Acceptance criteria. | The average compressive strength of three cores from the in-place work tested in accordance with ASTM C 39 shall equal or exceed 0.85 f’c with no single core less than 0.75 f’c. The average compressive strength of three cubes taken from the in-place work or a single test panel shall equal or exceed f’c with no individual cube less than 0. 88 f’c. To check accuracy, locations represented by erratic core or cube strengths shall be retested.
1912.1 General. | Reinforced concrete structures shall meet all the requirements of Sections 1912.1 through 1912.3. Concrete slabs on metal deck shall be governed by the provisions of Chapter 22. Reinforcement provided for gravity, seismic and wind forces or for other purposes may be regarded as forming part of, or the whole of, these requirements. Reinforcing provided for one requirement may be counted towards the other requirements.
1912.2 Continuity and ties. | The structural integrity requirements of ACI 318, Sections 4.10 and 8.7.4.2, shall apply. In addition, the following requirements shall be met.
1912.2.1 Slab reinforcement. | At all floor and roof levels, slabs shall have a mat of bottom reinforcement in two perpendicular (or roughly perpendicular) directions. Reinforcement in this bottom mat shall be made continuous with lap, mechanical or welded tension splices.
1912.2.1.1 Bottom mat reinforcement. | In each direction, the bottom mat reinforcement shall be not less than, the steel required for temperature reinforcement. The bottom mat reinforcement shall be anchored at discontinuous edges within the column strip, reentrant corners, elevation changes and anywhere else the continuity of the reinforcing is interrupted. Exception: Flat plate middle strip bottom mat reinforcing perpendicular to discontinuous slab edges. In addition, the main bottom mat reinforcement in one-way slabs shall be anchored at discontinuous edges.
1912.2.2 Peripheral ties. | At each floor and roof level, reinforcement forming a continuous peripheral tie shall be provided. Peripheral ties shall be located within perimeter beams or walls, where they occur, or within 4 feet (1219 mm) of the edge of slab, where perimeter beams or walls do not occur. Continuous tie reinforcement shall be equal to half of the bottom reinforcement within the edge or edge strip for two-way slabs but not less than two bars.
1912.2.3 Horizontal ties. | At each column, beam reinforcement or slab bottom reinforcement shall be provided at each level that can develop a tension force equal to the maximum of Item 1 or 2:
1912.2.3.1 Bottom reinforcing. | This beam or slab bottom reinforcement shall be distributed around the column perimeter and shall be extended on all sides of the column into the adjacent slab for at least one-third of the span length. Where reinforcing bars cannot be extended beyond the column (e.g., at slab edges and openings), they shall be hooked or otherwise developed within the column.
1912.2.4 Vertical ties. | Each column and each wall carrying vertical load shall be vertically tied continuously from its lowest to highest level. The vertical ties composed of vertical column reinforcement shall be capable of resisting a tensile force equal to the maximum design dead and live load received by the column or wall from any one story within four floors below. A concrete compression element subjected to load reversal may have a reinforcing bar splice length equal to the tension splice length required by ACI 318 reduced by the ratio of As required/As, provided but not less than the splice required for compression.
1912.3 Precast concrete general. | Precast concrete structural elements shall be reinforced to meet all of the requirements of this section. However, reinforcement provided for gravity, seismic and wind forces and for other purposes may be regarded as forming part of, or the whole of, these requirements. Reinforcing provided for one requirement may be counted towards the other requirements.
1912.3.1 Continuity and ties. | The structural integrity requirements of ACI 318, Section 4.10, shall apply. In precast and composite structures, ties within precast structural elements shall be continuous and shall be anchored to the supporting structure. In addition to Sections 1912.2.2 and 1912.2.4, the following requirements shall be met.
1912.3.1.1 End connections. | End connections of all precast slabs, beams and girders shall have an axial tension capacity equal to the larger of the vertical shear capacity of the connection at either end, or at least 2 percent of the maximum factored vertical dead and live load in the precast compression element, whichever is larger, but not less than 20 kips or 2,500 pounds per linear foot of slab (36.48 kN/m). Where more than one element frames in one direction, none of the elements or connections shall have an axial tension capacity of less than 1 percent of the column load but not less than 20 kips.
1912.3.1.2 Side connections. | Side connections of all precast elements shall have an axial tension capacity not less than the steel required for temperature reinforcement of the larger element at either side.
1912.3.1.3 Connection forces. | For design of the connections, the transverse shear force and the axial tensile force need not be considered to act simultaneously.
1912.3.2 Joints. | Joints in precast structures shall not rely on friction due to gravity to transfer load.
1912.3.3 Bearing. | The net bearing area shall not be less than 2 inches (51 mm) wide and 3 inches (76 mm) long in the direction of the member.
1913.1 Definitions. | The following terms are defined in Chapter 2.
1913.2 Reclaimed asphalt pavement content in asphaltic concrete. | Asphaltic concrete, other than I-4 mix or other approved heavy duty asphaltic concrete mix, shall contain not less than 30 percent reclaimed asphalt pavement, as measured by weight. I-4 mix or other approved heavy duty asphaltic concrete mix shall contain not less than 10 percent reclaimed asphalt pavement, as measured by weight. Reclaimed asphalt paving used in asphaltic concrete shall comply with ASTM D692 or ASTM D1073. Exceptions: 1. Asphaltic concrete used in a project where the content of asphaltic concrete is governed by a federal or state law, rule, regulation, guideline, or specification that requires a different composition. 2. Asphaltic concrete used for runways, taxiways, or other surfaces utilized by aircraft. 3. The commissioner may waive compliance with this section if the commissioner, after consulting with the commissioner of transportation and the owners or persons in charge of all asphalt plants located within the city, finds that a sufficient supply of reclaimed asphalt pavement is not available.
|  | 1901.7 Tolerances for structural concrete. | Where not indicated in construction documents, structural tolerances for concrete structural elements shall be in accordance with this section.
|  | 1901.7.1 Cast-in-place concrete tolerances. | Structural tolerances for cast-in-place concrete structural elements shall be in accordance with ACI 117. Exceptions: 1. Group R-3 detached one- or two-family dwellings are not required to comply with this section. 2. Shotcrete is not required to comply with this section.
|  | 1901.7.2 Precast concrete tolerances. | Structural tolerances for precast concrete structural elements shall be in accordance with ACI ITG-7. Exception: Group R-3 detached one- or two-family dwellings are not required to comply with this section.
|  | 1902.1 General. | Coordination of terminology used in ACI 318 and ASCE 7 shall be in accordance with Sections 1902.1.1 and 1902.1.2.
|  | 1902.1.1 Design displacement. | Design displacement at each level shall be the total lateral deflection at the level calculated for the design earthquake using the procedures defined in Section 12.8.6 of ASCE 7.
|  | 1902.1.2 Special structural wall. | Special structural walls made of cast-in-place or precast concrete shall comply with the requirements of Sections 18.2.4 through 18.2.8, 18.10 and 18.11 of ACI 318, as applicable, in addition to the requirements for ordinary reinforced concrete structural walls or ordinary precast structural walls, as applicable. Where ASCE 7 refers to a special reinforced concrete shear wall, it shall be deemed to mean a special structural wall.
|  | 1904.1 Structural concrete. | Structural concrete shall conform to the durability requirements of ACI 318. Exception: For Group R-2 and R-3 occupancies not more than three stories above grade plane, the specified com-pressive strength, f´c, for concrete in basement walls, foundation walls, exterior walls and other vertical surfaces ex-posed to the weather shall be not less than 3,000 psi (20.7 MPa).
|  | 1904.2 Nonstructural concrete. | The registered design professional shall assign nonstructural concrete a freeze-thaw exposure class, as defined in ACI 318, based on the anticipated exposure of nonstructural concrete. Nonstructural concrete shall have a minimum specified compressive strength, f´c, of 2,500 psi (17.2 MPa) for Class F0; 3,000 psi (20.7 MPa) for Class F1; and 3,500 psi (24.1 MPa) for Classes F2 and F3. Nonstructural concrete shall be air entrained in accordance with ACI 318.
|  | 1905.1.1 ACI 318, Section 2. | 3. Modify existing definitions and add the following definitions to ACI 318, Section 2.3.
|  | 1905.1.2 ACI 318, Section 18. | 2.1. Modify ACI 318 Sections 18.2.1.2 and 18.2.1.6 to read as follows:
|  | 1905.1.3 ACI 318, Section 18. | 5. Modify ACI 318, Section 18.5 by adding new Section 18.5.2.2 and renumbering existing Sections 18.5.2.2 and 18.5.2.3 to become 18.5.2.3 and 18.5.2.4, respectively.
|  | 1905.1.4 ACI 318, Section 18. | 11. Modify ACI 318, Section 18.11.2.1 to read as follows:
|  | 1905.1.5 ACI 318, Section 18. | 13.1.1. Modify ACI 318, Section 18.13.1.1 to read as follows:
|  | 1905.1.6 ACI 318, Section 14. | 6. Modify ACI 318, Section 14.6 by adding new Section 14.6.2 to read as follows:
|  | 1905.1.7 ACI 318, Section 14. | 1.4. Delete ACI 318, Section 14.1.4 and replace with the following: 14.1.4 – Plain concrete in structures assigned to Seismic Design Category C, D, E or F. 14.1.4.1 – Structures assigned to Seismic Design Category C, D, E or F shall not have elements of structural plain concrete, except as follows: • Structural plain concrete basement, foundation or other walls below the base as defined in ASCE 7 are permitted in detached one- and two-family dwellings three stories or less in height constructed with stud-bearing walls. In dwellings assigned to Seismic Design Category D or E, the height of the wall shall not ex-ceed 8 feet (2438 mm), the thickness shall be not less than 71/2 inches (190 mm), and the wall shall retain no more than 4 feet (1219 mm) of unbalanced fill. Walls shall have reinforcement in accordance with 14.6.1. • Isolated footings of plain concrete supporting pedestals or columns are permitted, provided the projection of the footing beyond the face of the supported member does not exceed the footing thickness. Exception: In detached one- and two-family dwellings three stories or less in height, the projection of the footing beyond the face of the supported member is permitted to exceed the footing thickness. • Plain concrete footings supporting walls are permitted, provided the footings have at least two continuous longitudinal reinforcing bars. Bars shall not be smaller than No. 4 and shall have a total area of not less than 0.002 times the gross cross-sectional area of the footing. For footings that exceed 8 inches (203 mm) in thickness, a minimum of one bar shall be provided at the top and bottom of the footing. Continuity of re-inforcement shall be provided at corners and intersections. Exceptions: 1. In Seismic Design Categories A, B and C, detached one- and two-family dwellings three stories or less in height constructed with stud-bearing walls are permitted to have plain concrete foot-ings without longitudinal reinforcement. 2. For foundation systems consisting of a plain concrete footing and a plain concrete stemwall, a minimum of one bar shall be provided at the top of the stemwall and at the bottom of the footing. 3. Where a slab on ground is cast monolithically with the footing, one No. 5 bar is permitted to be located at either the top of the slab or bottom of the footing.
|  | 1905.1.8 ACI 318, Section 17. | 2.3. Modify ACI 318 Sections 17.2.3.4.2, 17.2.3.4.3(d) and 17.2.3.5.2 to read as follows:
|  | 1906.1 Plain concrete footings. | For Group R-3 occupancies and buildings of other occupancies less than two stories above grade plane of light-frame construction, the required thickness of plain concrete footings is permitted to be 6 inches (152 mm), provided that the footing does not extend more than 4 inches (102 mm) on either side of the supported wall.
|  | 1907.1 General. | The thickness of concrete floor slabs supported directly on the ground shall be not less than 31/2 inches (89 mm). A 6-mil (0.006 inch; 0.15 mm) polyethylene vapor retarder with joints lapped not less than 6 inches (152 mm) shall be placed between the base course or subgrade and the concrete floor slab, or other approved equivalent methods or materials shall be used to retard vapor transmission through the floor slab. Exception: A vapor retarder is not required: 1. For detached structures accessory to occupancies in Group R-3, such as garages, utility buildings or other un-heated facilities. 2. For unheated storage rooms having an area of less than 70 square feet (6.5 m2) and carports attached to occu-pancies in Group R-3. 3. For buildings of other occupancies where migration of moisture through the slab from below will not be detri-mental to the intended occupancy of the building. 4. For driveways, walks, patios and other flatwork that will not be enclosed at a later date. 5. Where approved based on local site conditions.
|  | 1905.1.8 ACI 318, Section 17.2.3 | Modify ACI 318 Sections 17.2.3.4.2, 17.2.3.4.3(d) and 17.2.3.5.2 to read as follows: • 17.2.3.4.2 – Where the tensile component of the strength-level earthquake force applied to anchors exceeds 20 percent of the total factored anchor tensile force associated with the same load combination, anchors and their attachments shall be designed in accordance with 17.2.3.4.3. The anchor design tensile strength shall be determined in accordance with 17.2.3.4.4. Exception: Anchors designed to resist wall out-of-plane forces with design strengths equal to or greater than the force determined in accordance with ASCE 7 Equation 12.11-1 or 12.14-10 shall be deemed to satisfy Section 17.2.3.4.3(d). • 17.2.3.4.3(d) – The anchor or group of anchors shall be designed for the maximum tension obtained from de-sign load combinations that include E, with E increased by Ω0. The anchor design tensile strength shall be cal-culated from 17.2.3.4.4. • 17.2.3.5.2 – Where the shear component of the strength-level earthquake force applied to anchors exceeds 20 percent of the total factored anchor shear force associated with the same load combination, anchors and their attachments shall be designed in accordance with 17.2.3.5.3. The anchor design shear strength for resisting earthquake forces shall be determined in accordance with 17.5. Exceptions: 1. For the calculation of the in-plane shear strength of anchor bolts attaching wood sill plates of bearing or nonbearing walls of light-frame wood structures to foundations or foundation stem walls, the in-plane shear strength in accordance with 17.5.2 and 17.5.3 need not be computed and 17.2.3.5.3 shall be deemed to be satisfied provided all of the following are met: 1.1. The allowable in-plane shear strength of the anchor is determined in accordance with ANSI/AWC NDS Table 12E for lateral design values parallel to grain. 1.2. The maximum anchor nominal diameter is 5/8 inch (16 mm). 1.3. Anchor bolts are embedded into concrete a minimum of 7 inches (178 mm). 1.4. Anchor bolts are located a minimum of 13/4 inches (45 mm) from the edge of the concrete parallel to the length of the wood sill plate. 1.5. Anchor bolts are located a minimum of 15 anchor diameters from the edge of the concrete perpendicular to the length of the wood sill plate. 1.6. The sill plate is 2-inch (51 mm) or 3-inch (76 mm) nominal thickness. 2. For the calculation of the in-plane shear strength of anchor bolts attaching cold-formed steel track of bearing or nonbearing walls of light-frame construction to foundations or foundation stem walls, the in-plane shear strength in accordance with 17.5.2 and 17.5.3 need not be computed and 17.2.3.5.3 shall be deemed to be satisfied provided all of the following are met: 2.1. The maximum anchor nominal diameter is 5/8 inch (16 mm). 2.2. Anchors are embedded into concrete a minimum of 7 inches (178 mm). 2.3. Anchors are located a minimum of 13/4 inches (45 mm) from the edge of the concrete par-allel to the length of the track. 2.4. Anchors are located a minimum of 15 anchor diameters from the edge of the concrete per-pendicular to the length of the track. 2.5. The track is 33 to 68 mil (0.84 mm to 1.73 mm) designation thickness. Allowable in-plane shear strength of exempt anchors, parallel to the edge of concrete, shall be permitted to be determined in accordance with AISI S100 Section E3.3.1. 3. In light-frame construction bearing or nonbearing walls, shear strength of concrete anchors less than or equal to 1 inch [25 mm] in diameter attaching sill plate or track to foundation or founda-tion stem wall need not satisfy 17.2.3.5.3(a) through (c) when the design strength of the anchors is determined in accordance with 17.5.2.1(c).

## BC20
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2001.1 Scope. | This chapter shall govern the quality, design, fabrication and erection of aluminum. | 2001.1 Scope. | This chapter shall govern the quality, design, fabrication and erection of aluminum.
2002.1 General. | Aluminum used for structural purposes in buildings and structures shall comply with AA ASM 35 and AA ADM unless otherwise restricted by this code. The nomi­nal loads shall be the minimum design loads required by Chap­ter 16 of this code. | 2002.1 General. | Aluminum used for structural purposes in buildings and structures shall comply with AA ASM 35 and AA ADM. The nominal loads shall be the minimum design loads required by Chapter 16.
2003.1 Identification. | Aluminum for structural elements shall at all times in the fabricator’s plant, be marked, segregated, or otherwise handled so that the separate alloys and tempers are positively identified, and after completion of fabrication shall be marked to identify the alloy and temper. Such markings shall be affixed to completed members and assemblies or to boxed or bundled shipments of multiple units prior to shipment from the fabricator’s plant.
2003.2 Quality control. | In addition to the requirements of Section 2002, the quality control of aluminum used for structural purposes shall comply with Sections 2003.2.1 and 2003.2.2.
2003.2.1 Reference. | Welding operations shall be subjected to the special inspections as required by Chapter 17 of this code.
2003.2.2 Welding operations. | Welding operations per­formed on aluminum used for structural purposes shall comply with the following:

## BC21
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2101.1 Scope. | This chapter shall govern the materials, design, construction and quality of masonry. | 2101.1 Scope. | This chapter shall govern the materials, design, construction and quality of masonry.
2101.1.1 Referenced standards. | Where this code makes reference to the nationally recognized standard TMS 402, such standard shall be as modified for New York City in accordance with this chapter.
2101.2 Design methods. | Masonry shall comply with the provisions of TMS 402, TMS 403 or TMS 404, as well as the applicable requirements of this chapter. | 2101.2 Design methods. | Masonry shall comply with the provisions of TMS 402, TMS 403 or TMS 404 as well as applicable requirements of this chapter.
2101.2.1 Masonry veneer. | Masonry veneer shall comply with the provisions of Chapter 14. | 2101.2.1 Masonry veneer. | Masonry veneer shall comply with the provisions of Chapter 14.
2101.3 Special inspection. | The special inspection of masonry shall be as defined in Chapter 17, or an itemized testing and inspection program shall be provided that meets or exceeds the requirements of Chapter 17. | 2101.3 Special inspection. | The special inspection of masonry shall be as defined in Chapter 17, or an itemized testing and inspection program shall be provided that meets or exceeds the requirements of Chapter 17.
2102.1 General. | The following terms are defined in Chapter 2: | 2102.1 General. | The following notations are used in the chapter:
2103.1 Masonry units. | Concrete masonry units, clay or shale masonry units, stone masonry units, glass unit masonry and AAC masonry units shall comply with Article 2.3 of TMS 602. Architectural cast stone shall conform to ASTM C1364 and TMS 504. Adhered manufactured stone masonry veneer units shall conform to ASTM C1670. Exception: Structural clay tile for nonstructural use in fireproofing of structural members and in wall furring shall not be required to meet the compressive strength specifications. The fire-resistance rating shall be determined in accordance with ASTM E 119 or UL 263 and shall comply with the requirements of Table 602 of this code. | 2103.1 Masonry units. | Concrete masonry units, clay or shale masonry units, stone masonry units, glass unit masonry and AAC masonry units shall comply with Article 2.3 of TMS 602. Architectural cast stone shall conform to ASTM C1364 and TMS 504. Adhered manufactured stone masonry veneer units shall conform to ASTM C1670. Exception: Structural clay tile for nonstructural use in fireproofing of structural members and in wall furring shall not be required to meet the compressive strength specifications. The fire-resistance rating shall be determined in accordance with ASTM E119 or UL 263 and shall comply with the requirements of Table 705.5. | See BC6 Tables and Figures | See BC7 Tables and Figures
2103.1.1 Second-hand units. | Second-hand masonry units shall not be reused unless they conform to the requirements of new units. The units shall be of whole, sound materials and free from cracks and other defects that will interfere with proper laying or use. Old mortar shall be cleaned from the unit before reuse. Exception: Second-hand masonry units need not conform to the requirements for new units when their reuse is to comply with historic restoration standards or requirements of the New York City Landmarks Preservation Commission or the New York State Historic Preservation Office. | 2103.1.1 Second-hand units. | Second-hand masonry units shall not be reused unless they conform to the requirements of new units. The units shall be of whole, sound materials and free from cracks and other defects that will interfere with proper laying or use. Old mortar shall be cleaned from the unit before reuse.
2103.2 Mortar. | Mortar for masonry construction shall comply with Section 2103.2.1, 2103.2.2, 2103.2.3 or 2103.2.4. | 2103.2 Mortar. | Mortar for masonry construction shall comply with Section 2103.2.1, 2103.2.2, 2103.2.3 or 2103.2.4.
2103.2.1 Masonry mortar. | Mortar for use in masonry construction shall conform to Articles 2.1 and 2.6A of TMS 602. | 2103.2.1 Masonry mortar. | Mortar for use in masonry construction shall conform to Articles 2.1 and 2.6 A of TMS 602.
2103.2.2 Surface-bonding mortar. | Surface-bonding mortar shall comply with ASTM C 887. Surface bonding of concrete masonry units shall comply with ASTM C 946. | 2103.2.2 Surface-bonding mortar. | Surface-bonding mortar shall comply with ASTM C887. Surface bonding of concrete masonry units shall comply with ASTM C946.
2103.2.3 Mortars for ceramic wall and floor tile. | Portland cement mortars for installing ceramic wall and floor tile shall comply with ANSI A108.1A and ANSI A108.1B and be of the compositions indicated in Table 2103.2.3. | 2103.2.3 Mortars for ceramic wall and floor tile. | Portland cement mortars for installing ceramic wall and floor tile shall comply with ANSI A108.1A and ANSI A108.1B and be of the compositions indicated in Table 2103.2.3. | See BC21 Tables and Figures
2103.2.3.1 Dry-set portland cement mortars. | Premixed prepared portland cement mortars, which require only the addition of water and are used in the installation of ceramic tile, shall comply with ANSI A118.1. The shear bond strength for tile set in such mortar shall be as required in accordance with ANSI A118.1. Tile set in dry-set portland cement mortar shall be installed in accordance with ANSI A108.5. | 2103.2.3.1 Dry-set Portland cement mortars. | Premixed prepared Portland cement mortars, which require only the addition of water and are used in the installation of ceramic tile, shall comply with ANSI A118.1. The shear bond strength for tile set in such mortar shall be as required in accordance with ANSI A118.1. Tile set in dry-set Portland cement mortar shall be installed in accordance with ANSI A108.5.
2103.2.3.2 Latex-modified portland cement mortar. | Latex-modified portland cement thin-set mortars in which latex is added to dry-set mortar as a replacement for all or part of the gauging water that are used for the installation of ceramic tile shall comply with ANSI A118.4. Tile set in latex-modified portland cement shall be installed in accordance with ANSI A108.5. | 2103.2.3.2 Latex-modified Portland cement mortar. | Latex-modified Portland cement thin-set mortars in which latex is added to dry-set mortar as a replacement for all or part of the gauging water that are used for the installation of ceramic tile shall comply with ANSI A118.4. Tile set in latex-modified Portland cement shall be installed in accordance with ANSI A108.5.
2103.2.3.3 Epoxy mortar. | Ceramic tile set and grouted with chemical-resistant epoxy shall comply with ANSI A118.3. Tile set and grouted with epoxy shall be installed in accordance with ANSI A108.6. | 2103.2.3.3 Epoxy mortar. | Ceramic tile set and grouted with chemical-resistant epoxy shall comply with ANSI A118.3. Tile set and grouted with epoxy shall be installed in accordance with ANSI A108.6.
2103.2.3.4 Furan mortar and grout. | Chemical-resistant furan mortar and grout that are used to install ceramic tile shall comply with ANSI A118.5. Tile set and grouted with furan shall be installed in accordance with ANSI A108.8. | 2103.2.3.4 Furan mortar and grout. | Chemical-resistant furan mortar and grout that are used to install ceramic tile shall comply with ANSI A118.5. Tile set and grouted with furan shall be installed in accordance with ANSI A108.8.
2103.2.3.5 Modified epoxy-emulsion mortar and grout. | Modified epoxy-emulsion mortar and grout that are used to install ceramic tile shall comply with ANSI A118.8. Tile set and grouted with modified epoxy-emulsion mortar and grout shall be installed in accordance with ANSI A108.9. | 2103.2.3.5 Modified epoxy-emulsion mortar and grout. | Modified epoxy-emulsion mortar and grout that are used to install ceramic tile shall comply with ANSI A118.8. Tile set and grouted with modified epoxy-emulsion mortar and grout shall be installed in accordance with ANSI A108.9.
2103.2.3.6 Organic adhesives. | Water-resistant organic adhesives used for the installation of ceramic tile shall comply with ANSI A136.1. The shear bond strength after water immersion shall be not less than 40 psi (275 kPa) for Type I adhesive and not less than 20 psi (138 kPa) for Type II adhesive when tested in accordance with ANSI A136.1. Tile set in organic adhesives shall be installed in accordance with ANSI A108.4. | 2103.2.3.6 Organic adhesives. | Water-resistant organic adhesives used for the installation of ceramic tile shall comply with ANSI A136.1. The shear bond strength after water immersion shall be not less than 40 psi (275 kPa) for Type I adhesive and not less than 20 psi (138 kPa) for Type II adhesive when tested in accordance with ANSI A136.1. Tile set in organic adhesives shall be installed in accordance with ANSI A108.4.
2103.2.3.7 Portland cement grouts. | Portland cement grouts used for the installation of ceramic tile shall comply with ANSI A118.6. Portland cement grouts for tile work shall be installed in accordance with ANSI A108.10. | 2103.2.3.7 Portland cement grouts. | Portland cement grouts used for the installation of ceramic tile shall comply with ANSI A118.6. Portland cement grouts for tile work shall be installed in accordance with ANSI A108.10.
2103.2.4 Mortar for adhered masonry veneer. | Mortar for use with adhered masonry veneer shall conform to ASTM C 270 for Type N or S, or shall comply with ANSI A118.4 for latex-modified portland cement mortar. | 2103.2.4 Mortar for adhered masonry veneer. | Mortar for use with adhered masonry veneer shall conform to ASTM C270 for Type N or S, or shall comply with ANSI A118.4 for latex-modified Portland cement mortar.
2103.3 Grout. | Grout shall comply with Article 2.2 of TMS 602. | 2103.3 Grout. | Grout shall comply with Article 2.2 of TMS 602.
2103.4 Metal reinforcement and accessories. | Metal reinforcement and accessories shall conform to Article 2.4 of TMS 602. Where unidentified reinforcement is approved for use, not less than three tension and three bending tests shall be made on representative specimens of the reinforcement from each shipment and grade of reinforcing steel proposed for use in the work. | 2103.4 Metal reinforcement and accessories. | Metal reinforcement and accessories shall conform to Article 2.4 of TMS 602. Where unidentified reinforcement is approved for use, not less than three tension and three bending tests shall be made on representative specimens of the reinforcement from each shipment and grade of reinforcing steel proposed for use in the work.
2104.1 Masonry construction. | Masonry construction shall comply with the requirements of Sections 2104.1.1 through 2104.10, TMS 402, and TMS 602 or TMS 604. | 2104.1 Masonry construction. | Masonry construction shall comply with the requirements of Sections 2104.1.1 and 2104.1.2 and with the requirements of either TMS 602 or TMS 604.
2104.1.1 Lintels. | Minimum length of end support shall be 4 inches (102 mm). | 2104.1.1 Support on wood. | Masonry shall not be supported on wood girders or other forms of wood construction except as permitted in Section 2304.12.
2104.1.2 Support on wood. | Masonry shall not be supported on wood girders or other forms of wood construction except as permitted in Section 2304.12. | 2104.1.2 Molded cornices. | Unless structural support and anchorage are provided to resist the overturning moment, the center of gravity of projecting masonry or molded cornices shall lie within the middle one-third of the supporting wall. Terra cotta and metal cornices shall be provided with a structural frame of approved noncombustible material anchored in an approved manner.
2105.1 General. | A quality assurance program shall be used to ensure that the constructed masonry is in compliance with the approved construction documents. The quality assurance program shall comply with the inspection and testing requirements of Chapter 17 and TMS 602. | 2105.1 General. | A quality assurance program shall be used to ensure that the constructed masonry is in compliance with the approved construction documents.
2104.1.3 Projecting masonry and cornices. | Unless structural support and anchorage are provided to resist the overturning moment, the center of gravity of projecting masonry or molded cornices shall lie within the middle one-third of the supporting wall. Terra cotta and metal cornices shall be provided with a structural frame of approved noncombustible material anchored in a manner approved by the commissioner.
2106.1 Seismic design requirements for masonry. | Masonry structures and components shall comply with the requirements in Chapter 7 of TMS 402 depending on the structure’s seismic design category as determined in Section 1613 of this code. All masonry walls, unless isolated on three edges from in-plane motion of the basic structural systems, shall be considered to be part of the seismic-force-resisting system. | 2106.1 Seismic design requirements for masonry. | Masonry structures and components shall comply with the requirements in Chapter 7 of TMS 402 depending on the structure’s seismic design category.
2104.2 Cold weather construction. | The cold weather construction provisions of Article 1.8 C of TMS 602 shall be implemented when either the ambient temperature falls below 40°F (4°C) or the temperature of masonry units is below 40°F (4°C).
2107.1 General. | The design of masonry structures using allowable stress design shall comply with Section 2106 and the requirements of Chapters 1 through 8 of TMS 402 except as modified by Sections 2107.2 through 2107.4 of this code. | 2107.1 General. | The design of masonry structures using allowable stress design shall comply with Section 2106 and the requirements of Chapters 1 through 8 of TMS 402 except as modified by Sections 2107.2 through 2107.3.
2104.2.1 Preparation. | No salt or other chemicals for the purpose of lowering the freezing temperature of water shall be permitted in the mortar or grout mix.
2107.2 TMS 402, Section 6. | 1.6.1.1, lap splices. As an alternative to Section 6.1.6.1.1, it shall be permitted to design lap splices in accordance with Section 2107.2.1 of the New York City Building Code. | 2107.2 TMS 402, Section 6. | 1.6.1.1, lap splices. As an alternative to Section 6.1.6.1.1, it shall be permitted to design lap splices in accordance with Section 2107.2.1.
2104.3 Hot weather construction. | The hot weather construction provisions of Article 1.8 D of TMS 602 shall be implemented when the temperature exceeds 100°F (37.8°C), or 90°F (32.2°C) with a wind-velocity greater than 8 mph (12.9 km/hr).
2107.2.1 Lap splices. | The minimum length of lap splices for reinforcing bars in tension or compression, ld, shall be | 2107.2.1 Lap splices. | The minimum length of lap splices for reinforcing bars in tension or compression, ld, shall be:
2104.4 Wetting of brick. | Brick (clay or shale) at the time of laying shall require wetting if the unit’s initial rate of water absorption exceeds 21.42 grams per 30 square inches (19 355 mm2) per minute or 0.025 ounce psi (1 g/645 mm2), as determined by ASTM C 67.
2107.3 TMS 402, Section 6. | 1.6.1, splices of reinforcement. Modify Section 6.1.6.1 as follows: | 2107.3 TMS 402, Section 6. | 1.6.1, splices of reinforcement. Modify Section 6.1.6.1 as follows:
2104.5 Masonry construction bracing. | In accordance with Article 3.3E of TMS 602, the contractor shall design, provide, and install bracing that will assure stability of all masonry during construction. The contractor shall keep a bracing plan on site during all masonry construction. Bracing plans shall consider wind loads, initial and intermediate masonry strengths, and the contractor’s ability to evacuate the site. Construction bracing for walls within a distance less than their height from adjoining properties or other unprotected and uncontrolled areas shall be designed for code prescribed wind loads and the bracing plan shall be signed and sealed by a licensed professional engineer. Construction bracing for walls may be designed using reduced loading in accordance with Section 1619. Such reduced loading shall only be permitted when an action plan meeting the requirements of Section 1619.3 is provided and maintained at the site.
2108.1 General. | The design of masonry structures using strength design shall comply with Section 2106 and the requirements of Chapters 1 through 7 and Chapter 9 of TMS 402, except as modified by Sections 2108.2 through 2108.3 of this code. Exception: AAC masonry shall comply with the requirements of Chapters 1 through 7 and Chapter 11 of TMS 402. | 2108.1 General. | The design of masonry structures using strength design shall comply with Section 2106 and the requirements of Chapters 1 through 7 and Chapter 9 of TMS 402, except as modified by Sections 2108.2 through 2108.3. Exception: AAC masonry shall comply with the requirements of Chapters 1 through 7 and Chapter 11 of TMS 402.
2104.6 Parapet walls. | At a minimum, parapet walls shall meet the following requirements:
2104.6.1 Parapet wall construction. | All cells in the hollow masonry units and all joints in solid, cavity, or masonry-bonded hollow wall construction shall be filled solid. All corners of masonry parapet walls shall be reinforced with joint reinforcement or its equivalent at vertical intervals not greater than 16 inches (406 mm). Such reinforcement shall extend around the corner for at least 4 feet (1219 mm) in both directions, and splices shall be lapped at least 6 inches (152 mm).
2108.3 TMS 402, Section 6. | 1.6.1.1, splices. Modify subsections 6.1.6.1.2 and 6.1.6.1.3 as follows: | 2108.3 TMS 402, Section 6. | 1.6.1.1, splices. Modify Sections 6.1.6.1.2 and 6.1.6.1.3 as follows:
2104.6.2 Parapet anchorage. | Parapets shall be reinforced vertically and shall be anchored to the roof and floors that provide lateral support for the wall in accordance with Section 1604.8.2.
2109.1 General. | Empirically designed masonry shall conform to this chapter or the requirements of Appendix A of TMS 402, except where otherwise noted in this section. | 2109.1 General. | Empirically designed adobe masonry shall conform to the requirements of Appendix A of TMS 402, except where otherwise noted in this section.
2104.7 Floor and roof anchorage. | Floor and roof anchorage shall comply with Section 2104.7.1 through 2104.7.1.3.
2109.1.1 Limitations. | The use of empirical design of masonry shall be limited as noted in Section A.1.2 of TMS 402. The use of dry-stacked, surface-bonded masonry shall be prohibited in Risk Category IV structures. In buildings that exceed one or more of the limitations of Section A.1.2 of TMS 402, masonry shall be designed in accordance with the engineered design provisions of Section 2101.2 or the foundation wall provisions of Section 1807. | 2109.1.1 Limitations. | The use of empirical design of adobe masonry shall be limited as noted in Section A.1.2 of TMS 402. In buildings that exceed one or more of the limitations of Section A.1.2 of TMS 402, masonry shall be designed in accordance with the engineered design provisions of Section 2101.2 or the foundation wall provisions of Section 1807.1.5.
2104.7.1 Bearing details. | Concentrated loads shall be supported upon construction of solid masonry, concrete, or masonry of hollow units with cells filled with mortar, grout, or concrete. In addition, construction supporting concentrated loads shall be of sufficient height to distribute safely the loads to the wall or column, or other adequate provisions shall be made to distribute the loads.
2104.7.1.1 Joists. | Solid construction for support under joists shall be at least 2¼ inches (57 mm) in height, and joists supported on such construction shall extend into the masonry at least 3 inches (76 mm).
2104.7.1.2 Beams. | Solid construction for support under beams, girders, or other concentrated loads shall be at least 4 inches (102 mm) in height, and the bearing of beams shall extend into the masonry at least 4 inches (102 mm).
2104.7.1.3 Isolated piers. | Isolated masonry piers shall be bonded as required for solid walls of the same thickness and shall be provided with adequate means for distributing the load at the top of the pier.
2104.8 Walls adjoining structural framing. | Walls adjoining structural framing shall comply with Sections 2104.8.1 and 2104.8.2.
2104.8.1 Use of existing walls. | An existing masonry wall may be used in the alteration or extension of a building provided that it meets the requirements of this code.
2104.8.2 Walls of insufficient thickness. | Existing walls of masonry units that are structurally sound, but that are of insufficient thickness when increased in height, may be strengthened by an addition of similar masonry units laid in Type M or S mortar. The foundations and lateral support shall be equivalent to those required for newly constructed walls under similar conditions. All such linings shall be thoroughly bonded into existing masonry by toothings to assure combined action of wall and lining. Toothings shall be distributed uniformly throughout the wall, and shall aggregate in vertical cross-sectional area at least 15 percent of the total surface area of the lining. Stresses in the masonry under the new conditions shall not exceed the allowable stresses.
2104.9 Isolation joints. | All non-participating masonry walls and veneers shall be constructed with adequate depth and width of isolation joints to prevent masonry distress induced by deflections, drifts, shortening, expansion, or other similar movements in the plane of the wall.
2104.10 Substitution. | Mortar shall not be substituted for grout where grout is specified on the construction documents.
2105.2 Submittals. | Submittals required by Article 1.5 of TMS 602 shall be sent to the applicant of record for review prior to use of the materials or methods of construction. In addition the contractor shall submit a Material Storage and Protection Plan.
2106.1.1 Non-participating masonry walls. | Masonry walls that are not part of the lateral-force-resisting system shall be isolated from the structure so that the vertical and lateral forces are not imparted to these elements. Isolation joints and connectors between these elements and the structure shall be designed to accommodate the design story drift.
2107.4 TMS 402, Section 8. | 3.6, maximum bar size. Add the following to Chapter 8:
2108.2 TMS 402 Section 6. | 1.5.1.1, development. Modify the second paragraph of Section 6.1.5.1.1 as follows:
2109.1.1.1 TMS 402, Section A. | 1.2.3, Wind. Section A.1.2.3 of TMS 402 shall be modified as follows:
2109.2 Surface-bonded walls. | Dry-stacked, surface-bonded concrete masonry walls shall comply with the requirements of Appendix A of TMS 402, except where otherwise noted in this section. | 2109.2 Adobe construction. | Adobe construction shall comply with this section and shall be subject to the requirements of this code for Type V construction, Appendix A of TMS 402, and this section.
2109.2.1 Strength. | Dry-stacked, surface-bonded concrete masonry walls shall be of adequate strength and proportions to support all superimposed loads without exceeding the allowable stresses listed in Table 2109.2.1. Allowable stresses not specified in Table 2109.2.1 shall comply with the requirements of TMS 402. | 2109.2.1 Unstabilized adobe. | Unstabilized adobe shall comply with Sections 2109.2.1.1 through 2109.2.1.4. | See BC21 Tables and Figures
2109.2.2 Construction. | Construction of dry-stacked, surface-bonded masonry walls, including stacking and leveling of units, mixing and application of mortar and curing and protection shall comply with ASTM C 946.
2109.3 Reserved.
2109.4 Thickness of masonry. | Minimum thickness requirements shall be based on nominal dimensions of masonry.
2109.4.1 Thickness of walls. | The thickness of masonry walls shall conform to the requirements of Section 2109.4.
2109.4.2 Minimum thickness. | The minimum thickness of masonry bearing walls more than one story high shall be 8 inches (203 mm) where the height floor to floor does not exceed 12 feet (3658 mm), the floor live load does not exceed 60 pounds per square foot (psf) (0.156 kg/m2), and the roof is designed so that the dead load imparts no lateral thrust to the wall. Bearing walls of one-story buildings shall not be less than 6 inches (152 mm) thick. However, the overall thickness of cavity or masonry-bonded hollow walls shall not be less than 8 inches (203 mm), including cavity.
2109.4.2.1 Walls above roof level. | Masonry walls above roof level, 12 feet (3658 mm) or less in height, enclosing stairways, machinery rooms, shafts, or penthouses, may be up to 8 inches (203 mm) thick and shall be considered as neither increasing the height, nor requiring any increase in the thickness of the wall below.
2109.4.3 Partitions. | The minimum thickness for partitions shall be as follows:
2109.5 Horizontal joints. | All concrete framed buildings to be constructed over 35 feet (10 668 mm) in height (as measured from adjoining grade to the main roof level), whose exterior wythe are of cavity wall construction with steel lintels, shall have horizontal joints in the exterior wythe to prevent masonry distress induced by vertical shortening of the structural frame.
2109.5.1 Joint minimum thickness. | Unless substantiated as indicated by Section 2109.5.2, horizontal joints shall be 1/4 inch (6.4 mm) minimum thickness, with neoprene, polyethylene, or urethane gasket or equivalent joint filler filling the entire joint, except for a recess from the toe of the lintel angle to the exterior of the facing brick, to provide space for caulking. These joints shall be placed at each floor.
2109.5.2 Joint thickness by analysis. | The applicant of record shall submit an engineering analysis establishing that proposed building horizontal joints spaced further apart than in Section 2109.5.1 are sufficient to provide for the effects of vertical shortening of the structural frame.
2110.1 General. | Glass unit masonry construction shall comply with Chapter 13 of TMS 402 and this section. | 2110.1 General. | Glass unit masonry construction shall comply with Chapter 13 of TMS 402 and this section.
2110.1.1 Limitations. | Solid or hollow approved glass block shall not be used in fire walls, party walls, fire barriers, fire partitions, smoke barriers, or for load-bearing construction. Such blocks shall be erected with mortar and reinforcement in metal channel-type frames, structural frames, masonry or concrete recesses, embedded panel anchors as provided for both exterior and interior walls or other approved joint materials. Wood strip framing shall not be used in walls required to have a fire-resistance rating by other provisions of this code. Exceptions: 1. Glass-block assemblies having a fire protection rating of not less than ¾ hour shall be permitted as opening protectives in accordance with Section 716 in fire barriers, fire partitions and smoke barriers that have a required fire-resistance rating of 1 hour and do not enclose exit stairways or exit passageways. 2. Glass-block assemblies as permitted in Section 404.6, Exception 1╪. | 2110.1.1 Limitations. | Solid or hollow approved glass block shall not be used in fire walls, party walls, fire barriers, fire partitions or smoke barriers, or for load-bearing construction. Such blocks shall be erected with mortar and reinforcement in metal channel-type frames, structural frames, masonry or concrete recesses, embedded panel anchors as provided for both exterior and interior walls or other approved joint materials. Wood strip framing shall not be used in walls required to have a fire-resistance rating by other provisions of this code. Exceptions: 1. Glass-block assemblies having a fire protection rating of not less than 3/4 hour shall be permitted as opening protectives in accordance with Section 716 in fire barriers, fire partitions and smoke barriers that have a required fire-resistance rating of 1 hour or less and do not enclose exit stairways and ramps or exit passageways. 2. Glass-block assemblies as permitted in Section 404.6, Exception 2.
2111.1 General. | The construction of masonry fireplaces shall be in accordance with this section, Table 2111.1 and Figure 2111.1. All masonry fireplaces shall be installed, altered and maintained in buildings in conformity with the applicable provisions of the New York City Mechanical Code, the New York City Fuel Gas Code and the New York City Air Pollution Control Code. No new masonry fireplaces shall be permitted except those that burn the types of fuel allowed by Section 24-149.2 of the New York City Air Pollution Control Code. | 2111.1 General. | The construction of masonry fireplaces, consisting of concrete or masonry, shall be in accordance with this section. | See BC21 Tables and Figures
2111.2 Fireplace drawings. | The construction documents shall describe in sufficient detail the location, size and construction of masonry fireplaces. The thickness and characteristics of materials and the clearances from walls, partitions and ceilings shall be indicated. | 2111.2 Fireplace drawings. | The construction documents shall describe in sufficient detail the location, size and construction of masonry fireplaces. The thickness and characteristics of materials and the clearances from walls, partitions and ceilings shall be indicated.
2111.3 Footings and foundations. | Footings for masonry fireplaces and their chimneys shall be constructed of reinforced concrete or solid masonry at least 12 inches (305 mm) thick and shall extend at least 6 inches (152 mm) beyond the face of the fireplace or foundation wall on all sides. Footings shall be founded on natural undisturbed earth or engineered fill below frost depth. In areas not subjected to freezing, footings shall be at least 12 inches (305 mm) below finished grade. | 2111.3 Footings and foundations. | Footings for masonry fireplaces and their chimneys shall be constructed of concrete or solid masonry not less than 12 inches (305 mm) thick and shall extend not less than 6 inches (153 mm) beyond the face of the fireplace or foundation wall on all sides. Footings shall be founded on natural undisturbed earth or engineered fill below frost depth. In areas not subjected to freezing, footings shall be not less than 12 inches (305 mm) below finished grade.
2111.3.1 Ash dump cleanout. | Cleanout openings, located within foundation walls below fireboxes, when provided, shall be equipped with ferrous metal or masonry doors and frames constructed to remain tightly closed, except when in use. Cleanouts shall be accessible and located so that ash removal will not create a hazard to combustible materials. | 2111.3.1 Ash dump cleanout. | Cleanout openings, located within foundation walls below fireboxes, where provided, shall be equipped with ferrous metal or masonry doors and frames constructed to remain tightly closed, except when in use. Cleanouts shall be accessible and located so that ash removal will not create a hazard to combustible materials.
2111.3.2 Floor-supported fireplaces. | Fireplaces not supported on foundations shall be supported on noncombustible construction having a minimum fire-resistance rating of 3 hours for the members or assemblies in contact with the fireplace. Structural members or assemblies not directly in contact with the fireplace shall only be required to meet the fire-resistance rating specified elsewhere in this code.
2111.4 Seismic reinforcement. | In structures assigned to Seismic Design Category A or B, seismic reinforcement is not required. In structures assigned to Seismic Design Category C or D, masonry fireplaces shall be reinforced and anchored in accordance with Sections 2111.4.1, 2111.4.2 and 2111.5, and Table 2111.1, and Figure 2111.1. | 2111.4 Seismic reinforcement. | In structures assigned to Seismic Design Category A or B, seismic reinforcement is not required. In structures assigned to Seismic Design Category C or D, masonry fireplaces shall be reinforced and anchored in accordance with Sections 2111.4.1, 2111.4.2 and 2111.5. In structures assigned to Seismic Design Category E or F, masonry fireplaces shall be reinforced in accordance with the requirements of Sections 2101 through 2108. | See BC21 Tables and Figures
2111.4.1 Vertical reinforcing. | For fireplaces with chimneys up to 40 inches (1016 mm) wide, four No. 4 continuous vertical bars, anchored in the foundation, shall be placed in the concrete between wythes of solid masonry or within the cells of hollow unit masonry and grouted in accordance with Section 2103.3. For fireplaces with chimneys greater than 40 inches (1016 mm) wide, two additional No. 4 vertical bars shall be provided for each additional 40 inches (1016 mm) in width or fraction thereof. | 2111.4.1 Vertical reinforcing. | For fireplaces with chimneys up to 40 inches (1016 mm) wide, four No. 4 continuous vertical bars, anchored in the foundation, shall be placed in the concrete between wythes of solid masonry or within the cells of hollow unit masonry and grouted in accordance with Section 2103.3. For fireplaces with chimneys greater than 40 inches (1016 mm) wide, two additional No. 4 vertical bars shall be provided for each additional 40 inches (1016 mm) in width or fraction thereof.
2111.4.2 Horizontal reinforcing. | Vertical reinforcement shall be placed enclosed within ¼-inch (6.4 mm) ties or other reinforcing of equivalent net cross-sectional area, spaced not to exceed 18 inches (457 mm) on center in concrete; or placed in the bed joints of unit masonry at a minimum of every 18 inches (457 mm) of vertical height. Two such ties shall be provided at each bend in the vertical bars. | 2111.4.2 Horizontal reinforcing. | Vertical reinforcement shall be placed enclosed within 1/4-inch (6.4 mm) ties or other reinforcing of equivalent net cross-sectional area, spaced not to exceed 18 inches (457 mm) on center in concrete; or placed in the bed joints of unit masonry at not less than every 18 inches (457 mm) of vertical height. Two such ties shall be provided at each bend in the vertical bars.
2111.5 Seismic anchorage. | Masonry fireplaces shall have their chimneys anchored in accordance with Section 2113.4. | 2111.5 Seismic anchorage. | Masonry fireplaces and foundations shall be anchored at each floor, ceiling or roof line more than 6 feet (1829 mm) above grade with two 3/16-inch by 1-inch (4.8 mm by 25 mm) straps embedded not less than 12 inches (305 mm) into the chimney. Straps shall be hooked around the outer bars and extend 6 inches (152 mm) beyond the bend. Each strap shall be fastened to not fewer than four floor joists with two 1/2-inch (12.7 mm) bolts. Exception: Seismic anchorage is not required for the following: 1. In structures assigned to Seismic Design Category A or B. 2. Where the masonry fireplace is constructed completely within the exterior walls.
2111.6 Firebox walls. | Masonry fireboxes shall be constructed of solid masonry units, hollow masonry units grouted solid, or stone. When a lining of firebrick at least 2 inches (51 mm) in thickness or other approved lining is provided, the minimum thickness of back and sidewalls shall each be 8 inches (203 mm) of solid masonry, including the lining. The approved lining shall be able to withstand a temperature of 2000°F (1093°C) without cracking. The width of joints between firebricks shall be not greater than ¼ inch (6.4 mm). When no lining is provided, the total minimum thickness of back and sidewalls shall be 12 inches (305 mm) of solid masonry. Firebrick shall conform to ASTM C 27 or ASTM C 1261 and shall be laid with medium-duty refractory mortar conforming to ASTM C 199. | 2111.6 Firebox walls. | Masonry fireboxes shall be constructed of solid masonry units, hollow masonry units grouted solid, stone or concrete. Where a lining of firebrick not less than 2 inches (51 mm) in thickness or other approved lining is provided, the minimum thickness of back and sidewalls shall each be 8 inches (203 mm) of solid masonry, including the lining. The width of joints between firebricks shall be not greater than 1/4 inch (6.4 mm). Where a lining is not provided, the total minimum thickness of back and sidewalls shall be 10 inches (254 mm) of solid masonry. Firebrick shall conform to ASTM C27 or ASTM C1261 and shall be laid with medium-duty refractory mortar conforming to ASTM C199.
2111.6.1 Steel fireplace units. | Steel fireplace units are permitted to be installed with solid masonry to form a masonry fireplace provided they are installed according to either the requirements of their listing or the requirements of this section. Steel fireplace units incorporating a steel firebox lining shall be constructed with steel not less than ¼ inch (6.4 mm) in thickness, and an air-circulating chamber which is ducted to the interior of the building. The firebox lining shall be encased with solid masonry to provide a total thickness at the back and sides of not less than 8 inches (203 mm), of which not less than 4 inches (102 mm) shall be of solid masonry or concrete. Circulating air ducts employed with steel fireplace units shall be constructed of metal or masonry. | 2111.6.1 Steel fireplace units. | Steel fireplace units are permitted to be installed with solid masonry to form a masonry fireplace provided that they are installed according to either the requirements of their listing or the requirements of this section. Steel fireplace units incorporating a steel firebox lining shall be constructed with steel not less than 1/4 inch (6.4 mm) in thickness, and an air-circulating chamber that is ducted to the interior of the building. The firebox lining shall be encased with solid masonry to provide a total thickness at the back and sides of not less than 8 inches (203 mm), of which not less than 4 inches (102 mm) shall be of solid masonry or concrete. Circulating air ducts employed with steel fireplace units shall be constructed of metal or masonry.
2111.7 Firebox dimensions. | The firebox of a masonry fireplace shall have a minimum depth of 20 inches (508 mm). The throat shall be not less than 8 inches (203 mm) above the fireplace opening. The throat opening shall not be less than 4 inches (102 mm) in depth. The cross-sectional area of the passageway above the firebox, including the throat, damper and smoke chamber, shall be not less than the cross-sectional area of the flue. Exception: Rumford fireplaces shall be permitted provided that the depth of the fireplace is not less than 12 inches (305 mm) and at least one-third of the width of the fireplace opening, and the throat is not less than 12 inches (305 mm) above the lintel, and at least 1/20 the cross-sectional area of the fireplace opening. | 2111.7 Firebox dimensions. | The firebox of a concrete or masonry fireplace shall have a minimum depth of 20 inches (508 mm). The throat shall be not less than 8 inches (203 mm) above the fireplace opening. The throat opening shall be not less than 4 inches (102 mm) in depth. The cross-sectional area of the passageway above the firebox, including the throat, damper and smoke chamber, shall be not less than the cross-sectional area of the flue. Exception: Rumford fireplaces shall be permitted provided that the depth of the fireplace is not less than 12 inches (305 mm) and not less than one-third of the width of the fireplace opening, and the throat is not less than 12 inches (305 mm) above the lintel, and not less than 1/20 the cross-sectional area of the fireplace opening.
2111.8 Lintel and throat. | Masonry over a fireplace opening shall be supported by a lintel of noncombustible material. The minimum required bearing length on each end of the fireplace opening shall be 4 inches (102 mm). The fireplace throat or damper shall be located not less than 8 inches (203 mm) above the top of the fireplace opening. | 2111.8 Lintel and throat. | Masonry over a fireplace opening shall be supported by a lintel of noncombustible material. The minimum required bearing length on each end of the fireplace opening shall be 4 inches (102 mm). The fireplace throat or damper shall be located not less than 8 inches (203 mm) above the top of the fireplace opening.
2111.8.1 Damper. | Masonry fireplaces shall be equipped with a ferrous metal damper located not less than 8 inches (203 mm) above the top of the fireplace opening. Dampers shall be installed in the fireplace or at the top of the flue venting the fireplace, and shall be operable from the room containing the fireplace. Damper controls shall be permitted to be located in the fireplace. The damper shall be able to withstand distortion from binding, cracking or corrosion when exposed to the fireplace operating temperature. | 2111.8.1 Damper. | Masonry fireplaces shall be equipped with a ferrous metal damper located not less than 8 inches (203 mm) above the top of the fireplace opening. Dampers shall be installed in the fireplace or at the top of the flue venting the fireplace, and shall be operable from the room containing the fireplace. Damper controls shall be permitted to be located in the fireplace.
2111.9 Smoke chamber walls. | Smoke chamber walls shall be constructed of solid masonry units, hollow masonry units grouted solid, or stone. Corbeling of masonry units shall not leave unit cores exposed to the inside of the smoke chamber. The inside surface of corbeled masonry shall be parged smooth. Where no lining is provided, the total minimum thickness of front, back and sidewalls shall be 8 inches (203 mm) of solid masonry. When a lining of firebrick not less than 2 inches (51 mm) thick, or a lining of vitrified clay not less than ⅝ inch (15.9 mm) thick, is provided, the total minimum thickness of front, back and sidewalls shall be 6 inches (152 mm) of solid masonry, including the lining. Firebrick shall conform to ASTM C 27 or ASTM C 1261 and shall be laid with refractory mortar conforming to ASTM C 199. Vitrified clay linings shall conform to ASTM C 315. | 2111.9 Smoke chamber walls. | Smoke chamber walls shall be constructed of solid masonry units, hollow masonry units grouted solid, stone or concrete. The total minimum thickness of front, back and sidewalls shall be 8 inches (203 mm) of solid masonry. The inside surface shall be parged smooth with refractory mortar conforming to ASTM C199. Where a lining of firebrick not less than 2 inches (51 mm) thick, or a lining of vitrified clay not less than 5/8 inch (15.9 mm) thick, is provided, the total minimum thickness of front, back and sidewalls shall be 6 inches (152 mm) of solid masonry, including the lining. Firebrick shall conform to ASTM C1261 and shall be laid with refractory mortar conforming to ASTM C199. Vitrified clay linings shall conform to ASTM C315.
2111.9.1 Smoke chamber dimensions. | The inside height of the smoke chamber from the fireplace throat to the beginning of the flue shall be not greater than the inside width of the fireplace opening. The inside surface of the smoke chamber shall not be inclined more than 45 degrees (0.76 rad) from vertical when prefabricated smoke chamber linings are used or when the smoke chamber walls are rolled or sloped rather than corbeled. When the inside surface of the smoke chamber is formed by corbeled masonry, the walls shall not be corbeled more than 30 degrees (0.52 rad) from vertical. | 2111.9.1 Smoke chamber dimensions. | The inside height of the smoke chamber from the fireplace throat to the beginning of the flue shall be not greater than the inside width of the fireplace opening. The inside surface of the smoke chamber shall not be inclined more than 45 degrees (0.76 rad) from vertical where prefabricated smoke chamber linings are used or where the smoke chamber walls are rolled or sloped rather than corbeled. Where the inside surface of the smoke chamber is formed by corbeled masonry, the walls shall not be corbeled more than 30 degrees (0.52 rad) from vertical.
2111.10 Hearth and hearth extension. | Masonry fireplace hearths and hearth extensions shall be constructed of concrete, ceramic tile, masonry or equivalent, supported by noncombustible materials, and reinforced to carry their own weight and all imposed loads. No combustible material shall remain against the underside of hearths or hearth extensions after construction. | 2111.10 Hearth and hearth extension. | Masonry fireplace hearths and hearth extensions shall be constructed of concrete or masonry, supported by noncombustible materials, and reinforced to carry their own weight and all imposed loads. Combustible material shall not remain against the underside of hearths or hearth extensions after construction.
2111.10.1 Hearth thickness. | The minimum thickness of fireplace hearths shall be 4 inches (102 mm). | 2111.10.1 Hearth thickness. | The minimum thickness of fireplace hearths shall be 4 inches (102 mm).
2111.10.2 Hearth extension thickness. | The minimum thickness of hearth extensions shall be 2 inches (51 mm). Exception: When the bottom of the firebox opening is raised not less than 8 inches (203 mm) above the top of the hearth extension, a hearth extension of not less than ⅜-inch-thick (9.5 mm) brick, concrete, stone, tile or other approved noncombustible material is permitted. | 2111.10.2 Hearth extension thickness. | The minimum thickness of hearth extensions shall be 2 inches (51 mm). Exception: Where the bottom of the firebox opening is raised not less than 8 inches (203 mm) above the top of the hearth extension, a hearth extension of not less than 3/8-inch-thick (9.5 mm) brick, concrete, stone, tile or other approved noncombustible material is permitted.
2111.11 Hearth extension dimensions. | Hearth extensions shall extend not less than 16 inches (406 mm) in front of, and not less than 8 inches (203 mm) beyond, each side of the fireplace opening. Where the fireplace opening is 6 square feet (0.56 m2) or larger, the hearth extension shall extend not less than 20 inches (508 mm) in front of, and not less than 12 inches (305 mm) beyond, each side of the fireplace opening. | 2111.11 Hearth extension dimensions. | Hearth extensions shall extend not less than 16 inches (406 mm) in front of, and not less than 8 inches (203 mm) beyond, each side of the fireplace opening. Where the fireplace opening is 6 square feet (0.557 m2) or larger, the hearth extension shall extend not less than 20 inches (508 mm) in front of, and not less than 12 inches (305 mm) beyond, each side of the fireplace opening.
2111.11.1 Elevated or overhanging fireplace. | Where a fireplace is elevated or overhangs a floor, the hearth extension shall also extend beneath the entire area of the fireplace.
2111.12 Fireplace clearance. | Any portion of a masonry fireplace located in the interior of a building or within the exterior wall of a building shall have a clearance to combustibles of not less than 2 inches (51 mm) from the front faces and sides of masonry fireplaces and not less than 4 inches (102 mm) from the back faces of masonry fireplaces. The airspace shall not be filled, except to provide fireblocking in accordance with Section 2111.13. Exceptions: 1. Masonry fireplaces listed and labeled for use in contact with combustibles in accordance with UL 127 and installed in accordance with the manufacturer’s instructions are permitted to have combustible material in contact with their exterior surfaces. 2. When masonry fireplaces are constructed as part of masonry or concrete walls, combustible materials shall not be in contact with the masonry or concrete walls less than 12 inches (306 mm) from the inside surface of the nearest firebox lining. 3. Exposed combustible trim and the edges of sheathing materials, such as wood siding, flooring and drywall, are permitted to abut the masonry fireplace sidewalls and hearth extension, in accordance with Figure 2111.12, provided such combustible trim or sheathing is not less than 12 inches (306 mm) from the inside surface of the nearest firebox lining. 4. Exposed combustible mantels or trim is permitted to be placed directly on the masonry fireplace front surrounding the fireplace opening, provided such combustible materials shall not be placed within 6 inches (152 mm) of a fireplace opening. Combustible material within 12 inches (306 mm) of the fireplace opening shall not project more than 1/8 inch (3.2 mm) for each 1-inch (25 mm) distance from such opening. | 2111.12 Fireplace clearance. | Any portion of a masonry fireplace located in the interior of a building or within the exterior wall of a building shall have a clearance to combustibles of not less than 2 inches (51 mm) from the front faces and sides of masonry fireplaces and not less than 4 inches (102 mm) from the back faces of masonry fireplaces. The airspace shall not be filled, except to provide fireblocking in accordance with Section 2111.13. Exceptions: 1. Masonry fireplaces listed and labeled for use in contact with combustibles in accordance with UL 127 and installed in accordance with the manufacturer’s instructions are permitted to have combustible material in contact with their exterior surfaces. 2. Where masonry fireplaces are constructed as part of masonry or concrete walls, combustible materials shall not be in contact with the masonry or concrete walls less than 12 inches (306 mm) from the inside surface of the nearest firebox lining. 3. Exposed combustible trim and the edges of sheathing materials, such as wood siding, flooring and drywall, are permitted to abut the masonry fireplace sidewalls and hearth extension, in accordance with Figure 2111.12, provided that such combustible trim or sheathing is not less than 12 inches (306 mm) from the inside surface of the nearest firebox lining. 4. Exposed combustible mantels or trim is permitted to be placed directly on the masonry fireplace front surrounding the fireplace opening, provided that such combustible materials shall not be placed within 6 inches (153 mm) of a fireplace opening. Combustible material directly above and within 12 inches (305 mm) of the fireplace opening shall not project more than 1/8 inch (3.2 mm) for each 1-inch (25 mm) distance from such opening. Combustible materials located along the sides of the fireplace opening that project more than 11/2 inches (38 mm) from the face of the fireplace shall have an additional clearance equal to the projection.
2111.13 Fireplace fireblocking. | All spaces between fireplaces and floors and ceilings through which fireplaces pass shall be fireblocked with approved noncombustible material securely fastened in place. The fireblocking of spaces between wood joists, beams or headers shall be to a depth of 1 inch (25 mm) and shall only be placed on strips of metal or metal lath laid across the spaces between combustible material and the chimney. | 2111.13 Fireplace fireblocking. | All spaces between fireplaces and floors and ceilings through which fireplaces pass shall be fireblocked with noncombustible material securely fastened in place. The fireblocking of spaces between wood joists, beams or headers shall be to a depth of 1 inch (25 mm) and shall only be placed on strips of metal or metal lath laid across the spaces between combustible material and the chimney.
2111.14 Exterior air. | Factory-built or masonry fireplaces covered in this section shall be equipped with an exterior air supply to ensure proper fuel combustion unless the room is mechanically ventilated and controlled so that the indoor pressure is neutral or positive. | 2111.14 Exterior air. | Factory-built or masonry fireplaces covered in this section shall be equipped with an exterior air supply to ensure proper fuel combustion unless the room is mechanically ventilated and controlled so that the indoor pressure is neutral or positive.
2111.14.1 Factory-built fireplaces. | Exterior combustion air ducts for factory-built fireplaces shall be listed components of the fireplace, and installed according to the fireplace manufacturer’s instructions. | 2111.14.1 Factory-built fireplaces. | Exterior combustion air ducts for factory-built fireplaces shall be listed components of the fireplace, and installed according to the fireplace manufacturer’s instructions.
2111.14.2 Masonry fireplaces. | Listed combustion air ducts for masonry fireplaces shall be installed according to the terms of their listing and manufacturer’s instructions. | 2111.14.2 Masonry fireplaces. | Listed combustion air ducts for masonry fireplaces shall be installed according to the terms of their listing and manufacturer’s instructions.
2111.14.3 Exterior air intake. | The exterior air intake shall be capable of providing all combustion air from the exterior of the dwelling. The exterior air intake shall not be located within the garage, attic, basement or crawl space of the dwelling nor shall the air intake be located at an elevation higher than the firebox. The exterior air intake shall be covered with a corrosion-resistant screen of ¼-inch (6.4 mm) mesh. | 2111.14.3 Exterior air intake. | The exterior air intake shall be capable of providing all combustion air from the exterior of the dwelling. The exterior air intake shall not be located within a garage, attic, basement or crawl space of the dwelling nor shall the air intake be located at an elevation higher than the firebox. The exterior air intake shall be covered with a corrosion-resistant screen of 1/4-inch (6.4 mm) mesh.
2111.14.4 Clearance. | Unlisted combustion air ducts shall be installed with a minimum 1-inch (25 mm) clearance to combustibles for all parts of the duct within 5 feet (1524 mm) of the duct outlet. | 2111.14.4 Clearance. | Unlisted combustion air ducts shall be installed with a minimum 1-inch (25 mm) clearance to combustibles for all parts of the duct within 5 feet (1524 mm) of the duct outlet.
2111.14.5 Passageway. | The combustion air passageway shall be not less than 6 square inches (3870 mm2) and not more than 55 square inches (0.035 m2), except that combustion air systems for listed fireplaces or for fireplaces tested for emissions shall be constructed according to the fireplace manufacturer’s instructions. | 2111.14.5 Passageway. | The combustion air passageway shall be not less than 6 square inches (3870 mm2) and not more than 55 square inches (0.035 m2), except that combustion air systems for listed fireplaces or for fireplaces tested for emissions shall be constructed according to the fireplace manufacturer’s instructions.
2111.14.6 Outlet. | The exterior air outlet is permitted to be located in the back or sides of the firebox chamber or within 24 inches (610 mm) of the firebox opening on or near the floor. The outlet shall be closable and designed to prevent burning material from dropping into concealed combustible spaces. | 2111.14.6 Outlet. | The exterior air outlet is permitted to be located in the back or sides of the firebox chamber or within 24 inches (610 mm) of the firebox opening on or near the floor. The outlet shall be closable and designed to prevent burning material from dropping into concealed combustible spaces.
2112.1 Definition. | A masonry heater is a heating appliance constructed of concrete or solid masonry, hereinafter referred to as “masonry,” which is designed to absorb and store heat from a solid fuel fire built in the firebox by routing the exhaust gases through internal heat exchange channels in which the flow path downstream of the firebox may include flow in a horizontal or downward direction before entering the chimney and which delivers heat by radiation from the masonry surface of the heater. | 2112.1 Definition. | A masonry heater is a heating appliance constructed of concrete or solid masonry, hereinafter referred to as “masonry,” which is designed to absorb and store heat from a solid fuel fire built in the firebox by routing the exhaust gases through internal heat exchange channels in which the flow path downstream of the firebox includes flow in either a horizontal or downward direction before entering the chimney and which delivers heat by radiation from the masonry surface of the heater.
2112.2 Installation. | Masonry heaters may be installed only when their use is permitted by the New York City Air Pollution Control Code. When such use is permitted, such appliances shall be operated in compliance with the New York City Air Pollution Control Code. Masonry heaters shall also be installed in accordance with this section and comply with one of the following: | 2112.2 Installation. | Masonry heaters shall be installed in accordance with this section and comply with one of the following:
2112.3 Footings and foundation. | The firebox floor of a masonry heater shall be a minimum thickness of 4 inches (102 mm) of noncombustible material and be supported on a noncombustible footing and foundation in accordance with Section 2113.2. | 2112.3 Footings and foundation. | The firebox floor of a masonry heater shall be a minimum thickness of 4 inches (102 mm) of noncombustible material and be supported on a noncombustible footing and foundation in accordance with Section 2113.2.
2112.4 Seismic reinforcing. | In structures assigned to Seismic Design Category D, masonry heaters shall be anchored to the masonry foundation in accordance with Section 2113.3. Seismic reinforcing shall not be required within the body of a masonry heater with a height that is equal to or less than 3.5 times its body width and where the masonry chimney serving the heater is not supported by the body of the heater. Where the masonry chimney shares a common wall with the facing of the masonry heater, the chimney portion of the structure shall be reinforced in accordance with Section 2113. | 2112.4 Seismic reinforcing. | In structures assigned to Seismic Design Category D, E or F, masonry heaters shall be anchored to the masonry foundation in accordance with Section 2113.3. Seismic reinforcing shall not be required within the body of a masonry heater with a height that is equal to or less than 3.5 times its body width and where the masonry chimney serving the heater is not supported by the body of the heater. Where the masonry chimney shares a common wall with the facing of the masonry heater, the chimney portion of the structure shall be reinforced in accordance with Section 2113.
2112.5 Masonry heater clearance. | Combustible materials shall not be placed within 36 inches (914 mm) or the distance of the allowed reduction method from the outside surface of a masonry heater in accordance with NFPA 211, Section 12.6╪, and the required space between the heater and combustible material shall be fully vented to permit the free flow of air around all heater surfaces. Exceptions: 1. Where the masonry heater wall thickness is at least 8 inches (203 mm) of solid masonry and the wall thickness of the heat exchange channels is not less than 5 inches (127 mm) of solid masonry, combustible materials shall not be placed within 4 inches (102 mm) of the outside surface of a masonry heater. A clearance of not less than 8 inches (203 mm) shall be provided between the gas-tight capping slab of the heater and a combustible ceiling. 2. Masonry heaters listed and labeled in accordance with UL 1482 or EN 15250 and installed in accordance with the manufacturer’s instructions. | 2112.5 Masonry heater clearance. | Combustible materials shall not be placed within 36 inches (914 mm) or the distance of the allowed reduction method from the outside surface of a masonry heater in accordance with NFPA 211, Section 12.6, and the required space between the heater and combustible material shall be fully vented to permit the free flow of air around all heater surfaces. Exceptions: 1. Where the masonry heater wall thickness is not less than 8 inches (203 mm) of solid masonry and the wall thickness of the heat exchange channels is not less than 5 inches (127 mm) of solid masonry, combustible materials shall not be placed within 4 inches (102 mm) of the outside surface of a masonry heater. A clearance of not less than 8 inches (203 mm) shall be provided between the gas-tight capping slab of the heater and a combustible ceiling. 2. Masonry heaters listed and labeled in accordance with UL 1482 or EN 15250 and installed in accordance with the manufacturer’s instructions.
2113.1 General. | The construction of masonry chimneys consisting of solid masonry units, hollow masonry units grouted solid, or stone shall be in accordance with this section. | 2113.1 General. | The construction of masonry chimneys consisting of solid masonry units, hollow masonry units grouted solid, stone or concrete shall be in accordance with this section.
2113.1.1 Chimney adequacy for temperature and gas action. | Chimneys shall be of adequate structural strength and resistant to the temperatures to which they may be subjected and to the corrosive action of gases.
2113.1.2 Chimney linings. | The lining in chimneys shall not be considered as taking either compression or tension stresses.
2113.1.3 Chimney expansion and contraction. | Expansion and contraction in chimney walls due to temperature variations shall be accommodated solely by the use of steel reinforcing rings.
2113.1.4 Reinforcing rings. | Reinforcing rings shall be provided at all changes in wall thickness, at the top of the chimney, and above and below all flue openings.
2113.1.5 Existing chimneys and vents. | Existing chimneys and vents shall comply with the requirements of Section 28-104.13 of the Administrative Code and Sections 107.18 and 2113.1.5.1 through 2113.1.5.8 of this code.
2113.1.5.1 Responsibility of owner of taller building. | Whenever a building is erected, enlarged, or increased in height so that any portion of such building, except chimneys or vents, extends higher than the top of any existing chimneys or vents within 100 feet (30 480 mm), the owner of such new or altered building shall have the responsibility of altering such chimneys or vents to make them conform with the requirements of this chapter. A chimney or vent that is no longer connected with a fireplace or combustion or other equipment for which a chimney or vent was required, shall be exempt from this requirement. Such alterations shall be accomplished by one of the following means or a combination thereof:
2113.1.5.1.1 Chimney and vent plan. | Applications for a new or altered building shall include a chimney and vent plan submitted pursuant to Section 107.18.
2113.1.5.2 Protection of draft. | After the alteration of a chimney or vent as required by this section, it shall be the responsibility of the owner of the new or altered building to provide any mechanical equipment or devices necessary to maintain the proper draft in the equipment.
2113.2 Footings and foundations. | Footings for masonry chimneys shall be constructed of concrete or solid masonry not less than 12 inches (305 mm) thick and shall extend at least 6 inches (152 mm) beyond the face of the foundation or support wall on all sides. Footings shall be founded on natural undisturbed earth or engineered fill below frost depth. In areas not subjected to freezing, footings shall be not less than 12 inches (305 mm) below finished grade. | 2113.2 Footings and foundations. | Footings for masonry chimneys shall be constructed of concrete or solid masonry not less than 12 inches (305 mm) thick and shall extend not less than 6 inches (152 mm) beyond the face of the foundation or support wall on all sides. Footings shall be founded on natural undisturbed earth or engineered fill below frost depth. In areas not subjected to freezing, footings shall be not less than 12 inches (305 mm) below finished grade.
2113.1.5.3 Written notification, plans and required documents. | The owner of the new or altered building shall notify the owner of any building that may require a chimney or vent to be altered. Notification, plans and required documents shall comply with the requirements of Sections 2113.1.5.3.1 through 2113.1.5.3.3.
2113.1.5.3.1 First notice. | Written notice in a form acceptable to the department shall be provided to the building owner not less than 60 days prior to a request for permit for construction on the new or altered building. Such notice shall include a request for access to determine the need to alter the existing chimney or vent and a description of such work. Notice shall be sent by regular mail and certified mail, return receipt requested. A copy of such return receipt shall be filed with the department.
2113.3.1 Vertical reinforcement. | For chimneys up to 40 inches (1016 mm) wide, four No. 4 continuous vertical bars anchored in the foundation shall be placed in the concrete between wythes of solid masonry or within the cells of hollow unit masonry and grouted in accordance with Section 2103.3. Grout shall be prevented from bonding with the flue liner so that the flue liner is free to move with thermal expansion. For chimneys greater than 40 inches (1016 mm) wide, two additional No. 4 vertical bars shall be provided for each additional 40 inches (1016 mm) in width or fraction thereof. | 2113.3.1 Vertical reinforcement. | For chimneys up to 40 inches (1016 mm) wide, four No. 4 continuous vertical bars anchored in the foundation shall be placed in the concrete between wythes of solid masonry or within the cells of hollow unit masonry and grouted in accordance with Section 2103.3. Grout shall be prevented from bonding with the flue liner so that the flue liner is free to move with thermal expansion. For chimneys greater than 40 inches (1016 mm) wide, two additional No. 4 vertical bars shall be provided for each additional 40 inches (1016 mm) in width or fraction thereof.
2113.1.5.3.2 Second notice. | Written notice in a form acceptable to the department shall be provided to the building owner not more than 45 days following commencement of work after a permit has been issued for the new or altered building. Such notice shall include a request for access to determine the need to alter the existing chimney or vent and a description of such work. Notice shall be sent by regular mail and certified mail, return receipt requested. The second notice shall also be posted by a licensed process server at the public entrance of the building requiring a chimney or vent to be altered. A copy of such return receipt and proof of service by the licensed process server shall be filed with the department. Exceptions: 1. A second notice shall not be required where an application to alter the affected chimney or vent has been filed with the department. 2. A second notice shall not be required where access is granted and conditions are observed that result in a determination that chimney or vent alteration is not required and a revised chimney and vent plan is submitted to the department.
2113.3.2 Horizontal reinforcement. | Vertical reinforcement shall be placed enclosed within ¼-inch (6.4 mm) ties, or other reinforcing of equivalent net cross-sectional area, spaced not to exceed 18 inches (457 mm) on center in concrete, or placed in the bed joints of unit masonry, at not less than every 18 inches (457 mm) of vertical height. Two such ties shall be provided at each bend in the vertical bars. | 2113.3.2 Horizontal reinforcement. | Vertical reinforcement shall be placed enclosed within 1/4-inch (6.4 mm) ties, or other reinforcing of equivalent net cross-sectional area, spaced not to exceed 18 inches (457 mm) on center in concrete, or placed in the bed joints of unit masonry, at not less than every 18 inches (457 mm) of vertical height. Two such ties shall be provided at each bend in the vertical bars.
2113.1.5.3.3 Plans and required documentation for alteration work. | Where access is granted and conditions are observed that result in a determination that chimney or vent alteration is required, plans for such alteration work shall be provided to the owner of the existing building and a request for written consent to submit construction documents and perform such work shall be made.
2113.4 Seismic anchorage. | Masonry chimneys and foundations shall be anchored at each floor, ceiling or roof line more than 6 feet (1829 mm) above grade with two 3/16-inch by 1-inch (4.8 mm by 25 mm) straps embedded not less than 12 inches (305 mm) into the chimney. Straps shall be hooked around the outer bars and extend 6 inches (152 mm) beyond the bend. Each strap shall be fastened to not less than four floor joists with two ½-inch (12.7 mm) bolts. Exception: Seismic anchorage is not required for the following: 1. In structures assigned to Seismic Design Category A or B. 2. Where the masonry fireplace is constructed completely within the exterior walls. | 2113.4 Seismic anchorage. | Masonry chimneys and foundations shall be anchored at each floor, ceiling or roof line more than 6 feet (1829 mm) above grade with two 3/16-inch by 1-inch (4.8 mm by 25 mm) straps embedded not less than 12 inches (305 mm) into the chimney. Straps shall be hooked around the outer bars and extend 6 inches (152 mm) beyond the bend. Each strap shall be fastened to not less than four floor joists with two 1/2-inch (12.7 mm) bolts. Exception: Seismic anchorage is not required for the following: 1. In structures assigned to Seismic Design Category A or B. 2. Where the masonry fireplace is constructed completely within the exterior walls.
2113.1.5.4 Approval. | The construction documents for the proposed chimney extension, alteration or relocation shall be submitted to the department pursuant to Section 28-104 of the Administrative Code. No certificate of occupancy shall be issued for the new building pursuant to Section 28-118.23 of the Administrative Code until the work associated with such construction documents for the proposed chimney extension, alteration or relocation has been signed-off by the department. Exceptions: 1. A certificate of occupancy may be issued where access is granted and conditions are observed that result in a determination that chimney or vent alteration is not required and a revised chimney or vent plan is submitted pursuant to Section 107.18 of the New York City Building Code documenting such. 2. A certificate of occupancy may be issued in accordance with Section 28-118.23, Exception 2 of the Administrative Code.
2113.5 Corbeling. | Masonry chimneys shall not be corbeled more than half of the chimney’s wall thickness from a wall or foundation, nor shall a chimney be corbeled from a wall or foundation that is less than 12 inches (305 mm) in thickness unless it projects equally on each side of the wall, except that on the second story of a two-story dwelling, corbeling of chimneys on the exterior of the enclosing walls is permitted to equal the wall thickness. The projection of a single course shall not exceed one-half the unit height or one-third of the unit bed depth, whichever is less. No masonry shall be corbeled from hollow or cavity wall masonry units. | 2113.5 Corbeling. | Masonry chimneys shall not be corbeled more than half of the chimney’s wall thickness from a wall or foundation, nor shall a chimney be corbeled from a wall or foundation that is less than 12 inches (305 mm) in thickness unless it projects equally on each side of the wall, except that on the second story of a two-story dwelling, corbeling of chimneys on the exterior of the enclosing walls is permitted to equal the wall thickness. The projection of a single course shall not exceed one-half the unit height or one-third of the unit bed depth, whichever is less.
2113.1.5.5 Refusal of consent. | If consent is not granted by the owner of the affected building to do the alteration work required by this section, such owner shall signify his or her refusal in writing to the owner of the new or altered building and to the commissioner; and the owner of the new or altered building having provided the notices required by Section 2113.1.5.3 shall thereupon be released from any responsibility for the proper operation of the equipment due to loss of draft and for any health hazard or nuisance that may occur as a result of the new or altered building. Such responsibilities shall then be assumed by the owner of the previously constructed building. Similarly, should such owner fail to grant consent within 45 days from the date of the second notice or fail to signify his or her refusal, he or she shall then assume all responsibilities as prescribed above.
2113.6 Changes in dimension. | The chimney wall or chimney flue lining shall not change in size or shape within 6 inches (152 mm) above or below where the chimney passes through floor components, ceiling components or roof components. | 2113.6 Changes in dimension. | The chimney wall or chimney flue lining shall not change in size or shape within 6 inches (152 mm) above or below where the chimney passes through floor components, ceiling components or roof components.
2113.1.5.6 Procedure. | It shall be the obligation of the owner of the new or altered building to:
2113.7 Offsets. | Where a masonry chimney is constructed with a fireclay flue liner surrounded by one wythe of masonry, the maximum offset shall be such that the centerline of the flue above the offset does not extend beyond the center of the chimney wall below the offset. Where the chimney offset is supported by masonry below the offset in an approved manner, the maximum offset limitations shall not apply. Each individual corbeled masonry course of the offset shall not exceed the projection limitations specified in Section 2113.5. | 2113.7 Offsets. | Where a masonry chimney is constructed with a fireclay flue liner surrounded by one wythe of masonry, the maximum offset shall be such that the centerline of the flue above the offset does not extend beyond the center of the chimney wall below the offset. Where the chimney offset is supported by masonry below the offset in an approved manner, the maximum offset limitations shall not apply. Each individual corbeled masonry course of the offset shall not exceed the projection limitations specified in Section 2113.5.
2113.1.5.7 Existing violations. | Any existing violations on the previously constructed equipment shall be corrected by the owner of the equipment before any equipment is added or alterations made at the expense of the owner of the new or altered building.
2113.8 Additional load. | Chimneys shall not support loads other than their own weight unless they are designed and constructed to support the additional load. Masonry chimneys are permitted to be constructed as part of the masonry walls or concrete walls of the building. | 2113.8 Additional load. | Chimneys shall not support loads other than their own weight unless they are designed and constructed to support the additional load. Masonry chimneys are permitted to be constructed as part of the masonry walls or concrete walls of the building.
2113.1.5.8 Variance. | The commissioner may grant a variance in accordance with the provisions of this code.
2113.9 Termination. | Chimneys serving appliances that operate at less than 600°F (316°C) shall extend at least 3 feet (914 mm) above the highest construction, such as a roof ridge, parapet wall, or penthouse, within 10 feet (3048 mm) of the chimney outlet, whether the construction is on the same building as the chimney or on another building. However, such constructions do not include other chimneys, vents, or open structural framing. Any chimney located beyond 10 feet (3048 mm) from such construction, but not more than the distance determined from Equation 21-2 and Table 2113.9, shall be at least as high as the construction. | 2113.9 Termination. | Chimneys shall extend not less than 2 feet (610 mm) higher than any portion of the building within 10 feet (3048 mm), but shall be not less than 3 feet (914 mm) above the highest point where the chimney passes through the roof. | See BC21 Tables and Figures
2113.9.1 Chimney caps. | Masonry chimneys shall have a concrete, metal or stone cap, sloped to shed water, a drip edge and a caulked bond break around any flue liners in accordance with ASTM C 1283. | 2113.9.1 Chimney caps. | Masonry chimneys shall have a concrete, metal or stone cap, sloped to shed water, a drip edge and a caulked bond break around any flue liners in accordance with ASTM C1283.
2113.3 Seismic reinforcing. | In structures assigned to Seismic Design Category A or B, or those exempt from seismic analysis, seismic reinforcement is not required. In structures assigned to Seismic Design Category C or D, masonry chimneys shall be analyzed and designed for seismic loading in accordance with TMS 402, and at a minimum shall be reinforced and anchored in accordance with Sections 2113.3.1, 2113.3.2, and 2113.4, Table 2111.1 and Figure 2111.1. |  |  | See BC21 Tables and Figures
2113.9.2 Spark arrestors. | Where a spark arrestor is installed on a masonry chimney, the spark arrestor shall meet all of the following requirements: | 2113.9.2 Spark arrestors. | Where a spark arrestor is installed on a masonry chimney, the spark arrestor shall meet all of the following requirements:
2113.9.3 Rain caps. | Termination caps shall not be permitted and a 3-inch (76 mm) minimum drain shall be installed to receive collected water. A positive means shall be provided to prevent water from entering the appliance. Exception: Termination caps shall be permitted on listed factory-built chimneys. | 2113.9.3 Rain caps. | Where a masonry or metal rain cap is installed on a masonry chimney, the net free area under the cap shall be not less than four times the net free area of the outlet of the chimney flue it serves.
2113.10 Wall thickness. | Masonry chimney walls shall be constructed of concrete, solid masonry units or hollow masonry units grouted solid with not less than 4 inches (102 mm) nominal thickness, or 8 inches (203 mm) nominal thickness for chimney walls extending more than 3 feet (914 mm) above the highest lateral support point. | 2113.10 Wall thickness. | Masonry chimney walls shall be constructed of concrete, solid masonry units or hollow masonry units grouted solid with not less than 4 inches (102 mm) nominal thickness.
2113.11 Flue lining (material). | Masonry chimneys shall be lined. The lining material shall be appropriate for the type of appliance connected, according to the terms of the appliance listing and the manufacturer’s instructions. | 2113.11 Flue lining (material). | Masonry chimneys shall be lined. The lining material shall be appropriate for the type of appliance connected, according to the terms of the appliance listing and the manufacturer’s instructions.
2113.11.1.1 Flue linings for specific appliances. | Flue linings other than those covered in Section 2113.11.1 intended for use with specific appliances shall comply with Sections 2113.11.1.2 through 2113.11.1.4 and Sections 2113.11.2 and 2113.11.3. | 2113.11.1.1 Flue linings for specific appliances. | Flue linings other than those covered in Section 2113.11.1 intended for use with specific appliances shall comply with Sections 2113.11.1.2 through 2113.11.1.4, 2113.11.2 and 2113.11.3.
2113.11.1.2 Gas appliances. | Flue lining systems for gas appliances shall be in accordance with the New York City Fuel Gas Code and ULC-S635. | 2113.11.1.2 Gas appliances. | Flue lining systems for gas appliances shall be in accordance with the International Fuel Gas Code.
2113.11.1.3 Pellet fuel-burning appliances. | Pellet fuel-burning appliances may be installed only when their use is permitted by the New York City Air Pollution Control Code. Any such appliances shall be listed and labeled and shall be installed in accordance with the terms of the listing. If permitted, such appliances shall be operated in compliance with the New York City Air Pollution Control Code. Flue lining and vent systems for use in masonry chimneys with pellet fuel-burning appliances shall be limited to flue lining systems complying with Section 2113.11.1 and pellet vents listed for installation within masonry chimneys. See Section 2113.11.1.5 for marking. | 2113.11.1.3 Pellet fuel-burning appliances. | Flue lining and vent systems for use in masonry chimneys with pellet fuel-burning appliances shall be limited to flue lining systems complying with Section 2113.11.1 and pellet vents listed for installation within masonry chimneys (see Section 2113.11.1.5 for marking).
2113.11.1.4 Oil-fired appliances approved for use with L-vent. | Flue lining and vent systems for use in masonry chimneys with oil-fired appliances approved for use with Type L vent shall be limited to flue lining systems complying with Section 2113.11.1 and listed chimney liners complying with UL 641. See Section 2113.11.1.5 for marking. | 2113.11.1.4 Oil-fired appliances approved for use with L-vent. | Flue lining and vent systems for use in masonry chimneys with oil-fired appliances approved for use with Type L vent shall be limited to flue lining systems complying with Section 2113.11.1 and listed chimney liners complying with UL 641 (see Section 2113.11.1.5 for marking).
2113.11.1.5 Notice of usage. | When a flue is relined with a material not complying with Section 2113.11.1, the chimney shall be plainly and permanently identified by a label attached to a wall, ceiling or other conspicuous location adjacent to where the connector enters the chimney. The label shall include the following message or equivalent language: “This chimney is for use only with (type or category of appliance) that burns (type of fuel). Do not connect other types of appliances.” | 2113.11.1.5 Notice of usage. | When a flue is relined with a material not complying with Section 2113.11.1, the chimney shall be plainly and permanently identified by a label attached to a wall, ceiling or other conspicuous location adjacent to where the connector enters the chimney. The label shall include the following message or equivalent language: “This chimney is for use only with (type or category of appliance) that burns (type of fuel). Do not connect other types of appliances.”
2113.9.3.1 Decorative shrouds. | Decorative shrouds shall not be installed at the termination of factory-built chimneys except where such shrouds are listed and labeled for use with the specific factory-built chimney system and are installed in accordance with the manufacturers’ installation instructions.
2113.11.2.1 Construction. | Chimneys for medium-heat appliances shall be constructed of solid masonry units with walls not less than 8 inches (203 mm) thick, or with stone masonry not less than 12 inches (305 mm) thick. Chimneys for medium-heat appliances constructed with radial brick may be permitted to have different requirements. Design of all such chimneys shall be submitted to the commissioner for approval. | 2113.11.2.1 Construction. | Chimneys for medium-heat appliances shall be constructed of solid masonry units or of concrete with walls not less than 8 inches (203 mm) thick, or with stone masonry not less than 12 inches (305 mm) thick.
2113.11.2.2 Lining. | Masonry chimneys shall be lined with an approved medium-duty refractory brick not less than 4½ inches (114 mm) thick laid on the 4½-inch bed (114 mm) in an approved medium-duty refractory mortar. The lining shall start 2 feet (610 mm) or more below the lowest chimney connector entrance. Chimneys terminating 25 feet (7620 mm) or less above a chimney connector entrance shall be lined to the top. | 2113.11.2.2 Lining. | Concrete and masonry chimneys shall be lined with an approved medium-duty refractory brick not less than 41/2 inches (114 mm) thick laid on the 41/2-inch bed (114 mm) in an approved medium-duty refractory mortar. The lining shall start 2 feet (610 mm) or more below the lowest chimney connector entrance. Chimneys terminating 25 feet (7620 mm) or less above a chimney connector entrance shall be lined to the top.
2113.11.2.3 Multiple passageway. | Masonry chimneys containing more than one passageway shall have the liners separated by a minimum 4-inch-thick (102 mm) concrete or solid masonry wall. | 2113.11.2.3 Multiple passageway. | Concrete and masonry chimneys containing more than one passageway shall have the liners separated by a minimum 4-inch-thick (102 mm) concrete or solid masonry wall.
2113.11.1 Residential-type appliances and low heat appliances (general). | Flue lining systems shall comply with one of the following:
2113.11.2.4 Termination height. | Chimneys serving appliances that operate at greater than 1,000°F (538°C) shall extend at least 20 feet (6096 mm) above the highest construction, such as roof ridge, parapet wall, penthouse, or other obstruction within 50 feet (15 240 mm) of the chimney outlet, whether the construction is on the same building as the chimney or in another building. However, such construction does not include other chimneys, vents, or open structural framing. Any chimney located beyond 50 feet (15 240 mm) from such construction but not more than the distance determined from Equation 21-2 and Table 2113.9, shall be at least as high as the construction. | 2113.11.2.4 Termination height. | Concrete and masonry chimneys for medium-heat appliances shall extend not less than 10 feet (3048 mm) higher than any portion of any building within 25 feet (7620 mm). | See BC21 Tables and Figures
2113.11.2.5 Clearance. | A minimum clearance of 4 inches (102 mm) shall be provided between the exterior surfaces of a masonry chimney for medium-heat appliances and combustible material. | 2113.11.2.5 Clearance. | A minimum clearance of 4 inches (102 mm) shall be provided between the exterior surfaces of a concrete or masonry chimney for medium-heat appliances and combustible material.
2113.11.3.1 Construction. | Chimneys for high-heat appliances shall be constructed with double walls of solid masonry units or of concrete, each wall to be not less than 8 inches (203 mm) thick with a minimum airspace of 2 inches (51 mm) between the walls. Alternate chimney designs for high-heat appliances constructed with radial brick shall be permitted subject to the approval of the commissioner. | 2113.11.3.1 Construction. | Chimneys for high-heat appliances shall be constructed with double walls of solid masonry units or of concrete, each wall to be not less than 8 inches (203 mm) thick with a minimum airspace of 2 inches (51 mm) between the walls.
2113.11.3.2 Lining. | The inside of the interior wall shall be lined with an approved high-duty refractory brick, not less than 4½ inches (114 mm) thick laid on the 4½-inch bed (114 mm) in an approved high-duty refractory mortar. The lining shall start at the base of the chimney and extend continuously to the top. | 2113.11.3.2 Lining. | The inside of the interior wall shall be lined with an approved high-duty refractory brick, not less than 41/2 inches (114 mm) thick laid on the 41/2-inch bed (114 mm) in an approved high-duty refractory mortar. The lining shall start at the base of the chimney and extend continuously to the top.
2113.11.3.3 Termination height. | Masonry chimneys for high-heat appliances shall extend not less than 20 feet (6096 mm) above the highest construction, such as roof ridge, parapet wall, penthouse, or other obstruction within 50 feet (15 240 mm) of the chimney outlet, whether the construction is on the same building as the chimney or on another building. However, such constructions do not include other chimneys, vents, or open structural framing. Any chimney located beyond 50 feet (15 240 mm) from such construction but not more than the distance determined from Equation 21-2 and Table 2113.9, shall be at least as high as the construction. | 2113.11.3.3 Termination height. | Concrete and masonry chimneys for high-heat appliances shall extend not less than 20 feet (6096 mm) higher than any portion of any building within 50 feet (15 240 mm). | See BC21 Tables and Figures
2113.11.2 Masonry chimneys for medium-heat appliances. | Masonry chimneys for medium-heat appliances shall comply with the provisions of Sections 2113.11.2.1 through 2113.11.2.5.
2113.11.3.4 Clearance. | Masonry chimneys for high-heat appliances shall have approved clearance from buildings and structures to prevent overheating combustible materials, permit inspection and maintenance operations on the chimney and prevent danger of burns to persons. | 2113.11.3.4 Clearance. | Concrete and masonry chimneys for high-heat appliances shall have approved clearance from buildings and structures to prevent overheating combustible materials, permit inspection and maintenance operations on the chimney and prevent danger of burns to persons.
2113.12 Clay flue lining (installation). | Flue liners shall be installed in accordance with ASTM C 1283 and extend from a point not less than 8 inches (203 mm) below the lowest inlet or, in the case of fireplaces, from the top of the smoke chamber to a point above the enclosing walls. The lining shall be carried up vertically, with a maximum slope no greater than 30 degrees (0.52 rad) from the vertical. | 2113.12 Clay flue lining (installation). | Clay flue liners shall be installed in accordance with ASTM C1283 and extend from a point not less than 8 inches (203 mm) below the lowest inlet or, in the case of fireplaces, from the top of the smoke chamber to a point above the enclosing walls. The lining shall be carried up vertically, with a maximum slope not greater than 30 degrees (0.52 rad) from the vertical.
2113.13 Additional requirements. | Masonry chimneys shall also comply with the additional requirements of Sections 2113.13.1 and 2113.13.2. | 2113.13 Additional requirements.
2113.13.1 Listed materials. | Listed materials used as flue linings shall be installed in accordance with the terms of their listings and the manufacturer’s instructions. | 2113.13.1 Listed materials. | Listed materials used as flue linings shall be installed in accordance with the terms of their listings and the manufacturer’s instructions.
2113.13.2 Space around lining. | The space surrounding a chimney lining system or vent installed within a masonry chimney shall not be used to vent any other appliance. Exception: This shall not prevent the installation of a separate flue lining in accordance with the manufacturer’s instructions. | 2113.13.2 Space around lining. | The space surrounding a chimney lining system or vent installed within a masonry chimney shall not be used to vent any other appliance. Exception: This shall not prevent the installation of a separate flue lining in accordance with the manufacturer’s instructions.
2113.14 Multiple flues. | When two or more flues are located in the same chimney, masonry wythes shall be built between adjacent flue linings. The masonry wythes shall be at least 4 inches (102 mm) thick and bonded into the walls of the chimney. Exception: When venting only one appliance, two flues are permitted to adjoin each other in the same chimney with only the flue lining separation between them. The joints of the adjacent flue linings shall be staggered not less than 4 inches (102 mm). | 2113.14 Multiple flues. | Where two or more flues are located in the same chimney, masonry wythes shall be built between adjacent flue linings. The masonry wythes shall be not less than 4 inches (102 mm) thick and bonded into the walls of the chimney. Exception: Where venting only one appliance, two flues are permitted to adjoin each other in the same chimney with only the flue lining separation between them. The joints of the adjacent flue linings shall be staggered not less than 4 inches (102 mm).
2113.11.3 Masonry chimneys for high-heat appliances. | Masonry chimneys for high-heat appliances shall comply with the provisions of Sections 2113.11.3.1 through 2113.11.3.4.
2113.15 Flue area (appliance). | Chimney flues shall not be smaller in area than the area of the connector from the appliance. Chimney flues connected to more than one appliance shall be not less than the area of the largest connector plus 50 percent of the areas of additional chimney connectors. Exceptions: 1. Chimney flues serving oil-fired appliances sized in accordance with the New York City Mechanical Code and NFPA 31. 2. Chimney flues serving gas-fired appliances sized in accordance with the New York City Fuel Gas Code. | 2113.15 Flue area (appliance). | Chimney flues shall not be smaller in area than the area of the connector from the appliance. Chimney flues connected to more than one appliance shall be not less than the area of the largest connector plus 50 percent of the areas of additional chimney connectors. Exceptions: 1. Chimney flues serving oil-fired appliances sized in accordance with NFPA 31. 2. Chimney flues serving gas-fired appliances sized in accordance with the International Fuel Gas Code.
2113.16 Flue area (masonry fireplace). | Flue sizing for chimneys serving fireplaces shall be in accordance with Section 2113.16.1 or 2113.16.2. | 2113.16 Flue area (masonry fireplace). | Flue sizing for chimneys serving fireplaces shall be in accordance with Section 2113.16.1 or 2113.16.2.
2113.16.1 Minimum area. | Round chimney flues shall have a minimum net cross-sectional area of not less than 1/12 of the fireplace opening. Square chimney flues shall have a minimum net cross-sectional area of not less than 1/10 of the fireplace opening. Rectangular chimney flues with an aspect ratio less than 2 to 1 shall have a minimum net cross-sectional area of not less than 1/10 of the fireplace opening. Rectangular chimney flues with an aspect ratio of 2 to 1 or more shall have a minimum net cross-sectional area of not less than ⅛ of the fireplace opening. | 2113.16.1 Minimum area. | Round chimney flues shall have a minimum net cross-sectional area of not less than 1/12 of the fireplace opening. Square chimney flues shall have a minimum net cross-sectional area of not less than 1/10 of the fireplace opening. Rectangular chimney flues with an aspect ratio less than 2 to 1 shall have a minimum net cross-sectional area of not less than 1/10 of the fireplace opening. Rectangular chimney flues with an aspect ratio of 2 to 1 or more shall have a minimum net cross-sectional area of not less than 1/8 of the fireplace opening.
2113.16.2 Determination of minimum area. | The minimum net cross-sectional area of the flue shall be determined in accordance with Figure 2113.16. A flue size providing not less than the equivalent net cross-sectional area shall be used. Cross-sectional areas of clay flue linings are as provided in Tables 2113.16(1) and 2113.16(2) or as provided by the manufacturer or as measured in the field. The height of the chimney shall be measured from the firebox floor to the top of the chimney flue. | 2113.16.2 Determination of minimum area. | The minimum net cross-sectional area of the flue shall be determined in accordance with Figure 2113.16. A flue size providing not less than the equivalent net cross-sectional area shall be used. Cross-sectional areas of clay flue linings are as provided in Tables 2113.16(1) and 2113.16(2) or as provided by the manufacturer or as measured in the field. The height of the chimney shall be measured from the firebox floor to the top of the chimney flue. | See BC21 Tables and Figures
2113.17 Inlet. | Inlets to masonry chimneys shall enter from the side. Inlets shall have a thimble of fireclay, rigid refractory material or metal that will prevent the connector from pulling out of the inlet or from extending beyond the wall of the liner. | 2113.17 Inlet. | Inlets to masonry chimneys shall enter from the side. Inlets shall have a thimble of fireclay, rigid refractory material or metal that will prevent the connector from pulling out of the inlet or from extending beyond the wall of the liner.
2113.18 Masonry chimney cleanout openings. | Cleanout openings shall be provided within 6 inches (152 mm) of the base of each flue within every masonry chimney. The upper edge of the cleanout shall be located not less than 6 inches (152 mm) below the lowest chimney inlet opening. The height of the opening shall be not less than 6 inches (152 mm). The cleanout shall be provided with a noncombustible cover. Exception: Chimney flues serving masonry fireplaces, where cleaning is possible through the fireplace opening. | 2113.18 Masonry chimney cleanout openings. | Cleanout openings shall be provided within 6 inches (152 mm) of the base of each flue within every masonry chimney. The upper edge of the cleanout shall be located not less than 6 inches (152 mm) below the lowest chimney inlet opening. The height of the opening shall be not less than 6 inches (152 mm). The cleanout shall be provided with a noncombustible cover. Exception: Chimney flues serving masonry fireplaces, where cleaning is possible through the fireplace opening.
2113.19 Chimney clearances. | Any portion of a masonry chimney located in the interior of the building or within the exterior wall of the building shall have a minimum airspace clearance to combustibles of 2 inches (51 mm). Chimneys located entirely outside the exterior walls of the building, including chimneys that pass through the soffit or cornice, shall have a minimum airspace clearance of 1 inch (25 mm). The airspace shall not be filled, except to provide fireblocking in accordance with Section 2113.20. Exceptions: 1. Masonry chimneys equipped with a chimney lining system listed and labeled for use in chimneys in contact with combustibles in accordance with UL 1777 and ULC-S635, and installed in accordance with the manufacturer’s instructions, are permitted to have combustible material in contact with their exterior surfaces. 2. Where masonry chimneys are constructed as part of masonry walls, combustible materials shall not be in contact with the masonry wall less than 12 inches (305 mm) from the inside surface of the nearest flue lining. 3. Exposed combustible trim and the edges of sheathing materials, such as wood siding, are permitted to abut the masonry chimney sidewalls, in accordance with Figure 2113.19, provided such combustible trim or sheathing is not less than 12 inches (305 mm) from the inside surface of the nearest flue lining. Combustible material and trim shall not overlap the corners of the chimney by more than 1 inch (25 mm). | 2113.19 Chimney clearances. | Any portion of a masonry chimney located in the interior of the building or within the exterior wall of the building shall have a minimum airspace clearance to combustibles of 2 inches (51 mm). Chimneys located entirely outside the exterior walls of the building, including chimneys that pass through the soffit or cornice, shall have a minimum airspace clearance of 1 inch (25 mm). The airspace shall not be filled, except to provide fireblocking in accordance with Section 2113.20. Exceptions: 1. Masonry chimneys equipped with a chimney lining system listed and labeled for use in chimneys in contact with combustibles in accordance with UL 1777, and installed in accordance with the manufacturer’s instructions, are permitted to have combustible material in contact with their exterior surfaces. 2. Where masonry chimneys are constructed as part of masonry or concrete walls, combustible materials shall not be in contact with the masonry or concrete wall less than 12 inches (305 mm) from the inside surface of the nearest flue lining. 3. Exposed combustible trim and the edges of sheathing materials, such as wood siding, are permitted to abut the masonry chimney sidewalls, in accordance with Figure 2113.19, provided that such combustible trim or sheathing is not less than 12 inches (305 mm) from the inside surface of the nearest flue lining. Combustible material and trim shall not overlap the corners of the chimney by more than 1 inch (25 mm).
2113.19.1 Additional requirements for clearance.
2113.20 Chimney fireblocking. | All spaces between chimneys and floors and ceilings through which chimneys pass shall be fireblocked with noncombustible material securely fastened in place. The fireblocking of spaces between wood joists, beams or headers shall be self-supporting or be placed on strips of metal or metal lath laid across the spaces between combustible material and the chimney. | 2113.20 Chimney fireblocking. | All spaces between chimneys and floors and ceilings through which chimneys pass shall be fireblocked with noncombustible material securely fastened in place. The fireblocking of spaces between wood joists, beams or headers shall be self-supporting or be placed on strips of metal or metal lath laid across the spaces between combustible material and the chimney.
2113.21 Test run. | All new chimneys shall be test run by the registered design professional responsible for the testing under standard conditions to demonstrate fire safety and the complete exhausting of smoke and the products of combustion to the outer air. The results of such test run shall be certified as correct by the design professional engineer responsible for the test and shall be submitted in writing to the department.
2113.22 Requirement of a smoke test. | A smoke test shall be made as outlined below. Any faults or leaks found shall be corrected. Such smoke test shall be witnessed by a representative of the commissioner. In lieu thereof, the commissioner may accept the test report of the design professional engineer responsible for the test, which shall be submitted in writing to the department.
2113.22.1 Smoke test. | To determine the tightness of chimney construction, a smoke test shall be made in accordance with the following conditions and requirements:
2114.1 General. | Load-bearing masonry structures shall be reinforced to meet all of the requirements of this section. However, reinforcement provided for gravity, seismic or wind forces or for other purposes may be regarded as satisfying part of, or the whole of, these requirements. Reinforcement provided for one requirement may be counted towards the other requirements. | 2114.1 General. | The design of dry-stack masonry structures shall comply with the requirements of Chapters 1 through 8 of TMS 402 except as modified by Sections 2114.2 through 2114.5.
2114.2 Continuity and ties. | Load-bearing masonry structures shall be reinforced to obtain a continuous system of vertical and horizontal ties. Continuity of all ties shall be ensured by providing lap, welded or mechanical tension splices. The following requirements shall be met for walls, columns and piers:
2114.2.1 Horizontal. | At each floor and roof level, continuous horizontal ties shall be provided in all load-bearing masonry walls, and around the perimeter of the building. Minimum horizontal tie reinforcement shall be not less than the equivalent of two No. 4 bars.
2114.2.1.1 Location of horizontal ties. | Ties shall be located within the thickness of walls or beams, where they occur, or within 1 foot (305 mm) of the edge of slab, where walls or beams do not occur.
2114.2.1.2 End connections of horizontal ties. | All horizontal ties shall be terminated in a perpendicular horizontal tie. Where no perpendicular horizontal tie exists within 4 feet (1219 mm) of the end of a wall, the horizontal tie shall be anchored at the end of the wall. The vertical reinforcement at the end of such walls shall not be less than two No. 4 bars placed within 16 inches (406 mm) of the end of the wall. This vertical reinforcement shall be continuous from the lowest to highest level of the wall, and anchored at each end in a horizontal tie or the foundation element.
2114.2.2 End connections. | Where slab or beam elements are supported on a masonry wall, column or pier, the connection shall be designed to sustain an axial tension capacity equal to the greater of the vertical shear capacity of the connected element at either end or 2 percent of the maximum factored vertical dead and live load in the compression masonry element. The design of the end connections shall ensure the transfer of such loads to horizontal or vertical ties.
2114.2.3 Vertical ties. | Each column, pier and wall shall be vertically tied continuously from its lowest to highest level. The vertical reinforcement shall be terminated in a horizontal tie or foundation or their equivalent. Where openings in bearing walls greater than 24 inches (610 mm) in height occur, ties shall be provided at each side of the opening that extend and are anchored in the masonry above and below the opening. Vertical ties shall be placed on both sides of control joints in bearing walls.
2114.2.3.1 Vertical ties reinforcing. | Vertical tie reinforcing shall not be less than the equivalent of one No. 4 bar, at a maximum spacing of 48 inches (1219 mm) on center. A minimum of four continuous No.4 bars shall be provided per masonry column or pier.
|  | 2108.2 TMS 402, Section 6. | 1.5.1.1, development. Modify the second paragraph of Section 6.1.5.1.1 as follows:
|  | 2109.2.1.1 Compressive strength. | Adobe units shall have an average compressive strength of 300 psi (2068 kPa) when tested in accordance with ASTM C67. Five samples shall be tested and individual units are not permitted to have a compressive strength of less than 250 psi (1724 kPa).
|  | 2109.2.1.2 Modulus of rupture. | Adobe units shall have an average modulus of rupture of 50 psi (345 kPa) when tested in accordance with the following procedure. Five samples shall be tested and individual units shall not have a modulus of rupture of less than 35 psi (241 kPa).
|  | 2109.2.1.2.1 Support conditions. | A cured unit shall be simply supported by 2-inch-diameter (51 mm) cylindrical supports located 2 inches (51 mm) in from each end and extending the full width of the unit.
|  | 2109.2.1.2.2 Loading conditions. | A 2-inch-diameter (51 mm) cylinder shall be placed at midspan parallel to the supports.
|  | 2109.2.1.2.3 Testing procedure. | A vertical load shall be applied to the cylinder at the rate of 500 pounds per minute (37 N/s) until failure occurs.
|  | 2109.2.1.2.4 Modulus of rupture determination. | The modulus of rupture shall be determined by the equation:
|  | 2109.2.1.3 Moisture content requirements. | Adobe units shall have a moisture content not exceeding 4 percent by weight.
|  | 2109.2.1.4 Shrinkage cracks. | Adobe units shall not contain more than three shrinkage cracks and any single shrinkage crack shall not exceed 3 inches (76 mm) in length or 1/8 inch (3.2 mm) in width.
|  | 2109.2.2 Stabilized adobe. | Stabilized adobe shall comply with Section 2109.2.1 for unstabilized adobe in addition to Sections 2109.2.2.1 and 2109.2.2.2.
|  | 2109.2.2.1 Soil requirements. | Soil used for stabilized adobe units shall be chemically compatible with the stabilizing material.
|  | 2109.2.2.2 Absorption requirements. | A 4-inch (102 mm) cube, cut from a stabilized adobe unit dried to a constant weight in a ventilated oven at 212°F to 239°F (100°C to 115°C), shall not absorb more than 21/2 percent moisture by weight when placed on a constantly water-saturated, porous surface for seven days. Not fewer than five specimens shall be tested and each specimen shall be cut from a separate unit.
|  | 2109.2.3 Allowable stress. | The allowable compressive stress based on gross cross-sectional area of adobe shall not exceed 30 psi (207 kPa).
|  | 2109.2.3.1 Bolts. | Bolt values shall not exceed those set forth in Table 2109.2.3.1. | See BC21 Tables and Figures
|  | 2109.2.4 Detailed requirements. | Adobe construction shall comply with Sections 2109.2.4.1 through 2109.2.4.9.
|  | 2109.2.4.1 Number of stories. | Adobe construction shall be limited to buildings not exceeding one story, except that two-story construction is allowed where designed by a registered design professional.
|  | 2109.2.4.2 Mortar. | Mortar for adobe construction shall comply with Sections 2109.2.4.2.1 and 2109.2.4.2.2.
|  | 2109.2.4.2.1 General. | Mortar for adobe units shall be in accordance with Section 2103.2.1, or be composed of adobe soil of the same composition and stabilization as the adobe brick units. Unstabilized adobe soil mortar is permitted in conjunction with unstabilized adobe brick units.
|  | 2109.2.4.2.2 Mortar joints. | Adobe units shall be laid with full head and bed joints and in full running bond.
|  | 2109.2.4.3 Parapet walls. | Parapet walls constructed of adobe units shall be waterproofed.
|  | 2109.2.4.4 Wall thickness. | The minimum thickness of exterior walls in one-story buildings shall be 10 inches (254 mm). The walls shall be laterally supported at intervals not exceeding 24 feet (7315 mm). The minimum thickness of interior load-bearing walls shall be 8 inches (203 mm). The unsupported height of any wall constructed of adobe units shall not exceed 10 times the thickness of such wall.
|  | 2109.2.4.5 Foundations. | Foundations for adobe construction shall be in accordance with Sections 2109.2.4.5.1 and 2109.2.4.5.2.
|  | 2109.2.4.5.1 Foundation support. | Walls and partitions constructed of adobe units shall be supported by foundations or footings that extend not less than 6 inches (152 mm) above adjacent ground surfaces and are constructed of solid masonry (excluding adobe) or concrete. Footings and foundations shall comply with Chapter 18.
|  | 2109.2.4.5.2 Lower course requirements. | Stabilized adobe units shall be used in adobe walls for the first 4 inches (102 mm) above the finished first-floor elevation.
|  | 2109.2.4.6 Isolated piers or columns. | Adobe units shall not be used for isolated piers or columns in a load-bearing capacity. Walls less than 24 inches (610 mm) in length shall be considered to be isolated piers or columns.
|  | 2109.2.4.7 Tie beams. | Exterior walls and interior load-bearing walls constructed of adobe units shall have a continuous tie beam at the level of the floor or roof bearing and meeting the following requirements.
|  | 2109.2.4.7.1 Concrete tie beams. | Concrete tie beams shall be 6 inches (152 mm) or more in depth and 10 inches (254 mm) or more in width. Concrete tie beams shall be continuously reinforced with not fewer than two No. 4 reinforcing bars. The specified compressive strength of concrete shall be not less than 2,500 psi (17.2 MPa).
|  | 2109.2.4.7.2 Wood tie beams. | Wood tie beams shall be solid or built up of lumber having a nominal thickness of not less than 1 inch (25 mm), and shall have a depth of not less than 6 inches (152 mm) and a width of not less than 10 inches (254 mm). Joints in wood tie beams shall be spliced not less than 6 inches (152 mm). Splices shall not be allowed within 12 inches (305 mm) of an opening. Wood used in tie beams shall be approved naturally decay-resistant or preservative-treated wood.
|  | 2109.2.4.8 Exterior finish. | Exterior finishes applied to adobe masonry walls shall be of any type permitted by this section or Chapter 14, except where stated otherwise in this section.
|  | 2109.2.4.8.1 Where required. | Unstabilized adobe masonry walls shall receive a weather protective exterior finish in accordance with Section 2109.2.4.8.
|  | 2109.2.4.8.2 Vapor permeance. | Plaster and finish assemblies shall have a vapor permeance of not less than 5 perms. Exception: Insulation products applied to the exterior of stabilized adobe masonry walls in Climate Zones 2B, 3B, 4B and 5B shall not have a vapor permeance requirement.
|  | 2109.2.4.8.3 Plaster thickness and coats. | Plaster applied to adobe masonry shall be not less than 7/8 inch (22 mm) and not greater than 2 inches (51 mm) thick. Plaster shall be applied in not less than two coats.
|  | 2109.2.4.8.4 Plaster application. | Where plaster is applied directly to adobe masonry walls, no intermediate membrane shall be used.
|  | 2109.2.4.8.5 Lath for plaster. | Lath shall be provided for all plasters, except where not required elsewhere in Section 2109.2.4.8. Fasteners shall be corrosion resistant and spaced at a maximum of 16 inches (406 mm) on center with a minimum 11/2-inch (38 mm) penetration into the adobe wall. Metal lath shall comply with ASTM C1063, as modified by this section, and shall be corrosion resistant. Plastic lath shall comply with ASTM C1788, as modified by this section. Wood substrates shall be protected with No. 15 asphalt felt, an approved wood preservative or other protective coating prior to lath application.
|  | 2109.2.4.8.6 Cement plaster. | Cement plaster shall conform to ASTM C926 and shall comply with Chapter 25, except that the proportion of lime in plaster coats shall be not less than 1 part lime to 4 parts cement. The combined thickness of cement plaster coats shall not exceed 1 inch (25 mm).
|  | 2109.2.4.8.7 Lime plaster. | Lime plaster is any plaster with a binder composed of calcium hydroxide, including Type N or S hydrated lime, hydraulic lime, natural hydraulic lime, or slaked quicklime. Hydrated lime shall comply with ASTM C206. Hydraulic lime shall comply with ASTM C1707. Natural hydraulic lime shall comply with ASTM C141 and EN 459. Quicklime shall comply with ASTM C5.
|  | 2109.2.4.8.8 Cement-lime plaster. | Cement-lime plaster shall be any plaster mix type CL, F or FL, as described in ASTM C926.
|  | 2109.2.4.8.9 Clay plaster. | Clay plaster shall comply with this section.
|  | 2109.2.4.8.9.1 General. | Clay plaster shall be any plaster having a clay or clay subsoil binder. Such plaster shall contain sufficient clay to fully bind the aggregate and shall be permitted to contain reinforcing fibers. Acceptable reinforcing fibers include chopped straw, sisal, and animal hair.
|  | 2109.2.4.8.9.2 Clay subsoil requirements. | The suitability of clay subsoil shall be determined in accordance with the Figure 2 Ribbon Test and the Figure 3 Ball Test in the appendix of ASTM E2392/E2392M.
|  | 2109.2.4.8.9.3 Weather-exposed locations. | Clay plaster exposed to water from direct or wind-driven rain or snow shall be finished with an approved erosion-resistant finish. The use of clay plasters shall not be permitted on weather-exposed parapets.
|  | 2109.2.4.8.9.4 Prohibited finish coat. | Plaster containing Portland cement shall not be permitted as a finish over clay plaster.

## BC22
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2201.1 Scope. | The provisions of this chapter govern the quality, design, fabrication and erection of steel construction. | 2201.1 Scope. | The provisions of this chapter govern the quality, design, fabrication and erection of steel construction.
2201.2 Special inspection. | Steel shall be subject to the requirements of special inspection in accordance with Chapter 17.
2202.1 Definitions. | The following terms are defined in Chapter 2.
2203.1 Identification. | Identification of structural steel elements shall be in accordance with the requirements contained in AISC 303. Identification of cold-formed steel members shall be in accordance with the requirements contained in AISI S100. Identification of cold-formed steel light-frame construction shall also comply with the requirements contained in AISI S240 or AISI S220, as applicable. Other steel furnished for structural load-carrying purposes shall be properly identified for conformity to the ordered grade in accordance with the specified ASTM standard or other specification and the provisions of this chapter. Where the steel grade is not readily identifiable from marking and test records, the steel shall be tested to determine conformity to such standards.
2204.1 Welding. | The details of design, workmanship and technique for welding and qualification of welding procedures and personnel shall in accordance with the specifications listed in Sections 2205, 2206, 2207, 2208, 2210 and 2211. For special inspection of welding, see Section 1705.2. | 2204.1 Welding. | The details of design, workmanship and technique for welding and qualification of welding personnel shall be in accordance with the specifications listed in Sections 2205, 2206, 2207, 2208, 2210 and 2211. For special inspection of welding, see Section 1705.2.
2203.2 Protection. | Coating of structural steel elements shall be in accordance with AISC 360. Coating of open-web steel joists and joist girders shall be in accordance with SJI 100 and SJI 200. Individual structural members and assembled panels of cold-formed steel construction shall be protected against corrosion in accordance with the requirements contained in AISI S100. Protection of cold-formed steel light-frame construction shall be in accordance with AISI S240 or AISI S220, as applicable.
2204.2 Bolting. | The design, installation and inspection of bolts shall be in accordance with the requirements of Sections 2205, 2206, 2207, 2210 and 2211. For special╪ inspection of the installation of high-strength bolts, see Section 1705.2. | 2204.2 Bolting. | The design, installation and inspection of bolts shall be in accordance with the requirements of Sections 2205, 2206, 2207, 2210 and 2211. For special inspection of the installation of high-strength bolts, see Section 1705.2.
2204.3 Anchor rods. | Anchor rods shall be set in accordance with the approved construction documents. The protrusion of the threaded ends through the connected material shall. The entire projection of the rod beyond the connected material shall be fully threaded. | 2204.3 Anchor rods. | Anchor rods shall be set in accordance with the approved construction documents. The protrusion of the threaded ends through the connected material shall fully engage the threads of the nuts but shall not be greater than the length of the threads on the bolts.
2205.1 General. | The design, fabrication and erection of structural steel elements in buildings, including materials used for such elements, shall be in accordance with AISC 360. | 2205.1 General. | The design, fabrication and erection of structural steel elements in buildings, structures and portions thereof shall be in accordance with AISC 360.
2205.2.1 Structural steel seismic force-resisting systems. | The design, detailing, fabrication and erection of structural steel seismic force-resisting systems, and the material used for such systems, shall be in accordance with the provisions of Section 2205.2.1.1 or 2205.2.1.2, as applicable. | 2205.2.1 Structural steel seismic force-resisting systems. | The design, detailing, fabrication and erection of structural steel seismic force-resisting systems shall be in accordance with the provisions of Section 2205.2.1.1 or 2205.2.1.2, as applicable.
2205.1.1 Structural steel. | Material for use as structural steel not listed in AISC 360 may be used in accordance with AISC 360 when approved by the commissioner for such use. Refer to Section 28-113.2.2 of the Administrative Code for provisions relating to approval of alternative materials.
2205.2.1.1 Seismic Design Category B or C. | Structures assigned to Seismic Design Category B or C shall be of any construction permitted in Section 2205. Where a response modification coefficient, R, in accordance with Table 1613.5, is used for the design of structures assigned to Seismic Design Category B or C, the structures shall be designed and detailed in accordance with the requirements of AISC 341. Exception: The response modification coefficient, R, designated for “Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems” in Table 1613.5, shall be permitted for systems designed and detailed in accordance with AISC 360, and need not be designed and detailed in accordance with AISC 341. | 2205.2.1.1 Seismic Design Category B or C. | Structures assigned to Seismic Design Category B or C shall be of any construction permitted in Section 2205. Where a response modification coefficient, R, in accordance with ASCE 7, Table 12.2-1, is used for the design of structures assigned to Seismic Design Category B or C, the structures shall be designed and detailed in accordance with the requirements of AISC 341. Beam-to-column moment connections in special moment frames and intermediate moment frames shall be prequalified in accordance with AISC 341, Section K1, qualified by testing in accordance with AISC 341, Section K2, or shall be prequalified in accordance with AISC 358. Exception: The response modification coefficient, R, designated for “Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems” in ASCE 7, Table 12.2-1, shall be permitted for systems designed and detailed in accordance with AISC 360, and need not be designed and detailed in accordance with AISC 341. | See BC16 Tables and Figures | See BC 12 Tables and Figures
2205.2 Seismic design and detailing. | Where required,a building’s seismic design, detailing, material, fabrication and erection shall be in accordance with Section 2205.2.1 or 2205.2.2, as applicable.
2205.2.2 Structural steel elements. | The design, detailing, fabrication and erection of structural steel elements in seismic force-resisting systems other than those covered in Section 2205.2.1, including struts, collectors, chords and foundation elements, shall be in accordance with AISC 341 where either of the following applies: | 2205.2.2 Structural steel elements. | The design, detailing, fabrication and erection of structural steel elements in seismic force-resisting systems other than those covered in Section 2205.2.1, including struts, collectors, chords and foundation elements, shall be in accordance with AISC 341 where either of the following applies:
2206.1 General. | Systems of structural steel elements acting compositely with reinforced concrete shall be designed in accordance with AISC 360 and ACI 318, excluding ACI 318 Chapter 14. | 2206.1 General. | Systems of structural steel elements acting compositely with reinforced concrete shall be designed in accordance with AISC 360 and ACI 318, excluding ACI 318 Chapter 14.
2205.2.1.2 Seismic Design Category D. | Structures assigned to Seismic Design Category D shall be designed and detailed in accordance with AISC 341, except as specified in Table 1613.5. |  |  | See BC16 Tables and Figures
2206.2 Seismic design. | Where required, the seismic design, materials, fabrication and erection of composite steel and concrete systems shall be in accordance with Section 2206.2.1. | 2206.2 Seismic design. | Where required, the seismic design, fabrication and erection of composite steel and concrete systems shall be in accordance with Section 2206.2.1.
2206.2.1 Seismic requirements for composite structural steel and concrete construction. | Where a response modification coefficient, R, in accordance with Table 1613.5, is used for the design of systems of structural steel acting compositely with reinforced concrete, the structures shall be designed and detailed in accordance with the requirements of AISC 341. | 2206.2.1 Seismic requirements for composite structural steel and concrete construction. | Where a response modification coefficient, R, in accordance with ASCE 7, Table 12.2-1, is used for the design of systems of structural steel acting compositely with reinforced concrete, the structures shall be designed and detailed in accordance with the requirements of AISC 341. | See BC16 Tables and Figures | See BC 12 Tables and Figures
2205.3 Fabrication, erection and quality control. | In addition to the provisions for fabrication, erection and quality control in AISC 360, the following provisions shall be used.
2207.1 General. | The design, manufacture and use of open-web steel joists and joist girders shall be in accordance with SJI 100 or SJI 200, as applicable. | 2207.1 General. | The design, manufacture and use of open-web steel joists and joist girders shall be in accordance with either SJI 100 or SJI 200, as applicable.
2205.3.1 Shop drawings. | Shop drawings shall include the location of oversized, short slotted and long slotted holes, and shall comply with AISC 303.
2207.1.1 Seismic design. | Where required, the seismic design of buildings shall be in accordance with the additional provisions of Section 2205.2 or 2211.1.1. | 2207.1.1 Seismic design. | Where required, the seismic design of buildings shall be in accordance with the additional provisions of Section 2205.2 or 2211.1.1.
2205.3.2 Field connections. | Field connections shall meet the requirements for corresponding types of shop connections described in AISC 360. No holes, copes or cuts of any type, or alterations to anchor rods, shall be made to facilitate erection unless specifically shown on the shop or erection drawings or authorized in writing by the registered design professional of record for the structural design.
2207.2 Design. | The registered design professional of record shall indicate on the construction documents the steel joist and steel joist girder designations from the specifications listed in Section 2207.1; and shall indicate the requirements for joist and joist girder design, layout, end supports, anchorage, bridging design that differs from the SJI specifications listed in Section 2207.1, bridging termination connections and bearing connection design to resist uplift and lateral loads. These documents shall indicate special requirements as follows: | 2207.2 Design. | The registered design professional shall indicate on the construction documents the steel joist and steel joist girder designations from the specifications listed in Section 2207.1; and shall indicate the requirements for joist and joist girder design, layout, end supports, anchorage, bridging design that differs from the SJI specifications listed in Section 2207.1, bridging termination connections and bearing connection design to resist uplift and lateral loads. These documents shall indicate special requirements as follows:
2205.3.3 Structural steel erection. | The requirements of Section 3305.2 shall apply.
2207.3 Calculations. | The steel joist and joist girder manufacturer shall design the steel joists and steel joist girders in accordance with the SJI specifications listed in Section 2207.1 to support the load requirements of Section 2207.2. The registered design professional of record shall be permitted to require submission of the steel joist and joist girder calculations as prepared by a registered design professional responsible for the product design. Where requested by the registered design professional of record, the steel joist manufacturer shall submit design calculations with a cover letter bearing the seal and signature of the joist manufacturer’s registered design professional. In addition to the design calculations submitted under seal and signature, the following shall be included: | 2207.3 Calculations. | The steel joist and joist girder manufacturer shall design the steel joists and steel joist girders in accordance with the SJI specifications listed in Section 2207.1 to support the load requirements of Section 2207.2. The registered design professional shall be permitted to require submission of the steel joist and joist girder calculations as prepared by a registered design professional responsible for the product design. Where requested by the registered design professional, the steel joist manufacturer shall submit design calculations with a cover letter bearing the seal and signature of the joist manufacturer’s registered design professional. In addition to the design calculations submitted under seal and signature, the following shall be included:
2207.4 Steel joist drawings. | Steel joist placement plans shall be provided to show the steel joist products as specified on the approved construction documents and are to be utilized for field installation in accordance with specific project requirements as stated in Section 2207.2. Steel joist placement plans shall include, at a minimum, the following: | 2207.4 Steel joist drawings. | Steel joist placement plans shall be provided to show the steel joist products as specified on the approved construction documents and are to be utilized for field installation in accordance with specific project requirements as stated in Section 2207.2. Steel joist placement plans shall include, at a minimum, the following:
2207.5 Certification. | At completion of manufacture, the steel joist manufacturer shall submit a certificate of compliance in accordance with Section 1704.2.2 stating that work was performed in accordance with approved construction documents and with SJI specifications listed in Section 2207.1. | 2207.5 Certification. | At completion of manufacture, the steel joist manufacturer shall submit a certificate of compliance to the owner or the owner’s authorized agent for submittal to the building official as specified in Section 1704.5 stating that work was performed in accordance with approved construction documents and with SJI specifications listed in Section 2207.1.
2208.1 General. | The design, fabrication and erection including related connections, and protective coatings of steel cables for buildings shall be in accordance with ASCE 19. | 2208.1 General. | The design, fabrication and erection including related connections, and protective coatings of steel cables for buildings shall be in accordance with ASCE 19.
2206.3 Fabrication, erection and quality control. | The fabrication, erection and quality control of composite structural steel and concrete construction shall comply with the applicable requirements of Sections 2205 and 3305, and Chapter 19 of this code, AISC 360, AISC 341 and ACI 318.
2206.4 Concrete-filled steel columns. | Concrete-filled steel columns shall comply with Section 2206.4.1 through 2206.4.5 and shall be filled with concrete so placed and manipulated as to secure maximum density and to ensure complete filling of the steel without voids.
2206.4.1 Design. | The safe supporting capacity of concrete-filled steel columns shall be computed in accordance with AISC 360 or as determined by a test approved by the commissioner.
2206.4.2 Connections. | Caps, base plates and connections shall be in accordance with AISC 360 and shall be positively attached to the shell and anchored to the concrete core. Welding of brackets without mechanical anchorage is prohibited. Where the pipe is slotted to accommodate webs of brackets or other connections, the integrity of the shell shall be restored by welding to ensure hooping action of the composite section.
2210.1 General. | The design of cold-formed carbon and low-alloy steel structural members shall be in accordance with AISI S100. The design of cold-formed stainless-steel structural members shall be in accordance with ASCE 8. Cold-formed steel light-frame construction shall comply with Section 2211. Where required, the seismic design of cold-formed steel structures shall be in accordance with the additional provisions of Section 2210.2.╪ | 2210.1 General. | The design of cold-formed carbon and low-alloy steel structural members shall be in accordance with AISI S100. The design of cold-formed stainless-steel structural members shall be in accordance with ASCE 8. Cold-formed steel light-frame construction shall comply with Section 2211. Where required, the seismic design of cold-formed steel structures shall be in accordance with the additional provisions of Section 2210.2.
2206.4.3 Reinforcement. | Steel reinforcement shall be in the form of rods, structural shapes or pipe embedded in the concrete core in accordance with AISC 360 with sufficient clearance to ensure the composite action of the section, but not nearer than 1 inch (25 mm) to the exterior steel shell. Structural shapes used as reinforcement shall be milled to ensure bearing on cap and base plates.
2210.1.1 Steel decks. | The design and construction of cold-formed steel decks shall be in accordance with this section. | 2210.1.1 Steel decks. | The design and construction of cold-formed steel decks shall be in accordance with this section.
2206.4.4 Fire-resistance-rating protection of concrete filled columns. | Concrete-filled steel columns shall comply with the required fire-resistance ratings specified in Table 601. Where an outer steel shell is used to enclose the fire protective covering, the shell shall not be included in the calculations for strength of the column section. The minimum diameter of steel columns shall be 4 inches (102 mm) except that in structures of Type V construction not exceeding three stories or 40 feet (12 192 mm) above grade plane, steel columns used in basements and as secondary steel members shall have a minimum diameter of 3 inches (76 mm). |  |  | See BC6 Tables and Figures
2206.4.4.1 Vent holes. | Concrete-filled steel columns shall have a minimum of four ½ in. (12.7 mm) diameter holes that shall be placed opposite each other with two at the top and two at the bottom of the column. The two bottom holes shall be rotated 90° relative to the two top holes.
2206.4.5 Approvals. | Details of column connections and splices shall be shop-fabricated in accordance with AISC 360. Concrete-filled steel columns shall be inspected by an approved agency pursuant to Chapter 17 of this code.
2207.6 Limitations of use. | Open web steel joists shall be prohibited in high-rise buildings until the commissioner promulgates rules establishing minimum acceptable fireproofing methods.
2209.1 Storage racks. | The design, testing and utilization of storage racks made of cold-formed or hot-rolled steel structural members shall be in accordance with RMI ANSI /MH 16.1. Where required by ASCE 7, the seismic design of storage racks shall be in accordance with Section 15.5.3 of ASCE 7.
2209.2 Cantilevered steel storage racks. | The design, testing, and utilization of cantilevered storage racks made of cold-formed or hot-rolled steel structural members shall be in accordance with RMI ANSI/MH 16.3 Where required by ASCE 7, the seismic design of cantilevered steel storage racks shall be in accordance with Section 15.5.3 of ASCE 7.
2210.1.1.1 Noncomposite steel floor decks. | Noncomposite steel floor decks shall be permitted to be designed and constructed in accordance with ANSI/SDI-NC. | 2210.1.1.1 Noncomposite steel floor decks. | Noncomposite steel floor decks shall be permitted to be designed and constructed in accordance with ANSI/SDI-NC1.0.
2210.1.1.2 Steel roof deck. | Steel roof decks shall be permitted to be designed and constructed in accordance with ANSI/SDI-RD. | 2210.1.1.2 Steel roof deck. | Steel roof decks shall be permitted to be designed and constructed in accordance with ANSI/SDI-RD1.0.
2210.1.1.3 Composite slabs on steel decks. | Composite slabs of concrete and steel deck shall be permitted to be designed and constructed in accordance with SDI-C. | 2210.1.1.3 Composite slabs on steel decks. | Composite slabs of concrete and steel deck shall be permitted to be designed and constructed in accordance with SDI-C.
2210.2 Seismic requirements for cold-formed steel structures. | Where a response modification coefficient, R, in accordance with Table 1613.5, is used for the design of cold-formed steel structures, the structures shall be designed and detailed in accordance with the requirements of AISI S100, ASCE 8, or, for cold-formed steel special-bolted moment frames, AISI S400. | 2210.2 Seismic requirements for cold-formed steel structures. | Where a response modification coefficient, R, in accordance with ASCE 7, Table 12.2-1, is used for the design of cold-formed steel structures, the structures shall be designed and detailed in accordance with the requirements of AISI S100, ASCE 8, or, for cold-formed steel special-bolted moment frames, AISI S400. | See BC16 Tables and Figures | See BC 12 Tables and Figures
2211.1 Structural framing. | For cold-formed steel light-frame construction, the design and installation of the following structural framing systems, including their members and connections, shall be in accordance with AISI S240, and Sections 2211.1.1 through 2211.1.3, as applicable: | 2211.1 Structural framing. | For cold-formed steel light-frame construction, the design and installation of the following structural framing systems, including their members and connections, shall be in accordance with AISI S240, and Sections 2211.1.1 through 2211.1.3, as applicable:
2211.1.1 Seismic requirements for cold-formed steel structural systems. | The design of cold-formed steel light-frame construction to resist seismic forces shall be in accordance with the provisions of Section 2211.1.1.1 or 2211.1.1.2, as applicable. | 2211.1.1 Seismic requirements for cold-formed steel structural systems. | The design of cold-formed steel light-frame construction to resist seismic forces shall be in accordance with the provisions of Section 2211.1.1.1 or 2211.1.1.2, as applicable.
2211.1.1.1 Seismic Design Categories B and C. | Where a response modification coefficient, R, in accordance with Table 1613.5 is used for the design of cold-formed steel light-frame construction assigned to Seismic Design Category B or C, the seismic force-resisting system shall be designed and detailed in accordance with the requirements of AISI S400. Exception: The response modification coefficient, R, designated for "Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems" in Table 1613.5 shall be permitted for systems designed and detailed in accordance with AISI S240 and need not be designed and detailed in accordance with AISI S400. | 2211.1.1.1 Seismic Design Categories B and C. | Where a response modification coefficient, R, in accordance with ASCE 7, Table 12.2-1 is used for the design of cold-formed steel light-frame construction assigned to Seismic Design Category B or C, the seismic force-resisting system shall be designed and detailed in accordance with the requirements of AISI S400. Exception: The response modification coefficient, R, designated for “Steel systems not specifically detailed for seismic resistance, excluding cantilever column systems” in ASCE 7, Table 12.2-1, shall be permitted for systems designed and detailed in accordance with AISI S240 and need not be designed and detailed in accordance with AISI S400 | See BC16 Tables and Figures | See BC 12 Tables and Figures
2211.1.1.2 Seismic Design Categories D. | In cold-formed steel light-frame construction assigned to Seismic Design Category D, the seismic force-resisting system shall be designed and detailed in accordance with AISI S400.
2211.1.2 Prescriptive framing. | Detached one- and two-family dwellings and townhouses, less than or equal to three stories above grade plane, shall be permitted to be constructed in accordance with AISI S230 subject to the limitations therein. | 2211.1.2 Prescriptive framing. | Detached one- and two-family dwellings and townhouses, less than or equal to three stories above grade plane, shall be permitted to be constructed in accordance with AISI S230 subject to the limitations therein.
2211.1.3 Truss design. | Cold-formed steel trusses shall comply with the additional provisions of Sections 2211.1.3.1. through 2211.1.3.3. | 2211.1.3 Truss design. | Cold-formed steel trusses shall comply with the additional provisions of Sections 2211.1.3.1. through 2211.1.3.3.
2211.1.3.1 Truss design drawings. | The truss design drawings shall conform to the requirements of Section I1 of AISI S202 and shall be provided with the shipment of trusses delivered to the job site. The truss design drawings shall include the details of permanent individual truss member restraint/bracing in accordance with Section I1.6 of AISI S202 where these methods are utilized to provide restraint/bracing. | 2211.1.3.1 Truss design drawings. | The truss design drawings shall conform to the requirements of Section I1 of AISI S202 and shall be provided with the shipment of trusses delivered to the job site. The truss design drawings shall include the details of permanent individual truss member restraint/bracing in accordance with Section I1.6 of AISI S202 where these methods are utilized to provide restraint/bracing.
2211.1.3.2 Trusses spanning 60 feet or greater. | The owner or the owner’s authorized agent shall contract with a registered design professional for the design of the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing for trusses with clear spans 60 feet (18 288 mm) or greater. Special inspection of trusses over 60 feet (18 288 mm) in length shall be in accordance with Section 1705.2. | 2211.1.3.2 Trusses spanning 60 feet or greater. | The owner or the owner’s authorized agent shall contract with a registered design professional for the design of the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing for trusses with clear spans 60 feet (18 288 mm) or greater. Special inspection of trusses over 60 feet (18 288 mm) in length shall be in accordance with Section 1705.2.
2211.1.3.3 Truss quality assurance. | Trusses not part of a manufacturing process that provides requirements for quality control done under the supervision of a third-party quality control agency in accordance with AISI S240 Chapter D shall be fabricated in compliance with Sections 1704.2.2 and 1705.2, as applicable. | 2211.1.3.3 Truss quality assurance. | Trusses not part of a manufacturing process that provides requirements for quality control done under the supervision of a third-party quality control agency in accordance with AISI S240 Chapter D shall be fabricated in compliance with Sections 1704.2.5 and 1705.2, as applicable.
2211.2 Nonstructural members. | For cold-formed steel light-frame construction, the design and installation of non-structural members and connections shall be in accordance with AISI S220. | 2211.2 Nonstructural members. | For cold-formed steel light-frame construction, the design and installation of nonstructural members and connections shall be in accordance with AISI S220.
2212.1 General. | All steel of Chapter 22 shall conform to the minimum thickness of metal in accordance with Section 2212.2.
2212.2 Exterior members. | All exterior structural steel members exposed to weather shall have a minimum thickness of metal of 0.23 inches (5.8 mm). Exceptions: 1. When an approved type of atmospheric corrosion- resistant steel is used. 2. Exposed surfaces are zinc coated with a minimum weight of coating of approximately 0.6 ounces per square foot (0.00 156 kg/m2) of exposed surface and covered with a protective coating as required by Section 2203.2. 3. Exposed surfaces are protected by other means approved by the commissioner. 4. Temporary construction installations that will be in place for a period of 1 year or less, provided that all surfaces which are exposed to the weather shall have a protective coating as required by Section 2203.2. 5. Joists or purlins that are exposed to the weather but which do not support more than 200 square feet (19 m2) of floor or roof area, and which have a protective coating as required by Section 2203.2.
2213.1 General. | Steel structures shall be designed to meet all of the requirements of this section. However, details provided for gravity, seismic and wind forces and for other purposes may be regarded as forming part of, or the whole of, these requirements. Detailing provided for one requirement may be counted towards the other requirements. Exceptions: 1. One-story structures less than 5,000 square feet (465 m2) not to exceed 15 feet (4572 mm) in height. 2. Structures containing only Group R-3 occupancy not more than three stories in height.
2213.2 Continuity and ties. | The following requirements shall be met: 1. All bolted connections shall have at least two bolts. 2. Bolted connections of all columns, beams, braces and other structural elements that are part of the lateral load resisting system shall be designed as bearing-type connections with pretensioned bolts or as slip critical connections. 3. End connections of all beams and girders shall have a minimum available tensile strength equal to the larger of the required vertical shear strength of the connections at either end, but not less than 10 kips (45 kN)(LRFD) and 6.7 kips (30kN)(ASD). For the design of the connections, the shear force and this axial tensile force need not be considered to act simultaneously. For the purpose of this provision, a connection shall be considered compliant if it meets the following requirements: 3.1. For single-plate shear connections, the available tensile strength shall be determined only for the limit state of bolt bearing on the plate and beam web. 3.2. For single angle and double angle shear connections, the available tensile strength shall be determined for the limit states of bolt bearing on the angles and beam web and for tension yielding on the gross area of the angles. 3.3. All other connections shall be designed for the required tension force noted above in accordance with the provisions of AISC 360. 4. For the purpose of satisfying these integrity provisions only, bearing bolts in connections with short-slotted holes parallel to the direction of the tension force and inelastic deformation are permitted. Elements and their connections that brace compression members shall have a minimum available tensile strength equal to at least 2 percent of the required compressive strength of the member being braced, but not less than 10 kips (45 kN)(LRFD) and 6.7 kips (30kN)(ASD). For design of these bracing connections, the shear force and the tensile force need not be considered to act simultaneously. Where more than one element braces a compression member at a point in one direction, all elements and connections shall have a minimum available tensile strength equal to at least 1 percent of the required compressive strength of the member being braced but not less than 10 kips (45 kN)(LRFD) and 6.7 kips (30kN)(ASD).
2213.2.1 Vertical ties. | Column slices shall have an available tensile strength at least equal to the largest design gravity load reaction applied to the column at any floor level located within four floors below the splice.
2213.3 Composite construction. | For steel framing members and/or decking acting compositely with concrete slabs of roofs or floors, the following requirements shall be met: 1. Shear studs shall not be less than ½ inch (12.7 mm) in diameter. The spacing of shear studs shall not be greater than one every 12 inches (305 mm) averaged over the length of the beam. 2. Connections at the discontinuous edges of permanent metal decking to supporting members shall have a minimum connection strength in the direction parallel to the rib of the deck equal to the shear strength of a ¾-inch (19.1 mm) puddle weld every 12 inches (305 mm) on center. 3. Side lap connections of permanent metal decking shall have a minimum strength equal to the strength of a button punch every 24 inches (610 mm) on center. 4. Welded wire fabric reinforcement in concrete slabs shall be continuous over all supports and in all spans. Minimum area of continuous reinforcement in each direction shall be 0.0015 times the gross area of concrete. The welded wire fabric reinforcement shall have tension splices and be anchored at discontinuous edges, and shall not be substituted with alternative materials including but not limited to fibers.
|  | 2202.1 General. | Identification of structural steel elements shall be in accordance with AISC 360. Identification of cold-formed steel members shall be in accordance with AISI S100. Identification of cold-formed steel light-frame construction shall also comply with the requirements contained in AISI S240 or AISI S220, as applicable. Other steel furnished for structural load-carrying purposes shall be properly identified for conformity to the ordered grade in accordance with the specified ASTM standard or other specification and the provisions of this chapter. Where the steel grade is not readily identifiable from marking and test records, the steel shall be tested to verify conformity to such standards.
|  | 2203.1 General. | Painting of structural steel elements shall be in accordance with AISC 360. Painting of open-web steel joists and joist girders shall be in accordance with SJI 100 and SJI 200. Individual structural members and assembled panels of cold-formed steel construction shall be protected against corrosion in accordance with the requirements contained in AISI S100. Protection of cold-formed steel light-frame construction shall be in accordance with AISI S240 or AISI S220, as applicable.
|  | 2205.2 Seismic design. | Where required, the seismic design, fabrication and erection of buildings, structures and portions thereof shall be in accordance with Section 2205.2.1 or 2205.2.2, as applicable.
|  | 2205.2.1.2 Seismic Design Category D, E or F. | Structures assigned to Seismic Design Category D, E or F shall be designed and detailed in accordance with AISC 341, except as permitted in ASCE 7, Table 15.4-1. Beam-to-column moment connections in special moment frames and intermediate moment frames shall be prequalified in accordance with AISC 341, Section K1, qualified by testing in accordance with AISC 341, Section K2, or shall be prequalified in accordance with AISC 358. | See BC15 Tables and Figures
|  | 2209.1 Steel storage racks. | The design, testing and utilization of steel storage racks made of cold-formed or hot-rolled steel structural members shall be in accordance with RMI ANSI/MH 16.1. Where required by ASCE 7, the seismic design of steel storage racks shall be in accordance with Section 15.5.3 of ASCE 7.
|  | 2209.2 Steel cantilevered storage racks. | The design, testing and utilization of steel cantilevered storage racks made of cold-formed or hot-rolled steel structural members shall be in accordance with RMI ANSI/MH 16.3. Where required by ASCE 7, the seismic design of steel cantilevered storage racks shall be in accordance with Section 15.5.3 of ASCE 7.
|  | 2209.3 Certification. | For rack storage structures that are 8 feet (2438 mm) in height or greater to the top load level and assigned to Seismic Design Category D, E, or F at completion of the storage rack installation, a certificate of compliance shall be submitted to the owner or the owner’s authorized agent stating that the work was performed in accordance with approved construction documents.
|  | 2211.1.1.2 Seismic Design Categories D through F. | In cold-formed steel light-frame construction assigned to Seismic Design Category D, E or F, the seismic force-resisting system shall be designed and detailed in accordance with AISI S400.

## BC23
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2301.1 Scope. | The provisions of this chapter shall govern the materials, design, construction and quality of wood members and their fasteners. | 2301.1 Scope. | The provisions of this chapter shall govern the materials, design, construction and quality of wood members and their fasteners.
2301.2 General design requirements. | The design of structural elements or systems, constructed partially or wholly of wood or wood-based products, shall be in accordance with one of the following methods:
2301.3 Nominal sizes. | For the purposes of this chapter, where dimensions of lumber are specified, they shall be deemed to be nominal dimensions unless specifically designated as actual dimensions (see Section 2304.2).
2302.1 Definitions. | The following terms are defined in Chapter 2:
2303.1 General. | Structural sawn lumber; end-jointed lumber; prefabricated wood I-joists; structural glued-laminated timber; cross-laminated timber; wood structural panels; fiberboard sheathing (when used structurally); hardboard siding (when used structurally); particleboard; preservative-treated wood; structural log members; structural composite lumber; round timber poles and piles; engineered wood rim board; fire-retardant-treated wood; hardwood plywood; wood trusses; joist hangers; nails; and staples shall conform to the applicable provisions of this section. | 2303.1 General. | Structural sawn lumber; end-jointed lumber; prefabricated wood I-joists; structural glued-laminated timber; wood structural panels; fiberboard sheathing (where used structurally); hardboard siding (where used structurally); particleboard; preservative-treated wood; structural log members; structural composite lumber; round timber poles and piles; fire-retardant-treated wood; hardwood plywood; wood trusses; joist hangers; nails; and staples shall conform to the applicable provisions of this section.
2303.1.1 Sawn lumber. | Sawn lumber used for load-supporting purposes, including end-jointed or edge-glued lumber, machine stress-rated or machine-evaluated lumber, shall be identified by the grade mark of a lumber grading or inspection agency that has been approved by the commissioner that complies with DOC PS 20 or equivalent. Grading practices and identification shall comply with rules published by an agency approved in accordance with the procedures of DOC PS 20 or equivalent procedures. | 2303.1.1 Sawn lumber. | Sawn lumber used for load-supporting purposes, including end-jointed or edge-glued lumber, machine stress-rated or machine-evaluated lumber, shall be identified by the grade mark of a lumber grading or inspection agency that has been approved by an accreditation body that complies with DOC PS 20 or equivalent. Grading practices and identification shall comply with rules published by an agency approved in accordance with the procedures of DOC PS 20 or equivalent procedures.
2303.1.1.1 Certificate of inspection. | In lieu of a grade mark on the material, a certificate of inspection as to species and grade issued by a lumber grading or inspection agency meeting the requirements of this section is permitted to be accepted for precut, remanufactured or rough-sawn lumber and for sizes larger than 3 inches (76 mm) nominal thickness. | 2303.1.1.1 Certificate of inspection. | In lieu of a grade mark on the material, a certificate of inspection as to species and grade issued by a lumber grading or inspection agency meeting the requirements of this section is permitted to be accepted for precut, remanufactured or rough-sawn lumber and for sizes larger than 3 inches (76 mm) nominal thickness.
2303.1.1.2 End-jointed lumber. | Approved end-jointed lumber is permitted to be used interchangeably with solid-sawn members of the same species and grade. End-jointed lumber used in an assembly required to have a fire-resistance rating shall have the designation “Heat Resistant Adhesive” or “HRA” included in its grade mark. | 2303.1.1.2 End-jointed lumber. | Approved end-jointed lumber is permitted to be used interchangeably with solid-sawn members of the same species and grade. End-jointed lumber used in an assembly required to have a fire-resistance rating shall have the designation “Heat Resistant Adhesive” or “HRA” included in its grade mark.
2303.1.2 Prefabricated wood I-joists. | Structural capacities and design provisions for prefabricated wood I-joists shall be established and monitored in accordance with ASTM D 5055. The use of prefabricated wood I-joists structurally shall be subject to the special inspection requirements of Chapter 17. | 2303.1.2 Prefabricated wood I-joists. | Structural capacities and design provisions for prefabricated wood I-joists shall be established and monitored in accordance with ASTM D5055.
2303.1.3 Structural glued-laminated timber. | Glued-laminated timbers shall be manufactured and identified as required in ANSI/APA A190.1 and ASTM D3737. | 2303.1.3 Structural glued-laminated timber. | Glued-laminated timbers shall be manufactured and identified as required in ANSI/APA 190.1 and ASTM D3737.
2303.1.4 Cross-laminated timber. | Cross-laminated timber shall be manufactured and identified in accordance with ANSI/APA PRG 320.
2303.1.5 Wood structural panels. | Wood structural panels, when used structurally (including those used for siding, roof and wall sheathing, subflooring, diaphragms and built-up members), shall conform to the requirements for their type in DOC PS 1, DOC PS 2 or ANSI/APA PRP 210. Each panel or member shall be identified for grade, bond classification, and Performance Category by the trademarks of an approved testing and grading agency. The Performance Category value shall be used as the “nominal panel thickness” or “panel thickness” whenever referenced in this code. Wood structural panel components shall be designed and fabricated in accordance with the applicable standards listed in Section 2306.1 and identified by the trademarks of an approved testing and inspection agency indicating conformance to the applicable standard. In addition, wood structural panels when permanently exposed in outdoor applications shall be of Exterior type, except that wood structural panel roof sheathing exposed to the outdoors on the underside is permitted to be Exposure 1 type. | 2303.1.5 Wood structural panels. | Wood structural panels, where used structurally (including those used for siding, roof and wall sheathing, subflooring, diaphragms and built-up members), shall conform to the requirements for their type in DOC PS 1, DOC PS 2 or ANSI/APA PRP 210. Each panel or member shall be identified for grade, bond classification, and Performance Category by the trademarks of an approved testing and grading agency. The Performance Category value shall be used as the “nominal panel thickness” or “panel thickness” whenever referenced in this code. Wood structural panel components shall be designed and fabricated in accordance with the applicable standards listed in Section 2306.1 and identified by the trademarks of an approved testing and inspection agency indicating conformance to the applicable standard. In addition, wood structural panels where permanently exposed in outdoor applications shall be of exterior type, except that wood structural panel roof sheathing exposed to the outdoors on the underside is permitted to be Exposure 1 type.
2303.1.6 Fiberboard. | Fiberboard for its various uses shall conform to ASTM C208. Fiberboard sheathing, when used structurally, shall be identified by an approved agency as conforming to ASTM C208. | 2303.1.6 Fiberboard. | Fiberboard for its various uses shall conform to ASTM C208. Fiberboard sheathing, where used structurally, shall be identified by an approved agency as conforming to ASTM C208.
2303.1.6.1 Jointing. | To ensure tight-fitting assemblies, edges shall be manufactured with square, shiplapped, beveled, tongue-and-groove or U-shaped joints. | 2303.1.6.1 Jointing. | To ensure tight-fitting assemblies, edges shall be manufactured with square, shiplapped, beveled, tongue-and-groove or U-shaped joints.
2303.1.6.2 Roof insulation. | Where used as roof insulation in all types of construction, fiberboard shall be protected with an approved roof covering. | 2303.1.6.2 Roof insulation. | Where used as roof insulation in all types of construction, fiberboard shall be protected with an approved roof covering.
2303.1.6.3 Wall insulation. | Where installed and fireblocked to comply with Chapter 7, fiberboards are permitted as wall insulation in all types of construction. In fire walls and fire barriers, unless treated to comply with Section 803.1 for Class A materials, the boards shall be cemented directly to the concrete, masonry or other noncombustible base and shall be protected with an approved noncombustible veneer anchored to the base without intervening airspaces. | 2303.1.6.3 Wall insulation. | Where installed and fireblocked to comply with Chapter 7, fiberboards are permitted as wall insulation in all types of construction. In fire walls and fire barriers, unless treated to comply with Section 803.1 for Class A materials, the boards shall be cemented directly to the concrete, masonry or other noncombustible base and shall be protected with an approved noncombustible veneer anchored to the base without intervening airspaces.
2303.1.6.3.1 Protection. | Fiberboard wall insulation applied on the exterior of foundation walls shall be protected below ground level with a bituminous coating. | 2303.1.6.3.1 Protection. | Fiberboard wall insulation applied on the exterior of foundation walls shall be protected below ground level with a bituminous coating.
2303.1.7 Hardboard. | Hardboard siding used structurally shall be identified by an approved agency conforming to CPA/ANSI A135.6. Hardboard underlayment shall meet the strength requirements of 7/32-inch (5.6 mm) or ¼-inch (6.4 mm) service class hardboard planed or sanded on one side to a uniform thickness of not less than 0.200 inch (5.1 mm). Prefinished hardboard paneling shall meet the requirements of CPA/ANSI A135.5. Other basic hardboard products shall meet the requirements of CPA/ANSI A135.4. Hardboard products shall be installed in accordance with manufacturer’s recommendations. | 2303.1.7 Hardboard. | Hardboard siding shall conform to the requirements of ANSI A135.6 and, where used structurally, shall be identified by the label of an approved agency. Hardboard underlayment shall meet the strength requirements of 7/32-inch (5.6 mm) or 1/4-inch (6.4 mm) service class hardboard planed or sanded on one side to a uniform thickness of not less than 0.200 inch (5.1 mm). Prefinished hardboard paneling shall meet the requirements of ANSI A135.5. Other basic hardboard products shall meet the requirements of ANSI A135.4. Hardboard products shall be installed in accordance with manufacture’s recommendations.
2303.1.8 Particleboard. | Particleboard shall conform to ANSI A208.1. Particleboard shall be identified by the grade mark or certificate of inspection issued by an approved agency. Particleboard shall not be utilized for applications other than indicated in this section unless the particleboard complies with the provisions of Section 2306.3. | 2303.1.8 Particleboard. | Particleboard shall conform to ANSI A208.1. Particleboard shall be identified by the grade mark or certificate of inspection issued by an approved agency. Particleboard shall not be utilized for applications other than indicated in this section unless the particleboard complies with the provisions of Section 2306.3.
2303.1.8.1 Floor underlayment. | Particleboard floor underlayment shall conform to Type PBU of ANSI A208.1. Type PBU underlayment shall not be less than ¼-inch (6.4 mm) thick and shall be installed in accordance with the instructions of the Composite Panel Association. | 2303.1.8.1 Floor underlayment. | Particleboard floor underlayment shall conform to Type PBU of ANSI A208.1. Type PBU underlayment shall be not less than 1/4-inch (6.4 mm) thick and shall be installed in accordance with the instructions of the Composite Panel Association.
2303.1.9 Preservative-treated wood. | Lumber, timber, plywood, piles and poles supporting permanent structures required by Section 2304.12 to be preservative treated shall conform to AWPA U1 and M4. Lumber and plywood used in permanent wood foundation systems shall conform to Chapter 18 of this code. | 2303.1.9 Preservative-treated wood. | Lumber, timber, plywood, piles and poles supporting permanent structures required by Section 2304.12 to be preservative treated shall conform to AWPA U1 and M4. Lumber and plywood used in permanent wood foundation systems shall conform to Chapter 18.
2303.1.9.1 Identification. | Wood required by Section 2304.12 to be preservative treated shall bear the quality mark of an inspection agency that maintains continuing supervision, testing and inspection over the quality of the preservative-treated wood. Inspection agencies for preservative-treated wood shall be listed by an accreditation body that complies with the requirements of the American Lumber Standards Treated Wood Program, or its equivalent. The quality mark shall be on a stamp or label affixed to the preservative-treated wood, and shall include the following information: | 2303.1.9.1 Identification. | Wood required by Section 2304.12 to be preservative treated shall bear the quality mark of an inspection agency that maintains continuing supervision, testing and inspection over the quality of the preservative-treated wood. Inspection agencies for preservative-treated wood shall be listed by an accreditation body that complies with the requirements of the American Lumber Standards Treated Wood Program, or equivalent. The quality mark shall be on a stamp or label affixed to the preservative-treated wood, and shall include the following information:
2303.1.9.2 Moisture content. | Where preservative-treated wood is used in enclosed locations where drying in service cannot readily occur, such wood shall be at a moisture content of 19 percent or less before being covered with insulation, interior wall finish, floor covering or other materials. | 2303.1.9.2 Moisture content. | Where preservative-treated wood is used in enclosed locations where drying in service cannot readily occur, such wood shall be at a moisture content of 19 percent or less before being covered with insulation, interior wall finish, floor covering or other materials.
2303.1.10 Structural composite lumber. | Structural capacities for structural composite lumber shall be established and monitored in accordance with ASTM D5456. | 2303.1.10 Structural composite lumber. | Structural capacities for structural composite lumber shall be established and monitored in accordance with ASTM D5456.
2303.1.11 Structural log members. | Stress grading of structural log members of nonrectangular shape, as typically used in log buildings, shall be in accordance with ASTM D3957. Such structural log members shall be identified by the grade mark of an approved lumber grading or inspection agency. In lieu of a grade mark on the material, a certificate of inspection as to species and grade issued by a lumber grading or inspection agency meeting the requirements of this section shall be permitted. | 2303.1.11 Structural log members. | Stress grading of structural log members of nonrectangular shape, as typically used in log buildings, shall be in accordance with ASTM D3957. Such structural log members shall be identified by the grade mark of an approved lumber grading or inspection agency. In lieu of a grade mark on the material, a certificate of inspection as to species and grade issued by a lumber grading or inspection agency meeting the requirements of this section shall be permitted.
2303.1.12 Round timber poles and piles. | Round timber poles and piles shall comply with ASTM D3200 and ASTM D25, respectively. | 2303.1.12 Round timber poles and piles. | Round timber poles and piles shall comply with ASTM D3200 and ASTM D25, respectively.
2303.1.13 Engineered wood rim board. | Engineered wood rim boards shall conform to ANSI/APA PRR 410 or shall be evaluated in accordance with ASTM D7672. Structural capacities shall be in accordance with ANSI/APA PRR 410 or established in accordance with ASTM D7672. Rim boards conforming to ANSI/APA PRR 410 shall be marked in accordance with that standard. | 2303.1.13 Engineered wood rim board. | Engineered wood rim boards shall conform to ANSI/APA PRR 410 or shall be evaluated in accordance with ASTM D7672. Structural capacities shall be in accordance with ANSI/APA PRR 410 or established in accordance with ASTM D7672. Rim boards conforming to ANSI/APA PRR 410 shall be marked in accordance with that standard.
2303.2 Fire-retardant-treated wood. | Fire-retardant-treated wood is any wood product which, when impregnated with chemicals by a pressure process or other means during manufacture, shall have, when tested in accordance with ASTM E84 or UL 723, a listed flame spread index of 25 or less and show no evidence of significant progressive combustion when the test is continued for an additional 20-minute period. Additionally, the flame front shall not progress more than 10½-feet (3200 mm) beyond the centerline of the burners at any time during the test. | 2303.2 Fire-retardant-treated wood. | Fire-retardant-treated wood is any wood product that, when impregnated with chemicals by a pressure process or other means during manufacture, shall have, when tested in accordance with ASTM E84 or UL 723, a listed flame spread index of 25 or less. Additionally, the ASTM E84 or UL 723 test shall be continued for a 20-minute period and the flame front shall not progress more than 101/2 feet (3200 mm) beyond the centerline of the burners at any time during the test.
2303.2.1 Pressure process. | For wood products impregnated with chemicals by a pressure process, the process shall be performed in closed vessels under pressures not less than 50 pounds per square inch gauge (psig) (345 kPa). | 2303.2.1 Pressure process. | For wood products impregnated with chemicals by a pressure process, the process shall be performed in closed vessels under pressures not less than 50 pounds per square inch gauge (psig) (345 kPa).
2303.2.2 Other means during manufacture. | For wood products produced by other means during manufacture, the treatment shall be an integral part of the manufacturing process of the wood product. The treatment shall provide permanent protection to all surfaces of the wood product. | 2303.2.2 Other means during manufacture. | For wood products impregnated with chemicals by other means during manufacture, the treatment shall be an integral part of the manufacturing process of the wood product. The treatment shall provide permanent protection to all surfaces of the wood product. The use of paints, coating, stains or other surface treatments is not an approved method of protection as required in this section.
2303.2.3 Testing. | For wood products produced by other means during manufacture, other than a pressure process, all sides of the wood product shall be tested in accordance with and produce the results required in Section 2303.2. Wood structural panels shall be permitted to be tested on only the front and back faces.
2303.2.4 Labeling. | In addition to the labels required in Section 2303.1.1 for sawn lumber and Section 2303.1.5 for wood structural panels, each piece of fire-retardant-treated lumber and wood structural panels shall be labeled. The label shall contain the following items: | 2303.2.4 Labeling. | In addition to the labels required in Section 2303.1.1 for sawn lumber and Section 2303.1.5 for wood structural panels, each piece of fire-retardant-treated lumber and wood structural panels shall be labeled. The label shall contain the following items:
2303.2.5 Strength adjustments. | Design values for untreated lumber and wood structural panels, as specified in Section 2303.1, shall be adjusted for fire-retardant-treated wood. Adjustments to design values shall be based on an approved method of investigation that takes into consideration the effects of the anticipated temperature and humidity to which the fire-retardant-treated wood will be subjected, the type of treatment and redrying procedures. | 2303.2.5 Strength adjustments. | Design values for untreated lumber and wood structural panels, as specified in Section 2303.1, shall be adjusted for fire-retardant-treated wood. Adjustments to design values shall be based on an approved method of investigation that takes into consideration the effects of the anticipated temperature and humidity to which the fire-retardant-treated wood will be subjected, the type of treatment and redrying procedures.
2303.2.5.1 Wood structural panels. | The effect of treatment and the method of redrying after treatment, and exposure to high temperatures and high humidities on the flexure properties of fire-retardant-treated softwood plywood shall be determined in accordance with ASTM D5516. The test data developed by ASTM D5516 shall be used to develop adjustment factors, maximum loads and spans, or both, for untreated plywood design values in accordance with ASTM D6305. Each manufacturer shall publish the allowable maximum loads and spans for service as floor and roof sheathing for its treatment. | 2303.2.5.1 Wood structural panels. | The effect of treatment and the method of redrying after treatment, and exposure to high temperatures and high humidities on the flexure properties of fire-retardant-treated softwood plywood shall be determined in accordance with ASTM D5516. The test data developed by ASTM D5516 shall be used to develop adjustment factors, maximum loads and spans, or both, for untreated plywood design values in accordance with ASTM D6305. Each manufacturer shall publish the allowable maximum loads and spans for service as floor and roof sheathing for its treatment.
2303.2.5.2 Lumber. | For each species of wood that is treated, the effects of the treatment, the method of redrying after treatment and exposure to high temperatures and high humidities on the allowable design properties of fire-retardant-treated lumber shall be determined in accordance with ASTM D5664. The test data developed by ASTM D5664 shall be used to develop modification factors for use at or near room temperature and at elevated temperatures and humidity in accordance with ASTM D6841. Each manufacturer shall publish the modification factors for service at temperatures of not less than 80°F (27°C) and for roof framing. The roof framing modification factors shall take into consideration the climatological location. | 2303.2.5.2 Lumber. | For each species of wood that is treated, the effects of the treatment, the method of redrying after treatment and exposure to high temperatures and high humidities on the allowable design properties of fire-retardant-treated lumber shall be determined in accordance with ASTM D5664. The test data developed by ASTM D5664 shall be used to develop modification factors for use at or near room temperature and at elevated temperatures and humidity in accordance with ASTM D6841. Each manufacturer shall publish the modification factors for service at temperatures of not less than 80°F (27°C) and for roof framing. The roof framing modification factors shall take into consideration the climatological location.
2303.2.6 Exposure to weather, damp or wet locations. | Where fire-retardant-treated wood is exposed to weather, or damp or wet locations, it shall be identified as “Exterior” to indicate there is no increase in the listed flame spread index as defined in Section 2303.2 when subjected to ASTM D2898. | 2303.2.6 Exposure to weather, damp or wet locations. | Where fire-retardant-treated wood is exposed to weather, or damp or wet locations, it shall be identified as “Exterior” to indicate there is no increase in the listed flame spread index as defined in Section 2303.2 when subjected to ASTM D2898.
2303.2.7 Interior applications. | Interior fire-retardant-treated wood shall have moisture content of not over 28 percent when tested in accordance with ASTM D3201 procedures at 92-percent relative humidity. Interior fire-retardant-treated wood shall be tested in accordance with Section 2303.2.5.1 or 2303.2.5.2. Interior fire-retardant-treated wood designated as Type A shall be tested in accordance with the provisions of this section. | 2303.2.7 Interior applications. | Interior fire-retardant-treated wood shall have moisture content of not over 28 percent when tested in accordance with ASTM D3201 procedures at 92-percent relative humidity. Interior fire-retardant-treated wood shall be tested in accordance with Section 2303.2.5.1 or 2303.2.5.2. Interior fire-retardant-treated wood designated as Type A shall be tested in accordance with the provisions of this section.
2303.2.8 Moisture content. | Fire-retardant-treated wood shall be dried to a moisture content of 19 percent or less for lumber and 15 percent or less for wood structural panels before use. For wood kiln-dried after treatment (KDAT), the kiln temperatures shall not exceed those used in kiln drying the lumber and plywood submitted for the tests described in Section 2303.2.5.1 for plywood and 2303.2.5.2 for lumber. | 2303.2.8 Moisture content. | Fire-retardant-treated wood shall be dried to a moisture content of 19 percent or less for lumber and 15 percent or less for wood structural panels before use. For wood kiln-dried after treatment (KDAT), the kiln temperatures shall not exceed those used in kiln drying the lumber and plywood submitted for the tests described in Section 2303.2.5.1 for plywood and 2303.2.5.2 for lumber.
2303.2.9 Type I and II construction applications. | See Section 603.1 for limitations on the use of fire-retardant-treated wood in buildings of Type I or II construction.
2303.3 Hardwood plywood. | Hardwood and decorative plywood shall be manufactured and identified as required in HPVA HP-1.
2303.4 Trusses. | Wood trusses shall comply with Sections 2303.4.1 through 2303.4.8. | 2303.4 Trusses. | Wood trusses shall comply with Sections 2303.4.1 through 2303.4.7.
2303.4.1 Design. | Wood trusses shall be designed in accordance with the provisions of this code and accepted engineering practice. Members are permitted to be joined by nails, glue, bolts, timber connectors, metal connector plates or other approved framing devices. Metal-plate-connected wood trusses shall also be subject to the special inspection requirements of Chapter 17. | 2303.4.1 Design. | Wood trusses shall be designed in accordance with the provisions of this code and accepted engineering practice. Members are permitted to be joined by nails, glue, bolts, timber connectors, metal connector plates or other approved framing devices.
2303.4.1.1 Truss design drawings. | Truss construction documents shall be prepared by a registered design professional and the written, graphic and pictorial depiction of each individual truss shall be provided to the commissioner and approved prior to installation. Truss design drawings shall also be provided with the shipment of trusses delivered to the job site. Truss design drawings shall include, at a minimum, the information specified below: | 2303.4.1.1 Truss design drawings. | The written, graphic and pictorial depiction of each individual truss shall be provided to the building official for approval prior to installation. Truss design drawings shall be provided with the shipment of trusses delivered to the job site. Truss design drawings shall include, at a minimum, the following information:
2303.4.1.2 Permanent individual truss member restraint. | Where permanent restraint of truss members is required on the truss design drawings, it shall be accomplished by one of the following methods:
2303.4.1.3 Trusses spanning 60 feet or greater. | The owner or the owner’s authorized agent shall contract with any qualified registered design professional for the design of the temporary installation restraint/bracing and the permanent individual truss member restraint/bracing for all trusses with clear spans 60 feet (18 288 mm) or greater. | 2303.4.1.3 Trusses spanning 60 feet or greater. | The owner or the owner’s authorized agent shall contract with any qualified registered design professional for the design of the temporary installation restraint and diagonal bracing and the PITMR and PITMDB for all trusses with clear spans 60 feet (18 288 mm) or greater.
2303.4.1.4 Truss designer. | The individual or organization responsible for the design of trusses. | 2303.4.1.4 Truss designer. | The individual or organization responsible for the design of trusses.
2303.4.1.4.1 Truss design drawings. | Each individual truss design drawing shall bear the seal and signature of the truss designer. Exceptions: 1. Where a cover sheet and truss index sheet are combined into a single sheet and attached to the set of truss design drawings, the single cover/truss index sheet is the only document required to be signed and sealed by the truss designer. 2. When a cover sheet and a truss index sheet are separately provided and attached to the set of truss design drawings, the cover sheet and the truss index sheet are the only documents required to be signed and sealed by the truss designer. | 2303.4.1.4.1 Truss design drawings. | Where required by the registered design professional, the building official or the statutes of the jurisdiction in which the project is to be constructed, each individual truss design drawing shall bear the seal and signature of the truss designer.
2303.4.2 Truss placement diagram. | The truss manufacturer shall provide a truss placement diagram that identifies the proposed location for each individually designated truss and references the corresponding truss design drawing. The truss placement diagram shall be provided as part of the truss submittal package, and with the shipment of trusses delivered to the job site. Truss placement diagrams that serve only as a guide for installation and do not deviate from the Truss Designer’s approved construction drawings shall not be required to bear the seal or signature of the truss designer. | 2303.4.2 Truss placement diagram. | The truss manufacturer shall provide a truss placement diagram that identifies the proposed location for each individually designated truss and references the corresponding truss design drawing. The truss placement diagram shall be provided as part of the truss submittal package, and with the shipment of trusses delivered to the job site. Truss placement diagrams that serve only as a guide for installation and do not deviate from the permit submittal drawings shall not be required to bear the seal or signature of the truss designer.
2303.4.3 Truss submittal package. | The truss submittal package provided by the truss manufacturer shall consist of each individual truss design drawing, the truss placement diagram, the permanent individual truss member restraint/bracing method and details and any other structural details germane to the trusses; and, as applicable, the cover/truss index sheet. | 2303.4.3 Truss submittal package. | The truss submittal package provided by the truss manufacturer shall consist of each individual truss design drawing, the truss placement diagram, the permanent individual truss member restraint/bracing method and details and any other structural details germane to the trusses; and, as applicable, the cover/truss index sheet.
2303.4.4 Anchorage. | The design for the transfer of loads and anchorage of each truss to the supporting structure is the responsibility of the registered design professional. | 2303.4.4 Anchorage. | The design for the transfer of loads and anchorage of each truss to the supporting structure is the responsibility of the registered design professional.
2303.4.5 Alterations to trusses. | Truss members and components shall not be cut, notched, drilled, spliced or otherwise altered in any way without written concurrence and approval of a registered design professional. Alterations resulting in the addition of loads to any member (e.g., HVAC equipment, piping, additional roofing or insulation, etc.) shall not be permitted without verification that the truss is capable of supporting such additional loading. | 2303.4.5 Alterations to trusses. | Truss members and components shall not be cut, notched, drilled, spliced or otherwise altered in any way without written concurrence and approval of a registered design professional. Alterations resulting in the addition of loads to any member (for example, HVAC equipment, piping, additional roofing or insulation) shall not be permitted without verification that the truss is capable of supporting such additional loading.
2303.4.6 TPI 1 specifications. | In addition to Sections 2303.4.1 through 2303.4.5, the design, manufacture and quality assurance of metal-plate-connected wood trusses shall be in accordance with TPI 1. Job-site inspections shall be in compliance with Section 110.4, as applicable. | 2303.4.6 TPI 1 specifications. | In addition to Sections 2303.4.1 through 2303.4.5, the design, manufacture and quality assurance of metal-plate-connected wood trusses shall be in accordance with TPI 1. Job-site inspections shall be in compliance with Section 110.4, as applicable.
2303.4.7 Glued prefabricated parallel chord wood trusses. | In addition to Sections 2303.4.1 through 2303.4.5, the design, manufacture and quality assurance of glued prefabricated parallel chord wood trusses shall be in accordance with the rules of the department. Job-site inspections shall be in compliance with Sections 1704.6.2 and 1704.6.3, as applicable.
2303.4.8 Truss quality assurance. | Trusses not part of a manufacturing process in accordance with either Section 2303.4.6 or a referenced standard, which provides requirements for quality control done under the supervision of a third-party quality control agency, shall be manufactured in compliance with Sections 1704.2 and 1705.5, as applicable.
2303.5 Test standard for joist hangers. | Joist hangers shall be in accordance with ASTM D7147. | 2303.5 Test standard for joist hangers. | Joist hangers shall be in accordance with ASTM D7147.
2303.6 Nails and staples. | Nails and staples shall conform to requirements of ASTM F1667, including Supplement 1. Nails used for framing and sheathing connections shall have minimum average bending yield strengths as follows: 80 kips per square inch (ksi) (551 MPa) for shank diameters larger than 0.177 inch (4.50 mm) but not larger than 0.254 inch (6.45 mm), 90 ksi (620 MPa) for shank diameters larger than 0.142 inch (3.61 mm) but not larger than 0.177 inch (4.50 mm) and 100 ksi (689 MPa) for shank diameters of not less than 0.099 inch (2.51 mm) but not larger than 0.142 inch (3.61 mm). Staples used for framing and sheathing connections shall have minimum average bending moments as follows: 3.6 in.-lbs (0.41 N-m) for No. 16 gage staples, 4.0 in.-lbs (0.45 N-m) for No. 15 gage staples, and 4.3 in.-lbs (0.49 N-m) for No. 14 gage staples. | 2303.6 Nails and staples. | Nails and staples shall conform to requirements of ASTM F1667, including Supplement 1. Nails used for framing and sheathing connections shall have minimum average bending yield strengths as follows: 80 kips per square inch (ksi) (551 MPa) for shank diameters larger than 0.177 inch (4.50 mm) but not larger than 0.254 inch (6.45 mm), 90 ksi (620 MPa) for shank diameters larger than 0.142 inch (3.61 mm) but not larger than 0.177 inch (4.50 mm) and 100 ksi (689 MPa) for shank diameters of not less than 0.099 inch (2.51 mm) but not larger than 0.142 inch (3.61 mm). Staples used for framing and sheathing connections shall have minimum average bending moments as follows: 3.6 in.-lbs (0.41 N-m) for No. 16 gage staples, 4.0 in.-lbs (0.45 N-m) for No. 15 gage staples, and 4.3 in.-lbs (0.49 N-m) for No. 14 gage staples.
2303.7 Shrinkage. | Consideration shall be given in design to the possible effect of cross-grain dimensional changes considered vertically which may occur in lumber fabricated in a green condition. | 2303.7 Shrinkage. | Consideration shall be given in design for the effects of wood cross-grain dimensional changes that occur as a result of changes in the wood moisture content after installation.
2304.1 General. | The provisions of this section apply to design methods specified in Section 2301.2. | 2304.1 General. | The provisions of this section apply to design methods specified in Section 2302.1.
2304.2 Size of structural members. | Computations to determine the required sizes of members shall be based on the net dimensions (actual sizes) and not nominal sizes. | 2304.2 Size of structural members. | Computations to determine the required sizes of members shall be based on the net dimensions (actual sizes) and not nominal sizes.
2304.3 Wall framing. | The framing of exterior and interior walls shall be in accordance with the provisions specified in Section 2308 unless a specific design is furnished. | 2304.3 Wall framing. | The framing of exterior and interior walls shall be in accordance with the provisions specified in Section 2308 unless a specific design is furnished.
2304.3.1 Bottom plates. | Studs shall have full bearing on a 2-inch-thick (actual 1½-inch, 38 mm) or larger plate or sill having a width at least equal to the width of the studs. | 2304.3.1 Bottom plates. | Studs shall have full bearing on a 2-inch-thick (actual 11/2-inch, 38 mm) or larger plate or sill having a width not less than equal to the width of the studs.
2304.3.2 Framing over openings. | Headers, double joists, trusses or other approved assemblies that are of adequate size to transfer loads to the vertical members shall be provided over window and door openings in load-bearing walls and partitions. | 2304.3.2 Framing over openings. | Headers, double joists, trusses or other approved assemblies that are of adequate size to transfer loads to the vertical members shall be provided over window and door openings in load-bearing walls and partitions.
2304.3.3 Shrinkage. | Wood walls and bearing partitions shall not support more than two floors and a roof unless an analysis satisfactory to the commissioner shows that shrinkage of the wood framing will not have adverse effects on the structure or any plumbing, electrical or mechanical systems or other equipment installed therein due to excessive shrinkage or differential movements caused by shrinkage. The analysis shall also show that the roof drainage system and the foregoing systems or equipment will not be adversely affected or, as an alternate, such systems shall be designed to accommodate the differential shrinkage or movements. | 2304.3.3 Shrinkage. | Wood walls and bearing partitions shall not support more than two floors and a roof unless an analysis satisfactory to the building official shows that shrinkage of the wood framing will not have adverse effects on the structure or any plumbing, electrical or mechanical systems or other equipment installed therein due to excessive shrinkage or differential movements caused by shrinkage. The analysis shall show that the roof drainage system and the foregoing systems or equipment will not be adversely affected or, as an alternate, such systems shall be designed to accommodate the differential shrinkage or movements.
2304.4 Floor and roof framing. | The framing of wood-joisted floors and wood-framed roofs shall be in accordance with the provisions specified in Section 2308 unless a specific design is furnished. | 2304.4 Floor and roof framing. | The framing of wood-joisted floors and wood-framed roofs shall be in accordance with the provisions specified in Section 2308 unless a specific design is furnished.
2304.5 Framing around flues and chimneys. | Combustible framing shall be a minimum of 2 inches (51 mm), but shall not be less than the distance specified in Sections 2111 and 2113 and the New York City Mechanical Code, from flues, chimneys and fireplaces, and 6 inches (152 mm) away from flue openings. | 2304.5 Framing around flues and chimneys. | Combustible framing shall be not less than 2 inches (51 mm), but shall be not less than the distance specified in Sections 2111 and 2113 and the International Mechanical Code, from flues, chimneys and fireplaces, and 6 inches (152 mm) away from flue openings.
2304.4.1 Firecutting. | The ends of wood beams, joists and rafters resting on unreinforced masonry or plain concrete walls shall be firecut to a bevel of 3 inches (76 mm) in depth.
2304.6 Exterior wall sheathing. | Wall sheathing on the outside of exterior walls, including gables, and the connection of the sheathing to framing shall be designed in accordance with the general provisions of this code and shall be capable of resisting wind pressures in accordance with Section 1609. | 2304.6 Exterior wall sheathing. | Wall sheathing on the outside of exterior walls, including gables, and the connection of the sheathing to framing shall be designed in accordance with the general provisions of this code and shall be capable of resisting wind pressures in accordance with Section 1609.
2304.6.1 Wood structural panel sheathing. | Where wood structural panel sheathing is used as the exposed finish on the outside of exterior walls, it shall have an exterior exposure durability classification. Where wood structural panel sheathing is used elsewhere, but not as the exposed finish, it shall be of a type manufactured with exterior glue (Exposure 1 or Exterior). Wood structural panel sheathing, connections and framing spacing shall be in accordance with Table 2304.6.1 for the applicable wind speed and exposure category where used in enclosed buildings with a mean roof height not greater than 30 feet (9144 mm) and a topographic factor ( | 2304.6.1 Wood structural panel sheathing. | Where wood structural panel sheathing is used as the exposed finish on the outside of exterior walls, it shall have an exterior exposure durability classification. Where wood structural panel sheathing is used elsewhere, but not as the exposed finish, it shall be of a type manufactured with exterior glue (Exposure 1 or Exterior). Wood structural panel sheathing, connections and framing spacing shall be in accordance with Table 2304.6.1 for the applicable wind speed and exposure category where used in enclosed buildings with a mean roof height not greater than 30 feet (9144 mm) and a topographic factor (Kz t) of 1.0.
2304.7 Interior paneling. | Softwood wood structural panels used for interior paneling shall conform to the provisions of Chapter 8 and shall be installed in accordance with Table 2304.10.1. Panels shall comply with DOC PS 1, DOC PS 2 or ANSI/APA PRP 210. Prefinished hardboard paneling shall meet the requirements of CPA/ANSI A135.5. Hardwood plywood shall conform to HPVA HP-1. | 2304.7 Interior paneling. | Softwood wood structural panels used for interior paneling shall conform to the provisions of Chapter 8 and shall be installed in accordance with Table 2304.10.2. Panels shall comply with DOC PS 1, DOC PS 2 or ANSI/APA PRP 210. Prefinished hardboard paneling shall meet the requirements of ANSI A135.5. Hardwood plywood shall conform to HPVA HP-1.
2304.8 Floor and roof sheathing. | Structural floor sheathing and structural roof sheathing shall comply with Sections 2304.8.1 and 2304.8.2, respectively. | 2304.8 Floor and roof sheathing. | Structural floor sheathing and structural roof sheathing shall comply with Sections 2304.8.1 and 2304.8.2, respectively.
2304.8.1 Structural floor sheathing. | Structural floor sheathing shall be designed in accordance with the general provisions of this code. | 2304.8.1 Structural floor sheathing. | Structural floor sheathing shall be designed in accordance with the general provisions of this code.
2304.8.2 Structural roof sheathing. | Structural roof sheathing shall be designed in accordance with the general provisions of this code and the special provisions in this section. | 2304.8.2 Structural roof sheathing. | Structural roof sheathing shall be designed in accordance with the general provisions of this code and the special provisions in this section.
2304.9 Lumber decking. | Lumber decking shall be designed and installed in accordance with the general provisions of this code and Sections 2304.9.1 through 2304.9.5.3. | 2304.9 Lumber decking. | Lumber decking shall be designed and installed in accordance with the general provisions of this code and Sections 2304.9.1 through 2304.9.5.3. Other lumber decking patterns and connection designs shall be substantiated through engineering analysis.
2304.9.1 General. | Each piece of lumber decking shall be square-end trimmed. When random lengths are furnished, each piece shall be square-end trimmed across the face so that at least 90 percent of the pieces are within 0.5 degrees (0.00873 rad) of square. The ends of the pieces shall be permitted to be beveled up to 2 degrees (0.0349 rad) from the vertical with the exposed face of the piece slightly longer than the opposite face of the piece. Tongue-and-groove decking shall be installed with the tongues up on sloped or pitched roofs with pattern faces down. | 2304.9.1 General. | Each piece of lumber decking shall be square-end trimmed. Where random lengths are furnished, each piece shall be square end trimmed across the face so that not less than 90 percent of the pieces are within 0.5 degrees (0.00873 rad) of square. The ends of the pieces shall be permitted to be beveled up to 2 degrees (0.0349 rad) from the vertical with the exposed face of the piece slightly longer than the opposite face of the piece. Tongue-and-groove decking shall be installed with the tongues up on sloped or pitched roofs with pattern faces down.
2304.9.2 Layup patterns. | Lumber decking is permitted to be laid up following one of five standard patterns as defined in Sections 2304.9.2.1 through 2304.9.2.5. Other patterns are permitted to be used provided they are substantiated through engineering analysis. | 2304.9.2 Layup patterns. | Lumber decking is permitted to be laid up following one of five standard patterns as defined in Sections 2304.9.2.1 through 2304.9.2.5.
2304.9.2.1 Simple span pattern. | All pieces shall be supported on their ends (i.e., by two supports). | 2304.9.2.1 Simple span pattern. | All pieces shall be supported on their ends (in other words, by two supports).
2304.9.2.2 Two-span continuous pattern. | All pieces shall be supported by three supports, and all end joints shall occur in line on alternating supports. Supporting members shall be designed to accommodate the load redistribution caused by this pattern. | 2304.9.2.2 Two-span continuous pattern. | All pieces shall be supported by three supports, and all end joints shall occur in line on alternating supports. Supporting members shall be designed to accommodate the load redistribution caused by this pattern.
2304.9.2.3 Combination simple and two-span continuous pattern. | Courses in end spans shall be alternating simple-span pattern and two-span continuous pattern. End joints shall be staggered in adjacent courses and shall bear on supports. | 2304.9.2.3 Combination simple and two-span continuous pattern. | Courses in end spans shall be alternating simple-span pattern and two-span continuous pattern. End joints shall be staggered in adjacent courses and shall bear on supports.
2304.9.2.4 Cantilevered pieces intermixed pattern. | The decking shall extend across a minimum of three spans. Pieces in each starter course and every third course shall be simple span pattern. Pieces in other courses shall be cantilevered over the supports with end joints at alternating quarter or third points of the spans. Each piece shall bear on at least one support. | 2304.9.2.4 Cantilevered pieces intermixed pattern. | The decking shall extend across not fewer than three spans. Pieces in each starter course and every third course shall be simple span pattern. Pieces in other courses shall be cantilevered over the supports with end joints at alternating quarter or third points of the spans. Each piece shall bear on one support or more.
2304.9.2.5 Controlled random pattern. | The decking shall extend across a minimum of three spans. End joints of pieces within 6 inches (152 mm) of the end joints of the adjacent pieces in either direction shall be separated by at least two intervening courses. In the end bays, each piece shall bear on at least one support. Where an end joint occurs in an end bay, the next piece in the same course shall continue over the first inner support for at least 24 inches (610 mm). The details of the controlled random pattern shall be as specified for each decking material in Section 2304.9.3.3, 2304.9.4.3 or 2304.9.5.3. | 2304.9.2.5 Controlled random pattern. | The decking shall extend across not fewer than three spans. End joints of pieces within 6 inches (152 mm) of the end joints of the adjacent pieces in either direction shall be separated by not fewer than two intervening courses. In the end bays, each piece shall bear on one support or more. Where an end joint occurs in an end bay, the next piece in the same course shall continue over the first inner support for not less than 24 inches (610 mm). The details of the controlled random pattern shall be as specified for each decking material in Section 2304.9.3.3, 2304.9.4.3 or 2304.9.5.3.
2304.9.3 Mechanically laminated decking. | Mechanically laminated decking shall comply with Sections 2304.9.3.1 through 2304.9.3.3. | 2304.9.3 Mechanically laminated decking. | Mechanically laminated decking shall comply with Sections 2304.9.3.1 through 2304.9.3.3.
2304.9.3.1 General. | Mechanically laminated decking consists of square-edged dimension lumber laminations set on edge and mechanically fastened to the adjacent pieces and to the supports. | 2304.9.3.1 General. | Mechanically laminated decking consists of square-edged dimension lumber laminations set on edge and nailed to the adjacent pieces and to the supports.
2304.9.3.3 Controlled random pattern. | There shall be a minimum distance of 24 inches (610 mm) between end joints in adjacent courses. The pieces in the first and second courses shall bear on at least two supports with end joints in these two courses occurring on alternate supports. A maximum of seven intervening courses shall be permitted before this pattern is repeated. | 2304.9.3.3 Controlled random pattern. | There shall be a minimum distance of 24 inches (610 mm) between end joints in adjacent courses. The pieces in the first and second courses shall bear on not fewer than two supports with end joints in these two courses occurring on alternate supports. Not more than seven intervening courses shall be permitted before this pattern is repeated.
2304.9.3.2 Nailing and fastening to supports. | Nailing of adjacent laminations and fastening to supports shall conform to the requirements of Section 2304.9.3.2.1 through 2304.9.3.2.2.
2304.9.4 Two-inch sawn tongue-and-groove decking. | Two-inch (51 mm) sawn tongue-and-groove decking shall comply with Sections 2304.9.4.1 through 2304.9.4.3. | 2304.9.4 Two-inch sawn tongue-and-groove decking. | Two-inch (51 mm) sawn tongue-and-groove decking shall comply with Sections 2304.9.4.1 through 2304.9.4.3.
2304.9.3.2.1 Two-inch mechanically laminated decking. | For mechanically laminated decking constructed with laminations of 2-inch (51 mm) nominal thickness, nailing and fastening to supports in accordance with Table 2304.9.3.2.1 shall be permitted. Other connections are permitted to be used provided they are reviewed and approved by the registered design professional of record, but shall be spaced at no more than 16 inches (406 mm) on center.
2304.9.4.1 General. | Two-inch (51 mm) decking shall have a maximum moisture content of 15 percent when machined and installed. Decking shall be machined with a single tongue-and-groove pattern. Each decking piece shall be nailed to each support. | 2304.9.4.1 General. | Two-inch (51 mm) decking shall have a maximum moisture content of 15 percent. Decking shall be machined with a single tongue-and-groove pattern. Each decking piece shall be nailed to each support.
2304.9.3.2.2 Three- and four-inch mechanically laminated decking. | For mechanically laminated decking constructed with laminations of 3-inch (76 mm) and 4-inch (102 mm) thickness, the length of nails connecting laminations shall not be less than two and one-half times the net thickness of each lamination. Where decking supports are 48 inches (1219 mm) on center or less, side nails shall be installed not more than 30 inches (762 mm) on center alternating between top and bottom edges, and staggered one-third of the spacing in adjacent laminations. Where supports are spaced more than 48 inches (1219 mm) on center, side nails shall be installed not more than 18 inches (457 mm) on center alternating between top and bottom edges and staggered one-third of the spacing in adjacent laminations. Two side nails shall be installed at each end of butt-jointed pieces.
2304.9.4.2 Nailing. | Each piece of decking shall be toenailed at each support with one 16d common nail through the tongue and face-nailed with one 16d common nail. | 2304.9.4.2 Nailing. | Each piece of decking shall be toenailed at each support with one 16d common nail through the tongue and face-nailed with one 16d common nail.
2304.9.4.3 Controlled random pattern. | There shall be a minimum distance of 24 inches (610 mm) between end joints in adjacent courses. The pieces in the first and second courses shall bear on at least two supports with end joints in these two courses occurring on alternate supports. A maximum of seven intervening courses shall be permitted before this pattern is repeated. | 2304.9.4.3 Controlled random pattern. | There shall be a minimum distance of 24 inches (610 mm) between end joints in adjacent courses. The pieces in the first and second courses shall bear on not fewer than two supports with end joints in these two courses occurring on alternate supports. Not more than seven intervening courses shall be permitted before this pattern is repeated.
2304.9.5 Three- and four-inch sawn tongue-and-groove decking. | Three- and four-inch (76 mm and 102 mm) sawn tongue-and-groove decking shall comply with Sections 2304.9.5.1 through 2304.9.5.3. | 2304.9.5 Three- and four-inch sawn tongue-and-groove decking. | Three- and four-inch (76 mm and 102 mm) sawn tongue-and-groove decking shall comply with Sections 2304.9.5.1 through 2304.9.5.3.
2304.9.5.1 General. | Three-inch (76 mm) and four-inch (102 mm) decking shall have a maximum moisture content of 19 percent when machined and installed. Decking shall be machined with a double tongue-and-groove pattern. Decking pieces shall be interconnected and nailed to the supports. | 2304.9.5.1 General. | Three-inch (76 mm) and four-inch (102 mm) decking shall have a maximum moisture content of 19 percent. Decking shall be machined with a double tongue-and-groove pattern. Decking pieces shall be interconnected and nailed to the supports.
2304.9.5.2 Nailing. | Each piece shall be toenailed at each support with one 40d common nail and face-nailed with one 60d common nail. Courses shall be spiked to each other with 8-inch (203 mm) spikes at maximum intervals of 30 inches (762 mm) through predrilled edge holes penetrating to a depth of approximately 4 inches (102 mm). One spike shall be installed at a distance not exceeding 10 inches (254 mm) from the end of each piece. | 2304.9.5.2 Nailing. | Each piece shall be toenailed at each support with one 40d common nail and face-nailed with one 60d common nail. Courses shall be spiked to each other with 8-inch (203 mm) spikes at maximum intervals of 30 inches (762 mm) through predrilled edge holes penetrating to a depth of approximately 4 inches (102 mm). One spike shall be installed at a distance not exceeding 10 inches (254 mm) from the end of each piece.
2304.9.5.3 Controlled random pattern. | There shall be a minimum distance of 48 inches (1219 mm) between end joints in adjacent courses. Pieces not bearing on a support are permitted to be located in interior bays provided the adjacent pieces in the same course continue over the support for at least 24 inches (610 mm). This condition shall not occur more than once in every six courses in each interior bay. | 2304.9.5.3 Controlled random pattern. | There shall be a minimum distance of 48 inches (1219 mm) between end joints in adjacent courses. Pieces not bearing on a support are permitted to be located in interior bays provided that the adjacent pieces in the same course continue over the support for not less than 24 inches (610 mm). This condition shall not occur more than once in every six courses in each interior bay.
2304.10 Connectors and fasteners. | Connectors and fasteners shall comply with the applicable provisions of Sections 2304.10.1 through 2304.10.8. | 2304.10 Connectors and fasteners. | Connectors and fasteners shall comply with the applicable provisions of Sections 2304.10.1 through 2304.10.8 .
2304.10.1 Fastener requirements. | Connections for wood members shall be designed in accordance with the appropriate methodology in Section 2301.2. The number and size of fasteners connecting wood members shall not be less than that set forth in Table 2304.10.1.
23. 1 × 6 subfloor or less to each joist.
2304.10.2 Sheathing fasteners. | Sheathing nails or other approved sheathing connectors shall be driven so that their head or crown is flush with the surface of the sheathing.
2304.10.3 Joist hangers and framing anchors. | Connections depending on joist hangers or framing anchors, ties and other mechanical fastenings not otherwise covered are permitted where approved. The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers shall be determined in accordance with ASTM D7147.
2304.10.4 Other fasteners. | Clips, staples, glues and other approved methods of fastening are permitted where approved.
2304.10.5 Fasteners and connectors in contact with preservative-treated and fire-retardant-treated wood. | Fasteners, including nuts and washers, and connectors in contact with preservative-treated and fire-retardant-treated wood shall be in accordance with Sections 2304.10.5.1 through 2304.10.5.4. The coating weights for zinc-coated fasteners shall be in accordance with ASTM A153. Stainless steel driven fasteners shall be in accordance with the material requirements of ASTM F1667.
2304.10.5.1 Fasteners and connectors for preservative-treated wood. | Fasteners, including nuts and washers, in contact with preservative-treated wood shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Staples shall be of stainless steel. Fasteners other than nails, staples, timber rivets, wood screws and lag screws shall be permitted to be of mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B695, Class 55 minimum. Connectors that are used in exterior applications and in contact with preservative-treated wood shall have coating types and weights in accordance with the treated wood or connector manufacturer’s recommendations. In the absence of manufacturer’s recommendations, a minimum of ASTM A653, Type G185 zinc-coated galvanized steel, or equivalent, shall be used. Exception: Plain carbon steel fasteners, including nuts and washers, in SBX/DOT and zinc borate preservative-treated wood in an interior, dry environment shall be permitted.
2304.10.5.2 Fastenings for wood foundations. | Fastenings, including nuts and washers, for wood foundations shall be as required in AWC PWF.
2304.10.5.3 Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations. | Fasteners, including nuts and washers, for fire-retardant-treated wood used in exterior applications or wet or damp locations shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Staples shall be of stainless steel. Fasteners other than nails, staples, timber rivets, wood screws and lag screws shall be permitted to be of mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B695, Class 55 minimum.
2304.11 Heavy timber construction. | Where a structure, portion thereof or individual structural elements are required by other provisions of this code to be of heavy timber, the building elements therein shall comply with the applicable provisions of Sections 2304.11.1 through 2304.11.4. Minimum dimensions of heavy timber shall comply with the applicable requirements in Table 2304.11 based on roofs or floors supported and the configuration of each structural element, or the applicable requirements in Sections 2304.11.2 through 2304.11.4. Lumber decking shall be in accordance with Section 2304.9. | 2304.11 Heavy timber construction. | Where a structure, portion thereof or individual structural elements are required by provisions of this code to be of heavy timber, the building elements therein shall comply with the applicable provisions of Sections 2304.11.1 through 2304.11.4. Minimum dimensions of heavy timber shall comply with the applicable requirements in Table 2304.11 based on roofs or floors supported and the configuration of each structural element, or in Sections 2304.11.2 through 2304.11.4. Lumber decking shall be in accordance with Section 2304.9.
2304.10.5.4 Fasteners for fire-retardant-treated wood used in interior applications. | Fasteners, including nuts and washers, for fire-retardant-treated wood used in interior locations shall be in accordance with the manufacturer’s recommendations. In the absence of manufacturer’s recommendations, Section 2304.10.5.3 shall apply.
2304.11.1 Details of heavy timber structural members. | Heavy timber structural members shall be detailed and constructed in accordance with Sections 2304.11.1 through 2304.11.1.4. | 2304.11.1 Details of heavy timber structural members. | Heavy timber structural members shall be detailed and constructed in accordance with Sections 2304.11.1 through 2304.11.1.3.
2304.10.6 Load path. | Where wall framing members are not continuous from the foundation sill to the roof, the members shall be secured to ensure a continuous load path. Where required, sheet metal clamps, ties or clips shall be formed of galvanized steel or other approved corrosion-resistant material not less than 0.0329-inch (0.836 mm) base metal thickness.
2304.11.1.1 Columns. | Minimum dimensions of columns shall be in accordance with Table 2304.11. Columns shall be continuous or superimposed throughout all stories and connected in an approved manner. Girders and beams at column connections shall be closely fitted around columns and adjoining ends shall be cross tied to each other, or intertied by caps or ties, to transfer horizontal loads across joints. Wood bolsters shall not be placed on tops of columns unless the columns support roof loads only. Where traditional heavy timber detailing is used, connections shall be by means of reinforced concrete or metal caps with brackets, by properly designed steel or iron caps, with pintles and base plates, by timber splice plates affixed to the columns by metal connectors housed within the contact faces, or by other approved methods. | 2304.11.1.1 Columns. | Minimum dimensions of columns shall be in accordance with Table 2304.11. Columns shall be continuous or superimposed throughout all stories and connected in an approved manner. Girders and beams at column connections shall be closely fitted around columns and adjoining ends shall be cross tied to each other, or intertied by caps or ties, to transfer horizontal loads across joints. Wood bolsters shall not be placed on tops of columns unless the columns support roof loads only. Where traditional heavy timber detailing is used, connections shall be by means of reinforced concrete or metal caps with brackets, by properly designed steel or iron caps, with pintles and base plates, by timber splice plates affixed to the columns by metal connectors housed within the contact faces, or by other approved methods.
2304.10.7 Framing requirements. | Wood columns and posts shall be framed to provide full end bearing. Alternatively, column-and-post end connections shall be designed to resist the full compressive loads, neglecting end-bearing capacity. Column-and-post end connections shall be fastened to resist lateral and net induced uplift forces.
2304.11.1.2 Floor framing. | Minimum dimensions of floor framing shall be in accordance with Table 2304.11. Approved wall plate boxes or hangers shall be provided where wood beams, girders or trusses rest on masonry or concrete walls. Where intermediate beams are used to support a floor, they shall rest on top of girders, or shall be supported by an approved metal hanger into which the ends of the beams shall be closely fitted. Where traditional heavy timber detailing is used, these connections shall be permitted to be supported by ledgers or blocks securely fastened to the sides of the girders. | 2304.11.1.2 Floor framing. | Minimum dimensions of floor framing shall be in accordance with Table 2304.11. Approved wall plate boxes or hangers shall be provided where wood beams, girders or trusses rest on masonry or concrete walls. Where intermediate beams are used to support a floor, they shall rest on top of girders, or shall be supported by an approved metal hanger into which the ends of the beams shall be closely fitted. Where traditional heavy timber detailing is used, these connections shall be permitted to be supported by ledgers or blocks securely fastened to the sides of the girders.
2304.10.8 Connection fire resistance rating. | Wood structural connections, including connectors, fasteners, and portions of wood members included in the connection design, shall be protected from fire exposure for the required fire resistance time. For connections in Type IV construction, the required fire resistance time shall be at minimum one hour or as required for the building element by Table 601 and Section 602.4. Fire resistance ratings for connections shall be determined by one of the following:
2304.11.1.3 Roof framing. | Minimum dimensions of roof framing shall be in accordance with Table 2304.11. Every roof girder and not less than every alternate roof beam shall be anchored to its supporting member to resist forces as required in Chapter 16. | 2304.11.1.3 Roof framing. | Minimum dimensions of roof framing shall be in accordance with Table 2304.11. Every roof girder and not less than every alternate roof beam shall be anchored to its supporting member to resist forces as required in Chapter 16.
2304.11.2 Partitions and walls. | Partitions and walls shall comply with Section 2304.11.2.1 or 2304.11.2.2. | 2304.11.2 Partitions and walls. | Partitions and walls shall comply with Section 2304.11.2.1 or 2304.11.2.2.
2304.11.2.1 Exterior walls. | Exterior walls shall be of noncombustible materials or other materials as permitted by Section 602.4. | 2304.11.2.1 Exterior walls. | Exterior walls shall be permitted to be cross-laminated timber not less than 4 inches (102 mm) in thickness meeting the requirements of Section 2303.1.4.
2304.11.2.2 Interior walls and partitions. | Interior walls and partitions shall be of solid wood construction formed by not less than two layers of 1-inch (25 mm) matched boards or laminated construction 4 inches (102 mm) thick, or of 1-hour fire-resistance-rated construction. | 2304.11.2.2 Interior walls and partitions. | Interior walls and partitions shall be of solid wood construction formed by not less than two layers of 1-inch (25 mm) matched boards or laminated construction 4 inches (102 mm) thick, or of 1-hour fire-resistance-rated construction.
2304.11.3 Floors. | Floors shall be without concealed spaces. Wood floors shall be constructed in accordance with Section 2304.11.3.1 or 2304.11.3.2. | 2304.11.3 Floors. | Floors shall be without concealed spaces or with concealed spaces complying with Section 602.4.4.3. Wood floors shall be constructed in accordance with Section 2304.11.3.1 or 2304.11.3.2.
2304.11.3.1 Cross-laminated timber floors. | Cross-laminated timber shall be not less than 4 inches (102 mm) in actual thickness. Cross-laminated timber shall be continuous from support to support and mechanically fastened to one another. Cross-laminated timber shall be permitted to be connected to walls without a shrinkage gap providing swelling or shrinking is considered in the design. Corbelling of masonry walls under the floor shall be permitted to be used. | 2304.11.3.1 Cross-laminated timber floors. | Cross-laminated timber shall be not less than 4 inches (102 mm) in actual thickness. Cross-laminated timber shall be continuous from support to support and mechanically fastened to one another. Cross-laminated timber shall be permitted to be connected to walls without a shrinkage gap providing swelling or shrinking is considered in the design. Corbelling of masonry walls under the floor shall be permitted to be used.
2304.11.1.4 Cross-laminated timber. | Cross-laminated timber shall be used only when engineered by a registered design professional. The design shall take into account the effects of openings cut into the panels. Cross-laminated timber shall not be used as individual columns or beams.
2304.11.3.2 Sawn or glued-laminated plank floors. | Sawn or glued-laminated plank floors shall be one of the following: | 2304.11.3.2 Sawn or glued-laminated plank floors. | Sawn or glued-laminated plank floors shall be one of the following:
2304.11.4 Roof decks. | Roofs shall be without concealed spaces and roof decks shall be constructed in accordance with Section 2304.11.4.1 or 2304.11.4.2. Other types of decking shall be an alternative that provides equivalent fire resistance and structural properties. Where supported by a wall, roof decks shall be anchored to walls to resist forces determined in accordance with Chapter 16. Such anchors shall consist of steel bolts, lags, screws or approved hardware of sufficient strength to resist prescribed forces. | 2304.11.4 Roof decks. | Roofs shall be without concealed spaces or with concealed spaces complying with Section 602.4.4.3. Roof decks shall be constructed in accordance with Section 2304.11.4.1 or 2304.11.4.2. Other types of decking shall be an alternative that provides equivalent fire resistance and structural properties. Where supported by a wall, roof decks shall be anchored to walls to resist forces determined in accordance with Chapter 16. Such anchors shall consist of steel bolts, lags, screws or approved hardware of sufficient strength to resist prescribed forces.
2304.11.4.1 Cross-laminated timber roofs. | Cross-laminated timber roofs shall be not less than 3 inches (76 mm) nominal in thickness and shall be continuous from support to support and mechanically fastened to one another. | 2304.11.4.1 Cross-laminated timber roofs. | Cross-laminated timber roofs shall be not less than 3 inches (76 mm) nominal in thickness and shall be continuous from support to support and mechanically fastened to one another.
2304.11.4.2 Sawn, wood structural panel, or glued-laminated plank roofs. | Sawn, wood structural panel, or glued-laminated plank roofs shall be one of the following: | 2304.11.4.2 Sawn, wood structural panel, or glued-laminated plank roofs. | Sawn, wood structural panel, or glued-laminated plank roofs shall be one of the following:
2304.12 Protection against decay and termites. | Wood shall be protected from decay and termites in accordance with the applicable provisions of Sections 2304.12.1 through 2304.12.8. | 2304.12 Protection against decay and termites. | Wood shall be protected from decay and termites in accordance with the applicable provisions of Sections 2304.12.1 through 2304.12.4.
2304.12.1.1 Joists, girders and subfloor. | Wood joists or wood structural floors that are closer than 18 inches (457 mm) or wood girders that are closer than 12 inches (305 mm) to the exposed ground in crawl spaces or unexcavated areas located within the perimeter of the building foundation shall be of naturally durable or preservative-treated wood. | 2304.12.1.1 Joists, girders and subfloor. | Wood joists or wood structural floors that are closer than 18 inches (457 mm) or wood girders that are closer than 12 inches (305 mm) to the exposed ground in crawl spaces or unexcavated areas located within the perimeter of the building foundation shall be of naturally durable or preservative-treated wood.
2304.12.1.2 Wood supported by exterior foundation walls. | Wood framing members, including wood sheathing, that are in contact with exterior foundation walls and are less than 8 inches (203 mm) from exposed earth shall be of naturally durable or preservative-treated wood. | 2304.12.1.2 Wood supported by exterior foundation walls. | Wood framing members, including wood sheathing, that are in contact with exterior foundation walls and are less than 8 inches (203 mm) from exposed earth shall be of naturally durable or preservative-treated wood.
2304.12.1.3 Exterior walls below grade. | Wood framing members and furring strips in direct contact with the interior of exterior masonry or concrete walls below grade shall be of naturally durable or preservative-treated wood. | 2304.12.1.3 Exterior walls below grade. | Wood framing members and furring strips in direct contact with the interior of exterior masonry or concrete walls below grade shall be of naturally durable or preservative-treated wood.
2304.12.1.4 Sleepers and sills. | Sleepers and sills on a concrete or masonry slab that is in direct contact with earth shall be of naturally durable or preservative-treated wood. | 2304.12.1.4 Sleepers and sills. | Sleepers and sills on a concrete or masonry slab that is in direct contact with earth shall be of naturally durable or preservative-treated wood.
2304.12.1.5 Wood siding. | Clearance between wood siding and earth on the exterior of a building shall not be less than 8 inches (203 mm) or less than 2 inches (51 mm) vertical from covered concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood. | 2304.12.1.5 Wood siding. | Clearance between wood siding and earth on the exterior of a building shall be not less than 6 inches (152 mm) or less than 2 inches (51 mm) vertical from concrete steps, porch slabs, patio slabs and similar horizontal surfaces exposed to the weather except where siding, sheathing and wall framing are of naturally durable or preservative-treated wood.
2304.12.1 Locations requiring water-borne preservatives or naturally durable wood. | Wood used above ground in the locations specified in Sections 2304.12.1.1 through 2304.12.1.5, 2304.12.3 and 2304.12.5 shall be naturally durable wood or preservative-treated wood using water-borne preservatives, in accordance with AWPA U1 for above-ground use.
2304.12.2 Other locations. | Wood used in the locations specified in Sections 2304.12.2.1 through 2304.12.2.5 shall be naturally durable wood or preservative-treated wood in accordance with AWPA U1. Preservative-treated wood used in interior locations shall be protected with two coats of urethane, shellac, latex epoxy or varnish unless water-borne preservatives are used. Prior to application of the protective finish, the wood shall be dried in accordance with the manufacturer’s recommendations. | 2304.12.2 Other locations. | Wood used in the locations specified in Sections 2304.12.2.1 through 2304.12.2.8 shall be naturally durable wood or preservative-treated wood in accordance with AWPA U1. Preservative-treated wood used in interior locations shall be protected with two coats of urethane, shellac, latex epoxy or varnish unless waterborne preservatives are used. Prior to application of the protective finish, the wood shall be dried in accordance with the manufacturer’s recommendations.
2304.12.2.1 Girder ends. | The ends of wood girders entering exterior masonry or concrete walls shall be provided with a ½-inch (12.7 mm) airspace on top, sides and end, unless naturally durable or preservative-treated wood is used. | 2304.12.2.1 Girder ends. | The ends of wood girders entering exterior masonry or concrete walls shall be provided with a 1/2-inch (12.7 mm) airspace on top, sides and end, unless naturally durable or preservative-treated wood is used.
2304.12.2.2 Posts or columns. | Posts or columns supporting permanent structures and supported by a concrete or masonry slab or footing that is in direct contact with the earth shall be of naturally durable or preservative-treated wood. Exception: Posts or columns that meet all of the following: 1. Are not exposed to the weather, or are protected by a roof, eave, overhang, or other covering if exposed to the weather. 2. Are supported by concrete piers or metal pedestals projected not less than 1 inch (25 mm) above the slab or deck and are separated from the concrete pier by an impervious moisture barrier. 3. Are located not less than 8 inches (203 mm) above exposed earth. | 2304.12.2.2 Posts or columns. | Posts or columns supporting permanent structures and supported by a concrete or masonry slab or footing that is in direct contact with the earth shall be of naturally durable or preservative-treated wood. Exception: Posts or columns that meet all of the following: 1. Are not exposed to the weather, or are protected by a roof, eave, overhang, or other covering if exposed to the weather. 2. Are supported by concrete piers or metal pedestals projected not less than 1 inch (25 mm) above the slab or deck and are separated from the concrete pier by an impervious moisture barrier. 3. Are located not less than 8 inches (203 mm) above exposed earth.
2304.12.2.3 Supporting member for permanent appurtenances. | Naturally durable or preservative-treated wood shall be utilized for those portions of wood members that form the structural supports of buildings, balconies, porches or similar permanent building appurtenances where such members are exposed to the weather without adequate protection from a roof, eave, overhang or other covering to prevent moisture or water accumulation on the surface or at joints between members. | 2304.12.2.3 Supporting member for permanent appurtenances. | Naturally durable or preservative-treated wood shall be utilized for those portions of wood members that form the structural supports of buildings, balconies, porches or similar permanent building appurtenances where such members are exposed to the weather without adequate protection from a roof, eave, overhang or other covering to prevent moisture or water accumulation on the surface or at joints between members. Exception: Sawn lumber in buildings located in a geographical region where experience has demonstrated that climatic conditions preclude the need to use durable materials where the structure is exposed to the weather.
2304.12.2.4 Laminated timbers. | The portions of glued-laminated timbers that form the structural supports of a building or other structure and are exposed to weather and not fully protected from moisture by a roof, eave or similar covering shall be pressure treated with preservative or be manufactured from naturally durable or preservative-treated wood.
2304.12.2.5 Supporting members for permeable floors and roofs. | Wood structural members that support moisture-permeable floors or roofs that are exposed to the weather, such as concrete or masonry slabs, shall be of naturally durable or preservative-treated wood unless separated from such floors or roofs by an impervious moisture barrier. The impervious moisture barrier system protecting the structure supporting floors shall provide positive drainage of water that infiltrates the moisture-permeable floor topping.
2304.13 Long-term loading. | Wood members supporting concrete, masonry or similar materials shall be checked for the effects of long-term loading using the provisions of the ANSI/AWC NDS. The total deflection, including the effects of long-term loading, shall be limited in accordance with Section 1604.3.1 for these supported materials. Exception: Horizontal wood members supporting masonry or concrete nonstructural floor or roof surfacing not more than 4 inches (102 mm) thick need not be checked for long-term loading. | 2304.13 Long-term loading. | Wood members supporting concrete, masonry or similar materials shall be checked for the effects of long-term loading using the provisions of the ANSI/AWC NDS. The total deflection, including the effects of long-term loading, shall be limited in accordance with Section 1604.3.1 for these supported materials. Exception: Horizontal wood members supporting masonry or concrete nonstructural floor or roof surfacing not more than 4 inches (102 mm) thick need not be checked for long-term loading.
2304.12.2.6 Ventilation beneath balcony or elevated walking surfaces. | Enclosed framing in exterior balconies and elevated walking surfaces that are exposed to rain, snow or drainage from irrigation shall be provided with openings that provide a net free cross-ventilation area not less than 1/150 of the area of each separate space. | 2304.12.2.6 Wood in contact with the ground or fresh water. | Wood used in contact with exposed earth shall be naturally durable for both decay and termite resistance or preservative treated in accordance with AWPA U1 for soil or fresh water use. Exception: Untreated wood is permitted where such wood is continuously and entirely below the ground-water level or submerged in fresh water.
2305.1 General. | Structures using wood-frame shear walls or wood-frame diaphragms to resist wind, seismic or other lateral loads shall be designed and constructed in accordance with AWC SDPWS and the applicable provisions of Sections 2305, 2306 and 2307. | 2305.1 General. | Structures using wood-frame shear walls or wood-frame diaphragms to resist wind, seismic or other lateral loads shall be designed and constructed in accordance with AWC SDPWS and the applicable provisions of Sections 2305, 2306 and 2307.
2304.12.3 Wood in contact with the ground or fresh water. | Wood used in contact with exposed earth shall be naturally durable for both decay and termite resistance or preservative treated in accordance with AWPA U1 for soil or fresh water use. Exception: Untreated wood is permitted where such wood is continuously and entirely below the ground-water level or submerged in fresh water.
2305.1.1 Openings in shear panels. | Openings in shear panels that materially affect their strength shall be detailed on the plans and shall have their edges adequately reinforced to transfer all shearing stresses. | 2305.1.1 Openings in shear panels. | Openings in shear panels that materially affect their strength shall be detailed on the plans and shall have their edges adequately reinforced to transfer all shearing stresses.
2304.12.3.1 Posts or columns. | Posts and columns that are supporting permanent structures and embedded in concrete that is exposed to the weather or in direct contact with the earth shall be of preservative-treated wood.
2305.2 Diaphragm deflection. | The deflection of wood-frame diaphragms shall be determined in accordance with AWC SDPWS. The deflection (Δdia) of a blocked wood structural panel diaphragm uniformly fastened throughout with staples is permitted to be calculated in accordance with Equation 23-1. If not uniformly fastened, the constant 0.188 (For SI: 1/1627) in the third term shall be modified by an approved method. | 2305.2 Diaphragm deflection. | The deflection of wood-frame diaphragms shall be determined in accordance with AWC SDPWS. The deflection (Δdia) of a blocked wood structural panel diaphragm uniformly fastened throughout with staples is permitted to be calculated in accordance with Equation 23-1. If not uniformly fastened, the constant 0.188 (For SI: 1/1627) in the third term shall be modified by an approved method.
2304.12.4 Termite protection. | In geographical areas where hazard of termite damage is known to be very heavy, wood floor framing in the locations specified in Section 2304.12.1 & 2304.12.2 and exposed framing of exterior decks or balconies shall be of naturally durable species (termite resistant) or preservative treated in accordance with AWPA U1 for the species, product preservative and end use or provided with approved methods of termite protection.
2305.3 Shear wall deflection. | The deflection of wood-frame shear walls shall be determined in accordance with AWC SDPWS. The deflection (Δsw) of a blocked wood structural panel shear wall uniformly fastened throughout with staples is permitted to be calculated in accordance with Equation 23-2. | 2305.3 Shear wall deflection. | The deflection of wood-frame shear walls shall be determined in accordance with AWC SDPWS. The deflection (Δsw) of a blocked wood structural panel shear wall uniformly fastened throughout with staples is permitted to be calculated in accordance with Equation 23-2.
2304.12.5 Wood used in retaining walls and cribs. | Wood installed in retaining or crib walls shall be preservative treated in accordance with AWPA U1 for soil and fresh water use.
2306.1 Allowable stress design. | The design and construction of wood elements in structures using allowable stress design shall be in accordance with the following applicable standards: | 2306.1 Allowable stress design. | The design and construction of wood elements in structures using allowable stress design shall be in accordance with the following applicable standards:
2304.12.6 Attic ventilation. | For attic ventilation, see Section 1203.2.
2306.1.1 Joists and rafters. | The design of rafter spans is permitted to be in accordance with the AWC STJR. | 2306.1.1 Joists and rafters. | The design of rafter spans is permitted to be in accordance with the AWC STJR.
2304.12.7 Under-floor ventilation (crawl space). | For under-floor ventilation (crawl space), see Section 1203.4.
2306.1.2 Plank and beam flooring. | The design of plank and beam flooring is permitted to be in accordance with the AWC Wood Construction Data No. 4. | 2306.1.2 Plank and beam flooring. | The design of plank and beam flooring is permitted to be in accordance with the AWC Wood Construction Data No. 4.
2304.12.8 Debris. | All loose wood and debris and all wood forms shall be removed from spaces under the building. All stump and roots shall be grubbed to a minimum depth of 12 inches (305 mm).
2306.1.3 Treated wood stress adjustments. | The allowable unit stresses for preservative-treated wood shall be adjusted for treatment in accordance with the ANSI/AWC NDS. | 2306.1.3 Treated wood stress adjustments. | The allowable unit stresses for preservative-treated wood need not be adjusted for treatment, but are subject to other adjustments.
2306.1.4 Lumber decking. | The capacity of lumber decking arranged according to the patterns described in Section 2304.9.2 shall be the lesser of the capacities determined for flexure and deflection according to the formulas in Table 2306.1.4. | 2306.1.4 Lumber decking. | The capacity of lumber decking arranged according to the patterns described in Section 2304.9.2 shall be the lesser of the capacities determined for moment and deflection according to the formulas in Table 2306.1.4.
2306.2 Wood-frame diaphragms. | Wood-frame diaphragms shall be designed and constructed in accordance with AWC SDPWS. Where panels are fastened to framing members with staples, requirements and limitations of AWC SDPWS shall be met and the allowable shear values set forth in Table 2306.2(1) or 2306.2(2) shall be permitted. The allowable shear values in Tables 2306.2(1) and 2306.2(2) are permitted to be increased 40 percent for wind design. | 2306.2 Wood-frame diaphragms. | Wood-frame diaphragms shall be designed and constructed in accordance with AWC SDPWS. Where panels are fastened to framing members with staples, requirements and limitations of AWC SDPWS shall be met and the allowable shear values set forth in Table 2306.2(1) or 2306.2(2) shall be permitted. The allowable shear values in Tables 2306.2(1) and 2306.2(2) are permitted to be increased 40 percent for wind design.
2306.2.1 Gypsum board diaphragm ceilings. | Gypsum board diaphragm ceilings shall be in accordance with Section 2508.5. | 2306.2.1 Gypsum board diaphragm ceilings. | Gypsum board diaphragm ceilings shall be in accordance with Section 2508.6.
2306.3 Wood-frame shear walls. | Wood-frame shear walls shall be designed and constructed in accordance with AWC SDPWS. Where panels are fastened to framing members with staples, requirements and limitations of AWC SDPWS shall be met and the allowable shear values set forth in Table 2306.3(1), 2306.3(2) or 2306.3(3) shall be permitted. The allowable shear values in Tables 2306.3(1) and 2306.3(2) are permitted to be increased 40 percent for wind design. Panels complying with ANSI/APA PRP-210 shall be permitted to use design values for Plywood Siding in the AWC SDPWS. | 2306.3 Wood-frame shear walls. | Wood-frame shear walls shall be designed and constructed in accordance with AWC SDPWS. Where panels are fastened to framing members with staples, requirements and limitations of AWC SDPWS shall be met and the allowable shear values set forth in Table 2306.3(1), 2306.3(2) or 2306.3(3) shall be permitted. The allowable shear values in Tables 2306.3(1) and 2306.3(2) are permitted to be increased 40 percent for wind design. Panels complying with ANSI/APA PRP-210 shall be permitted to use design values for Plywood Siding in the AWC SDPWS.
2307.1 Load and resistance factor design. | The design and construction of wood elements and structures using load and resistance factor design shall be in accordance with ANSI/AWC NDS and AWC SDPWS. | 2307.1 Load and resistance factor design. | The design and construction of wood elements and structures using load and resistance factor design shall be in accordance with ANSI/AWC NDS and AWC SDPWS.
2308.1 General. | The requirements of this section are intended for conventional light-frame construction. Other construction methods are permitted to be used, provided a satisfactory design is submitted showing compliance with other provisions of this code. Interior nonload-bearing partitions, ceilings and curtain walls of conventional light-frame construction are not subject to the limitations of Section 2308.2. | 2308.1 General. | The requirements of this section are intended for conventional light-frame construction. Other construction methods are permitted to be used, provided that a satisfactory design is submitted showing compliance with other provisions of this code. Interior nonload-bearing partitions, ceilings and curtain walls of conventional light-frame construction are not subject to the limitations of Section 2308.2. Detached one- and two-family dwellings and townhouses not more than three stories above grade plane in height with a separate means of egress and their accessory structures shall comply with the International Residential Code.
2308.1.1 Portions exceeding limitations of conventional light-frame construction. | When portions of a building of otherwise conventional light-frame construction exceed the limits of Section 2308.2, those portions and the supporting load path shall be designed in accordance with accepted engineering practice and the provisions of this code. For the purposes of this section, the term “portions” shall mean parts of buildings containing volume and area such as a room or a series of rooms. The extent of such design need only demonstrate compliance of the nonconventional light-framed elements with other applicable provisions of this code and shall be compatible with the performance of the conventional light-framed system. | 2308.1.1 Portions exceeding limitations of conventional light-frame construction. | Where portions of a building of otherwise conventional light-frame construction exceed the limits of Section 2308.2, those portions and the supporting load path shall be designed in accordance with accepted engineering practice and the provisions of this code. For the purposes of this section, the term “portions” shall mean parts of buildings containing volume and area such as a room or a series of rooms. The extent of such design need only demonstrate compliance of the nonconventional light-framed elements with other applicable provisions of this code and shall be compatible with the performance of the conventional light-framed system.
2308.2 Limitations. | Buildings are permitted to be constructed in accordance with the provisions of conventional light-frame construction, subject to the limitations in Sections 2308.2. 1╪ through 2308.2.6. | 2308.2 Limitations. | Buildings are permitted to be constructed in accordance with the provisions of conventional light-frame construction, subject to the limitations in Sections 2308.2.1 through 2308.2.6.
2308.2.1 Stories. | Structures of conventional light-frame construction shall be limited in story height in accordance with Table 2308.2.1. | 2308.2.1 Stories. | Structures of conventional light-frame construction shall be limited in story height in accordance with Table 2308.2.1.
2308.2.2 Allowable floor-to-floor height. | Maximum floor-to-floor height shall not exceed 11 feet, 7 inches (3531 mm). Exterior bearing wall and interior braced wall heights shall not exceed a stud height of 10 feet (3048 mm). | 2308.2.2 Allowable floor-to-floor height. | Maximum floor-to-floor height shall not exceed 11 feet, 7 inches (3531 mm). Exterior bearing wall and interior braced wall heights shall not exceed a stud height of 10 feet (3048 mm).
2308.2.3 Allowable loads. | Loads shall be in accordance with Chapter 16 and shall not exceed the following: 1. Average dead loads shall not exceed 15 psf (718 N/m2) for combined roof and ceiling, exterior walls, floors and partitions. Exceptions: 1. Subject to the limitations of Section 2308.6.10, stone or masonry veneer up to the lesser of 5 inches (127 mm) thick or 50 psf (2395 N/m2) and installed in accordance with Chapter 14 is permitted to a height of 30 feet (9144 mm) above a noncombustible foundation, with an additional 8 feet (2438 mm) permitted for gable ends. 2. Concrete or masonry fireplaces, heaters and chimneys shall be permitted in accordance with the provisions of this code. 2. Live loads shall not exceed 40 psf (1916 N/m2) for floors. Exception: Live loads for concrete slab-on-ground floors in Risk Categories I and II shall be not more than 125 psf. | 2308.2.3 Allowable loads. | Loads shall be in accordance with Chapter 16 and shall not exceed the following: 1. Average dead loads shall not exceed 15 psf (718 N/m2) for combined roof and ceiling, exterior walls, floors and partitions. Exceptions: 1. Subject to the limitations of Section 2308.6.10, stone or masonry veneer up to the less of 5 inches (127 mm) thick or 50 pounds per square foot (2395 N/m2) and installed in accordance with Chapter 14 is permitted to a height of 30 feet (9144 mm) above a noncombustible foundation, with an additional 8 feet (2439) permitted for gable ends. 2. Concrete or masonry fireplaces, heaters and chimneys shall be permitted in accordance with the provisions of this code. 2. Live loads shall not exceed 40 psf (1916 N/m2) for floors. Exception: Live loads for concrete slab-on-ground floors in Risk Categories I and II shall be not more than 125 psf. 3. Ground snow loads shall not exceed 50 psf (2395 N/m2).
2308.2.5 Allowable roof span. | Ceiling joist and rafter framing constructed in accordance with Section 2308.7 and trusses shall not span more than 40 feet (12 192 mm) between points of vertical support. A ridge board in accordance with Section 2308.7 or 2308.7.3.1 shall not be considered a vertical support. | 2308.2.5 Allowable roof span. | Ceiling joist and rafter framing constructed in accordance with Section 2308.7 and trusses shall not span more than 40 feet (12 192 mm) between points of vertical support. A ridge board in accordance with Section 2308.7 or 2308.7.3.1 shall not be considered a vertical support.
2308.2.6 Risk category limitation. | The use of the provisions for conventional light-frame construction in this section shall not be permitted for Risk Category IV buildings assigned to Seismic Design Category B, C, or D, as determined in Section 1613. | 2308.2.6 Risk category limitation. | The use of the provisions for conventional light-frame construction in this section shall not be permitted for Risk Category IV buildings assigned to Seismic Design Category B, C, D or F.
2308.3 Foundations and footings. | Foundations and footings shall be designed and constructed in accordance with Chapter 18. Connections to foundations and footings shall comply with this section. | 2308.3 Foundations and footings. | Foundations and footings shall be designed and constructed in accordance with Chapter 18. Connections to foundations and footings shall comply with this section.
2308.1.2 Connectors and fasteners. | Connectors and fasteners used in conventional light-frame construction shall comply with the requirements of Section 2304.10.
2308.3.1 Foundation plates or sills. | Foundation plates or sills resting on concrete or masonry foundations shall comply with Section 2304.3.1. Foundation plates or sills shall be bolted or anchored to the foundation with not less than ½-inch-diameter (12.7 mm) steel bolts or approved anchors suitable for use with pressure-treated plates spaced to provide equivalent anchorage as the steel bolts. Bolts shall be embedded not less than 7 inches (178 mm) into concrete or masonry. The bolts shall be located in the middle third of the width of the plate. Bolts shall be spaced not more than 6 feet (1829 mm) on center and there shall be not less than two bolts or anchor straps per piece with one bolt or anchor strap located not more than 12 inches (305 mm) or less than 4 inches (102 mm) from each end of each piece. Bolts in sill plates of braced wall lines in structures over two stories above grade shall be spaced not more than 4 feet (1219 mm) on center. A properly sized nut and washer shall be tightened on each bolt to the plate. | 2308.3.1 Foundation plates or sills. | Foundation plates or sills resting on concrete or masonry foundations shall comply with Section 2304.3.1. Foundation plates or sills shall be bolted or anchored to the foundation with not less than 1/2-inch-diameter (12.7 mm) steel bolts or approved anchors spaced to provide equivalent anchorage as the steel bolts. Bolts shall be embedded not less than 7 inches (178 mm) into concrete or masonry. The bolts shall be located in the middle third of the width of the plate. Bolts shall be spaced not more than 6 feet (1829 mm) on center and there shall be not less than two bolts or anchor straps per piece with one bolt or anchor strap located not more than 12 inches (305 mm) or less than 4 inches (102 mm) from each end of each piece. Bolts in sill plates of braced wall lines in structures over two stories above grade shall be spaced not more than 4 feet (1219 mm) on center. A properly sized nut and washer shall be tightened on each bolt to the plate.
2308.4 Floor framing. | Floor framing shall comply with this section. | 2308.4 Floor framing. | Floor framing shall comply with this section.
2308.4.1 Girders. | Girders for single-story construction or girders supporting loads from a single floor shall be not less than 4 inches by 6 inches (102 mm by 152 mm) for spans 6 feet (1829 mm) or less, provided that girders are spaced not more than 8 feet (2438 mm) on center. Other girders shall be designed to support the loads specified in this code. Girder end joints shall occur over supports. | 2308.4.1 Girders. | Girders for single-story construction or girders supporting loads from a single floor shall be not less than 4 inches by 6 inches (102 mm by 152 mm) for spans 6 feet (1829 mm) or less, provided that girders are spaced not more than 8 feet (2438 mm) on center. Other girders shall be designed to support the loads specified in this code. Girder end joints shall occur over supports.
2308.2.4 Basic design wind speed. | The basic design wind speed, V, in miles per hour for determination of wind loads shall be as set forth in Table 1609.3. Values are ultimate design 3-second gust wind speeds in miles per hour at 33 feet (10 058 mm) above ground Exposure Category C.
2308.4.1.1 Allowable girder spans. | The allowable spans of girders that are fabricated of dimension lumber shall not exceed the values set forth in Table 2308.4.1.1(1) or 2308.4.1.1(2). | 2308.4.1.1 Allowable girder spans. | The allowable spans of girders that are fabricated of dimension lumber shall not exceed the values set forth in Table 2308.4.1.1(1) or 2308.4.1.1(2).
2308.4.2 Floor joists. | Floor joists shall comply with this section. | 2308.4.2 Floor joists. | Floor joists shall comply with this section.
2308.4.2.1 Span. | Spans for floor joists shall be in accordance with Table 2308.4.2.1(1) or 2308.4.2.1(2) or the AWC STJR. | 2308.4.2.1 Span. | Spans for floor joists shall be in accordance with Table 2308.4.2.1(1), Table 2308.4.2.1(2) or the AWC STJR.
2308.4.2.2 Bearing. | The ends of each joist shall have not less than 1½ inches (38 mm) of bearing on wood or metal, or not less than 3 inches (76 mm) on masonry, except where supported on a 1-inch by 4-inch (25 mm by 102 mm) ribbon strip and nailed to the adjoining stud. | 2308.4.2.2 Bearing. | The ends of each joist shall have not less than 11/2 inches (38 mm) of bearing on wood or metal, or not less than 3 inches (76 mm) on masonry, except where supported on a 1-inch by 4-inch (25 mm by 102 mm) ribbon strip and nailed to the adjoining stud.
2308.4.2.3 Framing details. | Joists shall be supported laterally at the ends and at each support by solid blocking except where the ends of the joists are nailed to a header, band or rim joist or to an adjoining stud or by other means. Solid blocking shall be not less than 2 inches (51 mm) in thickness and the full depth of the joist. Joist framing from opposite sides of a beam, girder or partition shall be lapped at least 3 inches (76 mm) or the opposing joists shall be tied together in an approved manner. Joists framing into the side of a wood girder shall be supported by framing anchors or on ledger strips not less than 2 inches by 2 inches (51 mm by 51 mm). | 2308.4.2.3 Framing details. | Joists shall be supported laterally at the ends and at each support by solid blocking except where the ends of the joists are nailed to a header, band or rim joist or to an adjoining stud or by other means. Solid blocking shall be not less than 2 inches (51 mm) in thickness and the full depth of the joist. Joist framing from opposite sides of a beam, girder or partition shall be lapped not less than 3 inches (76 mm) or the opposing joists shall be tied together in an approved manner. Joists framing into the side of a wood girder shall be supported by framing anchors or on ledger strips not less than 2 inches by 2 inches (51 mm by 51 mm).
2308.3.2 Braced wall line sill plate anchorage in Seismic Design Category D. | Sill plates along braced wall lines in buildings assigned to Seismic Design Category D shall be anchored with anchor bolts with steel plate washers between the foundation sill plate and the nut, or approved anchor straps load-rated in accordance with Section 2304.10.3. Such washers shall be a minimum of 0.229 inch by 3 inches by 3 inches (5.82 mm by 76 mm by 76 mm) in size. The hole in the plate washer is permitted to be diagonally slotted with a width of up to 3/16 inch (4.76 mm) larger than the bolt diameter and a slot length not to exceed 1¾ inches (44 mm), provided a standard cut washer is placed between the plate washer and the nut. All steel shall be of appropriate corrosion resistance when in contact with pressure-treated wood.
2308.4.2.4 Notches and holes. | Notches on the ends of joists shall not exceed one-fourth the joist depth. Notches in the top or bottom of joists shall not exceed one-sixth the depth, shall not be longer than one-third the depth and shall not be located in the middle third of the span. Holes bored in joists shall not be within 2 inches (51 mm) of the top or bottom of the joist and the diameter of any such hole shall not exceed one-third the depth of the joist. Holes bored in the middle third of the span shall be located at the center of the joist depth. Clear distance between holes & notches shall be a minimum of 2 inches (51 mm). See Figure 2308.4.2.4. | 2308.4.2.4 Notches and holes. | Notches on the ends of joists shall not exceed one-fourth the joist depth. Notches in the top or bottom of joists shall not exceed one-sixth the depth and shall not be located in the middle third of the span. Holes bored in joists shall not be within 2 inches (51 mm) of the top or bottom of the joist and the diameter of any such hole shall not exceed one-third the depth of the joist.
2308.4.3 Engineered wood products. | Engineered wood products shall be installed in accordance with manufacturer’s recommendations. Cuts, notches and holes bored in trusses, structural composite lumber, structural glued-laminated members or I-joists are prohibited except where permitted by the manufacturer’s recommendations or where the effects of such alterations are specifically considered in the design of the member by a registered design professional. | 2308.4.3 Engineered wood products. | Engineered wood products shall be installed in accordance with manufacturer’s recommendations. Cuts, notches and holes bored in trusses, structural composite lumber, structural glued-laminated members or I-joists are not permitted except where permitted by the manufacturer’s recommendations or where the effects of such alterations are specifically considered in the design of the member by a registered design professional.
2308.4.4 Framing around openings. | Trimmer and header joists shall be doubled, or of lumber of equivalent cross section, where the span of the header exceeds 4 feet (1219 mm). The ends of header joists more than 6 feet (1829 mm) in length shall be supported by framing anchors or joist hangers unless bearing on a beam, partition or wall. Tail joists over 12 feet (3658 mm) in length shall be supported at the header by framing anchors or on ledger strips not less than 2 inches by 2 inches (51 mm by 51 mm). | 2308.4.4 Framing around openings. | Trimmer and header joists shall be doubled, or of lumber of equivalent cross section, where the span of the header exceeds 4 feet (1219 mm). The ends of header joists more than 6 feet (1829 mm) in length shall be supported by framing anchors or joist hangers unless bearing on a beam, partition or wall. Tail joists over 12 feet (3658 mm) in length shall be supported at the header by framing anchors or on ledger strips not less than 2 inches by 2 inches (51 mm by 51 mm).
2308.4.5 Joists supporting bearing partitions. | Bearing partitions parallel to joists shall be supported on beams, girders, doubled joists, walls or other bearing partitions. Bearing partitions perpendicular to joists shall not be offset from supporting girders, walls or partitions more than the joist depth unless such joists are of sufficient size to carry the additional load. | 2308.4.5 Joists supporting bearing partitions. | Bearing partitions parallel to joists shall be supported on beams, girders, doubled joists, walls or other bearing partitions. Bearing partitions perpendicular to joists shall not be offset from supporting girders, walls or partitions more than the joist depth unless such joists are of sufficient size to carry the additional load.
2308.4.6 Lateral support. | Floor and ceiling framing with a nominal depth-to-thickness ratio not less than 5 to 1 shall have one edge held in line for the entire span. Where the nominal depth-to-thickness ratio of the framing member exceeds 6 to 1, there shall be one line of bridging for each 8 feet (2438 mm) of span, unless both edges of the member are held in line. The bridging shall consist of not less than 1-inch by 3-inch (25 mm by 76 mm) lumber, double nailed at each end, or equivalent metal bracing of equal rigidity, full-depth solid blocking or other approved means. A line of bridging shall also be required at supports where equivalent lateral support is not otherwise provided. | 2308.4.6 Lateral support. | Floor and ceiling framing with a nominal depth-to-thickness ratio not less than 5 to 1 shall have one edge held in line for the entire span. Where the nominal depth-to-thickness ratio of the framing member exceeds 6 to 1, there shall be one line of bridging for each 8 feet (2438 mm) of span, unless both edges of the member are held in line. The bridging shall consist of not less than 1-inch by 3-inch (25 mm by 76 mm) lumber, double nailed at each end, or equivalent metal bracing of equal rigidity, full-depth solid blocking or other approved means. A line of bridging shall be required at supports where equivalent lateral support is not otherwise provided.
2308.4.7 Structural floor sheathing. | Structural floor sheathing shall comply with the provisions of Section 2304.8.1. | 2308.4.7 Structural floor sheathing. | Structural floor sheathing shall comply with the provisions of Section 2304.8.1.
2308.4.8 Under-floor ventilation. | For under-floor ventilation, see Section 1203.4. | 2308.4.8 Under-floor ventilation. | For under-floor ventilation, see Section 1202.4.
2308.4.9 Floor framing supporting braced wall panels. | Where braced wall panels are supported by cantilevered floors or are set back from the floor joist support, the floor framing shall comply with Section 2308.6.7. | 2308.4.9 Floor framing supporting braced wall panels. | Where braced wall panels are supported by cantilevered floors or are set back from the floor joist support, the floor framing shall comply with Section 2308.6.7.
2308.4.4.1 Openings in floor diaphragms in Seismic Design Categories B, C, and D. | Openings in horizontal diaphragms in Seismic Design Categories B, C, and D with a dimension that is greater than 4 feet (1219 mm) shall be constructed with metal ties and blocking in accordance with this section and Figure 2308.4.4.1(1). Metal ties shall be not less than 0.058 inch (1.47 mm) (16 galvanized gage) in thickness by 1½ inches (38 mm) in width and shall have a yield stress not less than 33,000 psi (227 Mpa). Blocking shall extend not less than the dimension of the opening in the direction of the tie and blocking. Ties shall be attached to blocking in accordance with the manufacturer’s instructions but with not less than eight 16d common nails on each side of the header-joist intersection.
2308.5 Wall construction. | Walls of conventional light-frame construction shall be in accordance with this section. | 2308.5 Wall construction. | Walls of conventional light-frame construction shall be in accordance with this section.
2308.4.4.2 Vertical offsets in floor diaphragms in Seismic Design Category D. | In Seismic Design Category D, portions of a floor level shall not be vertically offset such that the framing members on either side of the offset cannot be lapped or tied together in an approved manner in accordance with Figure 2308.4.4.2 unless the portion of the structure containing the irregular offset is designed in accordance with accepted engineering practice. Exception: Framing supported directly by foundations need not be lapped or tied directly together.
2308.5.1 Stud size, height and spacing. | The size, height and spacing of studs shall be in accordance with Table 2308.5.1. Studs shall be continuous from a support at the sole plate to a support at the top plate to resist loads perpendicular to the wall. The support shall be a foundation or floor, ceiling or roof diaphragm or shall be designed in accordance with accepted engineering practice. Exception: Jack studs, trimmer studs and cripple studs at openings in walls that comply with Table 2308.4.1.1(1) or 2308.4.1.1(2). | 2308.5.1 Stud size, height and spacing. | The size, height and spacing of studs shall be in accordance with Table 2308.5.1. Exception: Jack studs, trimmer studs and cripple studs at openings in walls that comply with Table 2308.4.1.1(1) or 2308.4.1.1(2).
2308.5.2 Framing details. | Studs shall be placed with their wide dimension perpendicular to the wall. Not less than three studs shall be installed at each corner of an exterior wall. Exceptions: 1. In interior nonload-bearing walls and partitions that are not braced wall panels, studs are permitted to be set with the long dimension parallel to the wall. 2. At corners, two studs are permitted, provided that wood spacers or backup cleats of ⅜-inch-thick (9.5 mm) wood structural panel, ⅜-inch (9.5 mm) Type M “Exterior Glue” particleboard, 1-inch-thick (25 mm) lumber or other approved devices that will serve as an adequate backing for the attachment of facing materials are used. Where fire-resistance ratings or shear values are involved, wood spacers, backup cleats or other devices shall not be used unless specifically approved for such use. | 2308.5.2 Framing details. | Studs shall be placed with their wide dimension perpendicular to the wall. Not less than three studs shall be installed at each corner of an exterior wall. Exceptions: 1. In interior nonbearing walls and partitions, studs are permitted to be set with the long dimension parallel to the wall. 2. At corners, two studs are permitted, provided that wood spacers or backup cleats of 3/8-inch-thick (9.5 mm) wood structural panel, 3/8-inch (9.5 mm) Type M “Exterior Glue” particleboard, 1-inch-thick (25 mm) lumber or other approved devices that will serve as an adequate backing for the attachment of facing materials are used. Where fire-resistance ratings or shear values are involved, wood spacers, backup cleats or other devices shall not be used unless specifically approved for such use.
2308.5.3 Plates and sills. | Studs shall have plates and sills in accordance with this section. | 2308.5.3 Plates and sills. | Studs shall have plates and sills in accordance with this section.
2308.5.3.1 Bottom plate or sill. | Studs shall have full bearing on a plate or sill. Plates or sills shall be not less than 2 inches (51 mm) nominal in thickness and have a width not less than the width of the wall studs. | 2308.5.3.1 Bottom plate or sill. | Studs shall have full bearing on a plate or sill. Plates or sills shall be not less than 2 inches (51 mm) nominal in thickness and have a width not less than the width of the wall studs.
2308.5.3.2 Top plates. | Bearing and exterior wall studs shall be capped with double top plates installed to provide overlapping at corners and at intersections with other partitions. End joints in double top plates shall be offset not less than 48 inches (1219 mm), and shall be nailed in accordance with Table 2304.10.1. Plates shall be a nominal 2 inches (51 mm) in depth and have a width not less than the width of the studs. Exception: A single top plate is permitted, provided that the plate is adequately tied at corners and intersecting walls by not less than the equivalent of a 3-inch by 6-inch (76 mm by 152 mm) by 0.036-inch-thick (0.914 mm) galvanized steel plate that is nailed to each wall or segment of wall by six 8d (2½” × 0.113” (64 mm by 2.87 mm)) box nails or equivalent on each side of the joint. For the butt-jointed splice between adjacent single top plates, not less than the equivalent of a 3-inch by 12-inch (76 mm by 304 mm) by 0.036-inch-thick (0.914 mm) galvanized steel plate that is nailed to each wall or segment of wall by twelve 8d (2½-inch × 0.113-inch (64 mm by 2.87 mm)) box nails on each side of the joint shall be required, provided that the rafters, joists or trusses are centered over the studs with a tolerance of not more than 1 inch (25 mm). The top plate shall not be required over headers that are in the same plane and in line with the upper surface of the adjacent top plates and are tied to adjacent wall sections as required for the butt joint splice between adjacent single top plates. Where bearing studs are spaced at 24-inch (610 mm) intervals, top plates are less than two 2-inch by 6-inch (51 mm by 152 mm) or two 3-inch by 4-inch (76 mm by 102 mm) members and the floor joists, floor trusses or roof trusses that they support are spaced at more than 16-inch (406 mm) intervals, such joists or trusses shall bear within 5 inches (127 mm) of the studs beneath or a third plate shall be installed. | 2308.5.3.2 Top plates. | Bearing and exterior wall studs shall be capped with double top plates installed to provide overlapping at corners and at intersections with other partitions. End joints in double top plates shall be offset not less than 48 inches (1219 mm), and shall be nailed in accordance with Table 2304.10.2. Plates shall be a nominal 2 inches (51 mm) in depth and have a width not less than the width of the studs. Exception: A single top plate is permitted, provided that the plate is adequately tied at corners and intersecting walls by not less than the equivalent of 3-inch by 6-inch (76 mm by 152 mm) by 0.036-inch-thick (0.914 mm) galvanized steel plate that is nailed to each wall or segment of wall by six 8d [21/2” × 0.113” (64-mm by 2.87 mm)] box nails or equivalent on each side of the joint. For the butt-joint splice between adjacent single top plates, not less than the equivalent of a 3-inch by 12-inch (76 mm by 304 mm) by 0.036-inch-thick (0.914 mm) galvanized steel plate that is nailed to each wall or segment of wall by 12 8d [21/2-inch × 0.113-inch (64 mm by 2.87 mm)] box nails on each side of the joint shall be required, provided that the rafters, joists or trusses are centered over the studs with a tolerance of not more than 1 inch (25 mm). The top plate shall not be required over headers that are in the same plane and in line with the upper surface of the adjacent top plates and are tied to adjacent wall sections as required for the butt joint splice between adjacent single top plates. Where bearing studs are spaced at 24-inch (610 mm) intervals, top plates are less than two 2-inch by 6-inch (51 mm by 152 mm) or two 3-inch by 4-inch (76 mm by 102 mm) members and the floor joists, floor trusses or roof trusses that they support are spaced at more than 16-inch (406 mm) intervals, such joists or trusses shall bear within 5 inches (127 mm) of the studs beneath or a third plate shall be installed.
2308.5.4 Nonload-bearing walls and partitions. | In nonload-bearing walls and partitions that are not part of a braced wall panel, studs shall be spaced not more than 24╪ inches (610 mm) on center. In interior nonload-bearing walls and partitions, studs are permitted to be set with the long dimension parallel to the wall. Where studs are set with the long dimensions parallel to the wall, use of utility grade lumber or studs exceeding 10 feet (3048 mm) is not permitted. Interior nonload-bearing partitions shall be capped with not less than a single top plate installed to provide overlapping at corners and at intersections with other walls and partitions. The plate shall be continuously tied at joints by solid blocking not less than 16 inches (406 mm) in length and equal in size to the plate or by ½-inch by 1½-inch (12.7 mm by 38 mm) metal ties with spliced sections fastened with two 16d nails on each side of the joint. | 2308.5.4 Nonload-bearing walls and partitions. | In nonload-bearing walls and partitions, that are not part of a braced wall panel, studs shall be spaced not more than 24 inches (610 mm) on center. In interior nonload-bearing walls and partitions, studs are permitted to be set with the long dimension parallel to the wall. Where studs are set with the long dimensions parallel to the wall, use of utility grade lumber or studs exceeding 10 feet (3048 mm) is not permitted. Interior nonload-bearing partitions shall be capped with not less than a single top plate installed to provide overlapping at corners and at intersections with other walls and partitions. The plate shall be continuously tied at joints by solid blocking not less than 16 inches (406 mm) in length and equal in size to the plate or by 1/2-inch by 11/2-inch (12.7 mm by 38 mm) metal ties with spliced sections fastened with two 16d nails on each side of the joint.
2308.4.10 Anchorage of exterior means of egress components in Seismic Design Category D. | Exterior egress balconies, exterior stairways and ramps and similar means of egress components in structures assigned to Seismic Design Category D shall be positively anchored to the primary structure at not more than 8 feet (2438 mm) on center or shall be designed for lateral forces. Such attachment shall not be accomplished by use of toenails or nails subject to withdrawal.
2308.5.5 Openings in walls and partitions. | Openings in exterior and interior walls and partitions shall comply with Sections 2308.5.5.1 through 2308.5.5.3. | 2308.5.5 Openings in walls and partitions. | Openings in exterior and interior walls and partitions shall comply with Sections 2308.5.5.1 through 2308.5.5.3.
2308.5.5.1 Openings in exterior bearing walls. | Headers shall be provided over each opening in exterior bearing walls. The size and spans in Table 2308.4.1.1(1) are permitted to be used for one- and two-family dwellings. Headers for other buildings shall be designed in accordance with Section 2301.2, Item 1 or 2. Headers shall be of two pieces of nominal 2-inch (51 mm) framing lumber set on edge as permitted by Table 2308.4.1.1(1) and nailed together in accordance with Table 2304.10.1 or of solid lumber of equivalent size. | 2308.5.5.1 Openings in exterior bearing walls. | Headers shall be provided over each opening in exterior bearing walls. The size and spans in Table 2308.4.1.1(1) are permitted to be used for one- and two-family dwellings. Headers for other buildings shall be designed in accordance with Section 2302.1, Item 1 or 2. Headers of two or more pieces of nominal 2-inch (51 mm) framing lumber set on edge shall be permitted in accordance with Table 2308.4.1.1(1) and nailed together in accordance with Table 2304.10.2 or of solid lumber of equivalent size.
2308.5.5.2 Openings in interior bearing partitions. | Headers shall be provided over each opening in interior bearing partitions as required in Section 2308.5.5.1. The spans in Table 2308.4.1.1(2) are permitted to be used. Wall studs shall support the ends of the header in accordance with Table 2308.4.1.1(1) or 2308.4.1.1(2), as applicable. | 2308.5.5.2 Openings in interior bearing partitions. | Headers shall be provided over each opening in interior bearing partitions as required in Section 2308.5.5.1. The spans in Table 2308.4.1.1(2) are permitted to be used. Wall studs shall support the ends of the header in accordance with Table 2308.4.1.1(1) or 2308.4.1.1(2), as applicable.
2308.5.6 Cripple walls. | Foundation cripple walls shall be framed of studs that are not less than the size of the studding above and not less than 14 inches (356 mm) in length, or shall be framed of solid blocking. Where exceeding 4 feet (1219 mm) in height, such walls shall be framed of studs having the size required for an additional story. See Section 2308.6.6 for cripple wall bracing. | 2308.5.6 Cripple walls. | Foundation cripple walls shall be framed of studs that are not less than the size of the studding above. Exterior cripple wall studs shall be not less than 14 inches (356 mm) in length, or shall be framed of solid blocking. Where exceeding 4 feet (1219 mm) in height, such walls shall be framed of studs having the size required for an additional story. See Section 2308.6.6 for cripple wall bracing.
2308.5.7 Bridging. | Unless covered by interior or exterior wall coverings or sheathing meeting the minimum requirements of this code, stud partitions or walls with studs having a height-to-least-thickness ratio exceeding 50 shall have bridging that is not less than 2 inches (51 mm) in thickness and of the same width as the studs fitted snugly and nailed thereto to provide adequate lateral support. Bridging shall be placed in every stud cavity and at a frequency such that no stud so braced shall have a height-to-least-thickness ratio exceeding 50 with the height of the stud measured between horizontal framing and bridging or between bridging, whichever is greater. | 2308.5.7 Bridging. | Unless covered by interior or exterior wall coverings or sheathing meeting the minimum requirements of this code, stud partitions or walls with studs having a height-to-least-thickness ratio exceeding 50 shall have bridging that is not less than 2 inches (51 mm) in thickness and of the same width as the studs fitted snugly and nailed thereto to provide adequate lateral support. Bridging shall be placed in every stud cavity and at a frequency such that studs so braced shall not have a height-to-least-thickness ratio exceeding 50 with the height of the stud measured between horizontal framing and bridging or between bridging, whichever is greater.
2308.5.8 Pipes in walls. | Stud partitions containing plumbing, heating or other pipes shall be framed and the joists underneath spaced to provide proper clearance for the piping. Where a partition containing piping runs parallel to the floor joists, the joists underneath such partitions shall be doubled and spaced to permit the passage of pipes and shall be bridged. Where plumbing, heating or other pipes are placed in, or partly in, a partition, necessitating the cutting of the soles or plates, a metal tie not less than 0.058 inch (1.47 mm) (16 galvanized gage) and 1½ inches (38 mm) in width shall be fastened to each plate across and to each side of the opening a minimum of 6 inches (152 mm) with not less than six 16d nails. See Figure 2308.5.8. | 2308.5.8 Pipes in walls. | Stud partitions containing plumbing, heating or other pipes shall be framed and the joists underneath spaced to provide proper clearance for the piping. Where a partition containing piping runs parallel to the floor joists, the joists underneath such partitions shall be doubled and spaced to permit the passage of pipes and shall be bridged. Where plumbing, heating or other pipes are placed in, or partly in, a partition, necessitating the cutting of the soles or plates, a metal tie not less than 0.058 inch (1.47 mm) (16 galvanized gage) and 11/2 inches (38 mm) in width shall be fastened to each plate across and to each side of the opening with not less than six 16d nails.
2308.5.9 Cutting and notching. | In exterior walls and bearing partitions, wood studs are permitted to be cut or notched to a depth not exceeding 25 percent of the width of the stud. Cutting or notching of studs to a depth not greater than 40 percent of the width of the stud is permitted in nonload-bearing partitions supporting no loads other than the weight of the partition. See Figure 2308.5.8. | 2308.5.9 Cutting and notching. | In exterior walls and bearing partitions, a wood stud shall not be cut or notched in excess of 25 percent of its depth. In nonbearing partitions that do not support loads other than the weight of the partition, a stud shall not be cut or notched in excess of 40 percent of its depth.
2308.5.10 Bored holes. | Bored holes not greater than 40 percent of the stud width are permitted to be bored in any wood stud. Bored holes not greater than 60 percent of the stud width are permitted in nonload-bearing partitions or in any wall where each bored stud is doubled, provided not more than two such successive doubled studs are so bored. In no case shall the edge of a bored hole be nearer than ⅝ | 2308.5.10 Bored holes. | The diameter of bored holes in wood studs shall not exceed 40 percent of the stud depth. The diameter of bored holes in wood studs shall not exceed 60 percent of the stud depth in nonbearing partitions. The diameter of bored holes in wood studs shall not exceed 60 percent of the stud depth in any wall where each stud is doubled, provided that not more than two such successive doubled studs are so bored. The edge of the bored hole shall not be closer than 5/8 inch (15.9 mm) to the edge of the stud. Bored holes shall not be located at the same section of stud as a cut or notch.
2308.5.11 Exterior wall sheathing. | Except where stucco construction that complies with Section 2510 is installed, the outside of exterior walls of enclosed buildings, including gables, shall be sheathed with one of the materials of the minimum thickness specified in Table 2308.5.11. Fasteners shall be used that are designed in accordance with the requirements of Section 2304.10 or accepted engineering practice. Alternatively, sheathing materials and fasteners complying with Section 2304.6 shall be permitted. | 2308.5.11 Exterior wall sheathing. | Except where stucco construction that complies with Section 2510 is installed, the outside of exterior walls, including gables, of enclosed buildings shall be sheathed with one of the materials of the nominal thickness specified in Table 2308.5.11 with fasteners in accordance with the requirements of Section 2304.10 or fasteners designed in accordance with accepted engineering practice. Alternatively, sheathing materials and fasteners complying with Section 2304.6 shall be permitted.
2308.6 Wall bracing. | Buildings shall be provided with exterior and interior braced wall lines as described in Sections 2308.6.1 through 2308.6.10.2. | 2308.6 Wall bracing. | Buildings shall be provided with exterior and interior braced wall lines as described in Sections 2308.6.1 through 2308.6.10.2.
2308.5.5.3 Openings in interior nonload-bearing partitions. | Openings in nonload-bearing partitions are permitted to be framed with single studs and headers. Each end of a lintel or header shall have a bearing length of not less than 1½ inches (38 mm) for the full width of the lintel.
2308.6.1 Braced wall lines. | For the purpose of determining the amount and location of bracing required along each story level of a building, braced wall lines shall be designated as straight lines through the building plan in both the longitudinal and transverse direction and placed in accordance with Table 2308.6.1 and Figure 2308.6.1. Braced wall line spacing shall not exceed the distance specified in Table 2308.6.1. In structures assigned to Seismic Design Category D, braced wall lines shall intersect perpendicularly to each other. | 2308.6.1 Braced wall lines. | For the purpose of determining the amount and location of bracing required along each story level of a building, braced wall lines shall be designated as straight lines through the building plan in both the longitudinal and transverse direction and placed in accordance with Table 2308.6.1 and Figure 2308.6.1. Braced wall line spacing shall not exceed the distance specified in Table 2308.6.1. In structures assigned to Seismic Design Category D or E, braced wall lines shall intersect perpendicularly to each other.
2308.6.2 Braced wall panels. | Braced wall panels shall be placed along braced wall lines in accordance with Table 2308.6.1 and Figure 2308.6.1 and as specified in Table 2308.6.3(1). A braced wall panel shall be located at each end of the braced wall line and at the corners of intersecting braced wall lines or shall begin within the maximum distance from the end of the braced wall line in accordance with Table 2308.6.1. Braced wall panels in a braced wall line shall not be offset from each other by more than 4 feet (1219 mm). Braced wall panels shall be clearly indicated on the plans. | 2308.6.2 Braced wall panels. | Braced wall panels shall be placed along braced wall lines in accordance with Table 2308.6.1 and Figure 2308.6.1 and as specified in Table 2308.6.3(1). A braced wall panel shall be located at each end of the braced wall line and at the corners of intersecting braced wall lines or shall begin within the maximum distance from the end of the braced wall line in accordance with Table 2308.6.1. Braced wall panels in a braced wall line shall not be offset from each other by more than 4 feet (1219 mm). Braced wall panels shall be clearly indicated on the plans.
2308.6.3 Braced wall panel methods. | Construction of braced wall panels shall be by one or a combination of the methods in Table 2308.6.3(1). Braced wall panel length shall be in accordance with Section 2308.6.4 or 2308.6.5. | 2308.6.3 Braced wall panel methods. | Construction of braced wall panels shall be by one or a combination of the methods in Table 2308.6.3(1). Braced wall panel length shall be in accordance with Section 2308.6.4 or 2308.6.5.
2308.6.4 Braced wall panel construction. | For Methods DWB, WSP, SFB, PBS, PCP and HPS, each panel must be not less than 48 inches (1219 mm) in length, covering three stud spaces where studs are spaced 16 inches (406 mm) on center and covering two stud spaces where studs are spaced 24 inches (610 mm) on center. Braced wall panels less than 48 inches (1219 mm) in length shall not contribute toward the amount of required bracing. Braced wall panels that are longer than the required length shall be credited for their actual length. For Method GB, each panel must be not less than 96 inches (2438 mm) in length where applied to one side of the studs or 48 inches (1219 mm) in length where applied to both sides. | 2308.6.4 Braced wall panel construction. | For Methods DWB, WSP, SFB, PBS, PCP and HPS, each panel must be not less than 48 inches (1219 mm) in length, covering three stud spaces where studs are spaced 16 inches (406 mm) on center and covering two stud spaces where studs are spaced 24 inches (610 mm) on center. Braced wall panels less than 48 inches (1219 mm) in length shall not contribute toward the amount of required bracing. Braced wall panels that are longer than the required length shall be credited for their actual length. For Method GB, each panel must be not less than 96 inches (2438 mm) in length where applied to one side of the studs or 48 inches (1219 mm) in length where applied to both sides.
2308.6.5 Alternative bracing. | An alternate braced wall (ABW) or a portal frame with hold-downs (PFH) described in this section is permitted to substitute for a 48-inch (1219 mm) braced wall panel of Method DWB, WSP, SFB, PBS, PCP or HPS. For Method GB, each 96-inch (2438 mm) section (applied to one face) or 48-inch (1219 mm) section (applied to both faces) or portion thereof required by Table 2308.6.1 is permitted to be replaced by one panel constructed in accordance with Method ABW or PFH. | 2308.6.5 Alternative bracing. | An alternate braced wall (ABW) or a portal frame with hold-downs (PFH) described in this section is permitted to substitute for a 48-inch (1219 mm) braced wall panel of Method DWB, WSP, SFB, PBS, PCP or HPS. For Method GB, each 96-inch (2438 mm) section (applied to one face) or 48-inch (1219 mm) section (applied to both faces) or portion thereof required by Table 2308.6.1 is permitted to be replaced by one panel constructed in accordance with Method ABW or PFH.
2308.6.5.1 Alternate braced wall (ABW). | An ABW shall be constructed in accordance with this section and Figure 2308.6.5.1. In one-story buildings, each panel shall have a length of not less than 2 feet 8 inches (813 mm) and a height of not more than 10 feet (3048 mm). Each panel shall be sheathed on one face with ⅜-inch (3.2 mm) minimum-thickness wood structural panel sheathing nailed with 8d common or galvanized box nails in accordance with Table 2304.10.1 and blocked at wood structural panel edges. Two anchor bolts installed in accordance with Section 2308.3.1 shall be provided in each panel. Anchor bolts shall be placed at each panel outside quarter points. Each panel end stud shall have a hold-down device fastened to the foundation, capable of providing an approved allowable uplift capacity of not less than 1,800 pounds (8006 N). The hold-down device shall be installed in accordance with the manufacturer’s recommendations. The ABW shall be supported directly on a foundation or on floor framing supported directly on a foundation that is continuous across the entire length of the braced wall line. This foundation shall be reinforced with not less than one No. 4 bar top and bottom. Where the continuous foundation is required to have a depth greater than 12 inches (305 mm), a minimum 12-inch by 12-inch (305 mm by 305 mm) continuous footing or turned-down slab edge is permitted at door openings in the braced wall line. This continuous footing or turned-down slab edge shall be reinforced with not less than one No. 4 bar top and bottom. This reinforcement shall be lapped 15 inches (381 mm) with the reinforcement required in the continuous foundation located directly under the braced wall line. | 2308.6.5.1 Alternate braced wall (ABW). | An ABW shall be constructed in accordance with this section and Figure 2308.6.5.1. In one-story buildings, each panel shall have a length of not less than 2 feet 8 inches (813 mm) and a height of not more than 10 feet (3048 mm). Each panel shall be sheathed on one face with 3/8-inch (3.2 mm) minimum-thickness wood structural panel sheathing nailed with 8d common or galvanized box nails in accordance with Table 2304.10.2 and blocked at wood structural panel edges. Two anchor bolts installed in accordance with Section 2308.3.1 shall be provided in each panel. Anchor bolts shall be placed at each panel outside quarter points. Each panel end stud shall have a hold-down device fastened to the foundation, capable of providing an approved uplift capacity of not less than 1,800 pounds (8006 N). The hold-down device shall be installed in accordance with the manufacturer’s recommendations. The ABW shall be supported directly on a foundation or on floor framing supported directly on a foundation that is continuous across the entire length of the braced wall line. This foundation shall be reinforced with not less than one No. 4 bar top and bottom. Where the continuous foundation is required to have a depth greater than 12 inches (305 mm), a minimum 12-inch by 12-inch (305 mm by 305 mm) continuous footing or turned-down slab edge is permitted at door openings in the braced wall line. This continuous footing or turned-down slab edge shall be reinforced with not less than one No. 4 bar top and bottom. This reinforcement shall be lapped 15 inches (381 mm) with the reinforcement required in the continuous foundation located directly under the braced wall line.
2308.6.5.2 Portal frame with hold-downs (PFH). | A PFH shall be constructed in accordance with this section and Figure 2308.6.5.2. The adjacent door or window opening shall have a full-length header. | 2308.6.5.2 Portal frame with hold-downs (PFH). | A PFH shall be constructed in accordance with this section and Figure 2308.6.5.2. The adjacent door or window opening shall have a full-length header.
2308.6.6 Cripple wall bracing. | Cripple walls shall be braced in accordance with Section 2308.6.6.1 or 2308.6.6.2. | 2308.6.6 Cripple wall bracing. | Cripple walls shall be braced in accordance with Section 2308.6.6.1 or 2308.6.6.2.
2308.6.6.1 Cripple wall bracing in Seismic Design Categories A, B and C. | For the purposes of this section, cripple walls in Seismic Design Categories A, B and C having a stud height exceeding 14 inches (356 mm) shall be considered a story and shall be braced in accordance with Table 2308.6.1. Spacing of edge nailing for required cripple wall bracing shall not exceed 6 inches (152 mm) on center along the foundation plate and the top plate of the cripple wall. Nail size, nail spacing for field nailing and more restrictive boundary nailing requirements shall be as required elsewhere in the code for the specific bracing material used. | 2308.6.6.1 Cripple wall bracing in Seismic Design Categories A, B and C. | For the purposes of this section, cripple walls in Seismic Design Categories A, B and C having a stud height exceeding 14 inches (356 mm) shall be considered to be a story and shall be braced in accordance with Table 2308.6.1. Spacing of edge nailing for required cripple wall bracing shall not exceed 6 inches (152 mm) on center along the foundation plate and the top plate of the cripple wall. Nail size, nail spacing for field nailing and more restrictive boundary nailing requirements shall be as required elsewhere in the code for the specific bracing material used.
2308.6.7 Connections of braced wall panels. | Braced wall panel joints shall occur over studs or blocking. Braced wall panels shall be fastened to studs, top and bottom plates and at panel edges. Braced wall panels shall be applied to nominal 2-inch-wide (actual 1½-inch (38 mm)) or larger stud framing. | 2308.6.7 Connections of braced wall panels. | Braced wall panel joints shall occur over studs or blocking. Braced wall panels shall be fastened to studs, top and bottom plates and at panel edges. Braced wall panels shall be applied to nominal 2-inch-wide or larger stud framing.
2308.6.7.1 Bottom plate connection. | Braced wall line bottom plates shall be connected to joists or full-depth blocking below in accordance with Table 2304.10.1, or to foundations in accordance with Section 2308.6.7.3. | 2308.6.7.1 Bottom plate connection. | Braced wall line bottom plates shall be connected to joists or full-depth blocking below in accordance with Table 2304.10.2, or to foundations in accordance with Section 2308.6.7.3.
2308.6.7.2 Top plate connection. | Where joists or rafters are used, braced wall line top plates shall be fastened over the full length of the braced wall line to joists, rafters, rim boards or full-depth blocking above in accordance with Table 2304.10.1, as applicable, based on the orientation of the joists or rafters to the braced wall line. Blocking shall be not less than 2 inches (51 mm) in nominal thickness and shall be fastened to the braced wall line top plate as specified in Table 2304.10.1. Notching or drilling of holes in blocking in accordance with the requirements of Section 2308.4.2.4 or 2308.7.4 shall be permitted. At exterior gable end walls, braced wall panel sheathing in the top story shall be extended and fastened to the roof framing where the spacing between parallel exterior braced wall lines is greater than 50 feet (15 240 mm). Where roof trusses are used and are installed perpendicular to an exterior braced wall line, lateral forces shall be transferred from the roof diaphragm to the braced wall over the full length of the braced wall line by blocking of the ends of the trusses or by other approved methods providing equivalent lateral force transfer. Blocking shall be not less than 2 inches (51 mm) in nominal thickness and equal to the depth of the truss at the wall line and shall be fastened to the braced wall line top plate as specified in Table 2304.10.1. Notching or drilling of holes in blocking in accordance with the requirements of Section 2308.4.2.4 or 2308.7.4 shall be permitted. Exception: Where the roof sheathing is greater than 9¼ inches (235 mm) above the top plate, solid blocking is not required where the framing members are connected using one of the following methods: 1. In accordance with Figure 2308.6.7.2(1). 2. In accordance with Figure 2308.6.7.2(2). 3. Full-height engineered blocking panels designed for values listed in AWC WFCM. 4. A design in accordance with accepted engineering methods. | 2308.6.7.2 Top plate connection. | Where joists or rafters are used, braced wall line top plates shall be fastened over the full length of the braced wall line to joists, rafters, rim boards or full-depth blocking above in accordance with Table 2304.10.2, as applicable, based on the orientation of the joists or rafters to the braced wall line. Blocking shall be not less than 2 inches (51 mm) in nominal thickness and shall be fastened to the braced wall line top plate as specified in Table 2304.10.2. Notching or drilling of holes in blocking in accordance with the requirements of Section 2308.4.2.4 or 2308.7.4 shall be permitted. At exterior gable end walls, braced wall panel sheathing in the top story shall be extended and fastened to the roof framing where the spacing between parallel exterior braced wall lines is greater than 50 feet (15 240 mm). Where roof trusses are used and are installed perpendicular to an exterior braced wall line, lateral forces shall be transferred from the roof diaphragm to the braced wall over the full length of the braced wall line by blocking of the ends of the trusses or by other approved methods providing equivalent lateral force transfer. Blocking shall be not less than 2 inches (51 mm) in nominal thickness and equal to the depth of the truss at the wall line and shall be fastened to the braced wall line top plate as specified in Table 2304.10.2. Notching or drilling of holes in blocking in accordance with the requirements of Section 2308.4.2.4 or 2308.7.4 shall be permitted. Exception: Where the roof sheathing is greater than 91/4 inches (235 mm) above the top plate, solid blocking is not required where the framing members are connected using one of the following methods: 1. In accordance with Figure 2308.6.7.2(1). 2. In accordance with Figure 2308.6.7.2(2). 3. Full-height engineered blocking panels designed for values listed in AWC WFCM. 4. A design in accordance with accepted engineering methods.
2308.6.7.3 Sill anchorage. | Where foundations are required by Section 2308.6.8, braced wall line sills shall be anchored to concrete or masonry foundations. Such anchorage shall conform to the requirements of Section 2308.3. The anchors shall be distributed along the length of the braced wall line. Other anchorage devices having equivalent capacity are permitted. | 2308.6.7.3 Sill anchorage. | Where foundations are required by Section 2308.6.8, braced wall line sills shall be anchored to concrete or masonry foundations. Such anchorage shall conform to the requirements of Section 2308.3. The anchors shall be distributed along the length of the braced wall line. Other anchorage devices having equivalent capacity are permitted.
2308.6.7.4 Anchorage to all-wood foundations. | Where all-wood foundations are used, the force transfer from the braced wall lines shall be determined based on calculation and shall have a capacity that is not less than the connections required by Section 2308.3. | 2308.6.7.4 Anchorage to all-wood foundations. | Where all-wood foundations are used, the force transfer from the braced wall lines shall be determined based on calculation and shall have a capacity that is not less than the connections required by Section 2308.3.
2308.6.8 Braced wall line and diaphragm support. | Braced wall lines and floor and roof diaphragms shall be supported in accordance with this section. | 2308.6.8 Braced wall line and diaphragm support. | Braced wall lines and floor and roof diaphragms shall be supported in accordance with this section.
2308.6.8.1 Foundation requirements. | Braced wall lines shall be supported by continuous foundations. Exception: For structures with a maximum plan dimension not more than 50 feet (15 240 mm), continuous foundations are required at exterior walls only. For structures in Seismic Design Category D, exterior braced wall panels shall be in the same plane vertically with the foundation or the portion of the structure containing the offset shall be designed in accordance with accepted engineering practice and Section 2308.1.1. Exceptions: 1. Exterior braced wall panels shall be permitted to be located not more than 4 feet (1219 mm) from the foundation below where supported by a floor constructed in accordance with all of the following: 1.1. Cantilevers or setbacks shall not exceed four times the nominal depth of the floor joists. 1.2. Floor joists shall be 2 inches by 10 inches (51 mm by 254 mm) or larger and spaced not more than 16 inches (406 mm) on center. 1.3. The ratio of the back span to the cantilever shall be not less than 2 to 1. 1.4. Floor joists at ends of braced wall panels shall be doubled. 1.5. A continuous rim joist shall be connected to the ends of cantilevered joists. The rim joist is permitted to be spliced using a metal tie not less than 0.058 inch (1.47 mm) (16 galvanized gage), 1½ inches (38 mm) in width and 12 inches (305 mm) in length, fastened with six 16d common nails on each side. The metal tie shall have a yield stress not less than 33,000 psi (227 MPa). 1.6. Joists at setbacks or the end of cantilevered joists shall not carry gravity loads from more than a single story having uniform wall and roof loads nor carry the reactions from headers having a span of 8 feet (2438 mm) or more. 2. The end of a required braced wall panel shall be allowed to extend not more than 1 foot (305 mm) over an opening in the wall below. This requirement is applicable to braced wall panels offset in plane and braced wall panels offset out of plane as permitted by Exception 1. Braced wall panels are permitted to extend over an opening not more than 8 feet (2438 mm) in width where the header is a 4-inch by 12-inch (102 mm by 305 mm) or larger member. | 2308.6.8.1 Foundation requirements. | Braced wall lines shall be supported by continuous foundations. Exception: For structures with a maximum plan dimension not more than 50 feet (15 240 mm), continuous foundations are required at exterior walls only. For structures in Seismic Design Categories D and E, exterior braced wall panels shall be in the same plane vertically with the foundation or the portion of the structure containing the offset shall be designed in accordance with accepted engineering practice and Section 2308.1.1. Exceptions: 1. Exterior braced wall panels shall be permitted to be located not more than 4 feet (1219 mm) from the foundation below where supported by a floor constructed in accordance with all of the following: 1.1. Cantilevers or setbacks shall not exceed four times the nominal depth of the floor joists. 1.2. Floor joists shall be 2 inches by 10 inches (51 mm by 254 mm) or larger and spaced not more than 16 inches (406 mm) on center. 1.3. The ratio of the back span to the cantilever shall be not less than 2 to 1. 1.4. Floor joists at ends of braced wall panels shall be doubled. 1.5. A continuous rim joist shall be connected to the ends of cantilevered joists. The rim joist is permitted to be spliced using a metal tie not less than 0.058 inch (1.47 mm) (16 galvanized gage) and 11/2 inches (38 mm) in width fastened with six 16d common nails on each side. The metal tie shall have a yield stress not less than 33,000 psi (227 MPa). 1.6. Joists at setbacks or the end of cantilevered joists shall not carry gravity loads from more than a single story having uniform wall and roof loads nor carry the reactions from headers having a span of 8 feet (2438 mm) or more. 2. The end of a required braced wall panel shall be allowed to extend not more than 1 foot (305 mm) over an opening in the wall below. This requirement is applicable to braced wall panels offset in plane and braced wall panels offset out of plane as permitted by Exception 1. Braced wall panels are permitted to extend over an opening not more than 8 feet (2438 mm) in width where the header is a 4-inch by 12-inch (102 mm by 305 mm) or larger member.
2308.6.6.2 Cripple wall bracing in Seismic Design Category D. | For the purposes of this section, cripple walls in Seismic Design Category D having a stud height exceeding 14 inches (356 mm) shall be considered a story and shall be braced in accordance with Table 2308.6.1. Where interior braced wall lines occur without a continuous foundation below, the length of parallel exterior cripple wall bracing shall be one and one-half times the lengths required by Table 2308.6.1. Where the cripple wall sheathing type used is Method WSP or DWB and this additional length of bracing cannot be provided, the capacity of WSP or DWB sheathing shall be increased by reducing the spacing of fasteners along the perimeter of each piece of sheathing to 4 inches (102 mm) on center.
2308.6.9 Attachment of sheathing. | Fastening of braced wall panel sheathing shall be not less than that prescribed in Tables 2308.6.1 and 2304.10.1. Wall sheathing shall not be attached to framing members by adhesives. | 2308.6.9 Attachment of sheathing. | Fastening of braced wall panel sheathing shall be not less than that prescribed in Tables 2308.6.1 and 2304.10.2. Wall sheathing shall not be attached to framing members by adhesives.
2308.6.10 Limitations of concrete or masonry veneer. | Concrete or masonry veneer shall comply with Chapter 14 and this section. | 2308.6.10 Limitations of concrete or masonry veneer. | Concrete or masonry veneer shall comply with Chapter 14 and this section.
2308.7 Roof and ceiling framing. | The framing details required in this section apply to roofs having a slope of not less than three units vertical in 12 units horizontal (25-percent slope). Where the roof slope is less than three units vertical in 12 units horizontal (25-percent slope), members supporting rafters and ceiling joists such as ridge board, hips and valleys shall be designed as beams. | 2308.7 Roof and ceiling framing. | The framing details required in this section apply to roofs having a slope of not less than three units vertical in 12 units horizontal (25-percent slope). Where the roof slope is less than three units vertical in 12 units horizontal (25-percent slope), members supporting rafters and ceiling joists such as ridge board, hips and valleys shall be designed as beams.
2308.7.1 Ceiling joist spans. | Spans for ceiling joists shall be in accordance with Table 2308.7.1(1) or 2308.7.1(2). For other grades and species, and other loading conditions, refer to the AWC STJR. | 2308.7.1 Ceiling joist spans. | Spans for ceiling joists shall be in accordance with Table 2308.7.1(1) or 2308.7.1(2). For other grades and species, and other loading conditions, refer to the AWC STJR.
2308.6.8.2 Floor and roof diaphragm support in Seismic Design Category D. | In structures assigned to Seismic Design Category D, floor and roof diaphragms shall be laterally supported by braced wall lines on all edges and connected in accordance with Section 2308.6.7 (see Figure 2308.6.8.2(1)). Exception: Portions of roofs or floors that do not support braced wall panels above are permitted to extend up to 6 feet (1829 mm) beyond a braced wall line (see Figure 2308.6.8.2(2)) provided that the framing members are connected to the braced wall line below in accordance with Section 2308.6.7.
2308.7.2 Rafter spans. | Spans for rafters shall be in accordance with Table 2308.7.2(1), 2308.7.2(2), 2308.7.2(3), 2308.7.2(4), 2308.7.2(5), or 2308.7.2(6). For other grades and species and other loading conditions, refer to the AWC STJR. The span of each rafter shall be measured along the horizontal projection of the rafter. | 2308.7.2 Rafter spans. | Spans for rafters shall be in accordance with Table 2308.7.2(1), 2308.7.2(2), 2308.7.2(3), 2308.7.2(4), 2308.7.2(5) or 2308.7.2(6). For other grades and species and other loading conditions, refer to the AWC STJR. The span of each rafter shall be measured along the horizontal projection of the rafter.
2308.6.8.3 Stepped footings in Seismic Design Categories B, C and D. | In Seismic Design Categories B, C and D, where the height of a required braced wall panel extending from foundation to floor above varies more than 4 feet (1219 mm), the following construction shall be used:
2308.7.3 Ceiling joist and rafter framing. | Rafters shall be framed directly opposite each other at the ridge. There shall be a ridge board not less than 1-inch (25 mm) nominal thickness at ridges and not less in depth than the cut end of the rafter. At valleys and hips, there shall be a single valley or hip rafter not less than 2-inch (51 mm) nominal thickness and not less in depth than the cut end of the rafter. | 2308.7.3 Ceiling joist and rafter framing. | Rafters shall be framed directly opposite each other at the ridge. There shall be a ridge board not less than 1-inch (25 mm) nominal thickness at ridges and not less in depth than the cut end of the rafter. At valleys and hips, there shall be a single valley or hip rafter not less than 2-inch (51 mm) nominal thickness and not less in depth than the cut end of the rafter.
2308.6.10.1 Limitations of concrete or masonry veneer in Seismic Design Categories B and C. | Exceptions: 1. In structures assigned to Seismic Design Category B, stone and masonry veneer is permitted to be used in the first two stories above grade plane or the first three stories above grade plane where the lowest story has concrete or masonry walls, provided that wood structural panel wall bracing is used and the length of bracing provided is one and one-half times the required length specified in Table 2308.6.1. 2. Stone and masonry veneer is permitted to be used in the first story above grade plane or the first two stories above grade plane where the lowest story has concrete or masonry walls. 3. Stone and masonry veneer is permitted to be used in both stories of buildings with two stories above grade plane, provided the following criteria are met: 3.1. Type of brace in accordance with Section 2308.6.1 shall be WSP and the allowable shear capacity in accordance with Section 2306.3 shall be not less than 350 plf (5108 N/m). 3.2. Braced wall panels in the second story shall be located in accordance with Section 2308.6.1 and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 25 percent of the braced wall line length. Braced wall panels in the first story shall be located in accordance with Section 2308.6.1 and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 45 percent of the braced wall line length. 3.3. Hold-down connectors with an allowable capacity of 2,000 pounds (8896 N) shall be provided at the ends of each braced wall panel for the second story to the first story connection. Hold-down connectors with an allowable capacity of 3,900 pounds (17 347 N) shall be provided at the ends of each braced wall panel for the first story to the foundation connection. In all cases, the hold-down connector force shall be transferred to the foundation. 3.4. Cripple walls shall not be permitted. | 2308.7.3.1 Ceiling joist and rafter connections. | Ceiling joists and rafters shall be nailed to each other and the assembly shall be nailed to the top wall plate in accordance with Tables 2304.10.2 and 2308.7.5. Ceiling joists shall be continuous or securely joined where they meet over interior partitions and be fastened to adjacent rafters in accordance with Tables 2304.10.2 and 2308.7.3.1 to provide a continuous rafter tie across the building where such joists are parallel to the rafters. Ceiling joists shall have a bearing surface of not less than 11/2 inches (38 mm) on the top plate at each end.
2308.6.10.2 Limitations of concrete or masonry in Seismic Design Category D. | In Seismic Design Category D, concrete or masonry walls and stone or masonry veneer shall not extend above a basement. Exception: Stone and masonry veneer is permitted to be used in the first story above grade plane, provided the following criteria are met: 1. Type of brace in accordance with Section 2308.6.1 shall be WSP and the allowable shear capacity in accordance with Section 2306.3 shall be not less than 350 plf (5108 N/m). 2. The braced wall panels in the first story shall be located at each end of the braced wall line and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 45 percent of the braced wall line length. 3. Hold-down connectors shall be provided at the ends of braced walls for the first floor to foundation with an allowable capacity of 2,100 pounds (9341 N). 4. Cripple walls shall not be permitted. | 2308.7.4 Notches and holes. | Notching at the ends of rafters or ceiling joists shall not exceed one-fourth the depth. Notches in the top or bottom of the rafter or ceiling joist shall not exceed one-sixth the depth and shall not be located in the middle one-third of the span, except that a notch not more than one-third of the depth is permitted in the top of the rafter or ceiling joist not further from the face of the support than the depth of the member. Holes bored in rafters or ceiling joists shall not be within 2 inches (51 mm) of the top and bottom and their diameter shall not exceed one-third the depth of the member.
|  | 2308.7.5 Wind uplift. | The roof construction shall have rafter and truss ties to the wall below. Resultant uplift loads shall be transferred to the foundation using a continuous load path. The rafter or truss to wall connection shall comply with Tables 2304.10.2 and 2308.7.5.
|  | 2308.7.6 Framing around openings. | Trimmer and header rafters shall be doubled, or of lumber of equivalent cross section, where the span of the header exceeds 4 feet (1219 mm). The ends of header rafters that are more than 6 feet (1829 mm) in length shall be supported by framing anchors or rafter hangers unless bearing on a beam, partition or wall.
|  | 2308.7.7 Purlins. | Purlins to support roof loads are permitted to be installed to reduce the span of rafters within allowable limits and shall be supported by struts to bearing walls. The maximum span of 2-inch by 4-inch (51 mm by 102 mm) purlins shall be 4 feet (1219 mm). The maximum span of the 2-inch by 6-inch (51 mm by 152 mm) purlin shall be 6 feet (1829 mm), but the purlin shall not be smaller than the supported rafter. Struts shall be not less than 2-inch by 4-inch (51 mm by 102 mm) members. The unbraced length of struts shall not exceed 8 feet (2438 mm) and the slope of the struts shall be not less than 45 degrees (0.79 rad) from the horizontal.
|  | 2308.7.8 Blocking. | Roof rafters and ceiling joists shall be supported laterally to prevent rotation and lateral displacement in accordance with Section 2308.4.6 and connected to braced wall lines in accordance with Section 2308.6.7.2.
|  | 2308.7.9 Engineered wood products. | Prefabricated wood I-joists, structural glued-laminated timber and structural composite lumber shall not be notched or drilled except where permitted by the manufacturer’s recommendations or where the effects of such alterations are specifically considered in the design of the member by a registered design professional.
|  | 2308.8 Design of elements. | Combining of engineered elements or systems and conventionally specified elements or systems shall be permitted subject to the limits of Sections 2308.8.1 and 2308.8.2.
|  | 2308.8.1 Elements exceeding limitations of conventional construction. | Where a building of otherwise conventional construction contains structural elements exceeding the limits of Section 2308.2, these elements and the supporting load path shall be designed in accordance with accepted engineering practice and the provisions of this code.
|  | 2308.8.2 Structural elements or systems not described herein. | Where a building of otherwise conventional construction contains structural elements or systems not described in Section 2308, these elements or systems shall be designed in accordance with accepted engineering practice and the provisions of this code. The extent of such design need only demonstrate compliance of the nonconventional elements with other applicable provisions of this code and shall be compatible with the performance of the conventionally framed system.
|  | 2301.2 Nominal sizes. | For the purposes of this chapter, where dimensions of lumber are specified, they shall be deemed to be nominal dimensions unless specifically designated as actual dimensions (see Section 2304.2).
|  | 2302.1 General. | The design of structural elements or systems, constructed partially or wholly of wood or wood-based products, shall be in accordance with one of the following methods:
|  | 2303.1.4 Structural glued cross-laminated timber. | Cross-laminated timbers shall be manufactured and identified in accordance with ANSI/APA PRG 320.
|  | 2303.2.3 Fire testing of wood structural panels. | Wood structural panels shall be tested with a ripped or cut longitudinal gap of 1/8 inch (3.2 mm).
|  | 2303.2.9 Types I and II construction applications. | See Section 603.1 for limitations on the use of fire-retardant-treated wood in buildings of Type I or II construction.
|  | 2303.3 Hardwood and plywood. | Hardwood and decorative plywood shall be manufactured and identified as required in HPVA HP-1.
|  | 2303.4.1.2 Permanent individual truss member restraint (PITMR) and permanent individual truss member diagonal bracing (PITMDB). | Where the truss design drawings designate the need for permanent individual truss member restraint, it shall be accomplished by one of the following methods:
|  | 2303.4.1.2.1 Trusses installed without a diaphragm. | Trusses installed without a diaphragm on the top or bottom chord shall require a project specific PITMR and PITMDB design prepared by a registered design professional. Exception: Group U occupancies.
|  | 2303.4.7 Truss quality assurance. | Trusses not part of a manufacturing process in accordance with either Section 2303.4.6 or a referenced standard, which provides requirements for quality control done under the supervision of a third-party quality control agency, shall be manufactured in compliance with Sections 1704.2.5 and 1705.5, as applicable.
|  | 2304.9.3.2 Nailing. | The length of nails connecting laminations shall be not less than two and one-half times the net thickness of each lamination. Where decking supports are 48 inches (1219 mm) on center or less, side nails shall be installed not more than 30 inches (762 mm) on center alternating between top and bottom edges, and staggered one-third of the spacing in adjacent laminations. Where supports are spaced more than 48 inches (1219 mm) on center, side nails shall be installed not more than 18 inches (457 mm) on center alternating between top and bottom edges and staggered one-third of the spacing in adjacent laminations. For mechanically laminated decking constructed with laminations of 2-inch (51 mm) nominal thickness, nailing in accordance with Table 2304.9.3.2 shall be permitted. Two side nails shall be installed at each end of butt-jointed pieces.
|  | 2304.10.1 Connection fire-resistance rating. | Fire-resistance ratings for connections in Type IV-A, IV-B, or IV-C construction shall be determined by one of the following:
|  | 2304.10.2 Fastener requirements. | Connections for wood members shall be designed in accordance with the appropriate methodology in Section 2302.1. The number and size of fasteners connecting wood members shall be not less than that set forth in Table 2304.10.2.
|  | 2304.10.3 Sheathing fasteners. | Sheathing nails or other approved sheathing connectors shall be driven so that their head or crown is flush with the surface of the sheathing.
|  | 2304.10.4 Joist hangers and framing anchors. | Connections depending on joist hangers or framing anchors, ties and other mechanical fastenings not otherwise covered are permitted where approved. The vertical load-bearing capacity, torsional moment capacity and deflection characteristics of joist hangers shall be determined in accordance with ASTM D7147.
|  | 2304.10.5 Other fasteners. | Clips, staples, glues and other approved methods of fastening are permitted where approved.
|  | 2304.10.6 Fasteners and connectors in contact with preservative-treated and fire-retardant-treated wood. | Fasteners, including nuts and washers, and connectors in contact with preservative-treated and fire-retardant-treated wood shall be in accordance with Sections 2304.10.6.1 through 2304.10.6.4. The coating weights for zinc-coated fasteners shall be in accordance with ASTM A153. Stainless steel driven fasteners shall be in accordance with the material requirements of ASTM F1667.
|  | 2304.10.6.1 Fasteners and connectors for preservative-treated wood. | Fasteners, including nuts and washers, in contact with preservative-treated wood shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Staples shall be of stainless steel. Fasteners other than nails, staples, timber rivets, wood screws and lag screws shall be permitted to be of mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B695, Class 55 minimum. Connectors that are used in exterior applications and in contact with preservative-treated wood shall have coating types and weights in accordance with the treated wood or connector manufacturer’s recommendations. In the absence of manufacturer’s recommendations, not less than ASTM A653, Type G185 zinc-coated galvanized steel, or equivalent, shall be used. Exception: Plain carbon steel fasteners, including nuts and washers, in SBX/DOT and zinc borate preservative-treated wood in an interior, dry environment shall be permitted.
|  | 2304.10.6.2 Fastenings for wood foundations. | Fastenings, including nuts and washers, for wood foundations shall be as required in AWC PWF.
|  | 2304.10.6.3 Fasteners for fire-retardant-treated wood used in exterior applications or wet or damp locations. | Fasteners, including nuts and washers, for fire-retardant-treated wood used in exterior applications or wet or damp locations shall be of hot-dipped zinc-coated galvanized steel, stainless steel, silicon bronze or copper. Staples shall be of stainless steel. Fasteners other than nails, staples, timber rivets, wood screws and lag screws shall be permitted to be of mechanically deposited zinc-coated steel with coating weights in accordance with ASTM B695, Class 55 minimum.
|  | 2304.10.6.4 Fasteners for fire-retardant-treated wood used in interior applications. | Fasteners, including nuts and washers, for fire-retardant-treated wood used in interior locations shall be in accordance with the manufacturer’s recommendations. In the absence of manufacturer’s recommendations, Section 2304.10.6.3 shall apply.
|  | 2304.10.7 Load path. | Where wall framing members are not continuous from the foundation sill to the roof, the members shall be secured to ensure a continuous load path. Where required, sheet metal clamps, ties or clips shall be formed of galvanized steel or other approved corrosion-resistant material not less than 0.0329-inch (0.836 mm) base metal thickness.
|  | 2304.10.8 Framing requirements. | Wood columns and posts shall be framed to provide full end bearing. Alternatively, column-and-post end connections shall be designed to resist the full compressive loads, neglecting end-bearing capacity. Column-and-post end connections shall be fastened to resist lateral and net induced uplift forces.
|  | 2304.12.1 Locations requiring waterborne preservatives or naturally durable wood. | Wood used above ground in the locations specified in Sections 2304.12.1.1 through 2304.12.1.5 shall be naturally durable wood or preservative-treated wood using waterborne preservatives, in accordance with AWPA U1 for above-ground use.
|  | 2304.12.2.4 Supporting members for permeable floors and roofs. | Wood structural members that support moisture-permeable floors or roofs that are exposed to the weather, such as concrete or masonry slabs, shall be of naturally durable or preservative-treated wood unless separated from such floors or roofs by an impervious moisture barrier. The impervious moisture barrier system protecting the structure supporting floors shall provide positive drainage of water that infiltrates the moisture-permeable floor topping.
|  | 2304.12.2.5 Ventilation beneath balcony or elevated walking surfaces. | Enclosed framing in exterior balconies and elevated walking surfaces that have weather-exposed surfaces shall be provided with openings that provide a net free cross-ventilation area not less than 1/150 of the area of each separate space.
|  | 2304.12.2.6.1 Posts or columns. | Posts and columns that are supporting permanent structures and embedded in concrete that is exposed to the weather or in direct contact with the earth shall be of preservative-treated wood.
|  | 2304.12.2.7 Termite protection. | In geographical areas where hazard of termite damage is known to be very heavy, wood floor framing in the locations specified in Section 2304.12.1.1 and exposed framing of exterior decks or balconies shall be of naturally durable species (termite resistant) or preservative treated in accordance with AWPA U1 for the species, product preservative and end use or provided with approved methods of termite protection.
|  | 2304.12.2.8 Wood used in retaining walls and cribs. | Wood installed in retaining or crib walls shall be preservative treated in accordance with AWPA U1 for soil and fresh water use.
|  | 2304.12.3 Attic ventilation. | For attic ventilation, see Section 1202.2.2.
|  | 2304.12.4 Under-floor ventilation (crawl space). | For under-floor ventilation (crawl space), see Section 1202.4.
|  | 2308.1.2 Connections and fasteners. | Connectors and fasteners used in conventional construction shall comply with the requirements of Section 2304.10.
|  | 2308.2.4 Basic wind speed. | V shall not exceed 130 miles per hour (57 m/s) (3-second gust). Exceptions: 1. V shall not exceed 140 mph (63 m/s) (3-second gust) for buildings in Exposure Category B that are not located in a hurricane-prone region. 2. Where V exceeds 130 mph (3-second gust), the provisions of either AWC WFCM or ICC 600 are permitted to be used.
|  | 2308.3.1.1 Braced wall line sill plate anchorage in Seismic Design Category D. | Sill plates along braced wall lines in buildings assigned to Seismic Design Category D shall be anchored with not less than 1/2-inch (12.7 mm) diameter anchor bolts with steel plate washers between the foundation sill plate and the nut, or approved anchor straps load-rated in accordance with Section 2304.10.4 and spaced to provide equivalent anchorage. Plate washers shall be not less than 0.229 inch by 3 inches by 3 inches (5.82 mm by 76 mm by 76 mm) in size. The hole in the plate washer is permitted to be diagonally slotted with a width of up to 3/16 inch (4.76 mm) larger than the bolt diameter and a slot length not to exceed 13/4 inches (44 mm), provided that a standard cut washer is placed between the plate washer and the nut.
|  | 2308.3.1.2 Braced wall line sill plate anchorage in Seismic Design Category E. | Sill plates along braced wall lines in buildings assigned to Seismic Design Category E shall be anchored with not less than 5/8-inch diameter (15.9 mm) anchor bolts with steel plate washers between the foundation sill plate and the nut, or approved anchor straps load-rated in accordance with Section 2304.10.4 and spaced to provide equivalent anchorage. Plate washers shall be not less than 0.229 inch by 3 inches by 3 inches (5.82 mm by 76 mm by 76 mm) in size. The hole in the plate washer is permitted to be diagonally slotted with a width of up to 3/16 inch (4.76 mm) larger than the bolt diameter and a slot length not to exceed 13/4 inches (44 mm), provided that a standard cut washer is placed between the plate washer and the nut.
|  | 2308.4.4.1 Openings in floor diaphragms in Seismic Design Categories B, C, D and E. | Openings in horizontal diaphragms in Seismic Design Categories B, C, D and E with a dimension that is greater than 4 feet (1219 mm) shall be constructed with metal ties and blocking in accordance with this section and Figure 2308.4.4.1(1). Metal ties shall be not less than 0.058 inch in thickness by 11/2 inches (38 mm) in width and shall have a yield stress not less than 33,000 psi (227 Mpa). Blocking shall extend not less than the dimension of the opening in the direction of the tie and blocking. Ties shall be attached to blocking in accordance with the manufacturer’s instructions but with not less than eight 16d common nails on each side of the header-joist intersection.
|  | 2308.4.4.2 Vertical offsets in floor diaphragms in Seismic Design Categories D and E. | In Seismic Design Categories D and E, portions of a floor level shall not be vertically offset such that the framing members on either side of the offset cannot be lapped or tied together in an approved manner in accordance with Figure 2308.4.4.2 unless the portion of the structure containing the irregular offset is designed in accordance with accepted engineering practice. Exception: Framing supported directly by foundations need not be lapped or tied directly together.
|  | 2308.4.10 Anchorage of exterior means of egress components in Seismic Design Categories D and E. | Exterior egress balconies, exterior stairways and ramps and similar means of egress components in structures assigned to Seismic Design Category D or E shall be positively anchored to the primary structure at not more than 8 feet (2438 mm) on center or shall be designed for lateral forces. Such attachment shall not be accomplished by use of toenails or nails subject to withdrawal.
|  | 2308.5.5.3 Openings in interior nonbearing partitions. | Openings in nonbearing partitions are permitted to be framed with single studs and headers. Each end of a lintel or header shall have a bearing length of not less than 11/2 inches (38 mm) for the full width of the lintel.
|  | 2308.6.6.2 Cripple wall bracing in Seismic Design Categories D and E. | For the purposes of this section, cripple walls in Seismic Design Categories D and E shall not have a stud height exceeding 14 inches (356 mm), and studs shall be solid blocked in accordance with Section 2308.5.6 for the full dwelling perimeter and for the full length of interior braced walls lines supported on foundations, excepting ventilation and access openings.
|  | 2308.6.8.2 Floor and roof diaphragm support in Seismic Design Categories D and E. | In structures assigned to Seismic Design Categories D or E, floor and roof diaphragms shall be laterally supported by braced wall lines on all edges and connected in accordance with Section 2308.6.7 . Exception: Portions of roofs or floors that do not support braced wall panels above are permitted to extend up to 6 feet (1829 mm) beyond a braced wall line [see Figure 2308.6.8.2(2)] provided that the framing members are connected to the braced wall line below in accordance with Section 2308.6.7.
|  | 2308.6.8.3 Stepped footings in Seismic Design Categories B, C, D and E. | In Seismic Design Categories B, C, D and E, where the height of a required braced wall panel extending from foundation to floor above varies more than 4 feet (1219 mm), the following construction shall be used:
|  | 2308.6.10.1 Limitations of concrete or masonry veneer in Seismic Design Category B or C. | In Seismic Design Categories B and C, concrete or masonry walls and stone or masonry veneer shall not extend above a basement. Exceptions: 1. In structures assigned to Seismic Design Category B, stone and masonry veneer is permitted to be used in the first two stories above grade plane or the first three stories above grade plane where the lowest story has concrete or masonry walls, provided that wood structural panel wall bracing is used and the length of bracing provided is one and one-half times the required length specified in Table 2308.6.1. 2. Stone and masonry veneer is permitted to be used in the first story above grade plane or the first two stories above grade plane where the lowest story has concrete or masonry walls. 3. Stone and masonry veneer is permitted to be used in both stories of buildings with two stories above grade plane, provided that the following criteria are met: 3.1. Type of brace in accordance with Section 2308.6.1 shall be WSP and the allowable shear capacity in accordance with Section 2306.3 shall be not less than 350 plf (5108 N/m). 3.2. Braced wall panels in the second story shall be located in accordance with Section 2308.6.1 and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 25 percent of the braced wall line length. Braced wall panels in the first story shall be located in accordance with Section 2308.6.1 and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 45 percent of the braced wall line length. 3.3. Hold-down connectors with an allowable capacity of 2,000 pounds (8896 N) shall be provided at the ends of each braced wall panel for the second story to the first story connection. Hold-down connectors with an allowable capacity of 3,900 pounds (17 347 N) shall be provided at the ends of each braced wall panel for the first story to the foundation connection. In all cases, the hold-down connector force shall be transferred to the foundation. 3.4. Cripple walls shall not be permitted.
|  | 2308.6.10.2 Limitations of concrete or masonry in Seismic Design Categories D and E. | In Seismic Design Categories D and E, concrete or masonry walls and stone or masonry veneer shall not extend above a basement. Exception: In structures assigned to Seismic Design Category D, stone and masonry veneer is permitted to be used in the first story above grade plane, provided that the following criteria are met: 1. Type of brace in accordance with Section 2308.6.1 shall be WSP and the allowable shear capacity in accordance with Section 2306.3 shall be not less than 350 plf (5108 N/m). 2. The braced wall panels in the first story shall be located at each end of the braced wall line and not more than 25 feet (7620 mm) on center, and the total length of braced wall panels shall be not less than 45 percent of the braced wall line length. 3. Hold-down connectors shall be provided at the ends of braced walls for the first floor to foundation with an allowable capacity of 2,100 pounds (9341 N). 4. Cripple walls shall not be permitted. 2308.7 Roof and ceiling framing. The framing details required in this section apply to roofs havin
|  | 2308.7.6.1 Openings in roof diaphragms in Seismic Design Categories B, C, D and E. | In buildings classified as Seismic Design Category B, C, D or E. openings in horizontal diaphragms with a dimension that is greater than 4 feet (1219 mm) shall be constructed with metal ties and blocking in accordance with this section and Figure 2308.4.4.1(1). Metal ties shall be not less than 0.058 inch in thickness by 11/2 inches (38 mm) in width and shall have a yield stress not less than 33,000 psi (227 Mpa). Blocking shall extend not less than the dimension of the opening in the direction of the tie and blocking. Ties shall be attached to blocking in accordance with the manufacturer’s instructions but with not less than eight 16d common nails on each side of the header-joist intersection.
|  | 2308.7.10 Roof sheathing. | Roof sheathing shall be in accordance with Tables 2304.8(3) and 2304.8(5) for wood structural panels, and Tables 2304.8(1) and 2304.8(2) for lumber and shall comply with Section 2304.8.2.
|  | 2308.7.11 Joints. | Joints in lumber sheathing shall occur over supports unless approved end-matched lumber is used, in which case each piece shall bear on not fewer than two supports.
|  | 2308.7.12 Roof planking. | Planking shall be designed in accordance with the general provisions of this code.
|  | 2308.7.13 Wood trusses. | Wood trusses shall be designed in accordance with Section 2303.4. Connection to braced wall lines shall be in accordance with Section 2308.6.7.2.
|  | 2308.7.14 Attic ventilation. | For attic ventilation, see Section 1202.2.1.
|  | 2309.1 Wood Frame Construction Manual. | Structural design in accordance with the AWC WFCM shall be permitted for buildings assigned to Risk Category I or II subject to the limitations of Section 1.1.3 of the AWC WFCM and the load assumptions contained therein. Structural elements beyond these limitations shall be designed in accordance with accepted engineering practice.
|  | 23/4 × 0. | 148
|  | 23/4 × 0. | 131
|  | 23/4 × 0. | 120

## BC24
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2401.1 Scope. | The provisions of this chapter shall govern the materials, design, construction and quality of glass, light-transmitting ceramic and light-transmitting plastic panels for exterior and interior use in both vertical and sloped applications in buildings and structures. | 2401.1 Scope. | The provisions of this chapter shall govern the materials, design, construction and quality of glass, light-transmitting ceramic and light-transmitting plastic panels for exterior and interior use in both vertical and sloped applications in buildings and structures. Light-transmitting plastic glazing shall also meet the applicable requirements of Chapter 26.
2401.2 Glazing replacement. | The installation of replacement glass shall be as required for new installations. See Sections 28-101.4.1, 28-101.4.2, 28-101.4.3 and 28-101.4.4 of the Administrative Code for requirements relating to prior code buildings. Exception: Permit or inspection is not required for certain glazing repair or replacement work as described in Title 1 of the Rules of the City of New York.
2402.1 Definitions. | The following terms are defined in Chapter 2:
2403.1 Identification. | Each pane shall bear the manufacturer’s label designating the type and thickness of the glass or glazing material. The identification shall not be omitted unless approved and an affidavit is furnished by the glazing contractor certifying that each lite is glazed in accordance with approved construction documents that comply with the provisions of this chapter. Safety glazing shall be identified in accordance with Section 2406.3. Each pane of tempered glass shall be permanently identified by the manufacturer. The identification label shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that, once applied, cannot be removed without being destroyed. Exception: Tempered spandrel glass shall be permanently labeled unless doing so would weaken, alter the performance of, or cause breakage of the spandrel glass, as determined by the manufacturer. Where the manufacturer makes such a determination, the tempered spandrel glass shall be provided with a removable paper marking by the manufacturer, and an affidavit shall be provided in accordance with this section. | 2403.1 Identification. | Each pane shall bear the manufacturer’s mark designating the type and thickness of the glass or glazing material. The identification shall not be omitted unless approved and an affidavit is furnished by the glazing contractor certifying that each light is glazed in accordance with approved construction documents that comply with the provisions of this chapter. Safety glazing shall be identified in accordance with Section 2406.3.
2403.2 Glass supports. | Where one or more sides of any pane of glass are not firmly supported, or are subjected to unusual load conditions, or as requested by the applicant, detailed construction documents, detailed shop drawings and analysis or test data ensuring safe performance for the specific installation shall be prepared by a registered design professional. | 2403.2 Glass supports. | Where one or more sides of any pane of glass are not firmly supported, or are subjected to unusual load conditions, detailed construction documents, detailed shop drawings and analysis or test data ensuring safe performance for the specific installation shall be prepared by a registered design professional.
2403.3 Framing. | To be considered firmly supported, the framing members for each individual pane of glass shall be designed so the deflection of the edge of the glass perpendicular to the glass pane shall not exceed 1/175 of the glass edge length or ¾ inch (19.1 mm), whichever is less, when subjected to the larger of the positive or negative load where loads are combined as specified in Section 1605. Gaskets, washers, shims, seals or spacers shall be used where required to prevent contact of glass to metal components in framing and supports. The system shall allow for movement.
2403.4 Interior glazed areas. | Where interior glazing is installed adjacent to a walking surface, the differential deflection of two adjacent unsupported edges shall not be greater than the thickness of the panels when a force of 50 pounds per linear foot (plf) (730 N/m) is applied horizontally to one panel at any point up to 42 inches (1067 mm) above the walking surface. | 2403.4 Interior glazed areas. | Where interior glazing is installed adjacent to a walking surface, the differential deflection of two adjacent unsupported edges shall be not greater than the thickness of the panels when a force of 50 pounds per linear foot (plf) (730 N/m) is applied horizontally to one panel at any point up to 42 inches (1067 mm) above the walking surface.
2403.5 Louvered windows or jalousies. | Float, wired and patterned glass in louvered windows and jalousies shall be no thinner than nominal 3/16 inch (4.8 mm) and no longer than 48 inches (1219 mm). Exposed glass edges shall be smooth. | 2403.5 Louvered windows or jalousies. | Float, wired and patterned glass in louvered windows and jalousies shall be not thinner than nominal 3/16 inch (4.8 mm) and not longer than 48 inches (1219 mm). Exposed glass edges shall be smooth.
2404.1 Vertical glass. | Glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain walls and window walls, doors and other exterior applications shall be designed to resist the wind loads in accordance with Chapter 16 for components and cladding. Glass in glazed curtain walls, glazed storefronts and glazed partitions shall meet the seismic requirements of ASCE 7, Section 13.5.9, as modified by Chapter 16. The load resistance of glass under uniform load shall be determined in accordance with ASTM E 1300. The glass breakage probability for load resistance shall be less than or equal to 8 lites per 1,000. | 2404.1 Vertical glass. | Glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads due to basic design wind speed, V, in Section 1609 for components and cladding. Glass in glazed curtain walls, glazed storefronts and glazed partitions shall meet the seismic requirements of ASCE 7, Section 13.5.9. The load resistance of glass under uniform load shall be determined in accordance with ASTM E1300.
2404.2 Sloped glass. | Glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunrooms, sloped roofs and other exterior applications shall be designed to resist the most critical combinations of loads as determined by Equations 24-2, 24-3 and 24-4. Exception: The performance grade rating of unit skylights and tubular daylighting devices shall be determined in accordance with Section 2405.5. The design of sloped glazing shall be based on Equation 24-5. | 2404.2 Sloped glass. | Glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunrooms, sloped roofs and other exterior applications shall be designed to resist the most critical combinations of loads determined by Equations 24-2, 24-3 and 24-4. Fg = 0.6Wo – D (Equation 24-2) Fg = 0.6Wi + D + 0.5 S (Equation 24-3) Fg = 0.3 Wi + D + S (Equation 24-4) where: D = Glass dead load psf (kN/m2). For glass sloped 30 degrees (0.52 rad) or less from horizontal, = 13 tg (For SI: 0.0245 tg). For glass sloped more than 30 degrees (0.52 rad) from horizontal, = 13 tg cos θ (For SI: 0.0245 tg cos θ). Fg = Total load, psf (kN/m2) on glass. S = Snow load, psf (kN/m2) as determined in Section 1608. tg = Total glass thickness, inches (mm) of glass panes and plies. Wi = Inward wind force, psf (kN/m2) due to basic design wind speed, V, as calculated in Section 1609. Wo = Outward wind force, psf (kN/m2) due to basic design wind speed, V, as calculated in Section 1609. θ = Angle of slope from horizontal. Exception: The performance grade rating of unit skylights and tubular daylighting devices shall be determined in accordance with Section 2405.5. The design of sloped glazing shall be based on Equation 24-5. Fg  Fga (Equation 24-5) where: Fg = Total load on the glass as determined by Equations 24-2, 24-3 and 24-4. Fga = Short duration load resistance of the glass as determined in accordance with ASTM E1300 for Equations 24-2 and 24-3; or the long duration load resistance of the glass as determined in accordance with ASTM E1300 for Equation 24-4.
2404.3 Wired, patterned and sandblasted glass. |  | 2404.3 Wired, patterned and sandblasted glass.
2404.3.1 Vertical wired glass. | Wired glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to the following equation: | 2404.3.1 Vertical wired glass. | Wired glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to the following equation:
2404.3.2 Sloped wired glass. | Wired glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunspaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2. | 2404.3.2 Sloped wired glass. | Wired glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sun-spaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2.
2404.3.3 Vertical patterned glass. | Patterned glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to Equation 24-9. | 2404.3.3 Vertical patterned glass. | Patterned glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to Equation 24-9.
2404.3.4 Sloped patterned glass. | Patterned glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunspaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2. | 2404.3.4 Sloped patterned glass. | Patterned glass sloped more than 15 degrees (0.26 rad) from vertical in skylights, sunspaces, sloped roofs and other exterior applications shall be designed to resist the most critical of the combinations of loads from Section 2404.2.
2404.3.5 Vertical sandblasted glass. | Sandblasted glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors, and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to Equation 24-12. | 2404.3.5 Vertical sandblasted glass. | Sandblasted glass sloped 15 degrees (0.26 rad) or less from vertical in windows, curtain and window walls, doors, and other exterior applications shall be designed to resist the wind loads in Section 1609 for components and cladding according to Equation 24-12.
2404.4 Other designs. | For designs outside the scope of this section, an analysis or test data for the specific installation shall be prepared by a registered design professional. | 2404.4 Other designs. | For designs outside the scope of this section, an analysis or test data for the specific installation shall be prepared by a registered design professional.
2405.1 Scope. | This section applies to the installation of glass and other transparent, translucent or opaque glazing material installed at a slope more than 15 degrees (0.26 rad) from the vertical plane, including glazing materials in skylights, roofs and sloped walls. | 2405.1 Scope. | This section applies to the installation of glass and other transparent, translucent or opaque glazing material installed at a slope of more than 15 degrees (0.26 rad) from the vertical plane, including glazing materials in skylights, roofs and sloped walls.
2405.2 Allowable glazing materials and limitations. | Sloped glazing shall be any of the following materials, subject to the listed limitations. 1. For monolithic glazing systems, the glazing material of the single lite or layer shall be laminated glass with a minimum 30-mil (0.76 mm) polyvinyl butyral (or equivalent) interlayer, wired glass, light-transmitting plastic materials meeting the requirements of Section 2607. 2. For multiple-layer glazing systems, the exterior layer shall be fully tempered glass and the bottom layer shall consist of any of the glazing materials specified in Item 1 above. Annealed glass is permitted to be used as specified in Exceptions 2 and 3 of Section 2405.3. Heat-strengthened glass or fully tempered monolithic glass is permitted to be used with screens, as specified in Section 2405.3. For additional requirements for plastic skylights, see Section 2610. Glass-block construction shall conform to the requirements of Section 2110.1. | 2405.2 Allowable glazing materials and limitations. | Sloped glazing shall be any of the following materials, subject to the listed limitations.
2405.3 Screening. | Where used in monolithic glazing systems, heat-strengthened and fully tempered glass shall have screens installed below the glazing material. The screens and their fastenings shall: (i) be capable of supporting twice the weight of the glazing; (ii) be firmly and substantially fastened to the framing members; and (iii) be installed within 4 inches (102 mm) of the glass. The screens shall be constructed of a noncombustible material not thinner than No. 12 B&S gage (0.0808 inch) with mesh not larger than 1 inch by 1 inch (25 mm by 25 mm). In a corrosive atmosphere, structurally equivalent noncorrosive screen materials shall be used. Heat-strengthened glass, fully tempered glass and wired glass, when used in multiple-layer glazing systems as the bottom glass layer over the walking surface, shall be equipped with screening that conforms to the requirements for monolithic glazing systems. Exception: In monolithic and multiple-layer sloped glazing systems, the following applies: 1. Fully tempered glass installed without protective screens where glazed between intervening floors at a slope of 30 degrees (0.52 rad) or less from the vertical plane shall have the highest point of the glass 10 feet (3048 mm) or less above the walking surface. 2. Screens are not required below any glazing material, including annealed glass, where the walking surface below the glazing material is permanently protected from the risk of falling glass or the area below the glazing material is not a walking surface. 3. Any glazing material, including annealed glass, is permitted to be installed without screens in the sloped glazing systems of commercial or detached noncombustible greenhouses used exclusively for growing plants and not open to the public, provided that the height of the greenhouse at the ridge does not exceed 30 feet (9144 mm) above grade. 4. Screens shall not be required in individual dwelling units in Occupancy Groups R-2 and R-3 where fully tempered glass is used as single glazing or as both panes in an insulating glass unit, and the following conditions are met: 4.1 Each pane of the glass is 16 square feet (1.5 m2) or less in area. 4.2 The highest point of the glass is 12 feet (3658 mm) or less above any walking surface. 4.3 The glass thickness is 3/16 inch (4.8 mm) or less. 5. Screens shall not be required for laminated glass with a 15-mil (0.38 mm) polyvinyl butyral (or equivalent) interlayer used in individual dwelling units in Occupancy Groups R-2 and R-3 within the following limits: 5.1. Each pane of glass is 16 square feet (1.5 m2) or less in area. 5.2. The highest point of the glass is 12 feet (3658 mm) or less above a walking surface. | 2405.3 Screening. | Where used in monolithic glazing systems, annealed, heat-strengthened, fully tempered and wired glass shall have broken glass retention screens installed below the glazing material. The screens and their fastenings shall be: capable of supporting twice the weight of the glazing; firmly and substantially fastened to the framing members; and installed within 4 inches (102 mm) of the glass. The screens shall be constructed of a noncombustible material not thinner than No. 12 B&S gage (0.0808 inch) with mesh not larger than 1 inch by 1 inch (25 mm by 25 mm). In a corrosive atmosphere, structurally equivalent noncorrosive screen materials shall be used. Annealed, heat-strengthened, fully tempered and wired glass, where used in multiple-layer glazing systems as the bottom glass layer over the walking surface, shall be equipped with screening that conforms to the requirements for monolithic glazing systems. Exception: In monolithic and multiple-layer sloped glazing systems, the following applies: 1. Fully tempered glass installed without protective screens where glazed between intervening floors at a slope of 30 degrees (0.52 rad) or less from the vertical plane shall have the highest point of the glass 10 feet (3048 mm) or less above the walking surface. 2. Screens are not required below any glazing material, including annealed glass, where the walking surface below the glazing material is permanently protected from the risk of falling glass or the area below the glazing material is not a walking surface. 3. Any glazing material, including annealed glass, is permitted to be installed without screens in the sloped glazing systems of commercial or detached noncombustible greenhouses used exclusively for growing plants and not open to the public, provided that the height of the greenhouse at the ridge does not exceed 30 feet (9144 mm) above grade. 4. Screens shall not be required in individual dwelling units in Groups R-2, R-3 and R-4 where fully tempered glass is used as single glazing or as both panes in an insulating glass unit, and the following conditions are met: 4.1. Each pane of the glass is 16 square feet (1.5 m2) or less in area. 4.2. The highest point of the glass is 12 feet (3658 mm) or less above any walking surface or other accessible area. 4.3. The glass thickness is 3/16 inch (4.8 mm) or less. 5. Screens shall not be required for laminated glass with a 15-mil (0.38 mm) polyvinyl butyral (or equivalent) interlayer used in individual dwelling units in Groups R-2, R-3 and R-4 within the following limits: 5.1. Each pane of glass is 16 square feet (1.5 m2) or less in area. 5.2. The highest point of the glass is 12 feet (3658 mm) or less above a walking surface or other accessible area.
2405.4 Framing. | In Type I and II construction, sloped glazing and skylight frames shall be constructed of noncombustible materials. In structures where acid fumes deleterious to metal are incidental to the use of the buildings, approved pressure-treated wood or other approved noncorrosive materials are permitted to be used for sash and frames. Framing supporting sloped glazing and skylights shall be designed to resist the tributary roof loads in Chapter 16. Skylights set at an angle of less than 45 degrees (0.79 rad) from the horizontal plane shall be mounted not less than 4 inches (102 mm) above the plane of the roof on a curb constructed as required for the frame. Skylights shall not be installed in the plane of the roof where the roof pitch is less than 45 degrees (0.79 rad) from the horizontal. Exception: Installation of a skylight without a curb shall be permitted on roofs with a minimum slope of 14 degrees (three units vertical in 12 units horizontal) in Group R-3 occupancies. All unit skylights installed in a roof with a pitch flatter than 14 degrees (0.24 rad) shall be mounted not less than 4 inches (102 mm) above the plane of the roof on a curb constructed as required for the frame unless otherwise specified in the manufacturer’s instructions. | 2405.4 Framing. | In Types I and II construction, sloped glazing and skylight frames shall be constructed of noncombustible materials. In structures where acid fumes deleterious to metal are incidental to the use of the buildings, approved pressure-treated wood or other approved noncorrosive materials are permitted to be used for sash and frames. Framing supporting sloped glazing and skylights shall be designed to resist the tributary roof loads in Chapter 16. Skylights set at an angle of less than 45 degrees (0.79 rad) from the horizontal plane shall be mounted not less than 4 inches (102 mm) above the plane of the roof on a curb constructed as required for the frame. Skylights shall not be installed in the plane of the roof where the roof pitch is less than 45 degrees (0.79 rad) from the horizontal. Exception: Installation of a skylight without a curb shall be permitted on roofs with a minimum slope of 14 degrees (three units vertical in 12 units horizontal) in Group R-3 occupancies. Unit skylights installed in a roof with a pitch flatter than 14 degrees (0.25 rad) shall be mounted not less than 4 inches (102 mm) above the plane of the roof on a curb constructed as required for the frame unless otherwise specified in the manufacturer’s installation instructions.
2405.5 Unit skylights and tubular daylighting devices. | Unit skylights and tubular daylighting devices shall be tested and labeled as complying with AAMA/WDMA/CSA 101/I.S.2/A440. The label shall state the name of the manufacturer, the approved agency, the product designation and the performance grade rating as specified in AAMA/WDMA/CSA 101/I.S.2/A440. Where the product manufacturer has chosen to have the performance grade of the skylight rated separately for positive and negative design pressure, then the label shall state both performance grade ratings as specified in AAMA/WDMA/CSA 101/I.S.2/A440 and the skylight shall comply with Section 2405.5.2. Where the skylight is not rated separately for positive and negative pressure, then the performance grade rating shown on the label shall be the performance grade rating determined in accordance with AAMA/WDMA/CSA 101/I.S.2/A440 for both positive and negative design pressure and the skylight shall conform to Section 2405.5.1. | 2405.5 Unit skylights and tubular daylighting devices. | Unit skylights and tubular daylighting devices shall be tested and labeled as complying with AAMA/WDMA/CSA 101/I.S./A440. The label shall state the name of the manufacturer, the approved labeling agency, the product designation and the performance grade rating as specified in AAMA/WDMA/CSA 101/I.S.2/A440. Where the product manufacturer has chosen to have the performance grade of the skylight rated separately for positive and negative design pressure, then the label shall state both performance grade ratings as specified in AAMA/WDMA/CSA 101/I.S.2/A440 and the skylight shall comply with Section 2405.5.2. Where the skylight is not rated separately for positive and negative pressure, then the performance grade rating shown on the label shall be the performance grade rating determined in accordance with AAMA/WDMA/CSA 101/I.S.2/A440 for both positive and negative design pressure and the skylight shall conform to Section 2405.5.1.
2405.5.1 Skylights rated for the same performance grade for both positive and negative design pressure. | The design of skylights shall be based on Equation 24-13. | 2405.5.1 Skylights rated for the same performance grade for both positive and negative design pressure. | The design of skylights shall be based on Equation 24-13.
2405.5.2 Skylights rated for separate performance grades for positive and negative design pressure. | The design of skylights rated for performance grade for both positive and negative design pressures shall be based on Equations 24-14 and 24-15. | 2405.5.2 Skylights rated for separate performance grades for positive and negative design pressure. | The design of skylights rated for performance grade for both positive and negative design pressures shall be based on Equations 24-14 and 24-15.
2406.1 Human impact loads. | Individual glazed areas, including glass mirrors, in hazardous locations as defined in Section 2406.4 shall comply with Sections 2406.1.1 through 2406.1.4. Exception: Mirrors and other glass panels mounted or hung on a surface that provides a continuous backing support. | 2406.1 Human impact loads. | Individual glazed areas, including glass mirrors, in hazardous locations as defined in Section 2406.4 shall comply with Sections 2406.1.1 through 2406.1.4. Exception: Mirrors and other glass panels mounted or hung on a surface that provides a continuous backing support.
2406.1.1 Impact test. | Except as provided in Sections 2406.1.2 through 2406.1.4, all glazing shall pass the impact test requirements of Section 2406.2. | 2406.1.1 Impact test. | Except as provided in Sections 2406.1.2 through 2406.1.4, all glazing shall pass the impact test requirements of Section 2406.2.
2406.1.2 Plastic glazing. | Plastic glazing shall meet the weathering requirements of ANSI Z97.1. | 2406.1.2 Plastic glazing. | Plastic glazing shall meet the weathering requirements of ANSI Z97.1.
2406.1.3 Glass block. | Glass-block walls shall comply with Section 2101.2.5. | 2406.1.3 Glass block. | Glass-block walls shall comply with Section 2110.
2406.1.4 Louvered windows and jalousies. | Louvered windows and jalousies shall comply with Section 2403.5. | 2406.1.4 Louvered windows and jalousies. | Louvered windows and jalousies shall comply with Section 2403.5.
2406.2 Impact test. | Where required by other sections of this code, glazing shall be tested in accordance with CPSC 16 CFR Part 1201. Glazing shall comply with the test criteria for Category II, unless otherwise indicated in Table 2406.2(1). Exception: Glazing not in doors or enclosures for hot tubs, whirlpools, saunas, steam rooms, bathtubs and showers shall be permitted to be tested in accordance with ANSI Z97.1. Glazing shall comply with the test criteria for Class A, unless otherwise indicated in Table 2406.2(2). | 2406.2 Impact test. | Where required by other sections of this code, glazing shall be tested in accordance with CPSC 16 CFR Part 1201. Glazing shall comply with the test criteria for Category II, unless otherwise indicated in Table 2406.2(1). Exception: Glazing not in doors or enclosures for hot tubs, whirlpools, saunas, steam rooms, bathtubs and showers shall be permitted to be tested in accordance with ANSI Z97.1. Glazing shall comply with the test criteria for Class A, unless otherwise indicated in Table 2406.2(2). | See BC24 Tables and Figures
2406.3 Identification of safety glazing. | Except as indicated in Section 2406.3.1, each pane of safety glazing installed in hazardous locations shall be identified by a label specifying the labeler, the manufacturer or installer and the safety glazing standard with which it complies, as well as the information specified in Section 2403.1. A label as defined in Section 202 and meeting the requirements of this section shall be permitted in lieu of the manufacturer’s designation. Exceptions: 1. For other than tempered glass, labels are not required, provided the department approves the use of a certificate, affidavit or other evidence confirming compliance with this code. 2. Tempered spandrel glass shall be identified in accordance with Section 2403.1. | 2406.3 Identification of safety glazing. | Except as indicated in Section 2406.3.1, each pane of safety glazing installed in hazardous locations shall be identified by a manufacturer’s designation specifying who applied the designation, the manufacturer or installer and the safety glazing standard with which it complies, as well as the information specified in Section 2403.1. The designation shall be acid etched, sand blasted, ceramic fired, laser etched, embossed or of a type that once applied, cannot be removed without being destroyed. A label meeting the requirements of this section shall be permitted in lieu of the manufacturer’s designation. Exceptions: 1. For other than tempered glass, manufacturer’s designations are not required, provided that the building official approves the use of a certificate, affidavit or other evidence confirming compliance with this code. 2. Tempered spandrel glass is permitted to be identified by the manufacturer with a removable paper designation.
2406.3.1 Multi-pane assemblies. | Multi-pane glazed assemblies having individual panes not exceeding 1 square foot (0.09 m2) in exposed areas shall have at least one pane in the assembly marked as indicated in Section 2406.3. Other panes in the assembly shall be marked “CPSC 16 CFR Part 1201” or “ANSI Z97.1,” as appropriate.
2406.4 Hazardous locations. | The locations specified in Sections 2406.4.1 through 2406.4.7 shall be considered to be specific hazardous locations requiring safety glazing materials. | 2406.4 Hazardous locations. | The locations specified in Sections 2406.4.1 through 2406.4.7 shall be considered to be specific hazardous locations requiring safety glazing materials.
2406.4.1 Glazing in doors. | Glazing in all fixed and operable panels of swinging, sliding and bifold doors shall be considered a hazardous location. Exceptions: 1. Glazed openings of a size through which a 3-inch diameter (76 mm) sphere is unable to pass. 2. Decorative glazing. 3. Glazing materials used as curved glazed panels in revolving doors. 4. Commercial refrigerated cabinet glazed doors. | 2406.4.1 Glazing in doors. | Glazing in all fixed and operable panels of swinging, sliding and bifold doors shall be considered to be a hazardous location. Exceptions: 1. Glazed openings of a size through which a 3-inch-diameter (76 mm) sphere is unable to pass. 2. Decorative glazing. 3. Glazing materials used as curved glazed panels in revolving doors. 4. Commercial refrigerated cabinet glazed doors.
2406.4.2 Glazing adjacent to doors. | Glazing in an individual fixed or operable panel adjacent to a door where the nearest vertical edge of the glazing is within a 24-inch (610 mm) arc of either vertical edge of the door in a closed position and where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) above the walking surface shall be considered a hazardous location. Exceptions: 1. Decorative glazing. 2. Where there is an intervening wall or other permanent barrier between the door and glazing. 3. Where access through the door is to a closet or storage area 3 feet (914 mm) or less in depth. Glazing in this application shall comply with Section 2406.4.3. 4. Glazing in walls on the latch side of and perpendicular to the plane of the door in a closed position in one- and two-family dwellings or within dwelling units in Group R-2 occupancies. | 2406.4.2 Glazing adjacent to doors. | Glazing in an individual fixed or operable panel adjacent to a door where the nearest vertical edge of the glazing is within a 24-inch (610 mm) arc of either vertical edge of the door in a closed position and where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) above the walking surface shall be considered to be a hazardous location. Exceptions: 1. Decorative glazing. 2. Where there is an intervening wall or other permanent barrier between the door and glazing. 3. Where access through the door is to a closet or storage area 3 feet (914 mm) or less in depth. Glazing in this application shall comply with Section 2406.4.3. 4. Glazing in walls on the latch side of and perpendicular to the plane of the door in a closed position in one- and two-family dwellings or within dwelling units in Group R-2.
2406.4.3 Glazing in windows. | Glazing in an individual fixed or operable panel that meets all of the following conditions shall be considered to be a hazardous location: 1. The exposed area of an individual pane is greater than 9 square feet (0.84 m2). 2. The bottom edge of the glazing is less than 18 inches (457 mm) above the floor. 3. The top edge of the glazing is greater than 36 inches (914 mm) above the floor. 4. One or more walking surface(s) are within 36 inches (914 mm), measured horizontally and in a straight line, of the plane of the glazing. Exceptions: 1. Decorative glazing. 2. Where a horizontal rail is installed on the accessible side(s) of the glazing 34 to 38 inches (864 to 965 mm) above the walking surface. The rail shall be capable of withstanding a horizontal load of 50 pounds per linear foot (730 N/m) without contacting the glass and be not less than 1½ inches (38 mm) in cross-sectional height. 3. Outboard panes in insulating glass units or multiple glazing where the bottom exposed edge of the glass is 25 feet (7620 mm) or more above any grade, roof, walking surface or other horizontal or sloped (within 45 degrees of horizontal) (0.79 rad) surface adjacent to the glass exterior. | 2406.4.3 Glazing in windows. | Glazing in an individual fixed or operable panel that meets all of the following conditions shall be considered to be a hazardous location: 1. The exposed area of an individual pane is greater than 9 square feet (0.84 m2). 2. The bottom edge of the glazing is less than 18 inches (457 mm) above the floor. 3. The top edge of the glazing is greater than 36 inches (914 mm) above the floor. 4. One or more walking surface(s) are within 36 inches (914 mm), measured horizontally and in a straight line, of the plane of the glazing. Exceptions: 1. Decorative glazing. 2. Where a horizontal rail is installed on the accessible side(s) of the glazing 34 to 38 inches (864 to 965 mm) above the walking surface. The rail shall be capable of withstanding a horizontal load of 50 pounds per linear foot (730 N/m) without contacting the glass and be not less than 11/2 inches (38 mm) in cross-sectional height. 3. Outboard panes in insulating glass units or multiple glazing where the bottom exposed edge of the glass is 25 feet (7620 mm) or more above any grade, roof, walking surface or other horizontal or sloped (within 45 degrees of horizontal) (0.79 rad) surface adjacent to the glass exterior.
2406.4.4 Glazing in guards and railings. | Glazing in guards and railings, including structural baluster panels and nonstructural in-fill panels, regardless of area or height above a walking surface, shall be considered to be a hazardous location. | 2406.4.4 Glazing in guards and railings. | Glazing in guards and railings, including structural baluster panels and nonstructural in-fill panels, regardless of area or height above a walking surface shall be considered to be a hazardous location.
2406.4.5 Glazing and wet surfaces. | Glazing in walls, enclosures or fences containing or facing hot tubs, spas, whirlpools, saunas, steam rooms, bathtubs, showers and indoor or outdoor swimming pools where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) measured vertically above any standing or walking surface shall be considered a hazardous location. This shall apply to single glazing and all panes in multiple glazing. Exception: Glazing that is more than 60 inches (1524 mm), measured horizontally and in a straight line, from the water’s edge of a bathtub, hot tub, spa, whirlpool or swimming pool. | 2406.4.5 Glazing and wet surfaces. | Glazing in walls, enclosures or fences containing or facing hot tubs, spas, whirlpools, saunas, steam rooms, bathtubs, showers and indoor or outdoor swimming pools where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) measured vertically above any standing or walking surface shall be considered to be a hazardous location. This shall apply to single glazing and all panes in multiple glazing. Exception: Glazing that is more than 60 inches (1524 mm), measured horizontally and in a straight line, from the water’s edge of a bathtub, hot tub, spa, whirlpool or swimming pool.
2406.4.6 Glazing adjacent to stairways and ramps. | Glazing where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) above the plane of the adjacent walking surface of stairways, landings between flights of stairs and ramps shall be considered a hazardous location. Exceptions: 1. The side of a stairway, landing or ramp that has a guard complying with the provisions of Sections 1015 and 1607.8, and the plane of the glass is greater than 18 inches (457 mm) from the railing. 2. Glazing 36 inches (914 mm) or more measured horizontally from the walking surface. | 2406.4.6 Glazing adjacent to stairways and ramps. | Glazing where the bottom exposed edge of the glazing is less than 60 inches (1524 mm) above the plane of the adjacent walking surface of stairways, landings between flights of stairs and ramps shall be considered to be a hazardous location. Exceptions: 1. The side of a stairway, landing or ramp that has a guard complying with the provisions of Sections 1015 and 1607.9, and the plane of the glass is greater than 18 inches (457 mm) from the railing. 2. Glazing 36 inches (914 mm) or more measured horizontally from the walking surface.
2406.4.7 Glazing adjacent to the bottom stairway landing. | Glazing adjacent to the landing at the bottom of a stairway where the glazing is less than 60 inches (1524 mm) above the landing and within a 60-inch (1524 mm) horizontal arc that is less than 180 degrees (3.14 rad) from the bottom tread nosing shall be considered a hazardous location. Exception: Glazing that is protected by a guard complying with Sections 1015 and 1607.8 where the plane of the glass is greater than 18 inches (457 mm) from the guard. | 2406.4.7 Glazing adjacent to the bottom stairway landing. | Glazing adjacent to the landing at the bottom of a stairway where the glazing is less than 60 inches (1524 mm) above the landing and within a 60-inch (1524 mm) horizontal arc that is less than 180 degrees (3.14 rad) from the bottom tread nosing shall be considered to be a hazardous location. Exception: Glazing that is protected by a guard complying with Sections 1015 and 1607.9 where the plane of the glass is greater than 18 inches (457 mm) from the guard.
2406.5 Fire department access panels. | Fire department glass access panels shall be of nonlaminated tempered glass. For insulating glass units, all panes shall be nonlaminated tempered glass. Exception: Fire department access panels that are openable and meeting size requirements of Section 903.2.11.1. | 2406.5 Fire department access panels. | Fire department glass access panels shall be of tempered glass. For insulating glass units, all panes shall be tempered glass.
2407.1 Materials. | Glass used as structural balustrade panels and in-fill panels in railings shall be laminated glass constructed of fully tempered or heat-strengthened glass and shall comply with Category II or CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1. For all glazing types, the minimum nominal thickness shall be ¼ inch (6.4 mm). Exception: For Group R-3 occupancies, single fully tempered glass complying with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1 shall be permitted to be used in handrails and guardrails where there is no walking surface beneath them or the walking surface is permanently protected from the risk of falling glass. | 2407.1 Materials. | Glass used in a handrail or a guard shall be laminated glass constructed of fully tempered or heat-strengthened glass and shall comply with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1. Glazing in a handrail or a guard shall be of an approved safety glazing material that conforms to the provisions of Section 2406.1.1. For all glazing types, the minimum nominal thickness shall be 1/4 inch (6.4 mm). Exception: Single fully tempered glass complying with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1 shall be permitted to be used in handrails and guards where there is no walking surface beneath them or the walking surface is permanently protected from the risk of falling glass.
2407.1.1 Loads. | The panels and their support system shall be designed to withstand the loads specified in Section 1607.8. ╪ Glass guard elements shall be designed using a factor of safety of four. | 2407.1.1 Loads. | Glass handrails and guards and their support systems shall be designed to withstand the loads specified in Section 1607.9. Glass handrails and guards shall be designed using a factor of safety of four.
2407.1.2 Support and framing. | Support and framing of glass used in handrails and guards shall comply with the requirements of Sections 2403.2 and 2403.3. In glass structural balustrade systems, each handrail or guard section shall be supported by no fewer than three glass balusters or shall be otherwise supported to remain in place should one baluster panel fail. Glass balusters shall not be installed without an attached handrail or guard. Exception: An attached top rail or handrail is not required when panels are tested to remain in place as a barrier following impact or glass breakage in accordance with ASTM E2353, and designed to withstand the loads specified in Section 1607.8.
2407.1.3 Parking garages. | Glazing materials shall not be installed in handrails or guards in parking garages except for pedestrian areas not exposed to impact from vehicles. | 2407.1.3 Parking garages. | Glazing materials shall not be installed in handrails or guards in parking garages except for pedestrian areas not exposed to impact from vehicles.
2407.1.4 Glazing in wind-borne debris regions. | Glazing installed in in-fill panels or balusters in wind-borne debris regions shall comply with the following:
2408.1 General. | Glazing in athletic facilities and similar uses subject to impact loads, which forms whole or partial wall sections or which is used as a door or part of a door, shall comply with this section. | 2408.1 General. | Glazing in athletic facilities and similar uses subject to impact loads, which forms whole or partial wall sections or which is used as a door or part of a door, shall comply with this section.
2407.1.4.1 Balusters and in-fill panels. | Glass installed in exterior railing in-fill panels or balusters shall be laminated glass complying with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1.
2408.2 Racquetball and squash courts. | Glazing in racquetball, squash courts and similar athletic facilities subject to impact loads shall comply with this section. | 2408.2 Racquetball and squash courts.
2407.1.4.2 Glass supporting top rail. | When the top rail is supported by glass, the assembly shall be tested according to the impact requirements of Section 1609.1.2. The top rail shall remain in place after impact.
2408.2.1 Testing. | Test methods and loads for individual glazed areas in racquetball and squash courts subject to impact loads shall conform to those of CPSC 16 CFR Part 1201 or ANSI Z97.1, with impacts being applied at a height of 59 inches (1499 mm) above the playing surface to an actual or simulated glass wall installation with fixtures, fittings and methods of assembly identical to those used in practice. | 2408.2.1 Testing. | Test methods and loads for individual glazed areas in racquetball and squash courts subject to impact loads shall conform to those of CPSC 16 CFR Part 1201 or ANSI Z97.1 with impacts being applied at a height of 59 inches (1499 mm) above the playing surface to an actual or simulated glass wall installation with fixtures, fittings and methods of assembly identical to those used in practice.
2408.3 Gymnasiums and basketball courts. | Glazing in multipurpose gymnasiums, basketball courts and similar athletic facilities subject to human impact loads shall comply with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1. | 2408.3 Gymnasiums and basketball courts. | Glazing in multipurpose gymnasiums, basketball courts and similar athletic facilities subject to human impact loads shall comply with Category II of CPSC 16 CFR Part 1201 or Class A of ANSI Z97.1.
2409.1 Glass walkways. | Glass installed as floors, landings, stairs and in similar locations shall be designed and engineered by a registered design professional and the design shall include the applicable provisions of ASTM E 2751 and the load requirements of Chapter 16. Such assemblies shall comply with the fire-resistance rating and marking requirements of this code where applicable. | 2409.1 Glass walkways. | Glass installed as a part of a floor/ceiling assembly as a walking surface and constructed with laminated glass shall comply with ASTM E2751 or with the load requirements specified in Chapter 16. Such assemblies shall comply with the fire-resistance rating and marking requirements of this code where applicable.
2409.2 Glass in elevator hoistway enclosures. | Glass in elevator hoistway enclosures and hoistway doors shall be laminated glass conforming to ANSI Z97.1 or CPSC 16 CFR Part 1201 and ASME A17.1, as modified by Appendix K of this code. | 2409.2 Glass in elevator hoistway enclosures. | Glass in elevator hoistway enclosures and hoistway doors shall be laminated glass conforming to ANSI Z97.1 or CPSC 16 CFR Part 1201.
2409.2.1 Fire-resistance-rated hoistways. | Glass installed in hoistways and hoistway doors where the hoistway is required to have a fire-resistance rating shall also comply with Section 716. | 2409.2.1 Fire-resistance-rated hoistways. | Glass installed in hoistways and hoistway doors where the hoistway is required to have a fire-resistance rating shall comply with Section 716.
2409.3 Visions panels in elevator hoistway doors. | Glass in vision panels in elevator hoistway doors shall be permitted to be any transparent glazing material not less than ¼ inch (6.4 mm) in thickness conforming to Class A in accordance with ANSI Z97.1 or Category II in accordance with CPSC 16 CFR Part 1201. Glass in vision panels in elevator hoistway doors shall also comply with ASME A17.1, Section 2.11.7, as modified by Appendix K of this code for additional requirements. | 2409.3 Visions panels in elevator hoistway doors. | Glass in vision panels in elevator hoistway doors shall be permitted to be any transparent glazing material not less than 1/4 inch (6.4 mm) in thickness conforming to Class A in accordance with ANSI Z97.1 or Category II in accordance with CPSC 16 CFR Part 1201. The area of any single vision panel shall be not less than 24 square inches (15 484 mm2) and the total area of one or more vision panels in any hoistway door shall be not more than 85 square inches (54 839 mm2).
2409.4╪ Glass in elevator cars. | Glass in elevator cars shall be in accordance with ASME A17.1 section 2.14.1.8, as modified by Appendix K.
2409.4.1╪ Glass types. | Glass in elevator car enclosures, glass elevator car doors and glass used for lining walls and ceilings of elevator cars shall be laminated glass conforming to Class A in accordance with ANSI Z97.1 or Category II in accordance with CPSC 16 CFR Part 1201. See ASME A17.1, as modified by Appendix K of this code for additional requirements.
2410.1 Requirement. | Transparent doors and fixed adjacent sidelites shall be marked in accordance with Sections 2410.3 through 2410.4. Exceptions: 1. One- and two-family dwellings. 2. Fixed adjacent transparent sidelites 20 inches (508 mm) or less in width with opaque stiles at least 1¾ inches (44 mm) in width. 3. Where the ground, floor or equivalent surface area in the path of approach to a fixed adjacent transparent sidelite from either side for a minimum distance of 3 feet (914 mm) from such sidelite is so arranged, constructed or designed as to deter persons from approaching such or a permanent barrier is installed in the path of approach, provided that: 3.1. Decorative pools, horticultural planting or similar installations shall be considered as indicating that the ground, floor or equivalent surface area is not a path of approach. 3.2. Planters, benches and similar barriers which are securely fastened to the floor or wall to prevent their removal shall be considered as blocking the path of approach provided they shall be not less than 18 inches (457 mm) in height from the ground, floor or equivalent surface and extend across at least 2/3 of the total width of the glazed area of the sidelight. 4. Fixed adjacent transparent sidelites which are supported by opaque sill and wall construction of at least 18 inches (457 mm) above the ground, floor or equivalent surface immediately adjacent. 5. Display windows in any establishment, building or structure which fall within the definition of a sidelite if the top of the supporting sill and wall construction is not less than 18 inches (457 mm) above the ground, floor or equivalent surface immediately adjacent and the interior area is occupied with merchandise or similar displays to clearly indicate to the public that it is not a means of ingress or egress. 6. Opaque door pulls or push bars extending across at least two-thirds of the total width of the glazed area.
2410.2 Locations. | Transparent doors and fixed adjacent transparent sidelites shall be marked in two areas on the glass surface. One such area shall be located at least 30 inches (762 mm) but not more than 36 inches (914 mm) above the ground, floor or equivalent surface below the door or sidelite, and the other at least 60 inches (1524 mm) but not more than 66 inches (1676 mm) above the ground, floor or equivalent surface below the door or sidelite. Exception: The use of horizontal separation bars, muntin bars or other equivalent bars at least one and 1½ inches (38 mm) in vertical dimension that extend across the total width of the glazed area and are located at least 40 inches (1016 mm) but not more than 50 inches (1270 mm) above the bottom of the door or sidelite is permitted in lieu of markings.
2410.3 Design. | The marking design shall be at least 4 inches (102 mm) in diameter if circular or 4 inches (102 mm) in its least dimension if elliptical or polygonal, or shall be at least 12 inches (305 mm) in horizontal dimension if the marking is less than 4 inches (102 mm) in its least dimension. In no event shall the vertical dimension of any marking including lettering be less than 1½ inches (38 mm) in height.
2410.4 Materials. | Markings may be comprised of, but are not limited to:
|  | 2402.1 General. | The installation of replacement glass shall be as required for new installations.
|  | 2403.3 Glass framing. | To be considered firmly supported, the framing members for each individual pane of glass shall be designed so that the deflection of the edge of the glass perpendicular to the glass pane does not exceed 1/175 of the glass edge length where the glass edge length is not more than 13 feet 6 inches (4115 mm), or 1/240 of the glass edge length + 1/4 inch (6.4 mm) where the glass edge length is greater than 13 feet 6 inches (4115 mm), when subjected to the larger of the positive or negative load where loads are combined as specified in Section 1605.
|  | 2406.3.1 Multipane assemblies. | Multipane glazed assemblies having individual panes not exceeding 1 square foot (0.09 m2) in exposed areas shall have one pane or more in the assembly marked as indicated in Section 2406.3. Other panes in the assembly shall be marked “CPSC 16 CFR Part 1201” or “ANSI Z97.1,” as appropriate.
|  | 2407.1.2 Guards with structural glass balusters. | Guards with structural glass balusters, whether vertical posts, columns or panels, shall be installed with an attached top rail or handrail. The top rail or handrail shall be supported by not fewer than three glass balusters, or shall be otherwise supported to remain in place should one glass baluster fail. Exception: An attached top rail or handrail is not required where the glass baluster panels are laminated glass with two or more glass plies of equal thickness and of the same glass type. The balusters shall be tested to remain in place as a barrier following impact or glass breakage in accordance with ASTM E2353.
|  | 2407.1.4 Glazing in windborne debris regions. | Glazing installed in exterior handrails or guards in windborne debris regions shall be laminated glass complying with Category II of CPSC 16 CFR 1201 or Class A of ANSI Z97.1. Where the top rail is supported by glass, the assembly shall be tested according to the impact requirements of Section 1609.2 and the top rail shall remain in place after impact.
|  | 2409.2.2 Glass hoistway doors. | The glass in glass hoistway doors shall be not less than 60 percent of the total visible door panel surface area as seen from the landing side.
|  | 2409.4 Glass in elevator cars. | Glass in elevator cars shall be in accordance with this section.
|  | 2409.4.1 Glass types. | Glass in elevator car enclosures, glass elevator car doors and glass used for lining walls and ceilings of elevator cars shall be laminated glass conforming to Class A in accordance with ANSI Z97.1 or Category II in accordance with CPSC 16 CFR Part 1201. Exception: Tempered glass shall be permitted to be used for lining walls and ceilings of elevator cars provided that: 1. The glass is bonded to a nonpolymeric coating, sheeting or film backing having a physical integrity to hold the fragments when the glass breaks. 2. The glass is not subjected to further treatment such as sandblasting; etching; heat treatment or painting that could alter the original properties of the glass. 3. The glass is tested to the acceptance criteria for laminated glass as specified for Class A in accordance with ANSI Z97.l or Category II in accordance with CPSC 16 CFR Part 1201.
|  | 2409.4.2 Surface area. | The glass in glass elevator car doors shall be not less than 60 percent of the total visible door panel surface area as seen from the car side of the doors.

## BC25
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2501.1 Scope. | Provisions of this chapter shall govern the materials, design, construction and quality of gypsum board, gypsum panel products, lath, gypsum plaster, cement plaster, cement board and reinforced gypsum concrete. | 2501.1 Scope. | Provisions of this chapter shall govern the materials, design, construction and quality of gypsum board, gypsum panel products, lath, gypsum plaster, cement plaster and reinforced gypsum concrete.
|  | 2501.2 Other materials. | Other approved wall or ceiling coverings shall be permitted to be installed in accordance with the recommendations of the manufacturer and the conditions of approval.
|  | 2502.1 General. | Lathing, plastering and gypsum board and gypsum panel product construction shall be done in the manner and with the materials specified in this chapter and, where required for fire protection, shall comply with the provisions of Chapter 7.
|  | 2503.1 Inspection. | Lath, gypsum board and gypsum panel products shall be inspected in accordance with Section 110.3.6.
2504.1 Scope. | The following requirements shall be met where construction involves gypsum board, gypsum panel products or lath and plaster in vertical and horizontal assemblies. | 2504.1 Scope. | The following requirements shall be met where construction involves gypsum board, gypsum panel products or lath and plaster in vertical and horizontal assemblies.
2504.1.1 Wood framing. | Wood supports for lath, gypsum board or gypsum panel products, as well as wood stripping or furring, shall be not less than 2 inches (51 mm) nominal thickness in the least dimension. Exception: The minimum nominal dimension of wood furring strips installed over solid backing shall be not less than 1 inch by 2 inches (25 mm by 51 mm). | 2504.1.1 Wood framing. | Wood supports for lath, gypsum board or gypsum panel products, as well as wood stripping or furring, shall be not less than 2 inches (51 mm) nominal thickness in the least dimension. Exception: The minimum nominal dimension of wood furring strips installed over solid backing shall be not less than 1 inch by 2 inches (25 mm by 51 mm).
2504.1.2 Studless partitions. | The minimum thickness of vertically erected studless solid plaster partitions of ⅜-inch (9.5 mm) and ¾-inch (19.1 mm) rib metal lath, ½-inch-thick (12.7 mm) gypsum lath, gypsum board or gypsum panel product shall be 2 inches (51 mm). | 2504.1.2 Studless partitions. | The minimum thickness of vertically erected studless solid plaster partitions of 3/8-inch (9.5 mm) and 3/4-inch (19.1 mm) rib metal lath, 1/2-inch-thick (12.7 mm) gypsum lath, gypsum board or gypsum panel product shall be 2 inches (51 mm).
2505.1 Resistance to shear (wood framing). | Wood-frame shear walls sheathed with gypsum board, gypsum panel products or lath and plaster shall be designed and constructed in accordance with Section 2306.3 and are permitted to resist wind and seismic loads. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7. | 2505.1 Resistance to shear (wood framing). | Wood-frame shear walls sheathed with gypsum board, gypsum panel products or lath and plaster shall be designed and constructed in accordance with Section 2306.3 and are permitted to resist wind and seismic loads. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7.
2505.2 Resistance to shear (steel framing). | Cold-formed steel-frame shear walls sheathed with gypsum board or gypsum panel products and constructed in accordance with the materials and provisions of Section 2211.1.1 are permitted to resist wind and seismic loads. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7. | 2505.2 Resistance to shear (steel framing). | Cold-formed steel-frame shear walls sheathed with gypsum board or gypsum panel products and constructed in accordance with the materials and provisions of Section 2211.1.1 are permitted to resist wind and seismic loads. Walls resisting seismic loads shall be subject to the limitations in Section 12.2.1 of ASCE 7.
2506.1 General. | Gypsum board, gypsum panel products and accessories shall be identified by the manufacturer’s designation to indicate compliance with the appropriate standards referenced in this section and stored to protect such materials from the weather. | 2506.1 General. | Gypsum board, gypsum panel products and accessories shall be identified by the manufacturer’s designation to indicate compliance with the appropriate standards referenced in this section and stored to protect such materials from the weather.
2506.2 Standards. | Gypsum board and gypsum panel products shall conform to the appropriate standards listed in Table 2506.2 and Chapter 35 and, where required for fire protection, shall conform to the provisions of Chapter 7. | 2506.2 Standards. | Gypsum board and gypsum panel products shall conform to the appropriate standards listed in Table 2506.2 and Chapter 35 and, where required for fire protection, shall conform to the provisions of Chapter 7. | See BC25 Tables and Figures
2506.2.1 Other materials. | Metal suspension systems for acoustical and lay-in panel ceilings shall conform with Section 808.1. | 2506.2.1 Other materials. | Metal suspension systems for acoustical and lay-in panel ceilings shall comply with ASTM C635 listed in Chapter 35 and Section 13.5.6 of ASCE 7 for installation in high seismic areas.
2507.1 General. | Lathing and plastering materials and accessories shall be marked by the manufacturer’s designation to indicate compliance with the appropriate standards referenced in this section and stored in such a manner to protect them from the weather. | 2507.1 General. | Lathing and plastering materials and accessories shall be marked by the manufacturer’s designation to indicate compliance with the appropriate standards referenced in this section and stored in such a manner to protect them from the weather.
2507.2 Standards. | Lathing and plastering materials shall conform to the standards listed in Table 2507.2 and Chapter 35 and, where required for fire protection, shall also conform to the provisions of Chapter 7. | 2507.2 Standards. | Lathing and plastering materials shall conform to the standards listed in Table 2507.2 and Chapter 35 and, where required for fire protection, shall conform to the provisions of Chapter 7. | See BC25 Tables and Figures
2508.1 General. | Gypsum board, gypsum panel products and gypsum plaster construction shall be of the materials listed in Tables 2506.2 and 2507.2. These materials shall be assembled and installed in compliance with the appropriate standards listed in Tables 2508.1 and 2511.1.1, and Chapter 35. | 2508.1 General. | Gypsum board, gypsum panel products and gypsum plaster construction shall be of the materials listed in Tables 2506.2 and 2507.2. These materials shall be assembled and installed in compliance with the appropriate standards listed in Tables 2508.1 and 2511.1.1 and Chapter 35. | See BC25 Tables and Figures
2508.2 Limitations. | Gypsum wallboard or gypsum plaster shall not be used in any exterior surface where such gypsum construction will be exposed directly to the weather. Gypsum wallboard shall not be used where there will be direct exposure to water or continuous high humidity conditions beyond the published recommendations of the manufacturer. Gypsum sheathing shall be installed on exterior surfaces in accordance with ASTM C 1280. | 2508.2 Limitations. | Gypsum wallboard or gypsum plaster shall not be used in any exterior surface where such gypsum construction will be exposed directly to the weather. Gypsum wallboard shall not be used where there will be direct exposure to water or continuous high humidity conditions. Gypsum sheathing shall be installed on exterior surfaces in accordance with ASTM C1280.
2508.2.1 Weather protection. | Gypsum wallboard, gypsum lath or gypsum plaster shall not be installed until weather protection for the installation is provided. | 2508.2.1 Weather protection. | Gypsum wallboard, gypsum lath or gypsum plaster shall not be installed until weather protection for the installation is provided.
2508.3 Single-ply application. | Edges and ends of gypsum board and gypsum panel products shall occur on the framing members, except those edges and ends that are perpendicular to the framing members. Edges and ends of gypsum board and gypsum panel products shall be in moderate contact except in concealed spaces where fire-resistance-rated construction, shear resistance or diaphragm action is not required. | 2508.3 Single-ply application. | Edges and ends of gypsum board and gypsum panel products shall occur on the framing members, except those edges and ends that are perpendicular to the framing members. Edges and ends of gypsum board and gypsum panel products shall be in moderate contact except in concealed spaces where fire-resistance-rated construction, shear resistance or diaphragm action is not required.
2508.3.1 Floating angles. | Fasteners at the top and bottom plates of vertical assemblies, or the edges and ends of horizontal assemblies perpendicular to supports, and at the wall line are permitted to be omitted except on shear resisting elements or fire-resistance-rated assemblies. Fasteners shall be applied in such a manner as not to fracture the face paper with the fastener head. | 2508.3.1 Floating angles. | Fasteners at the top and bottom plates of vertical assemblies, or the edges and ends of horizontal assemblies perpendicular to supports, and at the wall line are permitted to be omitted except on shear resisting elements or fire-resistance-rated assemblies. Fasteners shall be applied in such a manner as not to fracture the face paper with the fastener head.
|  | 2508.4 Adhesives. | Gypsum board and gypsum panel products secured to framing with adhesives in ceiling assemblies shall be attached using an approved fastening schedule. Expandable foam adhesives for fastening gypsum wallboard shall conform to ASTM D6464. Other adhesives for the installation of gypsum wallboard shall conform to ASTM C557.
|  | 2508.5 Joint treatment. | Gypsum board and gypsum panel product fire-resistance-rated assemblies shall have joints and fasteners treated. Exception: Joint and fastener treatment need not be provided where any of the following conditions occur: 1. Where the gypsum board or the gypsum panel product is to receive a decorative finish such as wood paneling, battens, acoustical finishes or any similar application that would be equivalent to joint treatment. 2. On single-layer systems where joints occur over wood framing members. 3. Square edge or tongue-and-groove edge gypsum board (V-edge), gypsum panel products, gypsum backing board or gypsum sheathing. 4. On multilayer systems where the joints of adjacent layers are offset. 5. Assemblies tested without joint treatment.
|  | 2508.6 Horizontal gypsum board or gypsum panel product diaphragm ceilings. | Gypsum board or gypsum panel products shall be permitted to be used on wood joists to create a horizontal diaphragm ceiling in accordance with Table 2508.6. | See BC25 Tables and Figures
|  | 2508.6.1 Diaphragm proportions. | The maximum allowable diaphragm proportions shall be 11/2:1 between shear resisting elements. Rotation or cantilever conditions shall not be permitted.
|  | 2508.6.2 Installation. | Gypsum board or gypsum panel products used in a horizontal diaphragm ceiling shall be installed perpendicular to ceiling framing members. End joints of adjacent courses of gypsum board shall not occur on the same joist.
|  | 2508.6.3 Blocking of perimeter edges. | Perimeter edges shall be blocked using a wood member not less than 2-inch by 6-inch (51 mm by 152 mm) nominal dimension. Blocking material shall be installed flat over the top plate of the wall to provide a nailing surface not less than 2 inches (51 mm) in width for the attachment of the gypsum board or gypsum panel product.
|  | 2508.6.4 Fasteners. | Fasteners used for the attachment of gypsum board or gypsum panel products to a horizontal diaphragm ceiling shall be as defined in Table 2508.6. Fasteners shall be spaced not more than 7 inches (178 mm) on center at all supports, including perimeter blocking, and not more than 3/8 inch (9.5 mm) from the edges and ends of the gypsum board or gypsum panel product. | See BC25 Tables and Figures
|  | 2508.6.5 Lateral force restrictions. | Gypsum board or gypsum panel products shall not be used in diaphragm ceilings to resist lateral forces imposed by masonry or concrete construction.
2509.1 Wet areas. | Showers and public toilet walls shall conform to Section 1210.2. | 2509.1 Wet areas. | Showers and public toilet walls shall conform to Section 1210.2.
2509.2 Base for tile. | Materials used as a base for wall tile in tub and shower areas and wall and ceiling panels in shower areas shall be of materials listed in Table 2509.2 and installed in accordance with the manufacturer’s recommendations. Water-resistant gypsum backing board shall be used as a base for tile in water closet compartment walls when installed in accordance with GA-216 or ASTM C 840 and the manufacturer’s recommendations. Regular gypsum wallboard is permitted under tile or wall panels in other wall and ceiling areas when installed in accordance with GA-216 or ASTM C 840. | 2509.2 Base for tile. | Materials used as a base for wall tile in tub and shower areas and wall and ceiling panels in shower areas shall be of materials listed in Table 2509.2 and installed in accordance with the manufacturer’s recommendations. Water-resistant gypsum backing board shall be used as a base for tile in water closet compartment walls when installed in accordance with GA 216 or ASTM C840 and the manufacturer’s recommendations. Regular gypsum wallboard is permitted under tile or wall panels in other wall and ceiling areas when installed in accordance with GA 216 or ASTM C840. | See BC25 Tables and Figures
2509.3 Limitations. | Water-resistant gypsum backing board shall not be used in the following locations: | 2509.3 Limitations. | Water-resistant gypsum backing board shall not be used in the following locations:
2510.1 General. | Exterior and interior cement plaster and lathing shall be done with the appropriate materials listed in Table 2507.2 and Chapter 35. | 2510.1 General. | Exterior and interior cement plaster and lathing shall be done with the appropriate materials listed in Table 2507.2 and Chapter 35. | See BC25 Tables and Figures
2510.2 Weather protection. | Materials shall be stored in such a manner as to protect them from the weather. | 2510.2 Weather protection. | Materials shall be stored in such a manner as to protect them from the weather.
2510.3 Installation. | Installation of these materials shall be in compliance with ASTM C 926 and ASTM C 1063. | 2510.3 Installation. | Installation of these materials shall be in compliance with ASTM C926 and ASTM C1063.
2510.4 Corrosion resistance. | Metal lath and lath attachments shall be of corrosion-resistant material. | 2510.4 Corrosion resistance. | Metal lath and lath attachments shall be of corrosion-resistant material.
2510.5 Backing. | Backing or a lath shall provide sufficient rigidity to permit plaster applications. | 2510.5 Backing. | Backing or a lath shall provide sufficient rigidity to permit plaster applications.
2510.5.1 Support of lath. | Where lath on vertical surfaces extends between rafters or other similar projecting members, solid backing shall be installed to provide support for lath and attachments. | 2510.5.1 Support of lath. | Where lath on vertical surfaces extends between rafters or other similar projecting members, solid backing shall be installed to provide support for lath and attachments.
2510.5.2 Use of gypsum backing board. | Gypsum backing for cement plaster shall be in accordance with Section 2510.5.2.1 or 2510.5.2.2. | 2510.5.2 Use of gypsum backing board. | Gypsum backing for cement plaster shall be in accordance with Section 2510.5.2.1 or 2510.5.2.2.
|  | 2510.5.2.1 Gypsum board as a backing board. | Gypsum lath or gypsum wallboard shall not be used as a backing for cement plaster. Exception: Gypsum lath or gypsum wallboard is permitted, with a water-resistive barrier, as a backing for self-furred metal lath or self-furred wire fabric lath and cement plaster where either of the following conditions oc-cur: 1. On horizontal supports of ceilings or roof soffits. 2. On interior walls.
2510.5.2.2 Gypsum sheathing backing. | Gypsum sheathing is permitted as a backing for metal or wire fabric lath and cement plaster on walls. A water-resistive barrier shall be provided in accordance with Section 2510.6. | 2510.5.2.2 Gypsum sheathing backing. | Gypsum sheathing is permitted as a backing for metal or wire fabric lath and cement plaster on walls. A water-resistive barrier shall be provided in accordance with Section 2510.6.
2510.5.3 Backing not required. | Wire backing is not required under expanded metal lath or paperbacked wire fabric lath. | 2510.5.3 Backing not required. | Wire backing is not required under expanded metal lath or paperbacked wire fabric lath.
2510.6 Water-resistive barriers. | Water-resistive barriers shall be installed as required in Section 1404.2 and, where applied over wood-based sheathing, shall include a water-resistive barrier with a performance at least equivalent to two layers of water-resistive barrier complying with ASTM E 2556, Type I. The individual layers shall be installed independently such that each layer provides a separate continuous plane and any flashing (installed in accordance with Section 1405.4), has a means for draining water that enters the assembly to the exterior. Exception: Where the water-resistive barrier that is applied over wood-based sheathing has a water resistance equal to or greater than that of a water-resistive barrier complying with ASTM E 2556, Type II and is separated from the stucco by an intervening, substantially nonwater-absorbing layer or drainage space. | 2510.6 Water-resistive barriers. | Water-resistive barriers shall be installed as required in Section 1403.2 and, where applied over wood-based sheathing, shall comply with Section 2510.6.1 or 2510.6.2.
2510.7 Preparation of masonry and concrete. | Surfaces shall be clean, free from efflorescence, sufficiently damp and rough for proper bond. If the surface is insufficiently rough, approved bonding agents or a portland cement dash bond coat mixed in proportions of not more than two parts volume of sand to one part volume of portland cement or plastic cement shall be applied. The dash bond coat shall be left undisturbed and shall be moist cured not less than 24 hours. | 2510.7 Preparation of masonry and concrete. | Surfaces shall be clean, free from efflorescence, sufficiently damp and rough for proper bond. If the surface is insufficiently rough, approved bonding agents or a Portland cement dash bond coat mixed in proportions of not more than two parts volume of sand to one part volume of Portland cement or plastic cement shall be applied. The dash bond coat shall be left undisturbed and shall be moist cured not less than 24 hours.
|  | 2510.6.1 Dry climates. | One of the following shall apply for dry (B) climate zones:
2511.1 General. | Plastering gypsum plaster or cement plaster shall be not less than three coats where applied over metal lath or wire fabric lath and not less than two coats where applied over other bases permitted by this chapter. Exception: Gypsum veneer plaster and cement plaster specifically designed and approved for one-coat applications. | 2511.1 General. | Plastering gypsum plaster or cement plaster shall be not less than three coats where applied over metal lath or wire fabric lath and not less than two coats where applied over other bases permitted by this chapter. Exception: Gypsum veneer plaster and cement plaster specifically designed and approved for one-coat applications.
|  | 2510.6.2 Moist or marine climates. | In moist (A) or marine (C) climate zones, water-resistive barrier shall comply with one of the following:
2511.1.1 Installation. | Installation of lathing and plaster materials shall conform to Table 2511.1.1 and Section 2507. | 2511.1.1 Installation. | Installation of lathing and plaster materials shall conform to Table 2511.1.1 and Section 2507. | See BC25 Tables and Figures
2511.2 Limitations. | Plaster shall not be applied directly to fiber insulation board. Cement plaster shall not be applied directly to gypsum lath or gypsum plaster except as specified in Sections 2510.5.1 and 2510.5.2. | 2511.2 Limitations. | Plaster shall not be applied directly to fiber insulation board. Cement plaster shall not be applied directly to gypsum lath or gypsum plaster except as specified in Sections 2510.5.1 and 2510.5.2.
2511.3 Grounds. | Where installed, grounds shall ensure the minimum thickness of plaster as set forth in ASTM C 842 and ASTM C 926. Plaster thickness shall be measured from the face of lath and other bases. | 2511.3 Grounds. | Where installed, grounds shall ensure the minimum thickness of plaster as set forth in ASTM C842 and ASTM C926. Plaster thickness shall be measured from the face of lath and other bases.
2511.4 Interior masonry or concrete. | Condition of surfaces shall be as specified in Section 2510.7. Approved specially prepared gypsum plaster designed for application to concrete surfaces or approved acoustical plaster is permitted. The total thickness of base coat plaster applied to concrete ceilings shall be as set forth in ASTM C 842 or ASTM C 926. Should ceiling surfaces require more than the maximum thickness permitted in ASTM C 842 or ASTM C 926, metal lath or wire fabric lath shall be installed on such surfaces before plastering. | 2511.4 Interior masonry or concrete. | Condition of surfaces shall be as specified in Section 2510.7. Approved specially prepared gypsum plaster designed for application to concrete surfaces or approved acoustical plaster is permitted. The total thickness of base coat plaster applied to concrete ceilings shall be as set forth in ASTM C842 or ASTM C926. Should ceiling surfaces require more than the maximum thickness permitted in ASTM C842 or ASTM C926, metal lath or wire fabric lath shall be installed on such surfaces before plastering.
2511.5 Wet areas. | Showers and public toilet walls shall conform to Sections 1210.2 and 1210.3. When wood frame walls and partitions are covered on the interior with cement plaster or tile of similar material and are subject to water splash, the framing shall be protected with an approved moisture barrier. | 2511.5 Wet areas. | Showers and public toilet walls shall conform to Sections 1210.2 and 1210.3. Where wood frame walls and partitions are covered on the interior with cement plaster or tile of similar material and are subject to water splash, the framing shall be protected with an approved moisture barrier.
2512.1 General. | Plastering with cement plaster shall be not less than three coats when applied over metal lath or wire fabric lath or gypsum board backing as specified in Section 2510.5 and shall be not less than two coats when applied over masonry or concrete. If the plaster surface is to be completely covered by veneer or other facing material, or is completely concealed by another wall, plaster application need only be two coats, provided the total thickness is as set forth in ASTM C 926. | 2512.1 General. | Plastering with cement plaster shall be not less than three coats where applied over metal lath or wire fabric lath or gypsum board backing as specified in Section 2510.5 and shall be not less than two coats where applied over masonry or concrete. If the plaster surface is to be completely covered by veneer or other facing material, or is completely concealed by another wall, plaster application need only be two coats, provided that the total thickness is as set forth in ASTM C926.
2512.1.1 On-grade floor slab. | On wood frame or steel stud construction with an on-grade concrete floor slab system, exterior plaster shall be applied in such a manner as to cover, but not to extend below, the lath and paper. The application of lath, paper and flashing or drip screeds shall comply with ASTM C 1063. | 2512.1.1 On-grade floor slab. | On wood frame or steel stud construction with an on-grade concrete floor slab system, exterior plaster shall be applied in such a manner as to cover, but not to extend below, the lath and paper. The application of lath, paper and flashing or drip screeds shall comply with ASTM C1063.
2512.1.2 Weep screeds. | A minimum 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage), corrosion-resistant weep screed with a minimum vertical attachment flange of 3½ inches (89 mm) shall be provided at or below the foundation plate line on exterior stud walls in accordance with ASTM C 926. The weep screed shall be placed a minimum of 4 inches (102 mm) above the earth or 2 inches (51 mm) above paved areas and be of a type that will allow trapped water to drain to the exterior of the building. The water-resistive barrier shall lap the attachment flange. The exterior lath shall cover and terminate on the attachment flange of the weep screed. | 2512.1.2 Weep screeds. | A minimum 0.019-inch (0.48 mm) (No. 26 galvanized sheet gage), corrosion-resistant weep screed with a minimum vertical attachment flange of 31/2 inches (89 mm) shall be provided at or below the foundation plate line on exterior stud walls in accordance with ASTM C926. The weep screed shall be placed not less than 4 inches (102 mm) above the earth or 2 inches (51 mm) above paved areas and be of a type that will allow trapped water to drain to the exterior of the building. The water-resistive barrier shall lap the attachment flange. The exterior lath shall cover and terminate on the attachment flange of the weep screed.
2512.2 Plasticity agents. | Only approved plasticity agents and approved amounts thereof shall be added to portland cement or blended cements. When plastic cement or masonry cement is used, no additional lime or plasticizers shall be added. Hydrated lime or the equivalent amount of lime putty used as a plasticizer is permitted to be added to cement plaster or cement and lime plaster in an amount not to exceed that set forth in ASTM C 926. | 2512.2 Plasticity agents. | Only approved plasticity agents and approved amounts thereof shall be added to Portland cement or blended cements. Where plastic cement or masonry cement is used, additional lime or plasticizers shall not be added. Hydrated lime or the equivalent amount of lime putty used as a plasticizer is permitted to be added to cement plaster or cement and lime plaster in an amount not to exceed that set forth in ASTM C926.
2512.3 Limitations. | Gypsum plaster shall not be used on exterior surfaces. | 2512.3 Limitations. | Gypsum plaster shall not be used on exterior surfaces.
2512.4 Cement plaster. | Plaster coats shall be protected from freezing for a period of not less than 24 hours after set has occurred. Plaster shall be applied when the ambient temperature is higher than 40°F (4°C), unless provisions are made to keep cement plaster work above 40°F (4°C) during application and 48 hours thereafter. | 2512.4 Cement plaster. | Plaster coats shall be protected from freezing for a period of not less than 24 hours after set has occurred. Plaster shall be applied when the ambient temperature is higher than 40°F (4°C), unless provisions are made to keep cement plaster work above 40°F (4°C) during application and 48 hours thereafter.
2512.5 Second-coat application. | The second coat shall be brought out to proper thickness, rodded and floated sufficiently rough to provide adequate bond for the finish coat. The second coat shall have no variation greater than ¼ inch (6.4 mm) in any direction under a 5-foot (1524 mm) straight edge. | 2512.5 Second-coat application. | The second coat shall be brought out to proper thickness, rodded and floated sufficiently rough to provide adequate bond for the finish coat. The second coat shall not have variations greater than 1/4 inch (6.4 mm) in any direction under a 5-foot (1524 mm) straight edge.
2512.6 Curing and interval. | First and second coats of cement plaster shall be applied and moist cured as set forth in ASTM C 926 and Table 2512.6. | 2512.6 Curing and interval. | First and second coats of cement plaster shall be applied and moist cured as set forth in ASTM C926 and Table 2512.6. | See BC25 Tables and Figures
2512.7 Application to solid backings. | Where applied over gypsum backing as specified in Section 2510.5 or directly to unit masonry surfaces, the second coat is permitted to be applied as soon as the first coat has attained sufficient hardness. | 2512.7 Application to solid backings. | Where applied over gypsum backing as specified in Section 2510.5 or directly to unit masonry surfaces, the second coat is permitted to be applied as soon as the first coat has attained sufficient hardness.
2512.8 Alternate method of application. | The second coat is permitted to be applied as soon as the first coat has attained sufficient rigidity to receive the second coat. | 2512.8 Alternate method of application. | The second coat is permitted to be applied as soon as the first coat has attained sufficient rigidity to receive the second coat.
2512.8.1 Admixtures. | When using this method of application, calcium aluminate cement up to 15 percent of the weight of the portland cement is permitted to be added to the mix. | 2512.8.1 Admixtures. | Where using this method of application, calcium aluminate cement up to 15 percent of the weight of the Portland cement is permitted to be added to the mix.
2512.8.2 Curing. | Curing of the first coat is permitted to be omitted and the second coat shall be cured as set forth in ASTM C 926 and Table 2512.6. | 2512.8.2 Curing. | Curing of the first coat is permitted to be omitted and the second coat shall be cured as set forth in ASTM C926 and Table 2512.6. | See BC25 Tables and Figures
2512.9 Finish coats. | Cement plaster finish coats shall be applied over base coats that have been in place for the time periods set forth in ASTM C 926. The third or finish coat shall be applied with sufficient material and pressure to bond and to cover the brown coat and shall be of sufficient thickness to conceal the brown coat. | 2512.9 Finish coats. | Cement plaster finish coats shall be applied over base coats that have been in place for the time periods set forth in ASTM C926. The third or finish coat shall be applied with sufficient material and pressure to bond and to cover the brown coat and shall be of sufficient thickness to conceal the brown coat.
2513.1 General. | Exposed natural or integrally colored aggregate is permitted to be partially embedded in a natural or colored bedding coat of cement plaster or gypsum plaster, subject to the provisions of this section. | 2513.1 General. | Exposed natural or integrally colored aggregate is permitted to be partially embedded in a natural or colored bedding coat of cement plaster or gypsum plaster, subject to the provisions of this section.
2513.2 Aggregate. | The aggregate shall be applied manually or mechanically and shall consist of marble chips, pebbles or similar durable, moderately hard (three or more on the Mohs hardness scale), nonreactive materials. | 2513.2 Aggregate. | The aggregate shall be applied manually or mechanically and shall consist of marble chips, pebbles or similar durable, moderately hard (three or more on the Mohs hardness scale), nonreactive materials.
2513.3 Bedding coat proportions. | The bedding coat for interior or exterior surfaces shall be composed of one part portland cement and one part Type S lime; or one part blended cement and one part Type S lime; or masonry cement; or plastic cement and a maximum of three parts of graded white or natural sand by volume. The bedding coat for interior surfaces shall be composed of 100 pounds (45.4 kg) of neat gypsum plaster and a maximum of 200 pounds (90.8 kg) of graded white sand. A factory-prepared bedding coat for interior or exterior use is permitted. The bedding coat for exterior surfaces shall have a minimum compressive strength of 1,000 pounds per square inch (psi) (6895 kPa). | 2513.3 Bedding coat proportions. | The bedding coat for interior or exterior surfaces shall be composed of one part Portland cement and one part Type S lime; or one part blended cement and one part Type S lime; or masonry cement; or plastic cement and not more than three parts of graded white or natural sand by volume. The bedding coat for interior surfaces shall be composed of 100 pounds (45.4 kg) of neat gypsum plaster and not more than 200 pounds (90.8 kg) of graded white sand. A factory-prepared bedding coat for interior or exterior use is permitted. The bedding coat for exterior surfaces shall have a minimum compressive strength of 1,000 pounds per square inch (6895 kPa).
2513.4 Application. | The bedding coat is permitted to be applied directly over the first (scratch) coat of plaster, provided the ultimate overall thickness is a minimum of 7/8 inch (22 mm), including lath. Over concrete or masonry surfaces, the overall thickness shall be a minimum of ½ inch (12.7 mm). | 2513.4 Application. | The bedding coat is permitted to be applied directly over the first (scratch) coat of plaster, provided that the ultimate overall thickness is not less than 7/8 inch (22 mm), including lath. Over concrete or masonry surfaces, the overall thickness shall be not less than 1/2 inch (12.7 mm).
2513.5 Bases. | Exposed aggregate plaster is permitted to be applied over concrete, masonry, cement plaster base coats or gypsum plaster base coats installed in accordance with Section 2511 or 2512. | 2513.5 Bases. | Exposed aggregate plaster is permitted to be applied over concrete, masonry, cement plaster base coats or gypsum plaster base coats installed in accordance with Section 2511 or 2512.
2513.6 Preparation of masonry and concrete. | Masonry and concrete surfaces shall be prepared in accordance with the provisions of Section 2510.7. | 2513.6 Preparation of masonry and concrete. | Masonry and concrete surfaces shall be prepared in accordance with the provisions of Section 2510.7.
2513.7 Curing of base coats. | Cement plaster base coats shall be cured in accordance with ASTM C 926. Cement plaster bedding coats shall retain sufficient moisture for hydration (hardening) for 24 hours minimum or, where necessary, shall be kept damp for 24 hours by light water spraying. | 2513.7 Curing of base coats. | Cement plaster base coats shall be cured in accordance with ASTM C926. Cement plaster bedding coats shall retain sufficient moisture for hydration (hardening) for 24 hours minimum or, where necessary, shall be kept damp for 24 hours by light water spraying.
2514.1 General. | Reinforced gypsum concrete shall comply with the requirements of ASTM C 317 and ASTM C 956. | 2514.1 General. | Reinforced gypsum concrete shall comply with the requirements of ASTM C317 and ASTM C956.
2514.2 Minimum thickness. | The minimum thickness of reinforced gypsum concrete shall be 2 inches (51 mm) except the minimum required thickness shall be reduced to 1½ inches (38 mm), provided the following conditions are satisfied: | 2514.2 Minimum thickness. | The minimum thickness of reinforced gypsum concrete shall be 2 inches (51 mm) except the minimum required thickness shall be reduced to 11/2 inches (38 mm), provided that the following conditions are satisfied:
2501.2╪ Performance. | Lathing, plastering, gypsum board and gypsum panel product construction shall be done in the manner and with the materials specified in this chapter and the referenced standards listed in Chapter 35. When fire protection is required, such construction shall also comply with the provisions of Chapter 7.
2501.3╪ Other materials. | Other approved wall or ceiling coverings shall be permitted to be installed in accordance with the recommendations of the manufacturer and the approval of the commissioner.
2502.1 Definitions. | The following terms are defined in Chapter 2:
2506.3 Mold resistance. | Gypsum board or cement board, used in an assembly for the following areas, shall have a mold resistance rating of 10 in accordance with ASTM D3273:
2508.4 Joint treatment. | Gypsum board and gypsum panel product fire-resistance-rated assemblies shall have joints and fasteners treated. Exception: Joint and fastener treatment need not be provided where any of the following conditions occur: 1. Where the gypsum board or the gypsum panel product is to receive a decorative finish such as wood paneling, battens, acoustical finishes or any similar application that would be equivalent to joint treatment. 2. On single-layer systems where joints occur over wood framing members. 3. Square edge or tongue-and-groove edge gypsum board (V-edge), gypsum panel products, gypsum backing board or gypsum sheathing. 4. On multilayer systems where the joints of adjacent layers are offset. 5. Assemblies tested without joint treatment.
2508.5 Horizontal gypsum board or gypsum panel product diaphragm ceilings. | Gypsum board or gypsum panel products shall be permitted to be used on wood joists to create a horizontal diaphragm ceiling in accordance with Table 2508.5. |  |  | See BC25 Tables and Figures
2508.5.1 Diaphragm proportions. | The maximum allowable diaphragm proportions shall be 1½:1 between shear resisting elements. Rotation or cantilever conditions shall not be permitted.
2508.5.2 Installation. | Gypsum board or gypsum panel products used in a horizontal diaphragm ceiling shall be installed perpendicular to ceiling framing members. End joints of adjacent courses of gypsum board shall not occur on the same joist.
2508.5.3 Blocking of perimeter edges. | Perimeter edges shall be blocked using a wood member not less than 2-inch by 6-inch (51 mm by 152 mm) nominal dimension. Blocking material shall be installed flat over the top plate of the wall to provide a nailing surface not less than 2 inches (51 mm) in width for the attachment of the gypsum board or gypsum panel product.
2508.5.4 Fasteners. | Fasteners used for the attachment of gypsum board or gypsum panel products to a horizontal diaphragm ceiling shall be as defined in Table 2508.5. Fasteners shall be spaced not more than 7 inches (178 mm) on center at all supports, including perimeter blocking, and not more than ⅜ inch (9.5 mm) from the edges and ends of the gypsum board or gypsum panel product. |  |  | See BC25 Tables and Figures
2508.5.5 Lateral force restrictions. | Gypsum board or gypsum panel products shall not be used in diaphragm ceilings to resist lateral forces imposed by masonry or concrete construction.
2510.5.2.1 Use of gypsum board as a backing board. | Gypsum lath or gypsum wallboard shall not be used as a backing for cement plaster. Exception: Gypsum lath or gypsum wallboard is permitted, with a water-resistive barrier, as a backing for self-furred metal lath or self-furred wire fabric lath and cement plaster where either of the following conditions occur: 1. On horizontal supports of ceilings or roof soffits. 2. On interior walls.
2514.3 Limitations of use. | Reinforced gypsum concrete shall not be used where exposed directly to the weather or where subject to frequent or continuous wetting. Precast units shall be protected by coverings or coatings from the weather and from contact with moisture during shipment and during storage at the work site.

## BC26
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2601.1 Scope. | These provisions shall govern the materials, design, application, construction and installation of foam plastic, foam plastic insulation, plastic veneer, interior plastic finish and trim, light-transmitting plastics and plastic composites, including plastic lumber. See Chapter 14 for requirements for exterior wall finish and trim. | 2601.1 Scope. | 0
2601.2 Exterior wall coverings. | The use of plastics in exterior wall coverings is subject to the following limitations: 1. Exterior wall coverings containing plastics shall not be permitted on Type IV construction utilizing cross-laminated timber (CLT) or structural composite lumber (SCL) complying with Section 602.4. 2. Exterior wall coverings containing plastics shall not be permitted at exterior balconies and shall comply with Section 1406.3. Exception: Combustible water-resistive barriers complying with Section 1403.5.1.
2601.2.1 Construction documents. | Construction documents for exterior wall coverings required to be tested to NFPA 285 by this chapter shall comply with the requirements of Section 1401.2.
2602.1 Definitions. | The following terms are defined in Chapter 2:
2603.1 General. | The provisions of this section shall govern the requirements and uses of foam plastic insulation in buildings and structures. | 2603.1 General. | The provisions of this section shall govern the requirements and uses of foam plastic insulation in buildings and structures.
2603.2 Labeling and identification. | Packages and containers of foam plastic insulation and foam plastic insulation components delivered to the job site shall bear the label of an approved agency showing the manufacturer’s name, product listing, product identification and information sufficient to determine that the end use will comply with the code requirements. | 2603.2 Labeling and identification. | Packages and containers of foam plastic insulation and foam plastic insulation components delivered to the job site shall bear the label of an approved agency showing the manufacturer’s name, product listing, product identification and information sufficient to determine that the end use will comply with the code requirements.
2603.3 Surface-burning characteristics. | Unless otherwise indicated in this section, foam plastic insulation and foam plastic cores of manufactured assemblies shall have a flame spread index of not more than 75 and a smoke-developed index of not more than 450 where tested in the maximum thickness intended for use in accordance with ASTM E 84 or UL 723. Loose fill-type foam plastic insulation shall be tested as board stock for the flame spread and smoke-developed indexes. Exceptions: 1. Foam plastic interior trim shall comply with the flame spread and smoke-developed indexes as provided for in Section 2604.2. 2. In cold storage buildings, ice plants, food plants, food processing rooms and similar areas, foam plastic insulation where tested in a thickness of 4 inches (102 mm) shall be permitted in a thickness up to 10 inches (254 mm) where the building is equipped throughout with an automatic fire sprinkler system in accordance with Section 903.3.1.1. The approved automatic sprinkler system shall be provided in both the room and that part of the building in which the room is located. 3. Foam plastic insulation that is a part of a Class A, B or C roof-covering assembly shall be exempt from the flame spread requirements of this section provided the assembly with the foam plastic insulation satisfactorily passes NFPA 276 or UL 1256. The smoke-developed index shall not be limited for roof applications. 4. Foam plastic insulation greater than 4 inches (102 mm) in thickness shall have a maximum flame spread index of 75 and a smoke-developed index of 450 where tested at a minimum thickness of 4 inches (102 mm), provided the end use is approved in accordance with Section 2603.9 using the thickness and density intended for use. 5. Foam plastic interior signs in covered mall buildings shall not be required to comply with the flame spread and smoke-developed indexes of this section, provided the signs comply with Section 402.6.4. | 2603.3 Surface-burning characteristics. | Unless otherwise indicated in this section, foam plastic insulation and foam plastic cores of manufactured assemblies shall have a flame spread index of not more than 75 and a smoke-developed index of not more than 450 where tested in the maximum thickness intended for use in accordance with ASTM E84 or UL 723. Loose fill-type foam plastic insulation shall be tested as board stock for the flame spread and smoke-developed indices. Exceptions: 1. Smoke-developed index for interior trim as provided for in Section 2604.2. 2. In cold storage buildings, ice plants, food plants, food processing rooms and similar areas, foam plastic insulation where tested in a thickness of 4 inches (102 mm) shall be permitted in a thickness up to 10 inches (254 mm) where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. The approved automatic sprinkler system shall be provided in both the room and that part of the building in which the room is located. 3. Foam plastic insulation that is a part of a Class A, B or C roof-covering assembly provided that the assembly with the foam plastic insulation satisfactorily passes NFPA 276 or UL 1256. The smoke-developed index shall not be limited for roof applications. 4. Foam plastic insulation greater than 4 inches (102 mm) in thickness shall have a maximum flame spread index of 75 and a smoke-developed index of 450 where tested at a minimum thickness of 4 inches (102 mm), provided that the end use is approved in accordance with Section 2603.9 using the maximum thickness and density intended for use. 5. Flame spread and smoke-developed indices for foam plastic interior signs in covered and open mall buildings provided that the signs comply with Section 402.6.4.
2603.4 Thermal barrier. | Except as provided for in Sections 2603.4.1 and 2603.9, foam plastic shall be separated from the interior of a building by an approved thermal barrier of 1/2-inch (12.7 mm) gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (120°C) after 15 minutes of fire exposure, complying with the standard time-temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in such a manner that it will remain in place for 15 minutes based on FM 4880, UL 1040, NFPA 286 or UL 1715. Combustible concealed spaces shall comply with Section 719 of this code. Exception: Thermal barriers for exterior walls shall comply with Section 2603.5.2. | 2603.4 Thermal barrier. | Except as provided for in Sections 2603.4.1 and 2603.9, foam plastic shall be separated from the interior of a building by an approved thermal barrier of 1/2-inch (12.7 mm) gypsum wallboard, heavy timber in accordance with Section 602.4 or a material that is tested in accordance with and meets the acceptance criteria of both the Temperature Transmission Fire Test and the Integrity Fire Test of NFPA 275. Combustible concealed spaces shall comply with Section 718.
2603.4.1 Thermal barrier not required. | The thermal barrier specified in Section 2603.4 is not required under the conditions set forth in Sections 2603.4.1.1 through 2603.4.1.14. | 2603.4.1 Thermal barrier not required. | The thermal barrier specified in Section 2603.4 is not required under the conditions set forth in Sections 2603.4.1.1 through 2603.4.1.14.
2603.4.1.1 Masonry or concrete construction. | A thermal barrier is not required for foam plastic insulation installed in a masonry or concrete wall, floor or roof system where the foam plastic insulation is covered on each face by not less than 1 inch (25 mm) thickness of masonry or concrete. | 2603.4.1.1 Masonry or concrete construction. | A thermal barrier is not required for foam plastic installed in a masonry or concrete wall, floor or roof system where the foam plastic insulation is covered on each face by not less than 1-inch (25 mm) thickness of masonry or concrete.
2603.4.1.2 Cooler and freezer walls. | Foam plastic installed in a maximum thickness of 10 inches (254 mm) in cooler and freezer walls shall be permitted without thermal barrier, provided that the walls: | 2603.4.1.2 Cooler and freezer walls. | Foam plastic installed in a maximum thickness of 10 inches (254 mm) in cooler and freezer walls shall:
2603.4.1.3 Walk-in coolers. | In nonsprinklered buildings, foam plastic having a thickness that does not exceed 4 inches (102 mm) and a maximum flame spread index of 75 is permitted without a thermal barrier in walk-in coolers or freezer units where the aggregate floor area does not exceed 400 square feet (37 m2) and the foam plastic is covered by a metal facing not less than 0.032-inch-thick (0.81 mm) aluminum or corrosion-resistant steel having a minimum base metal thickness of 0.016 inch (0.41 mm). A thickness of up to 10 inches (254 mm) is permitted where protected by a thermal barrier. | 2603.4.1.3 Walk-in coolers. | In nonsprinklered buildings, foam plastic having a thickness that does not exceed 4 inches (102 mm) and a maximum flame spread index of 75 is permitted in walk-in coolers or freezer units where the aggregate floor area does not exceed 400 square feet (37 m2) and the foam plastic is covered by a metal facing not less than 0.032-inch-thick (0.81 mm) aluminum or corrosion-resistant steel having a minimum base metal thickness of 0.016 inch (0.41 mm). A thickness of up to 10 inches (254 mm) is permitted where protected by a thermal barrier.
2603.4.1.4 Exterior walls-one story buildings. | For one-story buildings, foam plastic having a flame spread index of 25 or less, and a smoke-developed index of not more than 450, shall be permitted without thermal barriers in or on exterior walls in a thickness not more than 4 inches (102 mm) where the foam plastic is covered by a thickness of not less than 0.032-inch-thick (0.81 mm) aluminum or corrosion-resistant steel having a base metal thickness of 0.0160 inch (0.41 mm) and the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
2603.4.1.5 Roofing. | A thermal barrier is not required for foam plastic insulation that is a part of a Class A, B or C roof-covering assembly that is installed in accordance with the code and the manufacturer’s instructions and is either constructed as described in Item 1 or tested as described in Item 2. | 2603.4.1.5 Roofing. | A thermal barrier is not required for foam plastic insulation that is a part of a Class A, B or C roof-covering assembly that is installed in accordance with the code and the manufacturer’s instructions and is either constructed as described in Item 1 or tested as described in Item 2.
2603.4.1.6 Attics and crawl spaces. | Within an attic or crawl space where entry is made only for service of utilities, foam plastic insulation shall be permitted without thermal barrier if protected against ignition by 1½-inch-thick (38 mm) mineral fiber insulation; ¼-inch-thick (6.4 mm) wood structural panel, particleboard or hardboard; ⅜-inch (9.5 mm) gypsum wallboard, corrosion-resistant steel having a base metal thickness of 0.016 inch (0.4 mm); 11/2-inch thick (38 mm) self-supported spray-applied cellulose insulation in attic spaces only or other approved material installed in such a manner that the foam plastic insulation is not exposed. The protective covering shall be consistent with the requirements for the type of construction. | 2603.4.1.6 Attics and crawl spaces. | Within an attic or crawl space where entry is made only for service of utilities, foam plastic insulation shall be protected against ignition by 11/2-inch-thick (38 mm) mineral fiber insulation; 1/4-inch-thick (6.4 mm) wood structural panel, particleboard or hardboard; 3/8-inch (9.5 mm) gypsum wallboard, corrosion-resistant steel having a base metal thickness of 0.016 inch (0.4 mm); 11/2-inch-thick (38 mm) self-supported spray-applied cellulose insulation in attic spaces only or other approved material installed in such a manner that the foam plastic insulation is not exposed. The protective covering shall be consistent with the requirements for the type of construction.
2603.4.1.7 Doors not required to have a fire protection rating. | Where pivoted or side-hinged doors are permitted without a fire protection rating, foam plastic insulation, having a flame spread index of 75 or less and a smoke-developed index of not more than 450, shall be permitted as a core material without a thermal barrier where the door facing is of metal having a minimum thickness of 0.032-inch (0.8 mm) aluminum or steel having a base metal thickness of not less than 0.016 inch (0.4 mm) at any point. | 2603.4.1.7 Doors not required to have a fire protection rating. | Where pivoted or side-hinged doors are permitted without a fire protection rating, foam plastic insulation, having a flame spread index of 75 or less and a smoke-developed index of not more than 450, shall be permitted as a core material where the door facing is of aluminum not less than 0.032 inch (0.8 mm) in thickness or steel having a base metal thickness of not less than 0.016 inch (0.4 mm) at any point.
2603.4.1.8 Exterior doors in buildings of Group R-2 or R-3. | In occupancies classified as Group R-2 or R-3, foam-filled exterior entrance doors to individual dwelling units that do not require a fire-resistance rating shall be permitted without a thermal barrier, provided that the doors are faced with aluminum, steel, fiberglass, wood or other approved materials. | 2603.4.1.8 Exterior doors in buildings of Group R-2 or R-3. | In occupancies classified as Group R-2 or R-3, foam-filled exterior entrance doors to individual dwelling units that do not require a fire-resistance rating shall be faced with aluminum, steel, fiberglass, wood or other approved materials.
2603.4.1.9 Garage doors. | Where garage doors are permitted without a fire-resistance rating and foam plastic is permitted as a core material, provided that the door facing shall be metal having a minimum thickness of 0.032-inch (0.8 mm) aluminum or 0.010-inch (0.25 mm) steel or the facing shall be minimum 0.125-inch-thick (3.2 mm) wood. Garage doors having facings other than those described above shall be tested in accordance with, and meet the acceptance criteria of DASMA 107. | 2603.4.1.9 Garage doors. | Where garage doors are permitted without a fire-resistance rating and foam plastic is used as a core material, the door facing shall be metal having a minimum thickness of 0.032-inch (0.8 mm) aluminum or 0.010-inch (0.25 mm) steel or the facing shall be minimum 0.125-inch-thick (3.2 mm) wood. Garage doors having facings other than those described in this section shall be tested in accordance with, and meet the acceptance criteria of, DASMA 107. Exception: Garage doors using foam plastic insulation complying with Section 2603.3 in detached and attached garages associated with one- and two-family dwellings need not be provided with a thermal barrier.
2603.4.1.9.1 Garage doors in one- and two-family dwellings. | Garage doors using foam plastic insula­tion complying with Section 2603.3 in detached and attached garages associated with one- and two-family dwellings need not be provided with a thermal barrier.
2603.4.1.10 Siding backer board. | Foam plastic insulation of not more than 2,000 British thermal units per square foot (Btu/sq. ft.) (22.7 mJ/m2) as determined by NFPA 259 shall be permitted as a siding backer board with a maximum thickness of ½ inch (12.7 mm) without a thermal barrier, provided it is separated from the interior of the building by not less than 2 inches (51 mm) of mineral fiber insulation or equivalent or where applied as insulation over existing wall construction. | 2603.4.1.10 Siding backer board. | Foam plastic insulation of not more than 2,000 British thermal units per square feet (Btu/sq. ft.) (22.7 mJ/m2) as determined by NFPA 259 shall be permitted as a siding backer board with a maximum thickness of 1/2 inch (12.7 mm), provided that it is separated from the interior of the building by not less than 2 inches (51 mm) of mineral fiber insulation or equivalent or where applied as insulation with re-siding over existing wall construction.
2603.4.1.11 Interior trim. | Foam plastic used as interior trim in accordance with Section 2604 shall be permitted without a thermal barrier. | 2603.4.1.11 Interior trim. | Foam plastic used as interior trim in accordance with Section 2604 shall be permitted without a thermal barrier.
2603.4.1.12 Interior signs. | Foam plastic used for interior signs in covered mall buildings in accordance with Section 402.6.4 of this code shall be permitted without a thermal barrier. Foam plastic signs that are not affixed to interior building surfaces shall comply with Chapter 8 of the New York City Fire Code. | 2603.4.1.12 Interior signs. | Foam plastic used for interior signs in covered mall buildings in accordance with Section 402.6.4 shall be permitted without a thermal barrier. Foam plastic signs that are not affixed to interior building surfaces shall comply with Chapter 8 of the International Fire Code.
2603.4.1.13 Type V construction. | Foam plastic spray applied to a sill plate, joist header and rim joist in Type V construction is permitted without a thermal barrier, subject to all of the following: | 2603.4.1.13 Type V construction. | Foam plastic spray applied to a sill plate, joist header and rim joist in Type V construction is subject to all of the following:
2603.4.1.14 Floors. | The thermal barrier specified in Section 2603.4 is not required to be installed on the walking surface of a structural floor system that contains foam plastic insulation when the foam is covered by a minimum nominal ½-inch-thick (12.7 mm) wood structural panel or approved equivalent. The thermal barrier specified in Section 2603.4 is required on the underside of the structural floor system that contains foam plastic insulation when the underside of the structural floor system is exposed to the interior of the building. Exception: Foam plastic used as part of an interior floor finish. | 2603.4.1.14 Floors. | The thermal barrier specified in Section 2603.4 is not required to be installed on the walking surface of a structural floor system that contains foam plastic insulation where the foam plastic is covered by a minimum nominal 1/2-inch-thick (12.7 mm) wood structural panel or approved equivalent. The thermal barrier specified in Section 2603.4 is required on the underside of the structural floor system that contains foam plastic insulation where the underside of the structural floor system is exposed to the interior of the building. Exception: Foam plastic used as part of an interior floor finish.
2603.5 Exterior walls of buildings of any height. | Exterior walls of buildings of Type I, II, III or IV construction of any height shall comply with Sections 2603.5.1 through 2603.5.7. Exterior walls of cold storage buildings required to be constructed of noncombustible materials, where the building is more than one story in height, shall comply with the provisions of Sections 2603.5.1 through 2603.5.7. Exterior walls of buildings of Type V construction shall comply with Sections 2603.2, 2603.3 and 2603.4. | 2603.5 Exterior walls of buildings of any height. | Exterior walls of buildings of Type I, II, III or IV construction of any height shall comply with Sections 2603.5.1 through 2603.5.7. Exterior walls of cold storage buildings required to be constructed of noncombustible materials, where the building is more than one story in height, shall comply with the provisions of Sections 2603.5.1 through 2603.5.7. Exterior walls of buildings of Type V construction shall comply with Sections 2603.2, 2603.3 and 2603.4. Fireblocking shall be in accordance with Section 718.2.
2603.5.1 Fire-resistance-rated walls. | Where the wall is required to have a fire-resistance rating, data based on tests conducted in accordance with ASTM E 119 or UL 263 shall be provided to substantiate that the fire-resistance rating is maintained. | 2603.5.1 Fire-resistance-rated walls. | Where the wall is required to have a fire-resistance rating, data based on tests conducted in accordance with ASTM E119 or UL 263 shall be provided to substantiate that the fire-resistance rating is maintained.
2603.5.2 Thermal barrier. | Any foam plastic insulation shall be separated from the building interior by a thermal barrier meeting the following provisions, unless special approval is obtained on the basis of Section 2603.9. For exterior walls, foam plastic shall be separated from the interior of a building by an approved thermal barrier of 5/8-inch (15.9 mm) Type X gypsum wallboard or equivalent thermal barrier material that will limit the average temperature rise of the unexposed surface to not more than 250°F (120°C) after 20 minutes of fire exposure, complying with the standard time-temperature curve of ASTM E 119 or UL 263. The thermal barrier shall be installed in accordance with criteria established by testing performed in accordance with FM 4880, UL 1040, NFPA 286 or UL 1715, where the thermal barrier shall remain in place for 20 minutes. Combustible concealed spaces shall comply with Section 718 of this code. Exception: One-story buildings complying with Section 2603.4.1.4. | 2603.5.2 Thermal barrier. | Any foam plastic insulation shall be separated from the building interior by a thermal barrier meeting the provisions of Section 2603.4, unless special approval is obtained on the basis of Section 2603.9. Exception: One-story buildings complying with Section 2603.4.1.4.
2603.5.3 Potential heat. | The potential heat of foam plastic insulation in any portion of the wall or panel shall not exceed the potential heat expressed in Btu per square foot (mJ/m2) of the foam plastic insulation contained in the wall assembly tested in accordance with Section 2603.5.5. The potential heat of the foam plastic insulation shall be determined by tests conducted in accordance with NFPA 259 and the results shall be expressed in Btu per square foot (mJ/m2). Exception: One-story buildings complying with Section 2603.4.1.4. | 2603.5.3 Potential heat. | The potential heat of foam plastic insulation in any portion of the wall or panel shall not exceed the potential heat expressed in Btu per square feet (mJ/m2) of the foam plastic insulation contained in the wall assembly tested in accordance with Section 2603.5.5. The potential heat of the foam plastic insulation shall be determined by tests conducted in accordance with NFPA 259 and the results shall be expressed in Btu per square feet (mJ/m2). Exception: One-story buildings complying with Section 2603.4.1.4.
2603.5.4 Flame spread and smoke-developed indexes. | Foam plastic insulation, exterior coatings and facings shall be tested separately in the thickness intended for use, but not to exceed 4 inches (102 mm), and shall each have a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E 84 or UL 723. Exception: Prefabricated or factory-manufactured panels having minimum 0.020-inch (0.51 mm) aluminum facings and a total thickness of ¼-inch (6.4 mm) or less are permitted to be tested as an assembly where the foam plastic core is not exposed in the course of construction.
2603.5.5 Vertical and lateral fire propagation. | The exterior wall assembly shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. NFPA 285 design documentation of the tested exterior wall assembly shall be included on the submitted construction documents complying with Section 2601.2.1. Exceptions: 1. One-story buildings complying with Section 2603.4.1.4. 2. Wall assemblies where the foam plastic insulation is covered on each face by not less than 1 inch (25 mm) thickness of masonry or concrete and meeting one of the following: 2.1. There is no airspace between the insulation and the concrete or masonry. 2.2. The insulation has a flame spread index of not more than 25 as determined in accordance with ASTM E 84 or UL 723 and the maximum airspace between the insulation and the concrete or masonry is not more than 1 inch (25 mm). | 2603.5.5 Vertical and lateral fire propagation. | The exterior wall assembly shall be tested in accordance with and comply with the acceptance criteria of NFPA 285. Exceptions: 1. One-story buildings complying with Section 2603.4.1.4. 2. Wall assemblies where the foam plastic insulation is covered on each face by not less than 1-inch (25 mm) thickness of masonry or concrete and meeting one of the following: 2.1. There is no airspace between the insulation and the concrete or masonry. 2.2. The insulation has a flame spread index of not more than 25 as determined in accordance with ASTM E84 or UL 723 and the maximum airspace between the insulation and the concrete or masonry is not more than 1 inch (25 mm).
2603.5.6 Label required. | The edge or face of each piece, package or container of foam plastic insulation shall bear the label of an approved agency. The label shall contain the manufacturer’s or distributor’s identification, model number, serial number or definitive information describing the product or materials’ performance characteristics and approved agency’s identification. | 2603.5.6 Label required. | The edge or face of each piece, package or container of foam plastic insulation shall bear the label of an approved agency. The label shall contain the manufacturer’s or distributor’s identification, model number, serial number or definitive information describing the product or materials’ performance characteristics and approved agency’s identification.
2603.5.5.1 Fireblocking. | Exterior wall coverings containing foam plastic insulation shall be fireblocked in accordance with Section 718.2.6.1.
2603.5.7 Ignition. | Exterior walls shall not exhibit sustained flaming where tested in accordance with NFPA 268. Where a material is intended to be installed in more than one thickness, tests of the minimum and maximum thickness intended for use shall be performed. Exception: Assemblies protected on the outside with one of the following: 1. A thermal barrier complying with Section 2603.5.2. 2. A minimum 1-inch (25 mm) thickness of concrete or masonry. 3. Glass-fiber-reinforced concrete panels of a minimum thickness of ⅜-inch (9.5 mm). 4. Metal-faced panels having minimum 0.019-inch-thick (0.48 mm) aluminum or 0.016-inch-thick (0.41 mm) corrosion-resistant steel outer facings. 5. A minimum ⅞-inch (22.2 mm) thickness of stucco complying with Section 2510. 6. A minimum ¼-inch (6.4 mm) thickness of fiber-cement lap, panel or shingle siding complying with Sections 1405.16 and 1405.16.1 or 1405.16.2. | 2603.5.7 Ignition. | Exterior walls shall not exhibit sustained flaming where tested in accordance with NFPA 268. Where a material is intended to be installed in more than one thickness, tests of the minimum and maximum thickness intended for use shall be performed. Exception: Assemblies protected on the outside with one of the following: 1. A thermal barrier complying with Section 2603.4. 2. A minimum 1-inch (25 mm) thickness of concrete or masonry. 3. Glass-fiber-reinforced concrete panels of a minimum thickness of 3/8 inch (9.5 mm). 4. Metal-faced panels having minimum 0.019-inch-thick (0.48 mm) aluminum or 0.016-inch-thick (0.41 mm) corrosion-resistant steel outer facings. 5. A minimum 7/8-inch (22.2 mm) thickness of stucco complying with Section 2510. 6. A minimum 1/4-inch (6.4 mm) thickness of fiber-cement lap, panel or shingle siding complying with Section 1404.16 and Section 1404.16.1 or 1404.16.2.
2603.5.8 Special inspection. | Foam plastic insulation in exterior wall coverings shall be subject to special inspection in accordance with Chapter 17.
2603.8 Protection against termites. | In areas where the probability of termite infestation is very heavy in accordance with Figure 2603.8, extruded and expanded polystyrene, polyisocyanurate and other foam plastics shall not be installed on the exterior face or under interior or exterior foundation walls or slab foundations located below grade. The clearance between foam plastics installed above grade and exposed earth shall be not less than 6 inches (152 mm). Exceptions: 1. Buildings where the structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or preservative-treated wood. 2. An approved method of protecting the foam plastic and structure from subterranean termite damage is provided; or 3. On the interior side of basement and cellar walls. | 2603.8 Protection against termites. | In areas where the probability of termite infestation is very heavy in accordance with Figure 2603.8, extruded and expanded polystyrene, polyisocyanurate and other foam plastics shall not be installed on the exterior face or under interior or exterior foundation walls or slab foundations located below grade. The clearance between foam plastics installed above grade and exposed earth shall be not less than 6 inches (152 mm). Exceptions: 1. Buildings where the structural members of walls, floors, ceilings and roofs are entirely of noncombustible materials or preservative-treated wood. 2. An approved method of protecting the foam plastic and structure from subterranean termite damage is provided. 3. On the interior side of basement walls.
2603.6 Roofing assembly. | Foam plastic insulation meeting the requirements of Sections 2603.2, 2603.3 and 2603.4 shall be permitted as part of a roof-covering assembly, provided the assembly with the foam plastic insulation is a Class A, B or C roofing assembly where tested in accordance with ASTM E 108 or UL 790.
2603.9 Special approval. | Foam plastic shall not be required to comply with the requirements of Sections 2603.4 or 2603.6 where specifically approved by the department based on large-scale tests such as, but not limited to, NFPA 286 (with the acceptance criteria of Section 803.1.2.1 of this code), FM 4880, UL 1040 or UL 1715. Such testing shall be related to the actual end-use configuration and be performed on the finished manufactured foam plastic assembly in the maximum thickness intended for use. Foam plastics that are used as interior finish on the basis of special tests shall also conform to the flame spread and smoke-developed index requirements of Chapter 8. Assemblies tested shall include seams, joints and other typical details used in the installation of the assembly and shall be tested in the manner intended for use. | 2603.9 Special approval. | Foam plastic shall not be required to comply with the requirements of Section 2603.4 or those of Section 2603.6 where specifically approved based on large-scale tests such as, but not limited to, NFPA 286 (with the acceptance criteria of Section 803.1.1.1), FM 4880, UL 1040 or UL 1715. Such testing shall be related to the actual end-use configuration and be performed on the finished manufactured foam plastic assembly in the maximum thickness intended for use. Foam plastics that are used as interior finish on the basis of special tests shall conform to the flame spread and smoke-developed requirements of Chapter 8. Assemblies tested shall include seams, joints and other typical details used in the installation of the assembly and shall be tested in the manner intended for use.
2603.7 Foam plastic insulation used as interior finish or interior trim in plenums. | Foam plastic insulation used as interior wall or ceiling finish or as interior trim in plenums shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E 84 or UL 723 and shall comply with one or more of Sections 2603.7.1, 2603.7.2 and 2607.3.
2603.10 Wind resistance. | Foam plastic insulation complying with ASTM C 578 and ASTM C 1289 and used as exterior wall sheathing on framed wall assemblies shall comply with ANSI/FS 100 for wind pressure resistance and withstand the loads indicated in Chapter 16 of this code. | 2603.10 Wind resistance. | Foam plastic insulation complying with ASTM C578 and ASTM C1289 and used as exterior wall sheathing on framed wall assemblies shall comply with ANSI/FS 100 for wind pressure resistance.
2603.7.1 Separation required. | The foam plastic insulation shall be separated from the plenum by a thermal barrier complying with Section 2603.4 and shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E 84 or UL 723 at the thickness and density intended for use.
2603.11 Cladding attachment over foam sheathing to masonry or concrete wall construction. | Cladding shall be specified and installed in accordance with Chapter 14 and the cladding manufacturer’s installation instructions or an approved design. Foam sheathing shall be attached to masonry or concrete construction in accordance with the insulation manufacturer’s installation instructions or an approved design. Furring and furring attachments through foam sheathing shall be designed to resist design loads determined in accordance with Chapter 16, including support of cladding weight as applicable. Fasteners used to attach cladding or furring through foam sheathing to masonry or concrete substrates shall be approved for application into masonry or concrete material and shall be installed in accordance with the fastener manufacturer’s installation instructions. Exceptions: 1. Where the cladding manufacturer has provided approved installation instructions for application over foam sheathing and connection to a masonry or concrete substrate, those requirements shall apply. 2. For exterior insulation and finish systems, refer to Section 1408. 3. For anchored masonry or stone veneer installed over foam sheathing, refer to Section 1405. | 2603.11 Cladding attachment over foam sheathing to masonry or concrete wall construction. | Cladding shall be specified and installed in accordance with Chapter 14 and the cladding manufacturer’s installation instructions or an approved design. Foam sheathing shall be attached to masonry or concrete construction in accordance with the insulation manufacturer’s installation instructions or an approved design. Furring and furring attachments through foam sheathing shall be designed to resist design loads determined in accordance with Chapter 16, including support of cladding weight as applicable. Fasteners used to attach cladding or furring through foam sheathing to masonry or concrete substrates shall be approved for application into masonry or concrete material and shall be installed in accordance with the fastener manufacturer’s installation instructions. Exceptions: 1. Where the cladding manufacturer has provided approved installation instructions for application over foam sheathing and connection to a masonry or concrete substrate, those requirements shall apply. 2. For exterior insulation and finish systems, refer to Section 1407. 3. For anchored masonry or stone veneer installed over foam sheathing, refer to Section 1404.
2603.7.2 Approval. | The foam plastic insulation shall exhibit a flame spread index of 25 or less and a smoke-developed index of 50 or less when tested in accordance with ASTM E 84 or UL 723 at the thickness and density intended for use and shall meet the acceptance criteria of Section 803.1.2 when tested in accordance with NFPA 286. The foam plastic insulation shall be approved based on tests conducted in accordance with Section 2603.9.
2603.12 Cladding attachment over foam sheathing to cold-formed steel framing. | Cladding shall be specified and installed in accordance with Chapter 14 and the cladding manufacturer’s approved installation instructions, including any limitations for use over foam plastic sheathing, or an approved design. Where used, furring and furring attachments shall be designed to resist design loads determined in accordance with Chapter 16. In addition, the cladding or furring attachments through foam sheathing to framing shall meet or exceed the minimum fastening requirements of Sections 2603.12.1 and 2603.12.2, or an approved design for support of cladding weight. Exceptions: 1. Where the cladding manufacturer has provided approved installation instructions for application over foam sheathing, those requirements shall apply. 2. For exterior insulation and finish systems, refer to Section 1408. 3. For anchored masonry or stone veneer installed over foam sheathing, refer to Section 1405. | 2603.12 Cladding attachment over foam sheathing to cold-formed steel framing. | Cladding shall be specified and installed in accordance with Chapter 14 and the cladding manufacturer’s approved installation instructions, including any limitations for use over foam plastic sheathing, or an approved design. Where used, furring and furring attachments shall be designed to resist design loads determined in accordance with Chapter 16. In addition, the cladding or furring attachments through foam sheathing to cold-formed steel framing shall meet or exceed the minimum fastening requirements of Sections 2603.12.1 and 2603.12.2, or an approved design for support of cladding weight. Exceptions: 1. Where the cladding manufacturer has provided approved installation instructions for application over foam sheathing, those requirements shall apply. 2. For exterior insulation and finish systems, refer to Section 1407. 3. For anchored masonry or stone veneer installed over foam sheathing, refer to Section 1404.
2603.7.3 Covering. | The foam plastic insulation shall be covered by corrosion-resistant steel having a base metal thickness of not less than 0.0160 inch (0.4 mm) and shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E 84 or UL 723 at the thickness and density intended for use.
2603.12.1 Direct attachment. | Where cladding is installed directly over foam sheathing without the use of furring, cladding minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.12.1. | 2603.12.1 Direct attachment. | Where cladding is installed directly over foam sheathing without the use of furring, cladding minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.12.1. | See BC26 Tables and Figures
2603.12.2 Furred cladding attachment. | Where steel or wood furring is used to attach cladding over foam sheathing, furring minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.12.2. Where placed horizontally, wood furring shall be preservative-treated wood in accordance with Section 2303.1.9 or naturally durable wood and fasteners shall be corrosion resistant in accordance Section 2304.10.5. Steel furring shall have a minimum G60 galvanized coating. | 2603.12.2 Furred cladding attachment. | Where steel or wood furring is used to attach cladding over foam sheathing, furring minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.12.2. Where placed horizontally, wood furring shall be preservative-treated wood in accordance with Section 2303.1.9 or naturally durable wood and fasteners shall be corrosion resistant in accordance Section 2304.10.6. Steel furring shall have a minimum G60 galvanized coating. | See BC26 Tables and Figures
2604.1 General. | Plastic materials installed as interior finish or trim shall comply with Chapter 8. Foam plastics shall only be installed as interior finish where approved in accordance with the special provisions of Section 2603.9. Foam plastics that are used as interior finish shall also meet the flame spread and smoke-developed index requirements for interior finish in accordance with Chapter 8. Foam plastics installed as interior trim shall comply with Section 2604.2. | 2604.1 General. | Plastic materials installed as interior finish or trim shall comply with Chapter 8. Foam plastics shall only be installed as interior finish where approved in accordance with the special provisions of Section 2603.9. Foam plastics that are used as interior finish shall meet the flame spread and smoke-developed index requirements for interior finish in accordance with Chapter 8. Foam plastics installed as interior trim shall comply with Section 2604.2.
2604.2.1 Density. | The minimum density of the interior trim shall be 20 pcf (320 kg/m3). | 2604.2.1 Density. | The minimum density of the interior trim shall be 20 pcf (320 kg/m3).
2604.2 Foam plastic interior trim. | Foam plastic used as interior trim shall comply with Sections 2604.2.1 through 2604.2.4.
2604.2.2 Thickness. | The maximum thickness of the interior trim shall be ½-inch (12.7 mm) and the maximum width shall be 8 inches (204 mm). | 2604.2.2 Thickness. | The maximum thickness of the interior trim shall be 1/2 inch (12.7 mm) and the maximum width shall be 8 inches (204 mm).
2604.2.3 Area limitation. | The interior trim shall not constitute more than 10 percent of the specific wall or ceiling area to which it is attached. | 2604.2.3 Area limitation. | The interior trim shall not constitute more than 10 percent of the specific wall or ceiling areas to which it is attached.
2604.2.4 Flame spread. | The flame spread index shall not exceed 75 where tested in accordance with ASTM E 84 or UL 723. The smoke-developed index shall not be limited. Exception: When the interior trim material has been tested as an interior finish in accordance with NFPA 286 and complies with the acceptance criteria in Section 803.1.2.1 of this code, it shall not be required to be tested for flame spread index in accordance with ASTM E 84 or UL 723. | 2604.2.4 Flame spread. | The flame spread index shall not exceed 75 where tested in accordance with ASTM E84 or UL 723. The smoke-developed index shall not be limited. Exception: Where the interior trim material has been tested as an interior finish in accordance with NFPA 286 and complies with the acceptance criteria in Section 803.1.1.1, it shall not be required to be tested for flame spread index in accordance with ASTM E84 or UL 723.
2605.1 Interior use. | Where used within a building, plastic veneer shall comply with the interior finish requirements of Chapter 8. | 2605.1 Interior use. | Where used within a building, plastic veneer shall comply with the interior finish requirements of Chapter 8.
2605.2 Exterior use. | Exterior plastic veneer, other than plastic siding, shall be permitted to be installed on the exterior walls of buildings of any type of construction in accordance with all of the following requirements: 1. Plastic veneer shall comply with Section 2606.4. 2. Plastic veneer shall not be attached to any exterior wall to a height greater than 50 feet (15 240 mm) above grade. 3. Sections of plastic veneer shall not exceed 300 square feet (27.9 m2) in area and shall be separated by not less than 4 feet (1219 mm) vertically. 4. Fireblocking complying with Section 718.2.6.1 shall be installed. Exception: The area and separation requirements and the smoke-density limitation are not applicable to plastic veneer applied to buildings constructed of Type VB construction, provided the walls are not required to have a fire-resistance rating. | 2605.2 Exterior use. | Exterior plastic veneer, other than plastic siding, shall be permitted to be installed on the exterior walls of buildings of any type of construction in accordance with all of the following requirements: 1. Plastic veneer shall comply with Section 2606.4. 2. Plastic veneer shall not be attached to any exterior wall to a height greater than 50 feet (15 240 mm) above grade. 3. Sections of plastic veneer shall not exceed 300 square feet (27.9 m2) in area and shall be separated by not less than 4 feet (1219 mm) vertically. Exception: The area and separation requirements and the smoke-density limitation are not applicable to plastic veneer applied to buildings constructed of Type VB construction, provided that the walls are not required to have a fire-resistance rating.
2605.3 Plastic siding. | Polypropylene siding and vinyl siding shall comply with the requirements of Sections 1404 and 1405. | 2605.3 Plastic siding. | Plastic siding shall comply with the requirements of Sections 1403 and 1404.
2606.1 General. | The provisions of this section and Sections 2607 through 2611 shall govern the quality and methods of application of light-transmitting plastics for use as light-transmitting materials in buildings and structures. Foam plastics shall comply with Section 2603. Light-transmitting plastic materials that meet the other code requirements for walls and roofs shall be permitted to be used in accordance with the other applicable chapters of the code. | 2606.1 General. | The provisions of this section and Sections 2607 through 2611 shall govern the quality and methods of application of light-transmitting plastics for use as light-transmitting materials in buildings and structures. Foam plastics shall comply with Section 2603. Light-transmitting plastic materials that meet the other code requirements for walls and roofs shall be permitted to be used in accordance with the other applicable chapters of the code.
2606.2 Approval for use. | Sufficient technical data shall be submitted to substantiate the proposed use of any light-transmitting material, as approved by the department and subject to the requirements of this section. | 2606.2 Approval for use. | Sufficient technical data shall be submitted to substantiate the proposed use of any light-transmitting material, as approved by the building official and subject to the requirements of this section.
2605.4 Special inspection. | Plastic veneers shall be subject to special inspection in accordance with Chapter 17.
2606.3 Identification. | Each unit or package of light-transmitting plastic shall be identified with a mark or decal satisfactory to the commissioner, which includes identification as to the material classification. | 2606.3 Identification. | Each unit or package of light-transmitting plastic shall be identified with a mark or decal satisfactory to the building official, which includes identification as to the material classification.
2606.4 Specifications. | Light-transmitting plastics, including thermoplastic, thermosetting or reinforced thermosetting plastic material, shall have a self-ignition temperature of 650°F (343°C) or greater where tested in accordance with ASTM D 1929; a smoke-developed index not greater than 450 where tested in the manner intended for use in accordance with ASTM E 84 or UL 723, or a maximum average smoke density rating not greater than 75 where tested in the thickness intended for use in accordance with ASTM D 2843 and shall conform to one of the following combustibility classifications: | 2606.4 Specifications. | Light-transmitting plastics, including thermoplastic, thermosetting or reinforced thermosetting plastic material, shall have a self-ignition temperature of 650°F (343°C) or greater where tested in accordance with ASTM D1929; a smoke-developed index not greater than 450 where tested in the manner intended for use in accordance with ASTM E84 or UL 723, or a maximum average smoke density rating not greater than 75 where tested in the thickness intended for use in accordance with ASTM D2843 and shall conform to one of the following combustibility classifications:
2606.5 Structural requirements. | Light-transmitting plastic materials in their assembly shall be of adequate strength and durability to withstand the loads indicated in Chapter 16. Technical data shall be submitted to establish stresses, maximum unsupported spans and such other information for the various thicknesses and forms used as deemed necessary by the department. | 2606.5 Structural requirements. | Light-transmitting plastic materials in their assembly shall be of adequate strength and durability to withstand the loads indicated in Chapter 16. Technical data shall be submitted to establish stresses, maximum unsupported spans and such other information for the various thicknesses and forms used as deemed necessary by the building official.
2606.6 Fastening. | Fastening shall be adequate to withstand the loads in Chapter 16. Proper allowance shall be made for expansion and contraction of light-transmitting plastic materials in accordance with accepted data on the coefficient of expansion of the material and other material in conjunction with which it is employed. | 2606.6 Fastening. | Fastening shall be adequate to withstand the loads in Chapter 16. Proper allowance shall be made for expansion and contraction of light-transmitting plastic materials in accordance with accepted data on the coefficient of expansion of the material and other material in conjunction with which it is employed.
2606.7 Light-diffusing systems. | Light-diffusing systems shall comply with Sections 2606.7.1 through 2606.7.5. Light-diffusing systems shall not be installed in the following occupancies and locations: | 2606.7 Light-diffusing systems. | Unless the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, light-diffusing systems shall not be installed in the following occupancies and locations:
2606.7.1 Support. | Light-transmitting plastic diffusers shall be supported directly or indirectly from ceiling or roof construction by use of noncombustible hangers. Hangers shall be not less than No. 12 steel-wire gage (0.106 inch) galvanized wire or equivalent. Exception: Light-transmitting plastic diffusers used in suspended acoustical ceiling systems shall conform with the support requirements as set forth in Section 808.1. | 2606.7.1 Support. | Light-transmitting plastic diffusers shall be supported directly or indirectly from ceiling or roof construction by use of noncombustible hangers. Hangers shall be not less than No. 12 steel-wire gage (0.106 inch) galvanized wire or equivalent.
2606.7.2 Installation. | Light-transmitting plastic diffusers shall comply with Chapter 8 unless the light-transmitting plastic diffusers will fall from the mountings before igniting, at an ambient temperature of not less than 200°F (111°C) below the ignition temperature of the panels. The panels shall remain in place at an ambient room temperature of 175°F (79°C) for a period of not less than 15 minutes. | 2606.7.2 Installation. | Light-transmitting plastic diffusers shall comply with Chapter 8 unless the light-transmitting plastic diffusers will fall from the mountings before igniting, at an ambient temperature of not less than 200°F (111°C) below the ignition temperature of the panels. The panels shall remain in place at an ambient room temperature of 175°F (79°C) for a period of not less than 15 minutes.
2606.7.3 Size limitations. | Individual panels or units shall not exceed 10 feet (3048 mm) in length nor 30 square feet (2.79 m2) in area. | 2606.7.3 Size limitations. | Individual panels or units shall not exceed 10 feet (3048 mm) in length nor 30 square feet (2.79 m2) in area.
2606.7.5 Electrical luminaires. | Light-transmitting plastic panels and light-diffuser panels that are installed in approved electrical luminaires shall comply with the requirements of Chapter 8 unless the light-transmitting plastic panels conform to the requirements of Section 2606.7.2. | 2606.7.5 Electrical luminaires. | Light-transmitting plastic panels and light-diffuser panels that are installed in approved electrical luminaires shall comply with the requirements of Chapter 8 unless the light-transmitting plastic panels conform to the requirements of Section 2606.7.2. The area of approved light-transmitting plastic materials that is used in required exits or corridors shall not exceed 30 percent of the aggregate area of the ceiling in which such panels are installed, unless the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
2606.8 Partitions. | Light-transmitting plastics used in or as partitions shall comply with the requirements of Chapters 6 and 8. | 2606.8 Partitions. | Light-transmitting plastics used in or as partitions shall comply with the requirements of Chapters 6 and 8.
2606.7.4 Fire suppression system. | In buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, plastic light-diffusing systems shall be protected both above and below unless the sprinkler system has been specifically approved for installation only above the light-diffusing system. Areas of light-diffusing systems that are protected in accordance with this section shall not be limited.
2606.9 Bathroom accessories. | Light-transmitting plastics shall be permitted as glazing in shower stalls, shower doors, bathtub enclosures and similar accessory units. Safety glazing shall be provided in accordance with Chapter 24. | 2606.9 Bathroom accessories. | Light-transmitting plastics shall be permitted as glazing in shower stalls, shower doors, bathtub enclosures and similar accessory units. Safety glazing shall be provided in accordance with Chapter 24.
2606.10 Awnings, patio covers and similar structures. | Awnings constructed of light-transmitting plastics shall be constructed in accordance with provisions specified in Section 3105 and Chapter 32 for projections. Patio covers constructed of light-transmitting plastics shall comply with Section 2606. Light-transmitting plastics used in canopies at motor fuel-dispensing facilities shall comply with Section 2606, except as modified by Section 406.7.2. | 2606.10 Awnings, patio covers and similar structures. | Awnings constructed of light-transmitting plastics shall be constructed in accordance with the provisions specified in Section 3105 and Chapter 32 for projections. Patio covers constructed of light-transmitting plastics shall comply with Section 2606. Light-transmitting plastics used in canopies at motor fuel-dispensing facilities shall comply with Section 2606, except as modified by Section 406.7.2.
2606.11 Greenhouses. | Light-transmitting plastics shall be permitted in lieu of plain glass in greenhouses. | 2606.11 Greenhouses. | Light-transmitting plastics shall be permitted in lieu of glass in greenhouses.
2606.12 Solar collectors. | Light-transmitting plastic covers on solar collectors having noncombustible sides and bottoms shall be permitted on buildings not over three stories above grade plane or 9,000 square feet (836.1 m2) in total floor area, provided the light-transmitting plastic cover does not exceed 33.33 percent of the roof area for CC1 materials or 25 percent of the roof area for CC2 materials. Exception: Light-transmitting plastic covers having a thickness of 0.010 inch (0.3 mm) or less shall be permitted to be of any plastic material provided the area of the solar collectors does not exceed 33.33 percent of the roof area. | 2606.12 Solar collectors. | Light-transmitting plastic covers on solar collectors having noncombustible sides and bottoms shall be permitted on buildings not over three stories above grade plane or 9,000 square feet (836.1 m2) in total floor area, provided that the light-transmitting plastic cover does not exceed 33.33 percent of the roof area for CC1 materials or 25 percent of the roof area for CC2 materials. Exception: Light-transmitting plastic covers having a thickness of 0.010 inch (0.3 mm) or less shall be permitted to be of any plastic material provided that the area of the solar collectors does not exceed 33.33 percent of the roof area.
2607.1 General. | Light-transmitting plastics shall be permitted to be used as wall panels in exterior walls, provided that the walls are not required to have a fire-resistance rating and the installation conforms to the requirements of this section. Such panels shall be erected and anchored on a foundation, waterproofed or otherwise protected from moisture absorption and sealed with a coat of mastic or other approved waterproof coating. Light-transmitting plastic wall panels shall comply with Section 2606. Exception: Light-transmitting plastics shall not be used as wall panels in exterior walls in occupancies in Groups A-l, A-2, H, I-2 and I-3. | 2607.1 General. | Light-transmitting plastics shall not be used as wall panels in exterior walls in occupancies in Groups A-l, A-2, H, I-2 and I-3. In other groups, light-transmitting plastics shall be permitted to be used as wall panels in exterior walls, provided that the walls are not required to have a fire-resistance rating and the installation conforms to the requirements of this section. Such panels shall be erected and anchored on a foundation, waterproofed or otherwise protected from moisture absorption and sealed with a coat of mastic or other approved waterproof coating. Light-transmitting plastic wall panels shall comply with Section 2606.
2607.2 Installation. | Exterior wall panels installed as provided for herein shall not alter the type of construction classification of the building. | 2607.2 Installation. | Exterior wall panels installed as provided for herein shall not alter the type of construction classification of the building.
2607.3 Height limitation. | Light-transmitting plastics shall not be installed more than 75 feet (22 860 mm) above grade plane, except as allowed by Section 2607.5. | 2607.3 Height limitation. | Light-transmitting plastics shall not be installed more than 75 feet (22 860 mm) above grade plane.
2607.4 Area limitation and separation. | The maximum area of a single wall panel and minimum vertical and horizontal separation requirements for exterior light-transmitting plastic wall panels shall be as provided for in Table 2607.4. The maximum percentage of wall area of any story in light-transmitting plastic wall panels shall not exceed that indicated in Table 2607.4 or the percentage of unprotected openings permitted by Section 705.8, whichever is smaller. Exceptions: 1. In structures provided with approved flame barriers extending 30 inches (760 mm) beyond the exterior wall in the plane of the floor, a vertical separation is not required at the floor except that provided by the vertical thickness of the flame barrier projection. 2. Veneers of approved weather-resistant light-transmitting plastics used as exterior siding in buildings of Type V construction in compliance with Section 1406. 3. The area of light-transmitting plastic wall panels in exterior walls of greenhouses shall be exempt from the area limitations of Table 2607.4 but shall be limited as required for unprotected openings in accordance with Section 705.8. | 2607.4 Area limitation and separation. | The maximum area of a single wall panel and minimum vertical and horizontal separation requirements for exterior light-transmitting plastic wall panels shall be as provided for in Table 2607.4. The maximum percentage of wall area of any story in light-transmitting plastic wall panels shall not exceed that indicated in Table 2607.4 or the percentage of unprotected openings permitted by Section 705.8, whichever is smaller. Exceptions: 1. In structures provided with approved flame barriers extending 30 inches (760 mm) beyond the exterior wall in the plane of the floor, a vertical separation is not required at the floor except that provided by the vertical thickness of the flame barrier projection. 2. Veneers of approved weather-resistant light-transmitting plastics used as exterior siding in buildings of Type V construction in compliance with Section 1405. 3. The area of light-transmitting plastic wall panels in exterior walls of greenhouses shall be exempt from the area limitations of Table 2607.4 but shall be limited as required for unprotected openings in accordance with Section 705.8. | See BC26 Tables and Figures
2607.5 Automatic sprinkler system. | Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum percentage area of exterior wall in any story in light-transmitting plastic wall panels and the maximum square footage of a single area given in Table 2607.4 shall be increased 100 percent, but the area of light-transmitting plastic wall panels shall not exceed 50 percent of the wall area in any story, or the area permitted by Section 705.8 for unprotected openings, whichever is smaller. These installations shall be exempt from height limitations. | 2607.5 Automatic sprinkler system. | Where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the maximum percentage area of exterior wall in any story in light-transmitting plastic wall panels and the maximum square footage of a single area given in Table 2607.4 shall be increased 100 percent, but the area of light-transmitting plastic wall panels shall not exceed 50 percent of the wall area in any story, or the area permitted by Section 705.8 for unprotected openings, whichever is smaller. These installations shall not be installed more than 75 feet (22 860 mm) above grade plane. | See BC26 Tables and Figures
2607.6 Combinations of glazing and wall panels. | Combinations of light-transmitting plastic glazing and light-transmitting plastic wall panels shall be subject to the area, height and percentage limitations and the separation requirements applicable to the class of light-transmitting plastic as prescribed for light-transmitting plastic wall panel installations. | 2607.6 Combinations of glazing and wall panels. | Combinations of light-transmitting plastic glazing and light-transmitting plastic wall panels shall be subject to the area, height and percentage limitations and the separation requirements applicable to the class of light-transmitting plastic as prescribed for light-transmitting plastic wall panel installations.
2608.1 Buildings of Type VB construction. | Openings in the exterior walls of buildings of Type VB construction, where not required to be protected by Section 705, shall be permitted to be glazed or equipped with light-transmitting plastic. Light-transmitting plastic glazing shall comply with Section 2606. | 2608.1 Buildings of Type VB construction. | Openings in the exterior walls of buildings of Type VB construction, where not required to be protected by Section 705, shall be permitted to be glazed or equipped with light-transmitting plastic. Light-transmitting plastic glazing shall comply with Section 2606.
2608.2 Buildings of other types of construction. | Openings in the exterior walls of buildings of types of construction other than Type VB, where not required to be protected by Section 705, shall be permitted to be glazed or equipped with light-transmitting plastic in accordance with Section 2606 and all of the following: 1. The aggregate area of light-transmitting plastic glazing shall not exceed 25 percent of the area of any wall face of the story in which it is installed. The area of a single pane of glazing installed above the first story above grade plane shall not exceed 16 square feet (1.5 m2) and the vertical dimension of a single pane shall not exceed 4 feet (1219 mm). Exception: Where an automatic sprinkler system is provided throughout in accordance with Section 903.3.1.1, the area of allowable glazing shall be increased to not more than 50 percent of the wall face of the story in which it is installed with no limit on the maximum dimension or area of a single pane of glazing. 2. Approved flame barriers extending 30 inches (762 mm) beyond the exterior wall in the plane of the floor, or approved vertical panels not less than 4 feet (1219 mm) in height, shall be installed between glazed units located in adjacent stories. Exception: Approved vertical panels not less than 3 feet (914 mm) in height or flame barriers extending 30 inches (762 mm) beyond the exterior wall shall be installed between glazed units located in adjacent stories in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. Light-transmitting plastics shall not be installed more than 75 feet (22 860 mm) above grade level. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. | 2608.2 Buildings of other types of construction. | Openings in the exterior walls of buildings of types of construction other than Type VB, where not required to be protected by Section 705, shall be permitted to be glazed or equipped with light-transmitting plastic in accordance with Section 2606 and all of the following: 1. The aggregate area of light-transmitting plastic glazing shall not exceed 25 percent of the area of any wall face of the story in which it is installed. The area of a single pane of glazing installed above the first story above grade plane shall not exceed 16 square feet (1.5 m2) and the vertical dimension of a single pane shall not exceed 4 feet (1219 mm). Exception: Where an automatic sprinkler system is provided throughout in accordance with Section 903.3.1.1, the area of allowable glazing shall be increased to not more than 50 percent of the wall face of the story in which it is installed with no limit on the maximum dimension or area of a single pane of glazing. 2. Approved flame barriers extending 30 inches (762 mm) beyond the exterior wall in the plane of the floor, or vertical panels not less than 4 feet (1219 mm) in height, shall be installed between glazed units located in adjacent stories. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. Light-transmitting plastics shall not be installed more than 75 feet (22 860 mm) above grade level. Exception: Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
2609.1 General. | Light-transmitting plastic roof panels shall comply with this section and Section 2606. Light-transmitting plastic roof panels shall not be installed in Groups H, I-2 and I-3. In all other groups, light-transmitting plastic roof panels shall comply with any one of the following conditions: | 2609.1 General. | Light-transmitting plastic roof panels shall comply with this section and Section 2606. Light-transmitting plastic roof panels shall not be installed in Groups H, I-2 and I-3. In all other groups, light-transmitting plastic roof panels shall comply with any one of the following conditions:
2609.2 Separation. | Individual roof panels shall be separated from each other by a distance of not less than 4 feet (1219 mm) measured in a horizontal plane. Exceptions: 1. The separation between roof panels is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The separation between roof panels is not required in low-hazard occupancy buildings complying with the conditions of Section 2609.4, Exception 2 or 3. | 2609.2 Separation. | Individual roof panels shall be separated from each other by a distance of not less than 4 feet (1219 mm) measured in a horizontal plane. Exceptions: 1. The separation between roof panels is not required in a building equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. The separation between roof panels is not required in low-hazard occupancy buildings complying with the conditions of Section 2609.4, Exception 2 or 3.
2609.3 Location. | Where exterior wall openings are required to be protected by Section 705.8, a roof panel shall not be installed within 6 feet (1829 mm) of such exterior wall. | 2609.3 Location. | Where exterior wall openings are required to be protected by Section 705.8, a roof panel shall not be installed within 6 feet (1829 mm) of such exterior wall.
2609.4 Area limitations. | Roof panels shall be limited in area and the aggregate area of panels shall be limited by a percentage of the floor area of the room or space sheltered in accordance with Table 2609.4. Exceptions: 1. The area limitations of Table 2609.4 shall be permitted to be increased by 100 percent in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Low-hazard occupancy buildings, such as swimming pool shelters, shall be exempt from the area limitations of Table 2609.4, provided that the buildings do not exceed 5,000 square feet (465 m2) in area and have a minimum fire separation distance of 10 feet (3048 mm). 3. Greenhouses that are occupied for growing plants on a production or research basis, without public access, shall be exempt from the area limitations of Table 2609.4 provided they have a minimum fire separation distance of 4 feet (1220 mm). 4. Roof coverings over terraces and patios in Group R-3 occupancies shall be exempt from the area limitations of Table 2609.4. | 2609.4 Area limitations. | Roof panels shall be limited in area and the aggregate area of panels shall be limited by a percentage of the floor area of the room or space sheltered in accordance with Table 2609.4. Exceptions: 1. The area limitations of Table 2609.4 shall be permitted to be increased by 100 percent in buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Low-hazard occupancy buildings, such as swimming pool shelters, shall be exempt from the area limitations of Table 2609.4, provided that the buildings do not exceed 5,000 square feet (465 m2) in area and have a minimum fire separation distance of 10 feet (3048 mm). 3. Greenhouses that are occupied for growing or maintaining plants, without public access, shall be exempt from the area limitations of Table 2609.4 provided that they have a minimum fire separation distance of 4 feet (1220 mm). 4. Roof coverings over terraces and patios in occupancies in Group R-3 shall be exempt from the area limitations of Table 2609.4 and shall be permitted with light-transmitting plastics. | See BC26 Tables and Figures
2610.1 Light-transmitting plastic glazing of skylight assemblies. | Skylight assemblies glazed with light-transmitting plastic shall conform to the provisions of this section and Section 2606. Unit skylights glazed with light-transmitting plastic shall comply with Section 2405.5. Exception: Skylights in which the light-transmitting plastic conforms to the required roof-covering class in accordance with Section 1505. | 2610.1 Light-transmitting plastic glazing of skylight assemblies. | Skylight assemblies glazed with light-transmitting plastic shall conform to the provisions of this section and Section 2606. Exception: Skylights in which the light-transmitting plastic conforms to the required roof-covering class in accordance with Section 1505.
2610.2 Mounting. | The light-transmitting plastic shall be mounted above the plane of the roof on a curb constructed in accordance with the requirements for the type of construction classification, but not less than 4 inches (102 mm) above the plane of the roof. Edges of the light-transmitting plastic skylights or domes shall be protected by metal or other approved noncombustible material, or the light-transmitting plastic dome or skylight shall be shown to be able to resist ignition where exposed at the edge to a flame from a Class B brand as described in ASTM E 108 or UL 790. The Class B brand test shall be conducted on a skylight that is elevated to a height as specified in the manufacturer’s instructions, but not less than 4 inches (102 mm). Exceptions: 1. Curbs shall not be required for skylights used on roofs having a minimum slope of three units vertical in 12 units horizontal (25-percent slope) in occupancies in Group R-3 and on buildings with a nonclassified roof covering. 2. The metal or noncombustible edge material is not required where nonclassified roof coverings are permitted. | 2610.2 Mounting. | The light-transmitting plastic shall be mounted above the plane of the roof on a curb constructed in accordance with the requirements for the type of construction classification, but not less than 4 inches (102 mm) above the plane of the roof. Edges of the light-transmitting plastic skylights or domes shall be protected by metal or other approved noncombustible material, or the light transmitting plastic dome or skylight shall be shown to be able to resist ignition where exposed at the edge to a flame from a Class B brand as described in ASTM E108 or UL 790. The Class B brand test shall be conducted on a skylight that is elevated to a height as specified in the manufacturer’s installation instructions, but not less than 4 inches (102 mm). Exceptions: 1. Curbs shall not be required for skylights used on roofs having a minimum slope of three units vertical in 12 units horizontal (25-percent slope) in occupancies in Group R-3 and on buildings with a nonclassified roof covering. 2. The metal or noncombustible edge material is not required where nonclassified roof coverings are permitted.
2610.3 Slope. | Flat or corrugated light-transmitting plastic skylights shall slope not less than four units vertical in 12 units horizontal (4:12). Dome-shaped skylights shall rise above the mounting flange a minimum distance equal to 10 percent of the maximum width of the dome but not less than 3 inches (76 mm). Exception: Skylights that pass the Class B Burning Brand Test specified in ASTM E 108 or UL 790 shall have no minimum slope requirement. | 2610.3 Slope. | Flat or corrugated light-transmitting plastic skylights shall slope not less than four units vertical in 12 units horizontal (4:12). Dome-shaped skylights shall rise above the mounting flange a minimum distance equal to 10 percent of the maximum width of the dome but not less than 3 inches (76 mm). Exception: Skylights that pass the Class B Burning Brand Test specified in ASTM E108 or UL 790.
2610.4 Maximum area of skylights. | Each skylight shall have a maximum area within the curb of 100 square feet (9.3 m2). Exception: The area limitation shall not apply where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or the building is equipped with smoke and heat vents in accordance with Section 910. | 2610.4 Maximum area of skylights. | Each skylight shall have a maximum area within the curb of 100 square feet (9.3 m2). Exception: The area limitation shall not apply where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or the building is equipped with smoke and heat vents in accordance with Section 910.
2610.5 Aggregate area of skylights. | The aggregate area of skylights shall not exceed 33⅓ percent of the floor area of the room or space sheltered by the roof in which such skylights are installed where Class CC1 materials are utilized, and 25 percent where Class CC2 materials are utilized. Exception: The aggregate area limitations of light-transmitting plastic skylights shall be increased 100 percent beyond the limitations set forth in this section where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or the building is equipped with smoke and heat vents in accordance with Section 910. | 2610.5 Aggregate area of skylights. | The aggregate area of skylights shall not exceed 331/3 percent of the floor area of the room or space sheltered by the roof in which such skylights are installed where Class CC1 materials are utilized, and 25 percent where Class CC2 materials are utilized. Exception: The aggregate area limitations of light-transmitting plastic skylights shall be increased 100 percent beyond the limitations set forth in this section where the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or the building is equipped with smoke and heat vents in accordance with Section 910.
2610.6 Separation. | Skylights shall be separated from each other by a distance of not less than 4 feet (1219 mm) measured in a horizontal plane. Exceptions: 1. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. In Group R-3, multiple skylights located above the same room or space with a combined area not exceeding the limits set forth in Section 2610.4. | 2610.6 Separation. | Skylights shall be separated from each other by a distance of not less than 4 feet (1219 mm) measured in a horizontal plane. Exceptions: 1. Buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. In Group R-3, multiple skylights located above the same room or space with a combined area not exceeding the limits set forth in Section 2610.4.
2610.7 Location. | Where exterior wall openings are required to be protected in accordance with Section 705, a skylight shall not be installed within 6 feet (1829 mm) of such exterior wall. | 2610.7 Location. | Where exterior wall openings are required to be protected in accordance with Section 705, a skylight shall not be installed within 6 feet (1829 mm) of such exterior wall.
2610.8 Combinations of roof panels and skylights. | Combinations of light-transmitting plastic roof panels and skylights shall be subject to the area and percentage limitations and separation requirements of Section 2609 applicable to roof panel installations. | 2610.8 Combinations of roof panels and skylights. | Combinations of light-transmitting plastic roof panels and skylights shall be subject to the area and percentage limitations and separation requirements applicable to roof panel installations.
2611.1 General. | Light-transmitting plastic interior wall signs shall be limited as specified in Sections 2611.2 through 2611.4. Light-transmitting plastic interior wall signs in covered and open mall buildings shall comply with Section 402.6.4. Light-transmitting plastic interior signs shall also comply with Section 2606. | 2611.1 General. | Light-transmitting plastic interior signs shall be limited as specified in Sections 2606 and 2611.2 through 2611.4. Exception: Light-transmitting plastic interior wall signs in covered and open mall buildings shall comply with Section 402.6.4.
2611.2 Aggregate area. | The sign shall not exceed 20 percent of the wall area.
2611.4 Encasement. | Edges and backs of the sign shall be fully encased in metal. | 2611.4 Encasement. | Backs of wall-mounted signs and non-illuminated portions of all signs regulated by this section shall be fully encased in metal.
2611.3 Maximum area. | The sign shall not exceed 24 square feet (2.2 m2).
2612.1 General. | Plastic composites shall consist of either wood/plastic composites or plastic lumber. Plastic composites shall comply with the provisions of this code and with the additional requirements of Section 2612. | 2612.1 General. | Plastic composites shall consist of either wood/plastic composites or plastic lumber. Plastic composites shall comply with the provisions of this code and with the additional requirements of Section 2612.
2612.3 Flame spread index. | Plastic composites shall exhibit a flame spread index not exceeding 200 when tested in accordance with ASTM E 84 or UL 723 with the test specimen remaining in place during the test. Exception: Materials determined to be noncombustible in accordance with Section 703.5. | 2612.3 Flame spread index. | Plastic composite deck boards, stair treads, handrails and guards shall exhibit a flame spread index not exceeding 200 when tested in accordance with ASTM E84 or UL 723 with the test specimen remaining in place during the test. Exception: Materials determined to be noncombustible in accordance with Section 703.3.
2612.2 Labeling and identification. | Packages and containers of plastic composites used in exterior applications shall bear a label showing the manufacturer’s name, product identification and information sufficient to determine that the end use will comply with code requirements.
2612.4 Termite and decay resistance. | Plastic composites containing wood, cellulosic or any other biodegradable materials shall be termite and decay resistant as determined in accordance with ASTM D 7032. | 2612.4 Termite and decay resistance. | Where required by Section 2304.12, plastic composite deck boards, stair treads, handrails and guards containing wood, cellulosic or any other biodegradable materials shall be termite and decay resistant as determined in accordance with ASTM D7032.
2612.2.1 Performance levels. | The label for plastic composites used in exterior applications as deck boards, stair treads, handrails and guards shall indicate the required performance levels and demonstrate compliance with the provisions of ASTM D 7032.
2612.5 Construction requirements. | Plastic composites shall be permitted to be used as exterior deck boards, stair treads, handrails and guards in buildings of Type VB construction. | 2612.5 Construction requirements. | Plastic composites meeting the requirements of Section 2612 shall be permitted to be used as exterior deck boards, stair treads, handrails and guards where combustible construction is permitted.
2612.2.2 Loading. | The label for plastic composites used in exterior applications as deck boards, stair treads, handrails and guards shall indicate the type and magnitude of the load determined in accordance with ASTM D 7032.
2612.5.1 Span rating. | Plastic composites used as exterior deck boards shall have a span rating determined in accordance with ASTM D 7032. | 2612.5.1 Span rating. | Plastic composites used as exterior deck boards shall have a span rating determined in accordance with ASTM D7032.
2613.1 General. | The provisions of this section shall govern the requirements and uses of fiber-reinforced polymer in and on buildings and structures. | 2613.1 General. | The provisions of this section shall govern the requirements and uses of fiber-reinforced polymer in and on buildings and structures.
2613.2 Labeling and identification. | Packages and containers of fiber-reinforced polymer and their components delivered to the job site shall bear the label of an approved agency showing the manufacturer’s name, product listing, product identification and information sufficient to determine that the end use will comply with the code requirements. | 2613.2 Labeling and identification. | Packages and containers of fiber-reinforced polymer and their components delivered to the job site shall bear the label of an approved agency showing the manufacturer’s name, product listing, product identification and information sufficient to determine that the end use will comply with the code requirements.
2613.3 Interior finishes. | Fiber-reinforced polymer used as interior finishes, decorative materials or trim shall comply with Chapter 8. | 2613.3 Interior finishes. | Fiber-reinforced polymer used as interior finishes, decorative materials or trim shall comply with Chapter 8.
2612.6 Plastic composite decking, handrails and guards. | Plastic composite decking, handrails and guards shall be installed in accordance with this code and the manufacturer’s instructions.
2613.3.1 Foam plastic cores. | Fiber-reinforced polymer used as interior finish and which contains foam plastic cores shall comply with Chapter 8 and this chapter. | 2613.3.1 Foam plastic cores. | Fiber-reinforced polymer used as interior finish and that contains foam plastic cores shall comply with Chapter 8 and this chapter.
2613.4 Light-transmitting materials. | Fiber-reinforced polymer used as light-transmitting materials shall comply with Sections 2606 through 2611 as required for the specific application. | 2613.4 Light-transmitting materials. | Fiber-reinforced polymer used as light-transmitting materials shall comply with Sections 2606 through 2611 as required for the specific application.
2613.5 Exterior use. | Fiber-reinforced polymer shall be permitted to be installed on the exterior walls of buildings of any type of construction when such polymers meet the requirements of Section 2603.5. Fireblocking shall be installed in accordance with Section 718. Exceptions: 1. Compliance with Section 2603.5 is not required when all of the following conditions are met: 1.1. The fiber-reinforced polymer shall not exceed an aggregate total of 20 percent of the area of the specific wall to which it is attached, and no single architectural element shall exceed 10 percent of the area of the specific wall to which it is attached, and no contiguous set of architectural elements shall exceed 10 percent of the area of the specific wall to which they are attached. 1.2. The fiber-reinforced polymer shall have a flame spread index of 25 or less. The flame spread index requirement shall not be required for coatings or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber-reinforced polymer. 1.3. Fireblocking complying with Section 718.2.6 shall be installed. 1.4. The fiber-reinforced polymer shall be installed directly to a noncombustible substrate or be separated from the exterior wall by one of the following materials: corrosion-resistant steel having a minimum base metal thickness of 0.016 inch (0.41 mm) at any point, aluminum having a minimum thickness of 0.019 inch (0.5 mm) or other approved noncombustible material. 2. Compliance with Section 2603.5 is not required when the fiber-reinforced polymer is installed on buildings that are 40 feet (12 190 mm) or less above grade when all of the following conditions are met: 2.1. The fiber-reinforced polymer shall meet the requirements of Section 1406.2. 2.2. Where the fire separation distance is 5 feet (1524 mm) or less, the area of the fiber-reinforced polymer shall not exceed 10 percent of the wall area. Where the fire separation distance is greater than 5 feet (1524 mm), there shall be no limit on the area of the exterior wall coverage using fiber-reinforced polymer. 2.3. The fiber-reinforced polymer shall have a flame spread index of 200 or less. The flame spread index requirements do not apply to coatings or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber-reinforced polymer. 2.4. Fireblocking complying with Section 718.2.6 shall be installed. | 2613.5 Exterior use. | Fiber-reinforced polymer shall be permitted to be installed on the exterior walls of buildings of any type of construction where such polymers meet the requirements of Section 2603.5. Fireblocking shall be installed in accordance with Section 718. Exceptions: 1. Compliance with Section 2603.5 is not required where all of the following conditions are met: 1.1. The fiber-reinforced polymer shall not exceed an aggregate total of 20 percent of the area of the specific wall to which it is attached, and single architectural elements shall not exceed 10 percent of the area of the specific wall to which it is attached, and no contiguous sets of architectural elements shall not exceed 10 percent of the area of the specific wall to which they are attached. 1.2. The fiber-reinforced polymer shall have a flame spread index of 25 or less. The flame spread index requirement shall not be required for coatings or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber-reinforced polymer. 1.3. Fireblocking complying with Section 718.2.6 shall be installed. 1.4. The fiber-reinforced polymer shall be installed directly to a noncombustible substrate or be separated from the exterior wall by one of the following materials: corrosion-resistant steel having a minimum base metal thickness of 0.016 inch (0.41 mm) at any point, aluminum having a minimum thickness of 0.019 inch (0.5 mm) or other approved noncombustible material. 2. Compliance with Section 2603.5 is not required where the fiber-reinforced polymer is installed on buildings that are 40 feet (12 190 mm) or less above grade and the following conditions are met: 2.1. The fiber-reinforced polymer shall meet the requirements of Section 1405.1. 2.2. Where the fire separation distance is 5 feet (1524 mm) or less, the area of the fiber-reinforced polymer shall not exceed 10 percent of the wall area. Where the fire separation distance is greater than 5 feet (1524 mm), the area of the exterior wall coverage using fiber-reinforced polymer shall not be limited. 2.3. The fiber-reinforced polymer shall have a flame spread index of 200 or less. The flame spread index requirements do not apply to coatings or paints having a thickness of less than 0.036 inch (0.9 mm) that are applied directly to the surface of the fiber-reinforced polymer. 2.4. Fireblocking complying with Section 718.2.6 shall be installed.
2614.1 General. | The provisions of this section shall govern the requirements and uses of reflective plastic core insulation in buildings and structures. Reflective plastic core insulation shall comply with the requirements of Section 2614.2 and of one of the following: Section 2614.3 or 2614.4. | 2614.1 General. | The provisions of this section shall govern the requirements and uses of reflective plastic core insulation in buildings and structures. Reflective plastic core insulation shall comply with the requirements of Section 2614 and of Section 2614.3 or 2614.4.
2614.2 Identification. | Packages and containers of reflective plastic core insulation delivered to the job site shall show the manufacturer’s or supplier’s name, product identification and information sufficient to determine that the end use will comply with the code requirements. | 2614.2 Identification. | Packages and containers of reflective plastic core insulation delivered to the job site shall show the manufacturer’s or supplier’s name, product identification and information sufficient to determine that the end use will comply with the code requirements.
2614.3 Surface-burning characteristics. | Reflective plastic core insulation shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in accordance with ASTM E 84 or UL 723. The reflective plastic core insulation shall be tested at the maximum thickness intended for use. Test specimen preparation and mounting shall be in accordance with ASTM E 2599. | 2614.3 Surface-burning characteristics. | Reflective plastic core insulation shall have a flame spread index of not more than 25 and a smoke-developed index of not more than 450 when tested in accordance with ASTM E84 or UL 723. The reflective plastic core insulation shall be tested at the maximum thickness intended for use. Test specimen preparation and mounting shall be in accordance with ASTM E2599.
2614.4 Room corner test heat release. | Reflective plastic core insulation shall comply with the acceptance criteria of Section 803.1.2.1 of this code when tested in accordance with NFPA 286 or UL 1715 in the manner intended for use and at the maximum thickness intended for use. | 2614.4 Room corner test heat release. | Reflective plastic core insulation shall comply with the acceptance criteria of Section 803.1.1.1 when tested in accordance with NFPA 286 or UL 1715 in the manner intended for use and at the maximum thickness intended for use.
|  | 2602.1 Exterior wall covering and architectural trim. | See Chapter 14 for requirements for exterior wall covering and architectural trim.
|  | 2602.2 Interior finish and trim. | See Section 2604 for requirements for interior finish and trim.
|  | 2603.1.1 Spray-applied foam plastic. | Single- and multiple-component spray-applied foam plastic insulation shall comply with the provisions of Section 2603 and ICC 1100-2018.
|  | 2603.4.1.4 Exterior walls, one-story buildings. | For one-story buildings, foam plastic having a flame spread index of 25 or less, and a smoke-developed index of not more than 450, shall be permitted without thermal barriers in or on exterior walls in a thickness not more than 4 inches (102 mm) where the foam plastic is covered by a thickness of not less than 0.032-inch-thick (0.81 mm) aluminum or corrosion-resistant steel having a base metal thickness of 0.0160 inch (0.41 mm) and the building is equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1.
|  | 2603.5.4 Flame spread and smoke-developed indices. | Foam plastic insulation, exterior coatings and facings shall be tested separately in the thickness intended for use, but not to exceed 4 inches (102 mm), and shall each have a flame spread index of 25 or less and a smoke-developed index of 450 or less as determined in accordance with ASTM E84 or UL 723. Exception: Prefabricated or factory-manufactured panels having minimum 0.020-inch (0.51 mm) aluminum facings and a total thickness of 1/4 inch (6.4 mm) or less are permitted to be tested as an assembly where the foam plastic core is not exposed in the course of construction.
|  | 2603.6 Roofing. | Foam plastic insulation meeting the requirements of Sections 2603.2, 2603.3 and 2603.4 shall be permitted as part of a roof-covering assembly, provided that the assembly with the foam plastic insulation is a Class A, B or C roofing assembly where tested in accordance with ASTM E108 or UL 790.
|  | 2603.7 Foam plastic in plenums as interior finish or interior trim. | Foam plastic in plenums used as interior wall or ceiling finish, or interior trim, shall exhibit a flame spread index of 25 or less and a smoke-developed index of 50 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, and shall be tested in accordance with NFPA 286 and meet the acceptance criteria of Section 803.1.1. As an alternative to testing to NFPA 286, the foam plastic shall be approved based on tests conducted in accordance with Section 2603.9. Exceptions: 1. Foam plastic in plenums used as interior wall or ceiling finish, or interior trim, shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by a thermal barrier complying with Section 2603.4. 2. Foam plastic in plenums used as interior wall or ceiling finish, or interior trim, shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by corrosion-resistant steel having a base metal thickness of not less than 0.0160 inch (0.4 mm). 3. Foam plastic in plenums used as interior wall or ceiling finish, or interior trim, shall exhibit a flame spread index of 75 or less and a smoke-developed index of 450 or less when tested in accordance with ASTM E84 or UL 723 at the maximum thickness and density intended for use, where it is separated from the airflow in the plenum by not less than a 1-inch (25 mm) thickness of masonry or concrete.
|  | 2603.13 Cladding attachment over foam sheathing to wood framing. | Cladding shall be specified and installed in accordance with Chapter 14 and the cladding manufacturer’s installation instructions. Where used, furring and furring attachments shall be designed to resist design loads determined in accordance with Chapter 16. In addition, the cladding or furring attachments through foam sheathing to framing shall meet or exceed the minimum fastening requirements of Section 2603.13.1 or 2603.13.2, or an approved design for support of cladding weight. Exceptions: 1. Where the cladding manufacturer has provided approved installation instructions for application over foam sheathing, those requirements shall apply. 2. For exterior insulation and finish systems, refer to Section 1407. 3. For anchored masonry or stone veneer installed over foam sheathing, refer to Section 1404.
|  | 2603.13.1 Direct attachment. | Where cladding is installed directly over foam sheathing without the use of furring, minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.13.1. | See BC26 Tables and Figures
|  | 2603.13.2 Furred cladding attachment. | Where wood furring is used to attach cladding over foam sheathing, furring minimum fastening requirements to support the cladding weight shall be as specified in Table 2603.13.2. Where placed horizontally, wood furring shall be preservative-treated wood in accordance with Section 2303.1.9 or naturally durable wood and fasteners shall be corrosion resistant in accordance with Section 2304.10.6. | See BC26 Tables and Figures
|  | 2604.1.1 Plenums. | Foam plastics installed in plenums as interior wall or ceiling finish shall comply with Section 2603.7. Foam plastics installed in plenums as interior trim shall comply with Sections 2604.2 and 2603.7.
|  | 2604.2 Interior trim. | Foam plastic used as interior trim shall comply with Sections 2604.2.1 through 2604.2.4.
|  | 2606.7.4 Automatic sprinkler system. | In buildings that are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, plastic light-diffusing systems shall be protected both above and below unless the sprinkler system has been specifically approved for installation only above the light-diffusing system, or the light-diffusing system is listed and labeled in accordance with UL 723S. Areas of light-diffusing systems that are protected in accordance with this section shall not be limited.
|  | 2610.1.1 Unit skylights. | Unit skylights glazed with light-transmitting plastic shall comply with Section 2405.5.
|  | 2611.2 Maximum area. | The aggregate area of all light-transmitting plastics shall not exceed 24 square feet (2.23 m2). Exception: In buildings equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, the aggregate area of light-transmitting plastics shall not exceed 100 square feet (9.29 m2), provided that all plastics are Class CC1 in accordance with Section 2606.4.
|  | 2611.3 Separation. | Signs exceeding the aggregate area of Section 2611.2 shall be separated from each other by not less than 4 feet (1219 mm) horizontally and 8 feet (2438 mm) vertically.
|  | 2612.2 Labeling. | Plastic composite deck boards and stair treads, or their packaging, shall bear a label that indicates compliance with ASTM D7032 and includes the allowable load and maximum allowable span determined in accordance with ASTM D7032. Plastic composite handrails and guards, or their packaging, shall bear a label that indicates compliance with ASTM D7032 and includes the maximum allowable span determined in accordance with ASTM D7032.
|  | 2612.6 Plastic composite deck boards, stair treads, handrails and guards. | Plastic composite deck boards, stair treads, handrails and guards shall be installed in accordance with this code and the manufacturer’s instructions.

## BC27
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2701.1 Scope. | This chapter governs the electrical components, equipment and systems used in buildings and structures covered by this code. Electrical components, equipment and systems shall be designed and constructed in accordance with the provisions of the New York City Electrical Code. | 2701.1 Scope. | The provisions of this chapter and NFPA 70 shall govern the design, construction, erection and installation of the electrical components, appliances, equipment and systems used in buildings and structures covered by this code. The International Fire Code, the International Property Maintenance Code and NFPA 70 shall govern the use and maintenance of electrical components, appliances, equipment and systems. The International Existing Building Code and NFPA 70 shall govern the alteration, repair, relocation, replacement and addition of electrical components, appliances, or equipment and systems.
2702.1 Installation. | Emergency power systems and standby power systems shall be installed in accordance with the New York City Electrical Code, NFPA 110 and NFPA 111.
2702.1.1 Fuel supply. | Systems relying on fuel supplies shall have an on-premises fuel supply sufficient for not less than 6-hour full-demand operation of the system. However, natural gas from the public utility street main shall be permitted as the sole fuel supply for (i) emergency power systems serving Group R-2 occupancies, (ii) emergency power systems where permitted by Appendix G of this code, and (iii) standby power systems, provided that an outside gas cut-off valve separate from other gas services is installed in accordance with Section E.6 of Appendix E of the New York City Fuel Gas Code.
2702.1.2 Stationary generators. | Stationary emergency and standby power generators required by this code shall be listed in accordance with UL 2200.
2702.1.2.1 Prohibited location. | Emergency and standby power generators shall not be located in the same room as the main or primary electrical service equipment. Distribution associated with emergency and standby power systems shall not pass through the room containing the main or primary electrical service equipment.
2702.1.2.2 Enclosure. | Emergency and standby generators within a building shall be located within a dedicated room separated by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both.
2702.1.2.2.1 Generator room contents. | Equipment and fuel tanks located within the emergency generator room shall be limited to equipment and fuel tanks associated with the emergency and standby power systems. Piping within the room shall be limited to sprinkler piping. Exceptions: 1. Uninterrupted conduits not associated with the emergency and standby power system may pass through the emergency generator room. 2. Piping associated with generator cooling systems may be located within the emergency generator room.
2702.1.2.3 Multiple generators. | Multiple generators supplying emergency power system loads only, or supplying emergency power system equipment in combination with optional standby power loads as a common system may be located in the same room. Such generators may also share a common room, fuel supply and other common equipment and systems.
2702.1.3 Capacity. | The emergency and standby power systems shall have capacity and ratings that supply all equipment required to be operational at the same time.
2702.1.4 Protection of fire pumps. | Where electrically powered fire pumps are connected to the emergency power system, overcurrent protection and feeder conductors shall be provided in accordance with the New York City Electrical Code. Automatic transfer switches shall be located in the same room as the fire pump as an integral part of the pump controller.
2702.1.5 Special inspection. | The installation of a required emergency or standby power system shall be subject to special inspection in accordance with Section 1705.
2702.2 Where required. | Emergency and standby power systems shall be provided where required by this section. | 2702.2 Where required. | Emergency and standby power systems shall be provided where required by Sections 2702.2.1 through 2702.2.19.
2702.1.6 Registration. | Fuel-burning equipment for an emergency or standby power system shall be registered with the Department of Environmental Protection in accordance with the requirements of Section 24-109 of the Administrative Code.
2702.1.7 Automatic transfer devices and power system feeders. | Automatic transfer devices, emergency generators and emergency or standby power system feeders shall comply with Sections 2702.1.7.1 through 2702.1.7.2.1.
2702.1.7.1 Prohibited location. | All automatic transfer devices and power system feeders that serve emergency and required standby power system equipment shall not be located in the same room as the emergency power system equipment or the main or primary electrical service equipment. Where emergency and standby transfer devices are installed in accordance with Articles 700 and 701 of the New York City Electrical Code, automatic transfer devices for optional standby power systems shall not be installed in the same room.
2702.1.7.2 Enclosure. | Any automatic transfer device that is not located at the load shall be located within a dedicated room separated by not less than 2-hour fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 712, or both.
2702.1.7.2.1 Automatic transfer device room. | Equipment located within the automatic transfer device room shall be limited to equipment associated with the emergency or standby power systems. Piping within the room shall be limited to sprinkler piping.
2702.2.1 Group A occupancies. | Emergency power shall be provided for voice/alarm communication systems in Group A occupancies in accordance with Section 907.5.2.2.5.
2702.2.1.1 Prior code buildings. | In prior code buildings, where a stationary generator is not otherwise required, the power source for emergency power to the voice/alarm communication system may be served by a gas generator or an uninterruptable power source (UPS) in accordance with the New York City Electrical Code.
2702.2.2 Smoke control systems. | Standby power shall be provided for smoke control systems in accordance with Section 909.11.
2702.2.3 Exit signs. | Emergency power shall be provided for exit signs in accordance with Section 1013.6.3.
2702.2.4 Means of egress illumination. | Emergency power shall be provided for means of egress illumination in accordance with Section 1008.3.
2702.2.5 Accessible means of egress elevators. | Standby power shall be provided for elevators that are part of an accessible means of egress in accordance with Section 1009.4.
2702.2.6 Horizontal sliding doors. | Standby power shall be provided for horizontal sliding doors in accordance with Section 1010.1.4.3.
2702.2.7 Semiconductor fabrication facilities. | Emergency power shall be provided for semiconductor fabrication facilities in accordance with Section 415.11.10.
2702.2.8 Membrane structures. | Standby power shall be provided for auxiliary inflation systems in accordance with Section 3102.8.2. Emergency power shall be provided for exit signs in tents and membrane structures.
2702.2.9 Hazardous materials. | Emergency or standby power shall be provided in occupancies with hazardous materials in accordance with the New York City Fire Code and Section 414.5.2 of this code.
2702.2.10 Highly toxic and toxic materials. | Emergency power shall be provided for occupancies with highly toxic or toxic materials in accordance with the New York City Fire Code.
2702.2.11 Organic peroxides. | Standby power shall be provided for occupancies with organic peroxides in accor­dance with the New York City Fire Code.
2702.2.12 Pyrophoric materials. | Emergency power shall be provided for occupancies with silane gas in accordance with the New York City Fire Code.
2702.2.13 Covered and open mall buildings. | Emergency power shall be provided for voice/alarm communication systems in covered and open mall buildings in accordance with Section 402.7.4.
2702.2.14 High-rise buildings. | Emergency and standby power shall be provided in high-rise buildings in accordance with Section 403.4.8.
2702.2.15 Underground buildings. | Emergency and standby power shall be provided in underground buildings in accordance with Section 405.8.
2702.2.16 Group I-3 occupancies. | Emergency power shall be provided for doors in Group I-3 occupancies in accordance with Section 408.4.2.
2702.2.17 Elevators. | Standby power for elevators, including elevators provided to accommodate ambulance stretchers pursuant to Section 3002.4, shall be provided as set forth in Section 3003.1.
2702.2.18 Airport traffic control towers. | Standby power shall be provided in airport traffic control towers in accordance with Section 412.3.9.
2702.2.19 Smokeproof enclosures and pressurized elevator shafts. | Standby power shall be provided for smokeproof enclosures as required by Section 909.20.6.2 and for pressurized elevator shafts provided in accordance with Section 3006.1.
2702.2.20 Occupancy Groups B, E and R-1. | Emergency and standby power shall be required throughout those Group B, E and R-1 occupancies specified in this section:
2702.2.20.1 Equipment requiring emergency power system. | With respect to such Occupancy Groups B, E and R-1, the following equipment, where such equipment is required by this code, shall be provided with an emergency power system:
2702.2.20.2 Equipment requiring standby power system. | With respect to such Occupancy Groups B, E and R-1, the following equipment, where such equipment is required by this code, shall be provided with a standby power system:
2702.2.21 Continuously operating HVAC systems. | Standby power systems shall be provided for fans or fan systems being designed in accordance with Section 607.5 of the New York City Mechanical Code and Section 717 of this code.
2702.2.22 Gas detection systems. | Emergency power systems shall be provided for gas detection systems in accordance with Section 918.5.
2702.3 Maintenance. | Emergency and standby power systems shall be maintained and tested in accordance with the New York City Fire Code and New York City Electrical Code.
2702.4 Required loads for optional standby power systems. | In addition to any other loads, optional standby power systems shall be capable of providing power to the following standby and emergency power loads upon failure of the normal power supply: 1. Emergency lighting; 2. Fire alarm systems; and 3. Elevators as follows: 3.1. For Group R-2 occupancies in buildings greater than 125 feet (38 100 mm) in height, at least one elevator serving all floors, or one elevator per bank where different banks serve different portions of the building; or 3.2. For all other buildings having occupied floors located more than 75 feet (22 860 mm) above the lowest level of fire department vehicle access, at least one elevator that serves all floors. Exception: Backup power systems that provide backup power for non-accessory public telecommunications equipment, such as rooftop telecommunications antennas, cooling equipment, routers, etc., need not provide power to the standby and emergency power loads listed in this section.
2702.4.1 Additional optional standby power systems. | Where a functioning emergency power system or required standby power system is in place and provides power to all required emergency or required standby power loads, any additional optional standby power system need not supply power to such emergency or required standby power loads.
2702.4.2 Compliance with NFPA 110 and UL 2200. | Where an optional standby power system is required to supply emergency or required standby power loads, such power system shall comply with the UL 2200 listing and NFPA 110.
2702.4.3 Special inspection. | Where an optional standby power system is required to supply emergency or required standby power loads, such power system shall be subject to special inspection in accordance with Section 1704.31 and the rules of the department.
|  | 2702.1 General. | Emergency power systems and standby power systems shall comply with Sections 2702.1.1 through 2702.1.8.
|  | 2702.1.1 Stationary generators. | Stationary emergency and standby power generators required by this code shall be listed in accordance with UL 2200.
|  | 2702.1.2 Fuel-line piping protection. | Fuel lines supplying a generator set inside a high-rise building shall be separated from areas of the building other than the room the generator is located in by one of the following methods:
|  | 2702.1.3 Installation. | Emergency power systems and standby power systems required by this code or the International Fire Code shall be installed in accordance with the International Fire Code, NFPA 70, NFPA 110 and NFPA 111.
|  | 2702.1.4 Load transfer. | Emergency power systems shall automatically provide secondary power within 10 seconds after primary power is lost, unless specified otherwise in this code. Standby power systems shall automatically provide secondary power within 60 seconds after primary power is lost, unless specified otherwise in this code.
|  | 2702.1.5 Load duration. | Emergency power systems and standby power systems shall be designed to provide the required power for a minimum duration of 2 hours without being refueled or recharged, unless specified otherwise in this code.
|  | 2702.1.6 Uninterruptable power source. | An uninterrupted source of power shall be provided for equipment where required by the manufacturer’s instructions, the listing, this code or applicable referenced standards.
|  | 2702.1.7 Interchangeability. | Emergency power systems shall be an acceptable alternative for installations that require standby power systems.
|  | 2702.1.8 Group I-2 occupancies. | In Group I-2 occupancies located in flood hazard areas established in Section 1612.3, where new essential electrical systems are installed, and where new essential electrical system generators are installed, the systems and generators shall be located and installed in accordance with ASCE 24. Where connections for hookup of temporary generators are provided, the connections shall be located at or above the elevation required in ASCE 24.
|  | 2702.2.1 Ambulatory care facilities. | Essential electrical systems for ambulatory care facilities shall comply with Section 422.6.
|  | 2702.2.2 Elevators and platform lifts. | Standby power shall be provided for elevators and platform lifts as required in Sections 1009.4.1, 1009.5, 3003.1, 3007.8 and 3008.8.
|  | 2702.2.3 Emergency responder communication coverage systems. | Standby power shall be provided for in-building 2-way emergency responder communication coverage systems required in Section 918 and the International Fire Code. The standby power supply shall be capable of operating the in-building 2-way emergency responder communication coverage system at 100-percent system operation capacity for a duration of not less than 12 hours.
|  | 2702.2.4 Emergency voice/alarm communication systems. | Standby power shall be provided for emergency voice/alarm communication systems in accordance with NFPA 72.
|  | 2702.2.5 Exhaust systems. | Standby power shall be provided for common exhaust systems for domestic kitchens located in multistory structures as required in Section 505.5 of the International Mechanical Code. Standby power shall be provided for common exhaust systems for clothes dryers located in multistory structures as required in Section 504.11 of the International Mechanical Code and Section 614.11 of the International Fuel Gas Code.
|  | 2702.2.6 Exit signs. | Emergency power shall be provided for exit signs as required in Section 1013.6.3. The system shall be capable of powering the required load for a duration of not less than 90 minutes.
|  | 2702.2.7 Gas detection system. | Emergency or standby power shall be provided for gas detection systems in accordance with the International Fire Code.
|  | 2702.2.8 Group I-2 occupancies. | Essential electrical systems for Group I-2 occupancies shall be in accordance with Section 407.11.
|  | 2702.2.9 Group I-3 occupancies. | Emergency power shall be provided for power-operated doors and locks in Group I-3 occupancies as required in Section 408.4.2.
|  | 2702.2.10 Hazardous materials. | Emergency or standby power shall be provided in occupancies with hazardous materials where required by the International Fire Code.
|  | 2702.2.11 High-rise buildings. | Emergency and standby power shall be provided in high-rise buildings as required in Section 403.4.8.
|  | 2702.2.12 Hydrogen fuel gas rooms. | Standby power shall be provided for hydrogen fuel gas rooms as required by the International Fire Code.
|  | 2702.2.13 Laboratory suites. | Standby or emergency power shall be provided in accordance with Section 5004.7 of the International Fire Code where laboratory suites are located above the sixth story above grade plane or located in a story below grade plane.
|  | 2702.2.14 Means of egress illumination. | Emergency power shall be provided for means of egress illumination as required in Section 1008.3. The system shall be capable of powering the required load for a duration of not less than 90 minutes.
|  | 2702.2.15 Membrane structures. | Standby power shall be provided for auxiliary inflation systems in permanent membrane structures as required in Section 3102.8.2. Standby power shall be provided for a duration of not less than 4 hours. Auxiliary inflation systems in temporary air-supported and air-inflated membrane structures shall be provided in accordance with Section 3103.10.4 of the International Fire Code.
|  | 2702.2.16 Semiconductor fabrication facilities. | Emergency power shall be provided for semiconductor fabrication facilities as required in Section 415.11.11.
|  | 2702.2.17 Smoke control systems. | Standby power shall be provided for smoke control systems as required in Sections 404.7, 909.11, 909.20.7.2 and 909.21.5.
|  | 2702.2.18 Special purpose horizontal sliding, accordion or folding doors. | Standby power shall be provided for special purpose horizontal sliding, accordion or folding doors as required in Section 1010.3.3. The standby power supply shall have a capacity to operate not fewer than 50 closing cycles of the door.
|  | 2702.2.19 Underground buildings. | Emergency and standby power shall be provided in underground buildings as required in Section 405.
|  | 2702.3 Critical circuits. | Required critical circuits shall be protected using one of the following methods:
|  | 2702.4 Maintenance. | Emergency and standby power systems shall be maintained and tested in accordance with the International Fire Code.

## BC28
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2801.1 Scope. | Mechanical appliances, equipment and systems shall be constructed, installed and maintained in accordance with the New York City Mechanical Code and the New York City Fuel Gas Code. Masonry chimneys, fireplaces and barbecues shall comply with the New York City Mechanical Code and Chapter 21 of this code. | 2801.1 Scope. | The provisions of this chapter, the International Mechanical Code and the International Fuel Gas Code shall govern the design, construction, erection and installation of mechanical appliances, equipment and systems used in buildings and structures covered by this code. Masonry chimneys, fireplaces and barbecues shall comply with the International Mechanical Code and Chapter 21 of this code. The International Fire Code, the International Property Maintenance Code, the International Mechanical Code and the International Fuel Gas Code shall govern the use and maintenance of mechanical components, appliances, equipment and systems. The International Existing Building Code, the International Mechanical Code and the International Fuel Gas Code shall govern the alteration, repair, relocation, replacement and addition of mechanical components, appliances, equipment and systems.

## BC29
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
2901.1 Scope. | The New York City Plumbing Code shall govern the construction, erection, installation, alteration, repairs, relocation, replacement, addition to, use or maintenance of plumbing equipment and systems. Toilet and bathing rooms shall be constructed in accordance with Section 1210. | 2901.1 Scope. | The provisions of this chapter and the International Plumbing Code shall govern the design, construction, erection and installation of plumbing components, appliances, equipment and systems used in buildings and structures covered by this code. Toilet and bathing rooms shall be constructed in accordance with Section 1210. Private sewage disposal systems shall conform to the International Private Sewage Disposal Code. The International Fire Code, the International Property Maintenance Code and the International Plumbing Code shall govern the use and maintenance of plumbing components, appliances, equipment and systems. The International Existing Building Code and the International Plumbing Code shall govern the alteration, repair, relocation, replacement and addition of plumbing components, appliances, equipment and systems.
|  | 2902.1 Minimum number of fixtures. | Plumbing fixtures shall be provided in the minimum number as shown in Table 2902.1 based on the actual use of the building or space. Uses not shown in Table 2902.1 shall be considered individually by the code official. The number of occupants shall be determined by this code. | See BC29 Tables and Figures
|  | 2902.1.1 Fixture calculations. | To determine the occupant load of each sex, the total occupant load shall be divided in half. To determine the required number of fixtures, the fixture ratio or ratios for each fixture type shall be applied to the occupant load of each sex in accordance with Table 2902.1. Fractional numbers resulting from applying the fixture ratios of Table 2902.1 shall be rounded up to the next whole number. For calculations involving multiple occupancies, such fractional numbers for each occupancy shall first be summed and then rounded up to the next whole number. Exceptions: 1. The total occupant load shall not be required to be divided in half where approved statistical data indicates a distribution of the sexes of other than 50 percent of each sex. 2. Where multiple-user facilities are designed to serve all genders, the minimum fixture count shall be calculated 100 percent, based on total occupant load. In such multiple-user user facilities, each fixture type shall be in accordance with ICC A117.1 and each urinal that is provided shall be located in a stall. 3. Distribution of the sexes is not required where single-user water closets and bathing room fixtures are provided in accordance with Section 2902.1.2. | See BC29 Tables and Figures
|  | 2902.1.2 Single-user toilet and bathing room fixtures. | The plumbing fixtures located in single-user toilet and bathing rooms, including family or assisted-use toilet and bathing rooms that are required by Section 1110.2.1, shall contribute toward the total number of required plumbing fixtures for a building or tenant space. Single-user toilet and bathing rooms, and family or assisted-use toilet rooms and bathing rooms shall be identified as being available for use by all persons regardless of their sex.
|  | 2902.1.3 Lavatory distribution. | Where two or more toilet rooms are provided for each sex, the required number of lavatories shall be distributed proportionately to the required number of water closets.
|  | 2902.2 Separate facilities. | Where plumbing fixtures are required, separate facilities shall be provided for each sex. Exceptions: 1. Separate facilities shall not be required for dwelling units and sleeping units. 2. Separate facilities shall not be required in structures or tenant spaces with a total occupant load, including both employees and customers, of 15 or fewer. 3. Separate facilities shall not be required in mercantile occupancies in which the maximum occupant load is 100 or fewer. 4. Separate facilities shall not be required in business occupancies in which the maximum occupant load is 25 or fewer. 5. Separate facilities shall not be required to be designated by sex where single-user toilets rooms are provided in accordance with Section 2902.1.2. 6. Separate facilities shall not be required where rooms having both water closets and lavatory fixtures are designed for use by both sexes and privacy for water closets are installed in accordance with Section 405.3.4 of the International Plumbing Code. Urinals shall be located in an area visually separated from the remainder of the facility or each urinal that is provided shall be located in a stall.
|  | 2902.2.1 Family or assisted-use toilet facilities serving as separate facilities. | Where a building or tenant space requires a separate toilet facility for each sex and each toilet facility is required to have only one water closet, two family or assisted-use toilet facilities shall be permitted to serve as the required separate facilities. Family or assisted-use toilet facilities shall not be required to be identified for exclusive use by either sex as required by Section 2902.4.
|  | 2902.3 Employee and public toilet facilities. | For structures and tenant spaces intended for public utilization, customers, patrons and visitors shall be provided with public toilet facilities. Employees associated with structures and tenant spaces shall be provided with toilet facilities. The number of plumbing fixtures located within the required toilet facilities shall be provided in accordance with Section 2902 for all users. Employee toilet facilities shall be either separate or combined employee and public toilet facilities. Exception: Public toilet facilities shall not be required for: 1. Parking garages where operated without parking attendants. 2. Structures and tenant spaces intended for quick transactions, including takeout, pickup and drop-off, having a public access area less than or equal to 300 square feet (28 m2).
|  | 2902.3.1 Access. | The route to the public toilet facilities required by Section 2902.3 shall not pass through kitchens, storage rooms or closets. Access to the required facilities shall be from within the building or from the exterior of the building. The public shall have access to the required toilet facilities at all times that the building is occupied.
|  | 2902.3.2 Prohibited toilet room location. | Toilet rooms shall not open directly into a room used for the preparation of food for service to the public.
|  | 2902.3.3 Location of toilet facilities in occupancies other than malls. | In occupancies other than covered and open mall buildings, the required public and employee toilet facilities shall be located not more than one story above or below the space required to be provided with toilet facilities, and the path of travel to such facilities shall not exceed a distance of 500 feet (152 m). Exceptions: 1. The location and maximum distances of travel to required employee facilities in factory and industrial occupancies shall be permitted to exceed that required by this section, provided that the location and maximum distances of travel are approved. 2. The location and maximum distances of travel to required public and employee facilities in Group S occupancies shall be permitted to exceed that required by this section, provided that the location and maximum distances of travel are approved.
|  | 2902.3.4 Location of toilet facilities in malls. | In covered and open mall buildings, the required public and employee toilet facilities shall be located not more than one story above or below the space required to be provided with toilet facilities, and the path of travel to such facilities shall not exceed a distance of 300 feet (91 m). In mall buildings, the required facilities shall be based on total square footage (m2) within a covered mall building or within the perimeter line of an open mall building, and facilities shall be installed in each individual store or in a central toilet area located in accordance with this section. The maximum distance of travel to central toilet facilities in mall buildings shall be measured from the main entrance of any store or tenant space. In mall buildings, where employees’ toilet facilities are not provided in the individual store, the maximum distance of travel shall be measured from the employees’ work area of the store or tenant space.
|  | 2902.3.5 Pay facilities. | Where pay facilities are installed, such facilities shall be in excess of the required minimum facilities. Required facilities shall be free of charge.
|  | 2902.3.6 Door locking. | Where a toilet room is provided for the use of multiple occupants, the egress door for the room shall not be lockable from the inside of the room. This section does not apply to family or assisted-use toilet rooms.
|  | 2902.4 Signage. | Required public facilities shall be provided with signs that designate the sex as required by Section 2902.2. Signs shall be readily visible and located near the entrance to each toilet facility. Signs for accessible toilet facilities shall comply with Section 1112.
|  | 2902.4.1 Directional signage. | Directional signage indicating the route to the required public toilet facilities shall be posted in a lobby, corridor, aisle or similar space, such that the sign can be readily seen from the main entrance to the building or tenant space.
|  | 2902.5 Drinking fountain location. | Drinking fountains shall not be required to be located in individual tenant spaces provided that public drinking fountains are located within a distance of travel of 500 feet (152 m) of the most remote location in the tenant space and not more than one story above or below the tenant space. Where the tenant space is in a covered or open mall, such distance shall not exceed 300 feet (91 m).
|  | 2902.6 Small occupancies. | Drinking fountains shall not be required for an occupant load of 15 or fewer.
|  | 2902.7 Service sink location. | Service sinks shall not be required to be located in individual tenant spaces in a covered mall provided that service sinks are located within a distance of travel of 300 feet (91 m) of the most remote location in the tenant space and not more than one story above or below the tenant space. Service sinks shall be located on an accessible route.
|  | 2903.1 Setting. | Fixtures shall be set level and in proper alignment with reference to adjacent walls.
|  | 2903.1.1 Water closets, urinals, lavatories and bidets. | A water closet, urinal, lavatory or bidet shall not be set closer than 15 inches (381 mm) from its center to any side wall, partition, vanity or other obstruction. Where partitions or other obstructions do not separate adjacent fixtures, fixtures shall not be set closer than 30 inches (762 mm) center to center between adjacent fixtures. There shall be not less than a 21-inch (533 mm) clearance in front of a water closet, urinal, lavatory or bidet to any wall, fixture or door. Water closet compartments shall be not less than 30 inches (762 mm) in width and not less than 60 inches (1524 mm) in depth for floor-mounted water closets and not less than 30 inches (762 mm) in width and 56 inches (1422 mm) in depth for wall-hung water closets. Exception: An accessible children’s water closet shall be set not closer than 12 inches (305 mm) from its center to the required partition or to the wall on one side.
|  | 2903.1.2 Public lavatories. | In employee and public toilet rooms, the required lavatory shall be located in the same room as the required water closet.
|  | 2903.1.3 Location of fixtures and piping. | Piping, fixtures or equipment shall not be located in such a manner as to interfere with the normal operation of windows, doors or other means of egress openings.
|  | 2903.1.4 Water closet compartment. | Each water closet utilized by the public or employees shall occupy a separate compartment with walls or partitions and a door enclosing the fixtures to ensure privacy. Exceptions: 1. Water closet compartments shall not be required in a single-occupant toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more water closets shall be permitted to have one water closet without an enclosing compartment. 3. This provision is not applicable to toilet areas located within Group I-3 housing areas.
|  | 2903.1.5 Urinal partitions. | Each urinal utilized by the public or employees shall occupy a separate area with walls or partitions to provide privacy. The horizontal dimension between walls or partitions at each urinal shall be not less than 30 inches (762 mm). The walls or partitions shall begin at a height not greater than 12 inches (305 mm) from and extend not less than 60 inches (1524 mm) above the finished floor surface. The walls or partitions shall extend from the wall surface at each side of the urinal not less than 18 inches (457 mm) or to a point not less than 6inches (152 mm) beyond the outermost front lip of the urinal measured from the finished backwall surface, whichever is greater. Exceptions: 1. Urinal partitions shall not be required in a single-occupant or family/assisted-use toilet room with a lockable door. 2. Toilet rooms located in child day care facilities and containing two or more urinals shall be permitted to have one urinal without partitions.

## BC30
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
3001.1 Scope. | This chapter establishes the minimum safety requirements for and governs the design, construction, installation, alteration, maintenance, inspection, test and operation of elevators, dumbwaiters, escalators, moving walks, industrial lifts and loading ramps, mechanical parking equipment, console or stage lifts, power-operated scaffolds, amusement devices, platform lifts, and special hoisting and conveying equipment. This chapter and all the provisions of this code for new installations shall also apply to elevators in existing buildings moved to new hoistways. High-rise building elevators shall also conform to the provisions of Section 403 of this code. Exception: Personnel and material hoists used for construction operations subject to the requirements of Chapter 33. | 3001.1 Scope. | This chapter governs the design, construction, installation, alteration and repair of elevators and conveying systems and their components.
3001.2 Reference standards. | Except as otherwise provided for in this code, the design, construction, installation, alteration, repair and maintenance of elevators and conveying systems and their components shall conform to ASME A17.1/CSA B44 as modified by Appendix K, Chapter K1, ASME A17.2, ASME A17.3 as modified by Appendix K, Chapter K3, ASME A17.5, ASME A17.6, ASME A17.7/CSA B44.7, ASME A18.1, ASME A90.1, ASME B20.1 as modified by Appendix K, Chapter K2, ANSI A10.4, ANSI E1.46, BSR 1.42, ANSI/ICC A117.1, and ASCE 24 for construction in flood hazard areas established in Appendix G. Where this code makes reference to the nationally recognized standards ASME A17.1/CSA B44, ASME A17.3, and ASME B20.1, such standard(s) shall be as modified for New York City in accordance with Appendix K of this code.
3001.3 Accessibility. | The following elevators and lifts shall conform to ICC A117.1:
3001.4 Change in use. | A change in use of an elevator from freight to passenger, passenger to freight, or from one freight class to another freight class shall comply with Section 8.7 of ASME A17.1/CSA B44.
3001.5 Piping or ductwork. | No piping or ductwork, except as permitted by ASME A17.1/CSA B44, Section 2.8, shall be permitted within hoistway or elevator enclosures except:
3001.6 Elevator mirrors. | A mirror shall be installed in each self-service passenger elevator in multiple dwellings. Such mirror shall be affixed and maintained in a manner sufficient to enable persons entering such elevator to view the inside thereof prior to entry to determine whether any person is in the elevator.
3002.1 Hoistway enclosure protection. | Elevator, dumbwaiter and other hoistway enclosures shall be shaft enclosures complying with Section 713. | 3002.1 Hoistway enclosure protection. | Elevator, dumbwaiter and other hoistway enclosures shall be shaft enclosures complying with Sections 712 and 713.
3001.7 Car switch operation. | Elevators with car switch operation (manual operation) shall be provided with a signal system by means of which signals can be given from any landing whenever the elevator is desired at that landing.
3001.8 Prohibited devices. | The following devices shall be prohibited:
3001.8.1 Manlifts. | The installation of manlifts is prohibited.
3002.2 Number of elevator cars in a hoistway. |  | 3002.2 Number of elevator cars in a hoistway. | Where four or more elevator cars serve all or the same portion of a building, the elevators shall be located in not fewer than two separate hoistways. Not more than four elevator cars shall be located in any single hoistway enclosure.
3001.8.2 Sidewalk elevators. | The installation of sidewalk elevators located outside the street line is prohibited.
3002.3 Emergency signs. | A sign shall be posted and maintained on every floor at the elevator landing. The sign shall read “IN FIRE EMERGENCY, DO NOT USE ELEVATOR. USE THE EXIT STAIRS.” The lettering shall be at least ½ inch (13 mm) block letters in red with white background or as otherwise approved by the commissioner. Such lettering shall be properly spaced to provide good legibility. The sign shall also contain a diagram showing the location where it is posted and the location and letter identification of the stairs on the floor. The sign shall be at least 10 inches by 12 inches (255 mm by 305 mm), located directly above a call button and securely attached to the wall or partition. The top of such sign shall not be more than 6 feet (1829 mm) above the floor level. The diagram on such sign may be omitted provided that signs containing such diagram are posted in conspicuous places on the respective floor. In such case, the sign at the elevator landing shall be at least 2½ inches by 10 inches (64 mm by 254 mm) and the diagram signs shall be at least 8 inches by 12 inches (203 mm by 305 mm). | 3002.3 Emergency signs. | An approved pictorial sign of a standardized design shall be posted adjacent to each elevator call station on all floors instructing occupants to use the exit stairways and not to use the elevators in case of fire. The sign shall read: IN CASE OF FIRE, ELEVATORS ARE OUT OF SERVICE. USE EXIT STAIRS. Exceptions: 1. The emergency sign shall not be required for elevators that are part of an accessible means of egress complying with Section 1009.4. 2. The emergency sign shall not be required for elevators that are used for occupant self-evacuation in accordance with Section 3008.
3001.9 Approved equipment. | All equipment listed in ASME A17.1/CSA B44, Section 8.3 as modified by New York City Building Code, Appendix K, Chapter K1, shall be listed by an approved agency in accordance with Section 28-113.2.3 of the Administrative Code, Section 8.3.1 of ASME A17.1/CSA B44, and the rules of the department, and shall be approved by the commissioner.
3001.10 Construction documents. | Applications for elevator, escalator, moving walkway and stairway, dumbwaiter, and similar equipment shall contain construction documents that include the following:
3002.5 Emergency doors. | Where an elevator is installed in a single blind hoistway or on the outside of a building, there shall be installed in the blind portion of the hoistway or blank face of the building, an emergency door in accordance with ASME A17.1/CSA B44. | 3002.5 Emergency doors. | Where an elevator is installed in a single blind hoistway or on the outside of a building, there shall be installed in the blind portion of the hoistway or blank face of the building, an emergency door in accordance with ASME A17.1/CSA B44.
3001.11 Special provisions for prior code buildings. | Prior code buildings shall be permitted to comply with Section 3001.11.1.
3002.6 Prohibited doors. | Doors, other than hoistway doors and the elevator car door, shall be prohibited at the point of egress from an elevator car unless such doors are readily openable from the car side without a key, tool, special knowledge or effort. | 3002.6 Prohibited doors. | Doors, other than hoistway doors and the elevator car door, shall be prohibited at the point of access to an elevator car unless such doors are readily openable from the car side without a key, tool, special knowledge or effort.
3001.11.1 Existing shafts. | Elevator cabs installed in existing shafts shall be permitted to be smaller than that required by this chapter where necessary to fit in the existing shaft. Exception: An existing elevator shaft shall be enlarged or a new elevator shaft shall be constructed to accommodate an elevator cab in compliance with Chapter 11 where the entire building is required to be accessible pursuant to either Item 1 of Section 1101.3.1, or Section 1101.3.2.
3002.7 Common enclosure with stairway. | Elevators shall not be in a common shaft enclosure with a stairway. Exception: Elevators within open parking garages need not be separated from stairway enclosures. | 3002.7 Common enclosure with stairway. | Elevators shall not be in a common shaft enclosure with a stairway. Exception: Elevators within open parking garages need not be separated from stairway enclosures.
3002.8 Glass in elevator enclosures. | Glass in elevator enclosures shall comply with ASME A17.1/CSA B44 and Section 2409.2 of this code. | 3002.8 Glass in elevator enclosures. | Glass in elevator enclosures shall comply with Section 2409.2.
3002.1.1 Definitions. | The following terms are defined in Chapter 2:
3002.9 Plumbing and mechanical systems. | Plumbing and mechanical systems shall not be located in an elevator hoistway enclosure. Exceptions: 1. Floor drains, sumps and sump pumps shall be permitted at the base of the hoistway enclosure provided they are indirectly connected to the plumbing system. 2. Sprinklers shall be permitted when otherwise required. | 3002.9 Plumbing and mechanical systems. | Plumbing and mechanical systems shall not be located in an elevator hoistway enclosure. Exception: Floor drains, sumps and sump pumps shall be permitted at the base of the hoistway enclosure provided that they are indirectly connected to the plumbing system.
3002.1.2 Opening protectives. | Openings in hoistway enclosures shall be protected as required in Chapter 7. Exception: The elevator car doors and the associated hoistway enclosure doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I Emergency Recall Operation in accordance with ASME A17.1/CSA B44, as modified by Appendix K, Chapter K1.
3003.1 Standby power. | In buildings and structures where standby power is required or furnished to operate an elevator, the operation shall be in accordance with Sections 3002.4.1 and 3003.1.1 through 3003.1.4. | 3003.1 Standby power. | In buildings and structures where standby power is required or furnished to operate an elevator, the operation shall be in accordance with Sections 3003.1.1 through 3003.1.4.
3002.1.3 Hardware. | Hardware on opening protectives shall be of an approved type installed as tested, except that approved interlocks, mechanical locks and electric contacts, door and gate electric contacts and door-operating mechanisms shall be exempt from the fire test requirements.
3003.1.1 Manual transfer. | Standby power shall be manually transferable to all elevators in each bank. | 3003.1.1 Manual transfer. | Standby power shall be manually transferable to all elevators in each bank.
3003.1.2 One elevator. | Where only one elevator is installed, the elevator shall automatically transfer to standby power within 60 seconds after failure of normal power. | 3003.1.2 One elevator. | Where only one elevator is installed, the elevator shall automatically transfer to standby power within 60 seconds after failure of normal power.
3003.1.3 Two or more elevators. | Where two or more elevators are controlled by a common operating system, all elevators shall automatically transfer to standby power within 60 seconds after failure of normal power where the standby power source is of sufficient capacity to operate all elevators at the same time. Where the standby power source is not of sufficient capacity to operate all elevators at the same time, all elevators shall transfer to standby power in sequence, return to the designated landing and disconnect from the standby power source. For buildings with multiple banks of elevators, at least one elevator from each bank shall remain operable from the standby power source. | 3003.1.3 Two or more elevators. | Where two or more elevators are controlled by a common operating system, all elevators shall automatically transfer to standby power within 60 seconds after failure of normal power where the standby power source is of sufficient capacity to operate all elevators at the same time. Where the standby power source is not of sufficient capacity to operate all elevators at the same time, all elevators shall transfer to standby power in sequence, return to the designated landing and disconnect from the standby power source. After all elevators have been returned to the designated level, not less than one elevator shall remain operable from the standby power source.
3002.3.1 Stair and elevator identification signs. | Each stair and each bank of elevators shall be identified by an alphabetic letter. A sign indicating the letter of identification for the elevator bank shall be posted and maintained at each elevator landing directly above or as part of the sign specified in Section 3002.3. The stair identification sign shall be posted and maintained on the occupancy side of the stair door. The letter on the sign shall be at least 3 inches (76 mm) high, of bold type and of contrasting color from the background. Such signs shall be securely attached. Exceptions: 1. The emergency sign shall not be required for elevators that are part of an accessible means of egress complying with Section 1009.4. 2. The emergency sign shall not be required for elevators that are used for occupant self-evacuation in accordance with Section 3008.
3003.1.4 Venting. | Where standby power is connected to elevators, the machine room ventilation or air conditioning shall be connected to the standby power source. | 3003.1.4 Venting. | Where standby power is connected to elevators, the machine room ventilation or air conditioning shall be connected to the standby power source.
3002.4 Elevator required. | In buildings five stories in height or more and buildings with four or more stories below grade plane, at least one elevator shall provide access to all floors.
3002.4.1 Standby power required for elevators. | Standby power shall be provided to elevators in the following categories:
3002.4.2 Elevator car to accommodate ambulance stretcher. | Where elevators are provided in buildings five or more stories above, or four or more stories below grade plane, or underground buildings as described in Section 405.1, not fewer than one elevator subject to Section 3003.3 shall be provided with an elevator car of such a size and arrangement to accommodate an ambulance stretcher 24 inches by 84 inches (610 mm by 2134 mm), with not less than 5 inch (127 mm) radius corners, in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall be not less than 3 inches (76 mm) in height and shall be placed on both jambs of the hoistway entrances on each floor. Standby power shall be required for such an elevator if it serves a building subject to Section 3002.4.1. Exceptions: 1. An elevator serving not more than one individual dwelling unit in a building pursuant to Section 3002.4.3.1 or 3002.4.3.2. 2. Limited-Use/Limited-Application (LULA) elevators (25 feet maximum rise).
3004.1 General. | Escalators, moving walks, conveyors, and amusement devices shall comply with the provisions of Sections 3004.2 through 3004.5 as applicable. | 3004.1 General. | Escalators, moving walks, conveyors, personnel hoists and material hoists shall comply with the provisions of Sections 3004.2 through 3004.4.
3002.4.3 Elevator serving individual dwelling unit. | Elevators provided in individual dwelling units in buildings in Occupancy Groups R-2 and R-3 shall comply with Section 3002.4.3.1 through 3002.4.3.3, as applicable.
3004.2 Escalators and moving walks. | Escalators and moving walks shall be constructed of approved noncombustible and fire-retardant materials. This requirement shall not apply to electrical equipment, wiring, wheels, handrails and the use of 1/28-inch (0.9 mm) wood veneers on balustrades backed up with noncombustible materials. | 3004.2 Escalators and moving walks. | Escalators and moving walks shall be constructed of approved noncombustible and fire-retardant materials. This requirement shall not apply to electrical equipment, wiring, wheels, handrails and the use of 1/28-inch (0.9 mm) wood veneers on balustrades backed up with noncombustible materials.
3002.4.3.1 Maximum rise of 60 feet (18 288 mm). | A private residence elevator with 60 feet (18 288 mm) of maximum rise shall be permitted to serve within an individual dwelling unit provided the elevator car is in compliance with ASME A17.1/CSA B44, and Section 3001.3 of this code.
3004.2.1 Enclosure. | Escalator floor openings shall be enclosed with shaft enclosures complying with Section 713. | 3004.2.1 Enclosure. | Escalator floor openings shall be enclosed with shaft enclosures complying with Section 713.
3002.4.3.2 Rise of over 60 feet (18 288 mm) but not more than 75 feet (22 860 mm). | An elevator with 60 feet (18 288 mm) but not more than 75 feet (22 860 mm) of maximum rise shall be permitted to serve within an individual dwelling unit provided the elevator car is in compliance with Parts 2 or 3 of ASME A17.1/CSA B44 and Section 3001.3 of this code even if it does not serve on an accessible route within the dwelling unit.
3004.2.2 Escalators. | Where provided in below-grade transportation stations, escalators shall have a clear width of not less than 32 inches (813 mm). Exception: The clear width is not required in existing facilities undergoing alterations. | 3004.2.2 Escalators. | Where provided in below-grade transportation stations, escalators shall have a clear width of not less than 32 inches (815 mm).
3002.4.3.3 Maximum rise of more than 75 feet (22 860 mm). | A passenger elevator shall be required to serve within an individual dwelling unit where the maximum rise is over 75 feet (22 860 mm). Such elevator shall comply with ASME A17.1/CSA B44, and Sections 3001.3 and 3002.4.2 of this code even if it does not serve on an accessible route within the dwelling unit.
3004.3 Conveyors. | Conveyors and conveying systems shall comply with ASME B20.1. | 3004.3 Conveyors. | Conveyors and conveying systems shall comply with ASME B20.1.
3004.3.1 Enclosure. | Conveyors and related equipment connecting successive floors or levels shall be enclosed with shaft enclosures complying with Section 713. | 3004.3.1 Enclosure. | Conveyors and related equipment connecting successive floors or levels shall be enclosed with shaft enclosures complying with Section 713.
3004.3.2 Conveyor safeties. | Power-operated conveyors, belts and other material-moving devices shall be equipped with automatic limit switches that will shut off the power in an emergency and automatically stop all operation of the device. | 3004.3.2 Conveyor safeties. | Power-operated conveyors, belts and other material-moving devices shall be equipped with automatic limit switches that will shut off the power in an emergency and automatically stop all operation of the device.
3005.1 Access. | An approved means of access shall be provided to elevator machine rooms, control rooms, control spaces and machinery spaces. | 3005.1 Access. | An approved means of access shall be provided to elevator machine rooms, control rooms, control spaces and machinery spaces.
3005.3 Pressurization. | The elevator machine room, control rooms or control space with openings into a pressurized elevator hoistway shall be pressurized upon activation of a heat or smoke detector located in the elevator machine room, control room or control space. | 3005.3 Pressurization. | The elevator machine room, control rooms or control space with openings into a pressurized elevator hoistway shall be pressurized upon activation of a heat or smoke detector located in the elevator machine room, control room or control space.
3005.4 Machine rooms, control rooms, machinery spaces, and control spaces. | Elevator machine rooms, control rooms, control spaces and machinery spaces shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both. The fire-resistance rating shall be not less than the required rating of the hoistway enclosure served by the machinery. Openings in the fire barriers shall be protected with assemblies having a fire protection rating not less than that required for the hoistway enclosure doors. Exception: For other than fire service access elevators and occupant evacuation elevators, where machine rooms, machinery spaces, control rooms and control spaces do not abut and have no openings to the hoistway enclosure they serve, the fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, shall be permitted to be reduced to a 2-hour fire-resistance rating. | 3005.4 Machine rooms, control rooms, machinery spaces, and control spaces. | The following rooms and spaces shall be enclosed with fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both: 1. Machine rooms 2. Control rooms 3. Control spaces 4. Machinery spaces outside of the hoistway enclosure The fire-resistance rating shall be not less than the required rating of the hoistway enclosure served by the machinery. Openings in the fire barriers shall be protected with assemblies having a fire protection rating not less than that required for the hoistway enclosure doors. Exceptions: 1. For other than fire service access elevators and occupant evacuation elevators, where machine rooms, machinery spaces, control rooms and control spaces do not abut and do not have openings to the hoistway enclosure they serve, the fire barriers constructed in accordance with Section 707 or horizontal assemblies constructed in accordance with Section 711, or both, shall be permitted to be reduced to a 1-hour fire-resistance rating. 2. For other than fire service access elevators and occupant evacuation elevators, in buildings four stories or less above grade plane where machine room, machinery spaces, control rooms and control spaces do not abut and do not have openings to the hoistway enclosure they serve, the machine room, machinery spaces, control rooms and control spaces are not required to be fire-resistance rated.
3005.6 Plumbing systems. | Plumbing systems not related to elevator machinery shall not be located in elevator equipment rooms. | 3005.6 Plumbing systems. | Plumbing systems shall not be located in elevator equipment rooms.
3003.2 Fire-fighters’ emergency operation. | Elevators shall be provided with Phase I emergency recall operation and Phase II emergency in-car operation where required by ASME A17.1/CSA B44 as modified by Appendix K.
3003.3 Elevator in readiness. | Requirements for elevator in readiness shall be as defined in Sections 3003.3.1 through 3003.3.2.
3003.3.1 Elevator in readiness for Fire Department emergency access. | Except as provided in Section 3003.3.2, in buildings five stories in height or more, underground buildings as described in Section 405.1, and high-rise buildings, at least one elevator shall be kept available for immediate use by the Fire Department during all hours of the night and day, including holidays, Saturdays and Sundays. The elevator in readiness shall serve all floors of the building. For buildings where a Fire Service Access Elevator (FSAE) is provided, the FSAE shall serve all floors of the building. There shall be available at all times a person competent to operate the elevator. However, an attendant shall not be required for buildings with occupied floors of 150 feet (45 720 mm) or less above the lowest level of the Fire Department vehicle access that have elevators with automatic or continuous pressure operation with keyed switches meeting the requirements of ASME A17.1/CSA B44 as modified by Appendix K so as to permit sole use of the elevators by the Fire Department.
3003.3.2 Number of elevators. | A number of elevators shall be kept available at every floor for the sole use of the Fire Department as required by Sections 3003.3.2.1 and 3003.3.2.2. This requirement shall apply to the following types of buildings: 1. High-rise buildings with occupancies classified in Groups A, B, E, I, F, H, M and S; 2. Buildings with Group B occupancies with a gross area of 200,000 square feet (18 581 m2); and 3. Buildings with a main use or dominant occupancy in Group R-1 or R-2. Exception: In buildings that are five stories or more in height but are not one of the types of buildings described in Items 1 through 3 in Section 3003.3.2, at least one elevator car in such buildings shall be kept available for sole use by the Fire Department.
3003.3.2.1 Three or fewer elevators. | Where a floor is serviced by three or fewer elevator cars, every car shall be kept available for sole use by the Fire Department.
3007.1 General. | Where required by Section 403.6.1, every floor of the building shall be served by a fire service access elevator complying with Sections 3007.1 through 3007.8. Except as modified in this section, the fire service access elevator shall be installed in accordance with this chapter and ASME A17.1/CSA B44 as modified by Appendix K, Chapter K1. | 3007.1 General. | Where required by Section 403.6.1, every floor above and including the lowest level of fire department vehicle access of the building shall be served by fire service access elevators complying with Sections 3007.1 through 3007.9. Except as modified in this section, fire service access elevators shall be installed in accordance with this chapter and ASME A17.1/CSA B44. Exceptions: 1. Elevators that only service an open or enclosed parking garage and the lobby of the building shall not be required to serve as fire service access elevators. 2. The elevator shall not be required to serve the top floor of a building where that floor is utilized only for equipment for building systems.
3003.3.2.2 More than three elevators. | Where a floor is serviced by more than three elevator cars, at least three elevator cars with a total rated load capacity of not less than 6,000 pounds (2722 kg) shall be kept available for the sole use of the Fire Department. Such cars shall include not more than two cars that service all floors and at least one other car in another bank servicing that floor. If the total load capacity of all cars servicing the floor is less than 6,000 pounds (2722 kg), all such cars shall be kept available for sole use of the Fire Department.
3007.2 Automatic sprinkler system. | The building shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3007.2.1. | 3007.2 Automatic sprinkler system. | The building shall be equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3007.2.1.
3003.3.3 Operation and control. | Elevators that are kept for the sole use of the Fire Department and that have automatic or continuous pressure operation shall be controlled by keyed switches meeting the requirements of ASME A17.1/CSA B44.
3007.2.1 Prohibited locations. | Automatic sprinklers shall not be installed in elevator machine rooms, machinery spaces, control rooms, control spaces, and elevator hoistways of fire service access elevators. | 3007.2.1 Prohibited locations. | Automatic sprinklers shall not be installed in machine rooms, elevator machinery spaces, control rooms, control spaces and elevator hoistways of fire service access elevators.
3003.3.4 Other elevator cars. | In high-rise buildings classified in Occupancy Groups A, B, E, F, H, I, M and S, in low-rise buildings classified in Occupancy Group B with a gross area of 200,000 square feet (18581 m2) or more and in buildings classified in Occupancy Group R-1 or R-2, all other automatically operated cars shall have manual operation capability.
3007.2.2 Sprinkler system monitoring. | The sprinkler system shall have a sprinkler control valve supervisory switch and water-flow-initiating device provided for each floor that is monitored by the building’s fire alarm system. | 3007.2.2 Sprinkler system monitoring. | The sprinkler system shall have a sprinkler control valve supervisory switch and water-flow-initiating device provided for each floor that is monitored by the building’s fire alarm system.
3007.3 Water protection. | An approved method to prevent water from infiltrating into the hoistway enclosure from the operation of the automatic sprinkler system shall be provided: 1. Where an elevator lobby is provided in accordance with Section 3007.6, with respect to the automatic sprinkler system outside of the enclosed elevator lobby. 2. Where a corridor is provided in accordance with Section 3007.6, Exception 2, with respect to the automatic sprinkler system outside of the corridor and with respect to the automatic sprinklers inside the corridor that are beyond 10 feet (3048 mm) of the entrance to the hoistway enclosure of the fire service access elevator . 3. Where neither an enclosed elevator lobby nor a corridor is provided in accordance with Section 3007.6, Exception 3, with respect to the automatic sprinklers that are located beyond 10 feet (3048 mm) of the entrance to the hoistway enclosure of the fire service access elevator. | 3007.3 Water protection. | Water from the operation of an automatic sprinkler system outside the enclosed lobby shall be prevented from infiltrating into the hoistway enclosure in accordance with an approved method.
3007.5 Hoistway enclosures. | The fire service access elevator hoistway shall be located in a shaft enclosure complying with Section 713. | 3007.5 Hoistway enclosures. | The fire service access elevator hoistway shall be located in a shaft enclosure complying with Section 713.
3007.5.1 Structural integrity of hoistway enclosures. | The fire service access elevator hoistway enclosure shall comply with Sections 403.2.3.1 through 403.2.3.4. | 3007.5.1 Structural integrity of hoistway enclosures. | The fire service access elevator hoistway enclosure shall comply with Sections 403.2.2.1 through 403.2.2.4.
3007.5.2 Hoistway lighting. | When fire-fighters’ emergency operation is active, the entire height of the hoistway shall be illuminated at not less than 1 footcandle (11 lux) as measured from the top of the car of each fire service access elevator. | 3007.5.2 Hoistway lighting. | When fire-fighters’ emergency operation is active, the entire height of the hoistway shall be illuminated at not less than 1 footcandle (11 lux) as measured from the top of the car of each fire service access elevator.
3007.6 Fire service access elevator lobby. | The fire service access elevator shall open into a fire service access elevator lobby in accordance with Sections 3007.6.1 through 3007.6.5. Egress is permitted through the elevator lobby in accordance with Item 1 of Section 1016.2. Exceptions: 1. Where a fire service access elevator has two entrances onto a floor, the second entrance shall be permitted to open into an elevator lobby in accordance with Section 3006.3. 2. A fire service access elevator lobby shall not be required on stories where the elevator opens to a corridor enclosed with a fire barrier, provided all doors opening onto such corridor are smoke and draft controlled doors complying with Section 716.5.3.1 with the UL 1784 test conducted without the artificial bottom seal. 3. A fire service access elevator lobby shall not be required on stories that are less than 3,000 square feet (279 m2) containing only Group R-2 occupancies. | 3007.6 Fire service access elevator lobby. | The fire service access elevator shall open into an enclosed fire service access elevator lobby in accordance with Sections 3007.6.1 through 3007.6.5. Egress is permitted through the enclosed elevator lobby in accordance with Item 1 of Section 1016.2. Exception: Where a fire service access elevator has two entrances onto a floor, the second entrance shall be permitted to be protected in accordance with Section 3006.3.
3004.4 Reserved.
3004.5 Amusement devices. | Amusement devices shall comply with rules of the department.
3005.2 Temperature control. | Elevator machine rooms, machinery spaces that contain the driving machine, and control rooms or spaces that contain the operation or motion controller for elevator operation shall be provided with an independent ventilation or air-conditioning system to protect against the overheating of the electrical equipment. The system shall be capable of maintaining temperatures within the range established for the elevator equipment.
3005.5 Sprinklers and shunt trip. | Sprinklers are not permitted in elevator machine rooms, machine spaces, control rooms and control spaces. Where elevator hoistways are protected with automatic sprinklers, a means installed in accordance with Section 21.4 of NFPA 72 as modified by Appendix Q shall be provided, where required, to disconnect automatically the main line power supply to the affected elevator prior to the application of water. This means shall not be self-resetting. The activation of automatic sprinklers outside the hoistway, machine room, machinery space, control room or control space shall not disconnect the main line power supply.
3005.7 Elevator machinery noise control in multiple dwellings. | Gear-driven machinery, gearless machinery, and motor generators located in an elevator machinery room or shaft on a roof, or on a floor other than a floor on grade, shall be supported on vibration isolator pads having a minimum thickness of ½ inch (12.7 mm).
3006.1 Elevator, dumbwaiter and other hoistways. | Elevator, dumbwaiter, and other hoistway enclosures shall be constructed in accordance with Section 713 and Chapter 30.
3006.1.1 Elevator lobby. | Except as provided by Sections 403.6.1 and 403.6.2, an enclosed elevator lobby shall be provided in high-rise buildings at the following locations: 1. Elevators opening onto a fire-resistance-rated corridor, in all occupancy groups. 2. Elevators serving Group B occupancies. Elevators that serve four or more stories that contain space classified in occupancy Group B, inclusive of any lobby or entrance level, shall provide elevator lobbies at every level served by such elevator. The lobby enclosure shall separate the elevator shaft enclosure doors from each floor by smoke partitions. In addition to the requirements in Section 710 for smoke partitions, doors protecting openings in the elevator lobby enclosure walls shall also comply with Section 710.5.2.3 and penetrations of the elevator lobby enclosure by ducts and air transfer openings shall be protected in accordance with Section 710.8. Elevator lobbies shall have at least one means of egress complying with Chapter 10 and other provisions within this code. Access to an exit on any story through an elevator lobby shall be permitted provided that access to at least one other required exit does not require passing through the elevator lobby. Exceptions: 1. Enclosed elevator lobbies are not required at the street floor, provided the entire street floor is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. 2. Elevators not required to be located in a shaft in accordance with Section 712 are not required to have enclosed elevator lobbies. 3. Enclosed elevator lobbies are not required where zero-clearance doors are provided at the hoistway opening in accordance with Section 3002.6. Such doors shall be tested in accordance with UL 1784 without an artificial bottom seal. 4. Enclosed elevator lobbies are not required on floors with less than 2,500 square feet (232 m2), provided that the commissioner accepts an alternative design or construction method that accomplishes the purposes of this section, or provided that the commissioner determines that compliance with this section is impracticable in whole or in part, whereby the commissioner may authorize an exemption from the requirements of this section. 5. Enclosed elevator lobbies are not required on Group R-2 occupied floors. 6. Enclosed elevator lobbies are not required where the elevator hoistway is pressurized in accordance with Section 3006.1.2. 7. Enclosed elevator lobbies are not required where the elevator serves only open parking garages in accordance with Section 406.5.
3006.1.1.1 Areas of rescue assistance. | Areas of rescue assistance shall be provided as required in Section 1009.6.
3006.1.2 Enclosed elevator lobby. | Where elevator hoistway pressurization is provided in lieu of required enclosed elevator lobbies, the pressurization system shall comply with this section except as provided by Sections 403.6.1 and 403.6.2.
3006.1.2.1 Pressurization requirements. | Elevator hoistways shall be pressurized to maintain a minimum positive pressure of 0.10 inches of water (25 Pa) and a maximum positive pressure of 0.25 inches of water (67 Pa) with respect to adjacent occupied space on all floors. This pressure shall be measured at the midpoint of each hoistway door, with all elevator cars at the floor of recall and all hoistway doors on the floor of recall open and all other hoistway doors closed. The opening and closing of hoistway doors at each level must be demonstrated during this test. The supply air intake shall be from an outside, uncontaminated source located a minimum distance of 20 feet (6096 mm) from any air exhaust system or outlet.
3006.1.2.2 Rational analysis. | A rational analysis complying with Section 909.4 shall be submitted with the construction documents.
3006.1.2.3 Ducts for system. | Any duct system that is part of the pressurization system shall be protected with the same fire-resistance rating as required for the elevator shaft enclosure.
3006.1.2.4 Fan system. | The fan system provided for the pressurization system shall be as required by this section.
3006.1.2.4.1 Fire resistance. | When located within the building, the fan system that provides the pressurization shall be protected with the same fire-resistance rating required for the elevator shaft enclosure.
3006.1.2.4.2 Smoke detection. | The fan system shall be equipped with a smoke detector that will automatically shut down the fan system when smoke is detected within the system.
3006.1.2.4.3 Separate systems. | A separate fan system shall be used for each elevator hoistway.
3006.1.2.4.4 Fan capacity. | The supply fan shall either be adjustable with a capacity of at least 1,000 cfm (0.4719 m3/s) per door, or that specified by a registered design professional to meet the requirements of a designed pressurization system.
3006.1.2.5 Standby power. | The pressurization system shall be provided with standby power from the same source as other required emergency systems for the building.
3006.1.2.6 Activation of pressurization system. | The elevator pressurization system shall be activated upon activation of the building fire alarm system or upon activation of the elevator lobby smoke detectors. Where both a building fire alarm system and elevator lobby smoke detectors are present, each shall be independently capable of activating the pressurization system.
3006.1.2.7 Special inspection. | Special inspection for performance shall be required in accordance with Section 909.18.8. System acceptance shall be in accordance with Section 909.19.
3006.1.2.8 Marking and identification. | Detection and control systems shall be marked in accordance with Section 909.14.
3006.1.2.9 Control diagrams. | Control diagrams shall be provided in accordance with Section 909.15.
3006.1.2.10 Control panel. | A fire-fighter’s smoke control panel complying with Section 909.16 shall be provided.
3006.1.2.11 System response time. | Hoistway pressurization systems shall comply with the requirements for smoke control system response time in Section 909.17.
3007.4 Reserved.
3007.6.1 Reserved.
3007.6.2 Lobby enclosure. | The fire service access elevator lobby shall be enclosed with a smoke barrier having a fire-resistance rating of not less than 1 hour, except that lobby doorways shall comply with Section 3007.6.3. Exception: Enclosed fire service access elevator lobbies are not required at the levels of exit discharge. | 3007.6.2 Lobby enclosure. | The fire service access elevator lobby shall be enclosed with a smoke barrier having a fire-resistance rating of not less than 1 hour, except that lobby doorways shall comply with Section 3007.6.3. Exception: Enclosed fire service access elevator lobbies are not required at the levels of exit discharge.
3007.6.3 Lobby doorways. | Other than doors to the hoistway, elevator control room or elevator control space, each doorway to a fire service access elevator lobby shall be provided with a ¾-hour fire door assembly complying with Section 716.5. The fire door assembly shall comply with the smoke and draft control door assembly requirements of Section 716.5.3.1 with the UL 1784 test conducted without the artificial bottom seal. | 3007.6.3 Lobby doorways. | Other than doors to the hoistway, elevator control room or elevator control space, each doorway to an enclosed fire service access elevator lobby shall be provided with a 3/4-hour fire door assembly complying with Section 716. The fire door assembly shall comply with the smoke and draft control door assembly requirements of Section 716.2.2.1.1 and be tested in accordance with UL 1784 without an artificial bottom seal.
3007.6.4 Lobby size. | The enclosed fire service access elevator lobby shall be not less than 120 square feet (11 m2) in an area with a minimum dimension of 6 feet (1828 mm). | 3007.6.4 Lobby size. | Regardless of the number of fire service access elevators served by the same elevator lobby, the enclosed fire service access elevator lobby shall be not less than 150 square feet (14 m2) in an area with a dimension of not less than 8 feet (2440 mm).
3007.6.5 Fire service access elevator symbol. | A pictorial symbol of a standardized design designating which elevators are fire service access elevators shall be installed on each side of the hoistway door frame on the portion of the frame at right angles to the fire service access elevator lobby. The fire service access elevator symbol shall be designed as shown in Figure 3007.6.5 and shall comply with the following: | 3007.6.5 Fire service access elevator symbol. | A pictorial symbol of a standardized design designating which elevators are fire service access elevators shall be installed on each side of the hoistway door frame on the portion of the frame at right angles to the fire service access elevator lobby. The fire service access elevator symbol shall be designed as shown in Figure 3007.6.5 and shall comply with the following:
3007.7 Elevator system monitoring. | The fire service access elevator shall be continuously monitored at the fire command center by a standard emergency service interface system meeting the requirements of NFPA 72 as modified by Appendix Q. | 3007.7 Elevator system monitoring. | The fire service access elevator shall be continuously monitored at the fire command center by a standard emergency service interface system meeting the requirements of NFPA 72.
3007.8 Electrical power. | The following features serving each fire service access elevator shall be supplied by both normal power and Type 60/Class 6/Level 1 standby power: 1. Elevator equipment. 2. Elevator hoistway lighting. 3. Ventilation and cooling equipment for elevator machine rooms, control rooms, machine spaces and machinery/control spaces. 4. Elevator car lighting. Exception: Standby power relying on natural gas as a fuel source need not be Class 6. | 3007.8 Electrical power. | The following features serving each fire service access elevator shall be supplied by both normal power and Type 60/Class 2/Level 1 standby power:
3007.8.1 Protection of wiring or cables. | Wires or cables that are located outside of the elevator hoistway and machine room and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to fire service access elevators shall be protected by construction having a fire-resistance rating of not less than 2 hours, shall be a circuit integrity cable having a fire-resistance rating of not less than 2 hours or shall be protected by a listed electrical protective system having a fire-resistance rating of not less than 2 hours. Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operations. | 3007.8.1 Protection of wiring or cables. | Wires or cables that are located outside of the elevator hoistway and machine room and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to fire service access elevators shall be protected using one of the following methods: 1. Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 2 hours. 2. Electrical circuit protective systems shall have a fire-resistance rating of not less than 2 hours. Electrical circuit protective systems shall be installed in accordance with their listing requirements. 3. Construction having a fire-resistance rating of not less than 2 hours. Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operations.
3007.9 Reserved.
3008.1 General. | Where elevators are to be used for occupant self-evacuation during fires, all passenger elevators for general public use shall comply with Sections 3008.1 through 3008.10. Where other elevators are used for occupant self-evacuation, those elevators shall comply with these sections. | 3008.1 General. | Elevators used for occupant self-evacuation during fires shall comply with Sections 3008.1 through 3008.10.
3008.1.1 Additional exit stairway. | Where an additional means of egress is required in accordance with Section 403.5.2, an additional exit stairway shall not be required to be installed in buildings provided with occupant evacuation elevators complying with Section 3008.1.
3008.1.2 Fire safety and emergency action plans. | The building shall have approved fire safety and emergency action plans in accordance with the applicable requirements of the New York City Fire Code. The fire safety and emergency action plans shall incorporate specific procedures for the occupants using evacuation elevators.
3008.1.3 Operation. | The occupant evacuation elevators shall be used for occupant self-evacuation in accordance with the occupant evacuation operation requirements as per ASME A17.1/CSA B44 as modified by Appendix K of this code and the building’s fire safety and emergency action plans.
3008.2 Reserved.
3008.3 Automatic sprinkler system. | The building shall be protected throughout by an approved, electrically-supervised automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3008.3.1.
3008.3.1 Prohibited locations. | Automatic sprinklers shall not be installed in elevator machine rooms, machinery spaces, control rooms, control spaces and elevator hoistways of occupant evacuation elevators.
3008.3.2 Sprinkler system monitoring. | The sprinkler system shall have a sprinkler control valve supervisory switch and water flow initiating device provided for each floor that is monitored by the building’s fire alarm system.
3008.4 Water protection. | An approved method to prevent water from infiltrating into the hoistway enclosure from the operation of the automatic sprinkler system outside the enclosed occupant evacuation elevator lobby shall be provided.
3008.5 Reserved.
3008.6 Hoistway enclosure protection. | Occupant evacuation elevator hoistways shall be located in shaft enclosures complying with Section 713.
3008.6.1 Structural integrity of hoistway enclosures. | Occupant evacuation elevator hoistway enclosures shall comply with Sections 403.2.3.1 through 403.2.3.4.
3008.7 Occupant evacuation elevator lobby. | The occupant evacuation elevators shall open into an elevator lobby in accordance with Sections 3008.7.1 through 3008.7.6. Egress is permitted through the elevator lobby in accordance with Item 1 of Section 1016.2.
3008.7.1 Access to interior exit stairway or ramp. | The occupant evacuation elevator lobby shall have direct access from the enclosed elevator lobby to an interior exit stairway or ramp. Exception: Access to an interior exit stairway or ramp shall be permitted to be through a protected path of travel protected with smoke partitions complying with Section 711. The protected path shall be separated from the enclosed elevator lobby through an opening protected by a smoke and draft control assembly in accordance with Section 716.5.3.
3008.7.2 Lobby enclosure. | The occupant evacuation elevator lobby shall be enclosed with a smoke barrier having a fire-resistance rating of not less than 1 hour, except that lobby doorways shall comply with Section 3008.7.3. Exception: Enclosed occupant evacuation elevator lobbies are not required at the levels of exit discharge.
3008.7.3 Lobby doorways. | Other than doors to the hoistway, and elevator machine rooms, machinery spaces, control rooms, and control spaces within the lobby enclosure smoke barrier, each doorway to an occupant evacuation elevator lobby shall comply with the smoke and draft control assembly requirements of Section 716.5.3.1 with the UL 1784 test conducted without the artificial bottom seal. Such doorway shall not be required to have a fire-resistance rating.
3008.7.3.1 Vision panel. | A vision panel shall be installed in each door assembly protecting the lobby doorway. The vision panel shall consist of glazing and shall be located to furnish clear vision of the occupant evacuation elevator lobby.
3008.7.3.2 Door closing. | Each door assembly protecting the lobby doorway shall be automatic closing upon receipt of any fire alarm signal from the emergency voice/alarm communication system serving the building.
3008.7.4 Lobby size. | Each occupant evacuation elevator lobby shall have minimum floor area as follows: 1. The occupant evacuation elevator lobby floor area shall accommodate, at 3 square feet (0.28 m2) per person, not less than 25 percent of the occupant load of the floor area served by the lobby. 2. The occupant evacuation elevator lobby floor area shall accommodate one wheelchair space of 30 inches by 48 inches (760 mm by 1220 mm) for each 50 persons, or portion thereof, of the occupant load of the floor area served by the lobby. Exception: The size of lobbies serving multiple banks of elevators shall have the minimum floor area approved on an individual basis and shall be consistent with the building’s fire safety and emergency action plans.
3008.7.5 Signage. | An approved sign indicating elevators are suitable for occupant self-evacuation shall be posted on all floors adjacent to each elevator call station serving occupant evacuation elevators.
3008.7.6 Two-way communication system. | A two-way communication system shall be provided in each occupant evacuation elevator lobby for the purpose of initiating communication with the fire command center or an alternate location approved by the Fire Department. The two-way communication system shall be designed and installed in accordance with Sections 1009.8.1 and 1009.8.2.
3008.8 Elevator system monitoring. | The occupant evacuation elevators shall be continuously monitored at the fire command center or a central control point approved by the Fire Department and arranged to display all of the following information:
3008.8.1 Elevator recall. | The fire command center or an alternate location approved by the Fire Department shall be provided with the means to manually initiate a Phase I Emergency Recall of the occupant evacuation elevators in accordance with ASME A17.1/CSA B44 as modified by Appendix K of this code.
3008.9 Electrical power. | The following features serving each occupant evacuation elevator shall be supplied by both normal power and Type 60/Class 6/Level 1 standby power: 1. Elevator equipment. 2. Ventilation and cooling equipment for elevator machine rooms, control rooms, machinery and control spaces. 3. Elevator car lighting. Exceptions: 1. Standby power relying on natural gas as a fuel source need not be Class 6. 2. Where Exception 2 of Section 403.5.2 is utilized, the standby power generating equipment need only be sized to satisfy the loads required to simultaneously operate those elevators identified in the timed egress analysis described in Exception 2.2.
3008.9.1 Protection of wiring or cables. | Wires or cables that are located outside of the elevator hoistway, machine room, control room and control space and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to occupant evacuation elevators shall be protected by construction having a fire-resistance rating of not less than 2 hours, or shall be circuit integrity cable having a fire-resistance rating of not less than 2 hours, or shall be protected by a listed electrical circuit protective system having a fire-resistance rating of not less than 2 hours. Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operation.
3008.10 Emergency voice/alarm communication system. | The building shall be provided with an emergency voice/alarm communication system. The emergency voice/alarm communication system shall be accessible to the Fire Department. The system shall be provided in accordance with Section 907.5.2.2.
3008.10.1 Notification appliances. | Not fewer than one audible and one visible notification appliance shall be installed within each occupant evacuation elevator lobby.
3008.11 Hazardous material areas. | No building areas shall contain hazardous materials exceeding the maximum allowable quantities per control area as addressed in Section 414.2.
3009.1 Required. | No service equipment shall be placed in operation until a service equipment certificate of compliance has been obtained in accordance with the provisions of this code.
3009.2 Posting of inspection certificate. | At the time a service equipment Certificate of Compliance is issued, an inspection certificate issued by the commissioner shall be posted. No such inspection certificate shall be issued for elevators that are not subject to periodic inspections pursuant to this code. The inspection certificate shall be in such form as the commissioner shall determine by rule and shall be posted in a frame with a transparent cover in the car of every passenger and freight elevator and on or near every escalator and moving walk and power-operated scaffold.
3009.2.1 Alternate posting locations. | In lieu of posting the inspection certificate in those locations specified in this section, the inspection certificate may be kept in the on-site building manager’s office. In such case, the building manager’s office must be open during normal business hours. In addition, notice must be posted in each location listed in Section 3009.2 and kept in a frame with a transparent cover, or a plaque or on the car operating panel, with an indelible inscription, stating that the inspection certificate is located in the building manager’s office and identifying the location of such office.
3009.3 Temporary use certificates. | The commissioner may issue temporary use certificates for any equipment or device regulated by this code, except power-operated scaffolds, provided that such partial use and operation may be made safely and without endangering public health, safety, and welfare and provided further that such temporary use certificate shall not be issued for a period of more than 30 calendar days, subject to renewal for additional 30-day periods at the discretion of the commissioner. Temporary use certificates for elevators shall also be conditioned upon compliance with the following:
3009.3.1 Posting of temporary use certificate. | The temporary use certificate shall be posted in a conspicuous location on, or adjacent to, the device covered by the certificate and shall state that the device has not been finally approved by the commissioner.
3010.1 Elevator operators. | With the exception of automatic operation elevators, every passenger and freight elevator with a rise of more than one story shall be in the charge of a designated competent operator, who shall be at least 18 years old and selected with consideration of his or her abilities to perform his or her duties in a careful and competent manner. Such designated competent operator shall be instructed in the safe and proper operation of the equipment.
3010.2 Amusement device operators. | Operators of amusement devices shall meet the requirements of rules of the department.
3010.3 Other device operators. | Other devices regulated by this code shall, when deemed necessary by the commissioner to protect public safety, be in the charge of a designated competent operator conforming to such qualifications as the commissioner may prescribe, except that operators for workers’ hoists shall be assigned as required by the applicable provisions of ANSI A10.4.
3010.4 Sanction for unlawful operation. | If the commissioner finds that any person engaged in operating an elevator, amusement, or other device is not competent to operate the elevator, amusement or other device, the owner, agent or lessee of such elevator, amusement, or other device shall, upon notice from the commissioner, discontinue the operation of such device by such operator.
3011.1 Signage. | When an existing or new automatic passenger elevator in any building or structure is being serviced, repaired, inspected or tested by an elevator company, or elevator personnel, and there are no elevator personnel available to remain in the elevator car, “CAUTION” sign tapes shall be placed across the car door jamb. One strip of “CAUTION” sign tape shall be placed at a height of 18 inches (457 mm) above the car floor and another strip of “CAUTION” sign tape shall be placed at a height of 54 inches (1372 mm) above the car floor.
3011.1.1 Sign tape. | The “CAUTION” sign tape shall be 3 inches (76 mm) in width with the words “CAUTION – DO NOT ENTER” repeated every 6 inches (152 mm). The lettering shall be black on yellow background. The letters shall be at least 2 inches (51 mm) high. Caution tape may be replaced with OSHA approved elevator barricades.
3011.1.2 Elevator out of service. | When an elevator is out of service with the car door open at a landing prior to the elevator personnel arriving, Sections 3011.1 and 3011.1.1 shall apply.
3012.1 Accidents. | The owner of any device regulated by this chapter shall promptly notify the commissioner of every accident involving injury to any person requiring the services of Emergency Medical Service (EMS) or damage to property or to apparatus exceeding $5,000 on, about, or in connection with such equipment, before commencing any repairs and shall afford the commissioner every facility for investigating such accident or damage. The commissioner shall make an investigation immediately thereafter, and shall prepare a full and complete report of such investigation. Such report shall give in detail all material facts and information available and the cause or causes as far as they can be determined. Such report shall be a public record. When an accident involves the failure or destruction of any part of the construction or operating mechanism of such equipment, no such equipment shall be used until it has been made safe, and re-inspected by the commissioner. The commissioner may order the discontinuance of such equipment until a new service equipment certificate has been issued by him or her for its use. No part shall be removed from the premises of the damaged construction or operating mechanism until permission to do so has been granted by the commissioner.
3013.1 General. | Existing installations shall be modified in accordance with Appendix K, Chapter K3.
3014.1 Elevators and conveying systems. | Inspection and testing of elevators and conveying systems shall be in accordance with Appendix K, including Table N1. Refer to Chapter 3 of Title 28 of the Administrative Code for additional requirements.
3014.2 Amusement devices. | Inspection and testing of amusement devices shall comply with rules of the department. Refer to Chapter 3 of Title 28 of the Administrative Code for additional requirements. Installation of amusement devices shall be subject to the requirements for special and progress inspections.
|  | 3001.2 Emergency elevator communication systems for the deaf, hard of hearing and speech impaired. | An emergency two-way communication system shall be provided. The system shall provide visible text and audible modes that meet all of the following requirements:
|  | 3001.3 Referenced standards. | Except as otherwise provided for in this code, the design, construction, installation, alteration, repair and maintenance of elevators and conveying systems and their components shall conform to the applicable standard specified in Table 3001.3 and ASCE 24 for construction in flood hazard areas established in Section 1612.3. | See BC30 Tables and Figures
|  | 3001.4 Accessibility. | Passenger elevators required to be accessible or to serve as part of an accessible means of egress shall comply with Sections 1009 and 1110.8.
|  | 3001.5 Change in use. | A change in use of an elevator from freight to passenger, passenger to freight, or from one freight class to another freight class shall comply with Section 8.7 of ASME A17.1/CSA B44.
|  | 3002.1.1 Opening protectives. | Openings in hoistway enclosures shall be protected as required in Chapter 7. Exception: The elevator car doors and the associated hoistway enclosure doors at the floor level designated for recall in accordance with Section 3003.2 shall be permitted to remain open during Phase I Emergency Recall Operation.
|  | 3002.1.2 Hardware. | Hardware on opening protectives shall be of an approved type installed as tested, except that approved interlocks, mechanical locks and electric contacts, door and gate electric contacts and door-operating mechanisms shall be exempt from the fire test requirements.
|  | 3002.4 Elevator car to accommodate ambulance stretcher. | Where elevators are provided in buildings four or more stories above, or four or more stories below, grade plane, not fewer than one elevator shall be provided for fire department emergency access to all floors. The elevator car shall be of such a size and arrangement to accommodate an ambulance stretcher 24 inches by 84 inches (610 mm by 2134 mm) with not less than 5-inch (127 mm) radius corners, in the horizontal, open position and shall be identified by the international symbol for emergency medical services (star of life). The symbol shall be not less than 3 inches (76 mm) in height and shall be placed inside on both sides of the hoistway door frame.
|  | 3003.2 Fire fighters’ emergency operation. | Elevators shall be provided with Phase I emergency recall operation and Phase II emergency in-car operation in accordance with ASME A17.1/CSA B44.
|  | 3003.3 Standardized fire service elevator keys. | All elevators shall be equipped to operate with a standardized fire service elevator key in accordance with the International Fire Code.
|  | 3004.4 Personnel and material hoists. | Personnel and material hoists shall be designed utilizing an approved method that accounts for the conditions imposed during the intended operation of the hoist device. The design shall include, but is not limited to, anticipated loads, structural stability, impact, vibration, stresses and seismic restraint. The design shall account for the construction, installation, operation and inspection of the hoist tower, car, machinery and control equipment, guide members and hoisting mechanism. Additionally, the design of personnel hoists shall include provisions for field testing and maintenance that will demonstrate that the hoist device functions in accordance with the design. Field tests shall be conducted upon the completion of an installation or following a major alteration of a personnel hoist.
|  | 3005.2 Venting. | Elevator machine rooms, machinery spaces that contain the driving machine, and control rooms or spaces that contain the operation or motion controller for elevator operation shall be provided with an independent ventilation or air-conditioning system to protect against the overheating of the electrical equipment. The system shall be capable of maintaining temperatures within the range established for the elevator equipment.
|  | 3005.5 Shunt trip. | Where elevator hoistways, elevator machine rooms, control rooms and control spaces containing elevator control equipment are protected with automatic sprinklers, a means installed in accordance with Section 21.4 of NFPA 72 shall be provided to automatically disconnect the main line power supply to the affected elevator prior to the application of water. This means shall not be self-resetting. The activation of automatic sprinklers outside the hoistway, machine room, machinery space, control room or control space shall not disconnect the main line power supply.
|  | 3006.1 General. | Elevator hoistway openings and enclosed elevator lobbies shall be provided in accordance with the following:
|  | 3006.2 Hoistway opening protection required. | Elevator hoistway door openings shall be protected in accordance with Section 3006.3 where an elevator hoistway connects more than three stories, is required to be enclosed within a shaft enclosure in accordance with Section 712.1.1 and any of the following conditions apply: 1. The building is not protected throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2. 2. The building contains a Group I-1, Condition 2 occupancy. 3. The building contains a Group I-2 occupancy. 4. The building contains a Group I-3 occupancy. 5. The building is a high rise and the elevator hoistway is more than 75 feet (22 860 mm) in height. The height of the hoistway shall be measured from the lowest floor to the highest floor of the floors served by the hoistway. Exceptions: 1. Protection of elevator hoistway door openings is not required where the elevator serves only open parking garages in accordance with Section 406.5. 2. Protection of elevator hoistway door openings is not required at the level(s) of exit discharge, provided that the level(s) of exit discharge is equipped with an automatic sprinkler system in accordance with Section 903.3.1.1. 3. Enclosed elevator lobbies and protection of elevator hoistway door openings are not required on levels where the elevator hoistway opens to the exterior.
|  | 3006.2.1 Rated corridors. | Where corridors are required to be fire-resistance rated in accordance with Section 1020.2, elevator hoistway openings shall be protected in accordance with Section 3006.3.
|  | 3006.3 Hoistway opening protection. | Where Section 3006.2 requires protection of the elevator hoistway door opening, the protection shall be provided by one of the following:
|  | 3006.4 Means of egress. | Elevator lobbies shall be provided with not less than one means of egress complying with Chapter 10 and other provisions in this code. Egress through an enclosed elevator lobby shall be permitted in accordance with Item 1 of Section 1016.2.
|  | 3007.4 Shunt trip. | Means for elevator shutdown in accordance with Section 3005.5 shall not be installed on elevator systems used for fire service access elevators.
|  | 3007.6.1 Access to interior exit stairway or ramp. | The enclosed fire service access elevator lobby shall have direct access from the enclosed elevator lobby to an enclosure for an interior exit stairway or ramp. Exception: Access to an interior exit stairway or ramp shall be permitted to be through a protected path of travel that has a level of fire protection not less than the elevator lobby enclosure. The protected path shall be separated from the enclosed elevator lobby through an opening protected by a smoke and draft control assembly in accordance Section 716.2.2.1. Exceptions: 1. Access to an interior exit stairway or ramp shall be permitted to be through a protected path of travel that has a level of fire protection not less than the elevator lobby enclosure. The protected path shall be separated from the enclosed elevator lobby through an opening protected by a smoke and draft control assembly in accordance Section 716.2.2.1. 2. Elevators that only service an open parking garage and the lobby of the building shall not be required to provide direct access.
|  | 3007.9 Standpipe hose connection. | A Class I standpipe hose connection in accordance with Section 905 shall be provided in the interior exit stairway and ramp having direct access from the enclosed fire service access elevator lobby.
|  | 3007.9.1 Access. | The exit enclosure containing the standpipe shall have access to the floor without passing through the enclosed fire service access elevator lobby.
|  | 3008.1.1 Number of occupant evacuation elevators. | The number of elevators available for occupant evacuation shall be determined based on an egress analysis that addresses one of the following scenarios:
|  | 3008.1.2 Additional exit stairway. | Where an additional means of egress is required in accordance with Section 403.5.2, an additional exit stairway shall not be required to be installed in buildings provided with occupant evacuation elevators complying with Section 3008.1.
|  | 3008.1.3 Fire safety and evacuation plan. | The building shall have an approved fire safety and evacuation plan in accordance with the applicable requirements of Section 404 of the International Fire Code. The fire safety and evacuation plan shall incorporate specific procedures for the occupants using evacuation elevators.
|  | 3008.1.4 Operation. | The occupant evacuation elevators shall be used for occupant self-evacuation in accordance with the occupant evacuation operation requirements in ASME A17.1/CSA B44 and the building’s fire safety and evacuation plan.
|  | 3008.2 Automatic sprinkler system. | The building shall be equipped throughout with an approved, electrically supervised automatic sprinkler system in accordance with Section 903.3.1.1, except as otherwise permitted by Section 903.3.1.1.1 and as prohibited by Section 3008.2.1.
|  | 3008.2.1 Prohibited locations. | Automatic sprinklers shall not be installed in elevator machine rooms, machinery spaces, control rooms, control spaces and elevator hoistways of occupant evacuation elevators.
|  | 3008.2.2 Sprinkler system monitoring. | The automatic sprinkler system shall have a sprinkler control valve supervisory switch and water-flow-initiating device provided for each floor that is monitored by the building’s fire alarm system.
|  | 3008.3 Water protection. | Water from the operation of an automatic sprinkler system outside the enclosed lobby shall be prevented from infiltrating into the hoistway enclosure in accordance with an approved method.
|  | 3008.4 Shunt trip. | Means for elevator shutdown in accordance with Section 3005.5 shall not be installed on elevator systems used for occupant evacuation elevators.
|  | 3008.5 Hoistway enclosure protection. | Occupant evacuation elevator hoistways shall be located in shaft enclosures complying with Section 713.
|  | 3008.5.1 Structural integrity of hoistway enclosures. | Occupant evacuation elevator hoistway enclosures shall comply with Sections 403.2.2.1 through 403.2.2.4.
|  | 3008.6 Occupant evacuation elevator lobby. | Occupant evacuation elevators shall open into an enclosed elevator lobby in accordance with Sections 3008.6.1 through 3008.6.6. Egress is permitted through the elevator lobby in accordance with Item 1 of Section 1016.2.
|  | 3008.6.1 Access to interior exit stairway or ramp. | The occupant evacuation elevator lobby shall have direct access from the enclosed elevator lobby to an interior exit stairway or ramp.
|  | 3008.6.2 Lobby enclosure. | The occupant evacuation elevator lobby shall be enclosed with a smoke barrier having a fire-resistance rating of not less than 1 hour, except that lobby doorways shall comply with Section 3008.6.3. Exception: Enclosed occupant evacuation elevator lobbies are not required at the levels of exit discharge.
|  | 3008.6.3 Lobby doorways. | Other than the doors to the hoistway, elevator machine rooms, machinery spaces, control rooms and control spaces within the lobby enclosure smoke barrier, each doorway to an occupant evacuation elevator lobby shall be provided with a 3/4-hour fire door assembly complying with Section 716. The fire door assembly shall comply with the smoke and draft control assembly requirements of Section 716.2.2.1.1 and be tested in accordance with UL 1784 without an artificial bottom seal.
|  | 3008.6.3.1 Vision panel. | A vision panel shall be installed in each fire door assembly protecting the lobby doorway. The vision panel shall consist of fire-protection-rated glazing, shall comply with the requirements of Section 716 and shall be located to furnish clear vision of the occupant evacuation elevator lobby.
|  | 3008.6.3.2 Door closing. | Each fire door assembly protecting the lobby doorway shall be automatic-closing upon receipt of any fire alarm signal from the emergency voice/alarm communication system serving the building.
|  | 3008.6.4 Lobby size. | Each occupant evacuation elevator lobby shall have minimum floor area as follows: 1. The occupant evacuation elevator lobby floor area shall accommodate, at 3 square feet (0.28 m2) per person, not less than 25 percent of the occupant load of the floor area served by the lobby. 2. The occupant evacuation elevator lobby floor area shall accommodate one wheelchair space of 30 inches by 52 inches (760 mm by 1320 mm) for each 50 persons, or portion thereof, of the occupant load of the floor area served by the lobby. Exception: The size of lobbies serving multiple banks of elevators shall have the minimum floor area approved on an individual basis and shall be consistent with the building’s fire safety and evacuation plan.
|  | 3008.6.5 Signage. | An approved sign indicating elevators are suitable for occupant self-evacuation shall be posted on all floors adjacent to each elevator call station serving occupant evacuation elevators.
|  | 3008.6.6 Two-way communication system. | A two-way communication system shall be provided in each occupant evacuation elevator lobby for the purpose of initiating communication with the fire command center or an alternate location approved by the fire department. The two-way communication system shall be designed and installed in accordance with Sections 1009.8.1 and 1009.8.2.
|  | 3008.7 Elevator system monitoring. | The occupant evacuation elevators shall be continuously monitored at the fire command center or a central control point approved by the fire department and arranged to display all of the following information:
|  | 3008.7.1 Elevator recall. | The fire command center or an alternate location approved by the fire department shall be provided with the means to manually initiate a Phase I Emergency Recall of the occupant evacuation elevators in accordance with ASME A17.1/CSA B44.
|  | 3008.8 Electrical power. | The following features serving each occupant evacuation elevator shall be supplied by both normal power and Type 60/Class 2/Level 1 standby power:
|  | 3008.8.1 Determination of standby power load. | Standby power loads shall be based on the determination of the number of occupant evacuation elevators in Section 3008.1.1.
|  | 3008.8.2 Protection of wiring or cables. | Wires or cables that are located outside of the elevator hoistway, machine room, control room and control space and that provide normal or standby power, control signals, communication with the car, lighting, heating, air conditioning, ventilation and fire-detecting systems to occupant evacuation elevators shall be protected using one of the following methods: 1. Cables used for survivability of required critical circuits shall be listed in accordance with UL 2196 and shall have a fire-resistance rating of not less than 2 hours. 2. Electrical circuit protective systems shall have a fire-resistance rating of not less than 2 hours. Electrical circuit protective systems shall be installed in accordance with their listing requirements. 3. Construction having a fire-resistance rating of not less than 2 hours. Exception: Wiring and cables to control signals are not required to be protected provided that wiring and cables do not serve Phase II emergency in-car operation.
|  | 3008.9 Emergency voice/alarm communication system. | The building shall be provided with an emergency voice/alarm communication system. The emergency voice/alarm communication system shall be accessible to the fire department. The system shall be provided in accordance with Section 907.5.2.2.
|  | 3008.9.1 Notification appliances. | Not fewer than one audible and one visible notification appliance shall be installed within each occupant evacuation elevator lobby.
|  | 3008.10 Hazardous material areas. | Building areas shall not contain hazardous materials exceeding the maximum allowable quantities per control area as addressed in Section 414.2.

## BC31
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
3101.1 Scope. | The provisions of this chapter shall govern special building construction including membrane structures, temporary structures, pedestrian walkways and tunnels, automatic vehicular gates, awnings, canopies, sun control devices, marquees, signs, telecommunications towers and antennas, swimming pools and enclosures, sidewalk cafés, and fences. | 3101.1 Scope. | The provisions of this chapter shall govern special building construction including membrane structures, temporary structures, pedestrian walkways and tunnels, automatic vehicular gates, awnings and canopies, marquees, signs, towers, antennas, relocatable buildings, swimming pool enclosures and safety devices, solar energy systems, public use restroom buildings on publicly owned lands in flood hazard areas and intermodal shipping containers.
3102.1 General. | The provisions of Sections 3102.1 through 3102.8 shall apply to air-supported structures, air-inflated structures, membrane-covered cable structures, membrane-covered frame structures and tents, and tensile membrane structures, collectively known as membrane structures. | 3102.1 General. | The provisions of Sections 3102.1 through 3102.8 shall apply to air-supported, air-inflated, membrane-covered cable, membrane-covered frame and tensile membrane structures, collectively known as membrane structures, erected for a period of 180 days or longer. Those erected for a shorter period of time shall comply with the International Fire Code. Membrane structures covering water storage facilities, water clarifiers, water treatment plants, sewage treatment plants, greenhouses and similar facilities not used for human occupancy are required to meet only the requirements of Sections 3102.3.1 and 3102.7. Membrane structures erected on a building, balcony, deck or other structure for any period of time shall comply with this section.
3102.1.1 Certificates of Occupancy. | The duration of Certificates of Occupancy for air-inflated structures, air-supported structures, and tents shall be limited in accordance with the requirements of Chapter 1 of Title 28 of the Administrative Code.
3102.1.2 Temporary installations. | In addition to the requirements of Section 3102 of this code, temporary installations of air-supported structures, air-inflated structures, membrane-covered cable structures, tensile membrane structures, membrane-covered frame structures and tents, collectively known as membrane structures shall comply with the requirements of Article 111 of Chapter 1 of Title 28 of the Administrative Code.
3102.3 Type of construction. | Noncombustible membrane structures shall be classified as Type IIB construction. Noncombustible frame or cable-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IIB construction. Heavy timber frame-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IV construction. Other membrane structures shall be classified as Type V construction. | 3102.3 Type of construction. | Noncombustible membrane structures shall be classified as Type IIB construction. Noncombustible frame or cable-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IIB construction. Heavy timber frame-supported structures covered by an approved membrane in accordance with Section 3102.3.1 shall be classified as Type IV-HT construction. Other membrane structures shall be classified as Type V construction. Exception: Plastic less than 30 feet (9144 mm) above any floor used in greenhouses, where occupancy by the general public is not authorized, and for aquaculture pond covers is not required to meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701.
3102.2 Definitions. | The following terms are defined in Chapter 2:
3102.3.1 Membrane and interior liner material. | Membranes and interior liners shall be either noncombustible as set forth in Section 703.5, or meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 and the manufacturer’s test protocol. | 3102.3.1 Membrane and interior liner material. | Membranes and interior liners shall be either noncombustible as set forth in Section 703.3 or meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 and the manufacturer’s test protocol. Exception: Plastic less than 20 mil (0.5 mm) in thickness used in greenhouses, where occupancy by the general public is not authorized, and for aquaculture pond covers is not required to meet the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701.
3102.4 Allowable floor areas. | The area of a membrane structure shall not exceed the limitations specified in Section 506. | 3102.4 Allowable floor areas. | The area of a membrane structure shall not exceed the limitations specified in Section 506.
3102.5 Maximum height. | Membrane structures shall not exceed one story nor shall such structures exceed the height limitations in feet specified in Section 504.3. Membrane structures may be erected above the roof of a building provided that such roof is of noncombustible construction required to have a fire-resistance rating. Exception: Noncombustible membrane structures serving as roofs only. | 3102.5 Maximum height. | Membrane structures shall not exceed one story nor shall such structures exceed the height limitations in feet specified in Section 504.3. Exception: Noncombustible membrane structures serving as roofs only.
3102.6 Mixed construction. | Membrane structures shall be permitted to be utilized as specified in this section as a portion of buildings of other types of construction. Height and area limits shall be as specified for the type of construction and occupancy of the building. | 3102.6 Mixed construction. | Membrane structures shall be permitted to be utilized as specified in this section as a portion of buildings of other types of construction. Height and area limits shall be as specified for the type of construction and occupancy of the building.
3102.6.1 Noncombustible membrane. | A noncombustible membrane shall be permitted for use as the roof or as a skylight of any building or atrium of a building of any type of construction provided such membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery, and meets the fire classification requirements of Section 1505 for roof assemblies. | 3102.6.1 Noncombustible membrane. | A noncombustible membrane shall be permitted for use as the roof or as a skylight of any building or atrium of a building of any type of construction provided that the membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery.
3102.6.1.1 Membrane. | A membrane meeting the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be permitted to be used as the roof or as a skylight on buildings of Type IIB, III, IV and V construction, provided such membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery, and meets the fire classification requirements of Section 1505 for roof assemblies. | 3102.6.1.1 Membrane. | A membrane meeting the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 shall be permitted to be used as the roof or as a skylight on buildings of Type IIB, III, IV-HT and V construction, provided that the membrane is not less than 20 feet (6096 mm) above any floor, balcony or gallery.
3102.7 Engineering design. | Membrane structures, except tensile membrane structures, shall be designed and constructed to sustain dead loads; loads due to tension or inflation; live loads including wind, snow or flood and seismic loads and in accordance with Chapter 16 and Appendix G. | 3102.7 Engineering design. | The structure shall be designed and constructed to sustain dead loads; loads due to tension or inflation; live loads including wind, snow or flood and seismic loads and in accordance with Chapter 16.
3102.7.1 Lateral restraint. | For membrane-covered frame structures, the membrane shall not be considered to provide lateral restraint in the calculation of the capacities of the frame members. | 3102.7.1 Lateral restraint. | For membrane-covered frame structures, the membrane shall not be considered to provide lateral restraint in the calculation of the capacities of the frame members.
3102.8 Inflation systems. | Air-supported structures and air-inflated structures shall be provided with primary and auxiliary inflation systems to meet the minimum requirements of Sections 3102.8.1 through 3102.8.3. | 3102.8 Inflation systems. | Air-supported and air-inflated structures shall be provided with primary and auxiliary inflation systems to meet the minimum requirements of Sections 3102.8.1 through 3102.8.3.
3102.8.1 Equipment requirements. | The primary inflation system shall consist of one or more blowers and shall include provisions for automatic control to maintain the required inflation pressures. Such system shall be so designed as to prevent overpressurization of the system. | 3102.8.1 Equipment requirements. | The inflation system shall consist of one or more blowers and shall include provisions for automatic control to maintain the required inflation pressures. The system shall be so designed as to prevent overpressurization of the system.
3102.7.2 Design. | Tents, air-inflated structures, and air-supported structures shall be designed by either an alternate engineering design approved by the commissioner or as follows:
3102.8.1.1 Auxiliary inflation system. | In addition to the primary inflation system, in structures exceeding 1,500 square feet (140 m2) in area, an auxiliary inflation system shall be provided with sufficient capacity to maintain the inflation of the structure in case of primary system failure. The auxiliary inflation system shall operate automatically when there is a loss of internal pressure and when the primary blower system becomes inoperative. Initiation of auxiliary inflation system shall be indicated by an audible and visual alert at the entrance or a regularly attended location. | 3102.8.1.1 Auxiliary inflation system. | In addition to the primary inflation system, in buildings larger than 1,500 square feet (140 m2) in area, an auxiliary inflation system shall be provided with sufficient capacity to maintain the inflation of the structure in case of primary system failure. The auxiliary inflation system shall operate automatically when there is a loss of internal pressure and when the primary blower system becomes inoperative.
3102.7.3 Tensile membrane structures. | The design and construction shall be in accordance with ASCE 55. The provisions of Sections 3102.1 through 3102.6 shall also apply.
3102.8.1.2 Blower equipment. | Blower equipment shall meet all of the following requirements: | 3102.8.1.2 Blower equipment. | Blower equipment shall meet all of the following requirements:
3102.8.2 Standby power. | Wherever an auxiliary inflation system is required, an approved standby power-generating system shall be provided. However, notwithstanding Section 2702.1, the standby power-generating system shall be equipped with a suitable means for automatically starting the generator set upon failure of the normal electrical service and for automatic transfer and operation of all of the required electrical functions at full power within 60 seconds of such service failure. Standby power shall be capable of operating independently for not less than 4 hours. Initiation of standby power shall be indicated by an audible and visual alert at the entrance or a regularly attended location. | 3102.8.2 Standby power. | Wherever an auxiliary inflation system is required, an approved standby power-generating system shall be provided. The system shall be equipped with a suitable means for automatically starting the generator set upon failure of the normal electrical service and for automatic transfer and operation of all of the required electrical functions at full power within 60 seconds of such service failure. Standby power shall be capable of operating independently for not less than 4 hours.
3102.8.3 Support provisions. | A system capable of supporting the membrane in the event of deflation shall be provided for in air-supported structures and air-inflated structures having an occupant load of 50 or more or where covering a swimming pool regardless of occupant load. Such support system shall be capable of maintaining the membranes not less than 7 feet (2134 mm) above the floor, seating area or surface of the water. When air-supported structures or air-inflated structures are used as a roof on Type I or II construction buildings, such support system shall be capable of maintaining the membranes not less than 20 feet (6096 mm) above the floor or seating area. | 3102.8.3 Support provisions. | A system capable of supporting the membrane in the event of deflation shall be provided for in air-supported and air-inflated structures having an occupant load of 50 or more or where covering a swimming pool regardless of occupant load. The support system shall be capable of maintaining membrane structures used as a roof for Type I construction not less than 20 feet (6096 mm) above floor or seating areas. The support system shall be capable of maintaining other membranes not less than 7 feet (2134 mm) above the floor, seating area or surface of the water.
3103.1 General. | The provisions of Sections 3103.1 through 3103.4 shall apply to temporary tents, grandstands, platforms, reviewing stands, outdoor bandstands, stages and similar miscellaneous structures erected for a period of 90 days or less. Such structures may be constructed of wood whether located inside or outside of the fire districts. | 3103.1 General. | The provisions of Sections 3103.1 through 3103.4 shall apply to structures erected for a period of less than 180 days. Special event structures, tents, umbrella structures and other membrane structures erected for a period of less than 180 days shall also comply with the International Fire Code. Those erected for a longer period of time shall comply with applicable sections of this code.
3103.2 Construction documents. | A permit application and construction documents shall be submitted for each installation of a temporary structure. The construction documents shall include a site plan indicating the location of the temporary structure and information delineating the means of egress and the occupant load. | 3103.2 Construction documents. | A permit application and construction documents shall be submitted for each installation of a temporary structure. The construction documents, shall include a site plan indicating the location of the temporary structure and information delineating the means of egress and the occupant load.
3102.9 Separation. | No air-inflated structure, air-supported structure, or tent shall be erected closer than 20 feet (6096 mm) to any interior lot line nor closer than 30 feet (9144 mm) in any direction to an unprotected opening, required exterior stairway or corridor, or required exit door, on the same level or above the level of such structure. Such structure may abut another building on the same tax lot if the following conditions exist:
3103.3 Location. | Temporary structures shall be located in accordance with the requirements of Table 602 based on the fire-resistance rating of the exterior walls for the proposed type of construction. | 3103.3 Location. | Temporary structures shall be located in accordance with the requirements of Table 705.5 based on the fire-resistance rating of the exterior walls for the proposed type of construction. | See BC6 Tables and Figures | See BC7 Tables and Figures
3102.10 Exits. | In addition to the requirements of Chapter 10, travel distance to an exit from any point within a tent, air-supported structure, or air-inflated structure shall not exceed 75 feet (22 860 mm).
3103.4 Means of egress. | Temporary structures shall conform to the means of egress requirements of Chapter 10 and shall have an exit access travel distance of 100 feet (30 480 mm) or less. | 3103.4 Means of egress. | Temporary structures shall conform to the means of egress requirements of Chapter 10 and shall have an exit access travel distance of 100 feet (30 480 mm) or less.
3102.10.1 Exit openings from tents. | Exit openings from tents shall remain open unless covered by a flame-resistant curtain of a contrasting color to the tent. Such curtain shall be supported not less than 80 inches (2032 mm) above the floor level at the exit and, when open, no part of the curtain shall obstruct the exit.
3104.1 General. | This section shall apply to connections between buildings such as pedestrian walkways or tunnels, located at, above or below grade level, that are used as a means of travel by persons. The pedestrian walkway shall not contribute to the building area or the number of stories or height of connected buildings. | 3104.1 General. | This section shall apply to connections between buildings such as pedestrian walkways or tunnels, located at, above or below grade level, that are used as a means of travel by persons. The pedestrian walkway shall not contribute to the building area or the number of stories or height of connected buildings.
3102.10.2 Exit openings from air-supported structures and air-inflated structures. | Exit doors in air-supported structures and air-inflated structures shall close automatically against normal operational pressures. Opening force at the edge of such doors shall not exceed 15 pounds (6.80 kg), with the structure at operational pressure. Exit doors shall be located in frames constructed such that they will remain operative and support the weight of the pressurized membrane structure in a state of total collapse.
3104.1.1 Application. | Pedestrian walkways shall be designed and constructed in accordance with Sections 3104.2 through 3104.9. Tunnels shall be designed and constructed in accordance with Sections 3104.2 and 3104.10. | 3104.1.1 Application. | Pedestrian walkways shall be designed and constructed in accordance with Sections 3104.2 through 3104.9. Tunnels shall be designed and constructed in accordance with Sections 3104.2 and 3104.10.
3104.2 Separate structures. | Buildings connected by pedestrian walkways or tunnels shall be considered to be separate structures. Exceptions: 1. Buildings that are on the same tax lot and considered as portions of a single building in accordance with Section 503.1.2. 2. For purposes of calculating the number of Type B units required by Chapter 11, structurally connected buildings and buildings with multiple wings shall be considered one structure. | 3104.2 Separate structures. | Buildings connected by pedestrian walkways or tunnels shall be considered to be separate structures. Exceptions: 1. Buildings that are on the same lot and considered as portions of a single building in accordance with Section 503.1.2. 2. For purposes of calculating the number of Type B units required by Chapter 11, structurally connected build-ings and buildings with multiple wings shall be considered to be one structure.
3103.1.1 Permit required. | Temporary structures shall not be erected, operated or maintained for any purpose without obtaining a permit from the department in accordance with Section 28-111.1.1 of the Administrative Code. Exception: No permit shall be required for: 1. The erection and use of temporary tents of less than 400 gross square feet (37 m2), for not more than 30 days. 2. The erection and use of temporary platforms, reviewing stands, outdoor bandstands, and similar miscellaneous structures that cover an area less than 120 square feet (11.16 m2), including connecting areas or spaces with a common means of egress or entrance, for not more than 30 days.
3104.3 Construction. | The pedestrian walkway shall be of a Construction Type that is at least equal to the higher type of the two buildings connected. Exception: Exterior pedestrian walkways serving as a required exit shall be constructed of noncombustible materials and comply with the fire-resistance rating requirements as set forth in Chapter 7. | 3104.3 Construction. | The pedestrian walkway shall be of noncombustible construction. Exceptions: 1. Combustible construction shall be permitted where connected buildings are of combustible construction. 2. Fire-retardant-treated wood, in accordance with Section 603.1, Item 1.3, shall be permitted for the roof con-struction of the pedestrian walkway where connected buildings are not less than Type I or II construction.
3104.4 Contents. | Only materials approved by the department shall be located in the pedestrian walkway. Decorations may be permitted in accordance with the New York City Fire Code. | 3104.4 Contents. | Only materials and decorations approved by the building official shall be located in the pedestrian walkway.
3104.5 Connections of pedestrian walkways to buildings. | The connection of a pedestrian walkway to a building shall comply with Section 3104.5.1, 3104.5.2, 3104.5.3 or 3104.5.4. Exception: Buildings that are on the same tax lot and considered as portions of a single building in accordance with Section 503.1.2. | 3104.5 Connections of pedestrian walkways to buildings. | The connection of a pedestrian walkway to a building shall comply with Section 3104.5.1, 3104.5.2, 3104.5.3 or 3104.5.4. Exception: Buildings that are on the same lot and considered as portions of a single building in accordance with Sec-tion 503.1.2.
3104.5.1 Fire barriers. | Pedestrian walkways shall be separated from the interior of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 and Sections 3104.5.1.1 through 3104.5.1.3. | 3104.5.1 Fire barriers. | Pedestrian walkways shall be separated from the interior of the building by not less than 2-hour fire barriers constructed in accordance with Section 707 and Sections 3104.5.1.1 through 3104.5.1.3.
3104.5.1.1 Exterior walls. | Exterior walls of buildings connected to pedestrian walkways shall be 2-hour fire-resistance-rated. This protection shall extend not less than 10 feet (3048 mm) in every direction surrounding the perimeter of the pedestrian walkway. | 3104.5.1.1 Exterior walls. | Exterior walls of buildings connected to pedestrian walkways shall be 2-hour fire-resistance rated. This protection shall extend not less than 10 feet (3048 mm) in every direction surrounding the perimeter of the pedestrian walkway.
3104.5.1.2 Openings in exterior walls of connected buildings. | Openings in exterior walls required to be fire-resistance-rated in accordance with Section 3104.5.1.1 shall be equipped with opening protectives providing a not less than ¾-hour fire protection rating in accordance with Section 716. | 3104.5.1.2 Openings in exterior walls of connected buildings. | Openings in exterior walls required to be fire-resistance rated in accordance with Section 3104.5.1.1 shall be equipped with opening protectives providing a not less than 3/4-hour fire protection rating in accordance with Section 716.
3104.5.1.3 Supporting construction. | The fire barrier shall be supported by construction as required by Section 707.5.1. | 3104.5.1.3 Supporting construction. | The fire barrier shall be supported by construction as required by Section 707.5.1.
3104.5.2 Alternative separation. | The wall separating the pedestrian walkway and the building shall comply with Section 3104.5.2.1 or 3104.5.2.2 where: 1. The distance between the connected buildings is more than 30 feet (9144 mm). 2. The pedestrian walkway and connected buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and the roof of the walkway is not more than 55 feet (16 764 mm) above grade connecting to the fifth, or lower, story above grade plane, of each building. Exception: Pedestrian walkways accessory to open parking garages need not be equipped with an automatic sprinkler system. | 3104.5.2 Alternative separation. | The wall separating the pedestrian walkway and the building shall comply with Section 3104.5.2.1 or 3104.5.2.2 where: 1. The distance between the connected buildings is more than 10 feet (3048 mm). 2. The pedestrian walkway and connected buildings are equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, and the roof of the walkway is not more than 55 feet (16 764 mm) above grade connecting to the fifth, or lower, story above grade plane, of each building. Exception: Open parking garages need not be equipped with an automatic sprinkler system.
3104.5.2.1 Passage of smoke. | The wall shall be capable of resisting the passage of smoke. | 3104.5.2.1 Passage of smoke. | The wall shall be capable of resisting the passage of smoke.
3104.5.2.2 Glass. | The wall shall be constructed of a tempered, wired or laminated glass wall and doors or glass separating the interior of the building from the pedestrian walkway. The glass shall be protected by an automatic sprinkler system in accordance with Section 903.3.1.1 that, when actuated, shall completely wet the entire surface of interior sides of the wall or glass. Obstructions shall not be installed between the sprinkler heads and the wall or glass. The glass shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler operates. | 3104.5.2.2 Glass. | The wall shall be constructed of a tempered, wired or laminated glass and doors separating the interior of the building from the pedestrian walkway. The glass shall be protected by an automatic sprinkler system in accordance with Section 903.3.1.1 that, when actuated, shall completely wet the entire surface of interior sides of the wall or glass. Obstructions shall not be installed between the sprinkler heads and the wall or glass. The glass shall be in a gasketed frame and installed in such a manner that the framing system will deflect without breaking (loading) the glass before the sprinkler operates.
3104.5.3 Open sides on walkway. | Where the distance between the connected buildings is more than 30 feet (9144 mm), the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance-rated provided both sidewalls of the pedestrian walkway are not less than 50 percent open with the open area uniformly distributed to prevent the accumulation of smoke and toxic gases. The roof of the walkway shall be located not more than 40 feet (12 160 mm) above grade plane, and the walkway shall only be permitted to connect to the third or lower story of each building. Exception: Where the pedestrian walkway is protected with a sprinkler system in accordance with Section 903.3.1.1, the roof of the walkway shall be located not more than 55 feet (16 764 mm) above grade plane and the walkway shall only be permitted to connect to the fifth or lower story of each building. | 3104.5.3 Open sides on walkway. | Where the distance between the connected buildings is more than 10 feet (3048 mm), the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance rated provided that both sidewalls of the pedestrian walkway are not less than 50 percent open with the open area uniformly distributed to prevent the accumulation of smoke and toxic gases. The roof of the walkway shall be located not more than 40 feet (12 160 mm) above grade plane, and the walkway shall only be permitted to connect to the third or lower story of each building. Exception: Where the pedestrian walkway is protected with an automatic sprinkler system in accordance with Sec-tion 903.3.1.1, the roof of the walkway shall be located not more than 55 feet (16 764 mm) above grade plane and the walkway shall only be permitted to connect to the fifth or lower story of each building.
3104.5.4 Exterior walls greater than 2 hours. | Where exterior walls of connected buildings are required by Section 705 to have a fire-resistance rating greater than 2 hours, the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance-rated provided: | 3104.5.4 Exterior walls greater than 2 hours. | Where exterior walls of connected buildings are required by Section 705 to have a fire-resistance rating greater than 2 hours, the walls at the intersection of the pedestrian walkway and each building need not be fire-resistance rated provided:
3104.6 Public way. | Pedestrian walkways over a public way shall comply with Chapter 32. | 3104.6 Public way. | Pedestrian walkways over a public way shall comply with Chapter 32.
3104.9 Exit access travel. | The length of exit access travel shall be 200 feet (60 960 mm) or less. Exceptions: 1. Exit access travel distance on a pedestrian walkway equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be 250 feet (76 200 mm) or less. 2. Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open shall be 300 feet (91 440 mm) or less. 3. Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open, and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, shall be 400 feet (122 m) or less. | 3104.9 Exit access travel. | The length of exit access travel shall be 200 feet (60 960 mm) or less. Exceptions: 1. Exit access travel distance on a pedestrian walkway equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1 shall be 250 feet (76 200 mm) or less. 2. Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open shall be 300 feet (91 440 mm) or less. 3. Exit access travel distance on a pedestrian walkway constructed with both sides not less than 50 percent open, and equipped throughout with an automatic sprinkler system in accordance with Section 903.3.1.1, shall be 400 feet (122 m) or less.
3104.10 Tunneled walkway. | Separation between the tunneled walkway and the building to which it is connected shall be not less than 2-hour fire-resistant construction and openings therein shall be protected in accordance with Table 716.5. | 3104.10 Tunneled walkway. | Separation between the tunneled walkway and the building to which it is connected shall be not less than 2-hour fire-resistant construction and openings therein shall be protected in accordance with Section 716. | See BC7 Tables and Figures
3105.1 General. | Awnings, canopies, and sun control devices shall comply with the requirements of this section, the requirements of Chapter 32 for projections over public ways, and other applicable sections of this code. Exception: Canopies projecting over public rights-of-way governed by Title 19 of the Administrative Code and rules of the New York City Department of Transportation. | 3105.1 General. | Awnings and canopies shall comply with the requirements of Sections 3105.2 and 3105.3 and other applicable sections of this code.
3104.7 Width. | The unobstructed width of pedestrian walkways shall be not less than 36 inches (914 mm). The total width shall be not greater than 30 feet (9144 mm).
3106.1 General. | Marquees shall comply with this section and other applicable sections of this code. Marquees projecting beyond the street line shall also comply with the requirements of Chapter 32. Signs placed on marquees shall also comply with Section 3107. | 3106.1 General. | Marquees shall comply with Sections 3106.2 through 3106.5 and other applicable sections of this code.
3104.8 Egress. | Access shall be provided at all times to a pedestrian walkway that serves as a required exit. Doors satisfying the requirements of Chapter 10 shall enclose each end of such pedestrian walkway. The width of such pedestrian walkway shall be at least equal to the width of the doors opening onto such pedestrian walkway, but in no case less than 44 inches (1118 mm). The floor level at doors shall be the same as that of the connected building. Exception: The floor level at doors of open pedestrian walkways shall be not less than 7½ inches (191 mm) below the level of the door. Where the requirements of Chapter 11 are applicable, these differences in level shall be accommodated by means of ramps in compliance with the provisions of Chapter 11.
3106.2 Thickness. | The maximum height or thickness of a marquee measured vertically from its lowest to its highest point shall not be limited. Exception: Marquees projecting beyond the street line shall meet the height and thickness requirements of Chapter 32. | 3106.2 Thickness. | The height or thickness of a marquee measured vertically from its lowest to its highest point shall be not greater than 3 feet (914 mm) where the marquee projects more than two-thirds of the distance from the lot line to the curb line, and shall be not greater than 9 feet (2743 mm) where the marquee is less than two-thirds of the distance from the lot line to the curb line.
3106.3 Roof construction. | Where the roof or any part thereof is a skylight, the skylight shall comply with the requirements of Chapter 24. Every roof and skylight of a marquee shall be drained in accordance with the provisions of the New York City Plumbing Code. | 3106.3 Roof construction. | Where the roof or any part thereof is a skylight, the skylight shall comply with the requirements of Chapter 24. Every roof and skylight of a marquee shall be sloped to downspouts that shall conduct any drainage from the marquee in such a manner so as not to spill over the sidewalk.
3106.4 Location prohibited. | Every marquee shall be so located as not to interfere with the operation of any exterior standpipe, and such that the marquee does not obstruct the clear passage of stairways or exit discharge from the building or the installation or maintenance of street lighting. | 3106.4 Location prohibited. | Every marquee shall be so located as not to interfere with the operation of any exterior standpipe, and such that the marquee does not obstruct the clear passage of stairways or exit discharge from the building or the installation or maintenance of street lighting.
3106.5 Construction. | A marquee shall be supported entirely from the building and constructed of noncombustible materials. Marquees shall be designed as required in Chapter 16. Structural members shall be protected to prevent deterioration. | 3106.5 Construction. | A marquee shall be supported entirely from the building and constructed of noncombustible materials. Marquees shall be designed as required in Chapter 16. Structural members shall be protected to prevent deterioration.
3105.2 Definitions. | The following term is defined in Chapter 2:
3107.1 General. | Signs shall be designed, constructed and maintained in accordance with Appendix H. | 3107.1 General. | Signs shall be designed, constructed and maintained in accordance with this code.
3105.3 Design and construction. | Awnings, canopies, and sun control devices shall be designed and constructed to withstand wind or other lateral loads and live loads as required by Chapter 16 with due allowance for shape, open construction and similar features that relieve the pressures or loads. Structural members shall be protected to prevent deterioration. Awnings and canopies shall have frames of noncombustible material, covered with fabric that meets the fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701 or has a flame spread index not greater than 25 when tested in accordance with ASTM E 84 or UL 723, or covered in plastic in accordance with Section 2605, sheet metal, or other equivalent material, and shall be either fixed, retractable, folding or collapsible. Sun control devices shall be constructed of noncombustible materials.
3108.1 General. | Subject to the provisions of Chapter 16 and the requirements of Chapter 15 governing the fire-resistance ratings of buildings for the support of roof structures, radio, television, and telecommunications towers and antennas shall be designed and constructed as herein provided. All such towers and antennas shall be collectively referred to as “towers” for the purposes of this section. Towers shall be designed and constructed in accordance with the provisions of TIA-222. Exceptions: 1. Exceptions related to seismic design in Section 2.7.3 of TIA-222 shall not apply; 2. The specified values for seismic coefficients Ss, S1 and Site Factors Fa and Fv shall comply with Section 1613.3; and 3. The horizontal extent of Topographic Category 2, escarpments, shall be 16 times the height of the escarpment. | 3108.1 General. | Towers shall be designed and constructed in accordance with the provisions of TIA 222. Towers shall be designed for seismic loads; exceptions related to seismic design listed in Section 2.7.3 of TIA 222 shall not apply. In Section 2.6.6.2 of TIA 222, the horizontal extent of Topographic Category 2, escarpments, shall be 16 times the height of the escarpment. Exception: Single free-standing poles used to support antennas not greater than 75 feet (22 860 mm), measured from the top of the pole to grade, shall not be required to be noncombustible.
3105.4 Reserved.
3108.2 Location and access. | Towers shall be located and equipped with step bolts and ladders so as to provide ready access for inspection purposes. Guy wires or other accessories shall not cross or encroach upon any street or other public space, or over above-ground electric utility lines, or encroach upon any privately owned property without written consent of the owner of the encroached-upon property, space or above-ground electric utility lines. Towers shall be equipped with climbing and working facilities in compliance with TIA-222. See applicable OSHA, FCC and EPA regulations relating to limitations on access to tower sites. | 3108.2 Location and access. | Towers shall be located such that guy wires and other accessories shall not cross or encroach on any street or other public space, or over above-ground electric utility lines, or encroach on any privately owned property without the written consent of the owner of the encroached-upon property, space or above-ground electric utility lines. Towers shall be equipped with climbing and working facilities in compliance with TIA 222. Access to the tower sites shall be limited as required by applicable OSHA, FCC and EPA regulations.
3109.1 General. | Swimming pools, swimming pool enclosures, and swimming pool safety devices shall comply with the requirements of this section and other applicable sections of this code. | 3109.1 General. | The design and construction of swimming pools, spas and hot tubs shall comply with the International Swimming Pool and Spa Code.
3108.3 Construction. | Towers shall be constructed of approved corrosion-resistant noncombustible material. The minimum type of construction of isolated radio towers not more than 100 feet (30 480 mm) in height shall be Type IIB.
3108.4 Loads. | Towers shall be designed to resist wind loads in accordance with TIA-222 and Chapter 16 of this code. The design criteria shall not be less stringent than required by Chapter 16. Consideration shall be given to conditions involving wind load on ice-covered sections.
3108.4.1 Dead load. | Towers shall be designed for the dead load plus ice load.
3108.4.2 Wind load. | Towers shall be provided with adequate foundations and anchorage designed to resist two times the calculated wind load.
3108.4.3 Earthquake load. | Towers shall be provided with adequate foundations and anchorage designed to resist two times the calculated earthquake load.
3108.5 Grounding. | Towers shall be permanently and effectively grounded in accordance with the New York City Electrical Code.
3109.2 Definitions. | The following terms are defined in Chapter 2:
3109.3 Pool safety and accessibility. | Public and private swimming pools shall comply with the requirements for safety and accessibility as provided in this section.
3109.3.1 Entrapment protection. | Entrapment protection shall be provided in compliance with this section.
3109.3.1.1 Suction entrapment avoidance. | Suction outlets shall be designed and installed in accordance with ANSI/APSP-7.
3109.3.2 Swimming pool and spa alarms. | Swimming pool and spa alarms shall comply with Sections 3109.3.2.1 through 3109.3.2.4.
3109.3.2.1 Applicability. | All swimming pools and spas shall be equipped with an approved pool alarm. Pool alarms shall comply with ASTM F 2208 and shall be installed, used and maintained in accordance with the manufacturer’s instructions and this section. Exceptions: 1. A hot tub or spa equipped with a safety cover that complies with ASTM F 1346. 2. A swimming pool (other than a hot tub or spa) equipped with an automatic power safety cover that complies with ASTM F 1346.
3109.3.2.2 Multiple alarms. | A pool alarm must be capable of detecting entry into the water at any point on the surface of the swimming pool. If necessary to provide detection capability at every point on the surface of the swimming pool, more than one pool alarm shall be provided.
3109.3.2.3 Alarm activation. | Pool alarms shall activate upon detecting entry into the water and shall sound poolside and inside the building.
3109.3.2.4 Prohibited alarms. | The use of personal immersion alarms shall not be construed as compliance with this section.
3109.3.3 Water circulation, water treatment and drainage. | The supply, circulation, treatment, and drainage of water for swimming pools shall meet the requirements of the New York City Plumbing Code.
3109.3.4 Electrical precautions. | No overhead electrical conductors shall be installed within 15 feet (4572 mm) of any swimming pool. All metal fences, enclosures, or railings that might become electrically charged as a result of contact with broken overhead conductors or from any other cause near, or adjacent to, a swimming pool shall be grounded in accordance with the provisions of lightning protection in the New York City Electrical Code.
3109.3.5 Facilities for people with disabilities. | Facilities for people with physical disabilities shall be provided where required by Chapter 11 of this code.
3109.4 Public swimming pools. | Public swimming pools shall comply with the requirements for safety and accessibility as provided in Sections 3109.3 and 3109.4. Exception: A swimming pool with a power safety cover or a spa with a safety cover complying with ASTM F 1346.
3109.4.1 Barrier height and clearances. | Public swimming pools shall be completely enclosed by a fence, wall, building, or other solid barrier, or any combination thereof, not less than 6 feet (1829 mm) in height. Openings in the enclosure and pedestrian access gates shall not permit the passage of a 4-inch-diameter (102 mm) sphere. The enclosure shall be equipped with self-closing and self-latching gates. Exception: Enclosures shall be not less than 4 feet (1219 mm) in height when surrounding wading pools with water less than 24 inches (610 mm) in depth.
3109.4.2 Gates. | Gates shall comply with Sections 3109.4.2.1 through 3109.4.2.3.
3109.4.2.1 Self-closing; opening configuration. | All gates shall be self-closing. In addition, if the gate is a pedestrian access gate, the gate shall open outward, away from the pool.
3109.4.2.2 Self-latching; location of latch handle. | All gates shall be self-latching, with the latch handle located within the enclosure (i.e., on the pool side of the enclosure) and not less than 40 inches (1016 mm) above grade. If the latch handle is located less than 54 inches (1372 mm) from the bottom of the gate, the latch handle shall be located not less than 3 inches (76 mm) below the top of the gate, and neither the gate nor barrier shall have any opening greater than 0.5 inch (12.7 mm) within 18 inches (457 mm) of the latch handle.
3109.4.2.3 Locking. | All gates shall be securely locked with a key, combination or other child proof lock sufficient to prevent access to the swimming pool through such gate when the swimming pool is not in use or supervised.
3109.4.3 Other laws. | In addition to the requirements of this section, any other, more stringent requirements for the construction and design of swimming pool and barriers that may be provided for in Article 165 of the New York City Health Code, as administered by the New York City Department of Health and Mental Hygiene, shall also be applicable.
3109.5 Private swimming pools. | Private swimming pools shall comply with the requirements for safety and accessibility as provided in Section 3109.3 and this section. Exception: An above-ground private swimming pool which has a maximum water depth of 4 feet (1219mm) and an area not exceeding 500 square feet (46.45 m2) that is accessory to an R-3 occupancy and is privately used for noncommercial purposes shall not be required to comply with Sections 3109.3.1, 3109.3.2, 3109.5.2, 3109.5.3 and 3109.5.4.
3109.5.1 Barrier height and clearances. | The top of the barrier enclosing a private swimming pool shall be not less than 48 inches (1219 mm) above grade measured on the side of the barrier that faces away from the swimming pool. The vertical clearance between grade and the bottom of the barrier shall be not greater than 2 inches (51 mm) measured on the side of the barrier that faces away from the swimming pool. Where the top of the pool structure is above grade, the barrier is authorized to be erected at grade level or mounted on top of the pool structure, and the vertical clearance between the top of the pool structure and the bottom of the barrier shall be not greater than 4 inches (102 mm).
3109.5.1.1 Openings. | Openings in the barrier shall not allow passage of a 4-inch-diameter (102 mm) sphere.
3109.5.1.2 Solid barrier surfaces. | Solid barriers which do not have openings shall not contain indentations or protrusions except for normal construction tolerances and tooled masonry joints.
3109.5.1.3 Closely spaced horizontal members. | Where the barrier is composed of horizontal and vertical members and the distance between the tops of the horizontal members is less than 45 inches (1143 mm), the horizontal members shall be located on the swimming pool side of the fence. Spacing between vertical members shall be not greater than 1¾ inches (44 mm) in width. Where there are decorative cutouts within vertical members, spacing within the cutouts shall be not greater than 1¾ inches (44 mm) in width.
3109.5.1.4 Widely spaced horizontal members. | Where the barrier is composed of horizontal and vertical members and the distance between the tops of the horizontal members is 45 inches (1143 mm) or more, spacing between vertical members shall be not greater than 4 inches (102 mm). Where there are decorative cutouts within vertical members, spacing within the cutouts shall be not greater than 1¾ inches (44 mm) in width.
3109.5.1.5 Chain link dimensions. | Mesh size for chain link fences shall be not greater than a 2¼ inch square (57 mm square) unless the fence is provided with slats fastened at the top or the bottom that reduce the openings to not more than 1¾ inches (44 mm).
3109.5.1.6 Diagonal members. | Where the barrier is composed of diagonal members, the opening formed by the diagonal members shall be not greater than 1¾ inches (44 mm).
3109.5.1.7 Gates. | Gates shall comply with Sections 3109.5.1.1 through 3109.5.1.6 and Sections 3109.5.1.7.1 through 3109.5.1.7.3.
3109.5.1.7.1 Self-closing; opening configuration. | All gates shall be self-closing. In addition, if the gate is a pedestrian access gate, the gate shall open outward, away from the pool.
3109.5.1.7.2 Self-latching; location of latch handle. | All gates shall be self-latching, with the latch handle located within the enclosure (i.e., on the pool side of the enclosure) and not less than 40 inches (1016 mm) above grade. In addition, if the latch handle is located less than 54 inches (1372 mm) from the bottom of the gate, the latch handle shall be located not less than 3 inches (76 mm) below the top of the gate, and neither the gate nor barrier shall have any opening greater than 0.5 inch (12.7 mm) within 18 inches (457 mm) of the latch handle.
3109.5.1.7.3 Locking. | All gates shall be securely locked with a key, combination or other child proof lock sufficient to prevent access to the swimming pool through such gate when the swimming pool is not in use or supervised.
3109.5.1.8 Dwelling wall as a barrier. | Where a wall of a dwelling serves as part of the barrier, one of the following shall apply:
3109.5.1.9 Pool structure as barrier. | Where an above-ground private swimming pool structure is used as a barrier or where the barrier is mounted on top of the pool structure, and the means of access is a ladder or steps, then the ladder or steps either shall be capable of being secured, locked or removed to prevent access, or the ladder or steps shall be surrounded by a barrier that meets the requirements of Sections 3109.5.1.1 through 3109.5.1.8. Where the ladder or steps are secured, locked or removed, any opening created shall not allow the passage of a 4-inch-diameter (102 mm) sphere.
3109.5.2 Indoor swimming pools. | Walls surrounding indoor private swimming pools shall not be required to comply with Section 3109.5.1.8.
3109.5.3 Prohibited locations. | Barriers shall be located so as to prohibit permanent structures, equipment or similar objects from being used to climb the barriers.
3109.5.4 Construction requirements. | Private swimming pools shall be constructed so as to be water tight and easily cleaned. They shall be built of nonabsorbent materials with smooth surfaces and shall be free of open cracks and open joints.
3109.5.4.1 Walls. | The walls of swimming pools shall be vertical for not less than the top 30 inches (762 mm) below the normal water level. The junctions between the side walls and the bottom shall be coved. A swimming pool overflow shall be provided meeting the requirements of the New York City Plumbing Code.
3109.5.4.2 Bottom slopes. | The bottom of the swimming pool shall slope downward toward the main drains. The slope in shallow areas with depths less than 5 feet (1524 mm) shall not exceed 1 unit vertical in 12 units horizontal (8-percent slope). In portions of the swimming pool with depth greater than 5 feet (1524 mm), the slope shall not be steeper than 1 unit vertical in 3 units horizontal (33-percent slope).
3109.5.4.3 Ladders. | There shall be a ladder or steps with handrails at the deep end and at the shallow end of every swimming pool. Ladders and steps shall have no-slip treads. All ladders shall be rigidly installed and shall be constructed of corrosion-resistant materials.
3109.5.4.4 Walkways. | Every swimming pool shall have a walkway not less than 5 feet (1524 mm) wide around its entire perimeter. The walkway shall have a nonslip surface and shall be constructed to drain away from the swimming pool.
3109.5.4.5 Handholds. | Every swimming pool shall be constructed so that either the overflow gutter, if provided, or the tops of the side walls afford a continuous handhold for bathers.
3109.5.4.6 Markings. | Permanent markings showing the depth of the shallow end, break points, diving depth and deep end shall be provided so as to be visible from both inside and outside the swimming pool.
3109.5.4.7 Diving boards and towers. | Diving towers shall be rigidly constructed and permanently anchored. The depth of the water below a diving board shall be not less than 102 inches (2591 mm) for a board 39 inches (991 mm) or less above the water. For a diving board more than 39 inches (991 mm) and not more than 118 inches (2997 mm) above the water, the depth of the water below the board shall be not less than 144 inches (3658 mm). For a diving board or platform more than 118 inches (2997 mm) above the water, the depth of the water below the board shall be not less than 192 inches (4877 mm). Indoor swimming pools shall provide not less than 144 inches (3658 mm) overhead clearance above all diving boards.
3109.6 Temporary barriers. | An outdoor swimming pool, including an in-ground, above ground or on-ground pool, hot tub or spa shall be surrounded by a temporary barrier during installation or construction. Such barrier shall remain in place until a permanent fence in compliance with Section 3109.4 is provided for public swimming pools, or a barrier in compliance with Section 3109.5 is provided for residential private pools. Exceptions: 1. Above-ground or on-ground residential swimming pools where the pool structure is the barrier in compliance with Section 3109. 2. Spas or hot tubs with a safety cover which complies with ASTM F 1346, provided that such safety cover is in place during the period of installation or construction of such hot tub or spa. The temporary removal of a safety cover as required to facilitate the installation or construction of a hot tub or spa during periods when at least one person engaged in the installation or construction is present is permitted.
3109.6.1 Height. | The top of the temporary barrier shall be not less than 48 inches (1219 mm) above grade measured on the side of the barrier which faces away from the swimming pool.
3109.6.2 Replacement by a permanent barrier. | A temporary barrier shall be replaced by a complying permanent barrier within either of the following periods:
3109.6.2.1 Replacement extension. | Subject to the approval of the code enforcement official, the time period for completion of the permanent barrier may be extended for good cause, including, but not limited to, adverse weather conditions delaying construction.
3110.1 General. | Automatic vehicular gates shall comply with the requirements of Sections 3110.2 through 3110.4 and other applicable sections of this code. | 3110.1 General. | Automatic vehicular gates shall comply with the requirements of Sections 3110.2 and 3110.3 and other applicable sections of this code.
3110.2 Definitions. | The following term is defined in Chapter 2:
3110.3 Vehicular gates intended for automation. | Vehicular gates intended for automation shall be designed, constructed and installed to comply with the class of gate in accordance with the requirements of ASTM F 2200.
3110.3.1 Entrapment protection. | Defined classes of gates shall be subject to the entrapment protection provisions per UL 325.
3110.4 Vehicular gate operators. | Vehicular gate operators, when provided, shall be listed in accordance with UL 325.
3111.1 General. | Sidewalk cafés provided beyond the building line shall comply with the requirements of this section, the New York City Zoning Resolution, the Commissioners of the Department of Consumer Affairs and Department of Transportation, and with the projection limitations of Chapter 32 of this code. | 3111.1 General. | Solar energy systems shall comply with the requirements of this section.
3111.2 Enclosures. | Enclosed sidewalk cafés shall be constructed of noncombustible material. The walls of such enclosures shall not extend more than 8 feet (2438 mm) above the sidewalk. Light-transmitting plastic glazing complying with Section 2606 shall be permitted as glazing within such walls. Light-transmitting plastic skylight glazing complying with Section 2610 may be installed in the roofs of such enclosures.
3111.3 Awnings. | Awnings supported entirely from the building may be placed over unenclosed sidewalk cafés provided they are not less than 8 feet (2438 mm) clear above the sidewalk and within the limits specified by the Commissioner of the Department of Consumer Affairs. Such awnings shall be in compliance with Section 3105 of this code.
3111.4 Obstructions prohibited. | No part of any awning, enclosure, fixture, equipment or removable platform of a sidewalk café shall be located: 1. Beneath a fire escape so as to obstruct operation of fire escape drop ladders or counter-balanced stairs; 2. So as to obstruct any exit from a building; 3. So as to obstruct any cellar access hatch or areaway; 4. So as to interfere with any vent or other mechanical ventilation outlet or inlet; or 5. So as to interfere with or obscure any standpipe connections, hydrant or associated signage in any way that would hinder its use by the Fire Department. Exception: Upon special application, the commissioner may permit an easily removable, prominently designated platform, designed in accordance with Section 3111.5, to cover a cellar entrance or areaway that is not used as a required means of egress.
3111.5 Removable platforms. | Removable platforms of sidewalk cafés shall be constructed in accordance with the requirements of this section.
3111.5.1 Continuity. | Removable platforms shall be constructed to provide for a continuous unbroken and level floor without openings or cracks so as to prevent any material or liquid from falling through to the area beneath.
3111.5.2 Maintenance. | No papers, trash or other materials may be permitted to accumulate in the area beneath the floor of any removable platform.
3111.6 Accessibility. | Sidewalk cafés and access thereto shall comply with Chapter 11.
3111.7 Assembly seating. | Unless separated from seating inside the building by fire partitions complying with Section 713, the seating for enclosed sidewalk cafés shall be added to that inside the building in order to determine whether a place of assembly certificate of operation is required.
3111.8 Rules. | In addition to the requirements specified herein, the commissioner may promulgate such additional rules necessary to secure safety.
3112.1 Permitted heights. | Fences are permitted to be erected to a maximum height of 10 feet (3048 mm) above the ground. Exceptions: 1. In residence districts, as established by the New York City Zoning Resolution, fences are permitted to be erected to a maximum height of 4 or 6 feet (1829 mm) above the ground, depending upon its location on the zoning lot. 2. Fences in residence districts used in conjunction with nonresidential buildings and public playgrounds, excluding buildings accessory to dwellings, are permitted to be erected to a maximum height of 15 feet (4572 mm) above the ground. 3. Higher fences may be permitted by the commissioner where required for the enclosure of public playgrounds, school yards, parks, and similar public facilities.
3113.1 General. | Photovoltaic panels and modules shall comply with the requirements of this code, the New York City Electrical Code, the Zoning Resolution and the New York City Fire Code. | 3113.1 General. | The provisions of this section shall apply to relocatable buildings. Relocatable buildings manufactured after the effective date of this code shall comply with the applicable provisions of this code. Exception: This section shall not apply to manufactured housing used as dwellings.
3113.1.1 Rooftop-mounted photovoltaic panels and modules. | Photovoltaic panels and modules installed on a roof or as an integral part of a roof assembly shall comply with the requirements of the New York City Fire Code and Chapter 15 of this code.
3114.1 General. | Large wind turbines shall be designed and constructed in accordance with this section. | 3114.1 General. | For the purpose of this section, public restroom buildings are located on publicly owned lands in flood hazard areas and intended for public use. Public restroom buildings and portions of other buildings that contain public restrooms are limited to toilet rooms, bathrooms, showers and changing rooms. Public restroom buildings and portions of buildings that contain public restrooms shall comply with the requirements of this section. Public-use restrooms that are not elevated or dry floodproofed in accordance with Section 1612 shall comply with Section 3114.2. Portions of buildings that include uses other than public-use toilet rooms, bathrooms, showers and changing rooms shall comply with Section 1612.
3114.2 Definitions. | The following terms are defined in Chapter 2:
3114.3 Design standards. | A large wind turbine shall be designed in accordance with standards adopted by rules of the commissioner. Such standards shall include but need not be limited to standards relating to the design of large wind turbines that are developed by the American Wind Energy Association, the New York State Energy Research and Development Authority, the California Energy Commission, the European Wind Turbine Certification, the British Wind Energy Association, the International Electrotechnical Commission, the National Renewable Energy Laboratory, or the Underwriters Laboratory.
3114.4 Wind speed. | A large wind turbine shall be designed to withstand winds of up to and including 130 mph (58.1 m/s) or such higher wind load as may be specified in this code or the design standard for such turbine pursuant to Section 3114.3.
3114.5 Brakes and locks. | Where necessary for public safety, the commissioner may require that a large wind turbine shall be equipped with a redundant braking system and a passive lock, including aerodynamic overspeed controls and mechanical brakes.
3114.6 Visual appearance. | A large wind turbine shall be white, off-white, grey, or another non-obtrusive color specified by the commissioner.
3114.8 Access. | Access to a large wind turbine shall be limited as follows:
3114.9 Noise. | A large wind turbine shall be designed to comply with the sound level limit of Section 24-232.1 of the Administrative Code.
3114.10 Shadow flicker. | The commissioner shall by rule establish shadow flicker limitations for large wind turbines for the purpose of limiting, to the extent practicable, such flicker on buildings adjacent to such turbines.
3114.11 Signal interference. | The commissioner shall establish rules governing large wind turbines for purpose of minimizing, to the extent practicable, interference by such turbines with radio, telephone, television, cellular or other similar signals.
3114.12 Setback. | No part of a large wind turbine or large wind turbine tower shall be located within a horizontal distance of a property line that is equal or less than one-half the height of such turbine, including such tower, measured from the base of such tower or, if there is no such tower, the base of such turbine.
3115.1 General. | In addition to other applicable requirements in this code, other law or rule, and established by the commissioner, small wind turbines shall be designed and constructed in accordance with this section. | 3115.1 General. | The provisions of Section 3115 and other applicable sections of this code shall apply to intermodal shipping containers that are repurposed for use as buildings or structures, or as a part of buildings or structures. Exceptions: 1. Intermodal shipping containers previously approved as existing relocatable buildings complying with Chapter 14 of the International Existing Building Code. 2. Stationary storage battery arrays located in intermodal shipping containers complying with Chapter 12 of the International Fire Code. 3. Intermodal shipping containers that are listed as equipment complying with the standard for equipment, such as air chillers, engine generators, modular data centers, and other similar equipment. 4. Intermodal shipping containers housing or supporting experimental equipment are exempt from the require-ments of Section 3115, provided that they comply with all of the following: 4.1. Such units shall be single stand-alone units supported at grade level and used only for occupancies as specified under Risk Category I in Table 1604.5. 4.2. Such units are located a minimum of 8 feet (2438 mm) from adjacent structures, and are not connected to a fuel gas system or fuel gas utility. 4.3. In hurricane-prone regions and flood hazard areas, such units are designed in accordance with the ap-plicable provisions of Chapter 16. | See BC15 Tables and Figures
3115.2 Definitions. | The following terms are defined in Chapter 2:
3115.3 Design standards. | A small wind turbine shall be designed in accordance with standards adopted by rules of the commissioner. Such standards shall include but need not be limited to standards relating to the design of small wind turbines that are developed by the American Wind Energy Association, the New York State Energy Research and Development Authority, the California Energy Commission, the Small Wind Certification Council, the British Wind Energy Association, the International Electrotechnical Commission, the National Renewable Energy Laboratory, or the Underwriters Laboratory.
3115.4 Wind speed. | A small wind turbine shall be designed to withstand winds of up to and including 130 mph (58.1 m/s) or such higher wind load as may be specified in this code or the design standard for such turbine pursuant to Section 3113.3.
3115.5 Brakes and locks. | Where deemed necessary by the commissioner, a small wind turbine shall be equipped with a redundant braking system and a passive lock, including aerodynamic overspeed controls and mechanical brakes.
3115.5.1 Locking before hurricane or strong wind conditions. | If a hurricane or strong wind conditions are expected, the commissioner may order that small turbines equipped with passive locks be stopped and locked.
3115.6 Visual appearance. | A small wind turbine shall be white, off-white, grey, or another non-obtrusive color specified by the commissioner.
3115.7 Lighting. | A small wind turbine shall not be artificially lighted. Exception: Lighting that is required by this code or other applicable laws or rules, provided that such lighting is shielded in accordance with rules promulgated by the commissioner.
3115.8 Access. | Access to a small wind turbine shall be limited as follows:
3115.9 Noise. | A small wind turbine shall be designed in accordance with applicable sections of the New York City Noise Control Code.
3115.10 Shadow flicker. | The commissioner shall by rule establish shadow flicker limitations for small wind turbines for the purpose of limiting, to the extent practicable, such flicker on buildings adjacent to such turbines.
3115.11 Signal interference. | The commissioner shall establish rules governing small wind turbines for purpose of minimizing, to the extent practicable, interference by such turbines with radio, telephone, television, cellular or other similar signals.
3115.12 Setback. | No part of a small wind turbine or small wind turbine tower shall be located within a horizontal distance of a property line that is equal or less than one-half the height of such turbine, including such tower, measured from the base of such tower or, if there is no such tower, the base of such turbine. Exception: Turbines or towers for which each owner of property adjacent to such property line has entered into a written agreement providing that such turbine or tower or a part thereof may be located closer to such property line than this section allows.
|  | 3102.2 Tensile membrane structures and air-supported structures. | Tensile membrane structures and air-supported structures, including permanent and temporary structures, shall be designed and constructed in accordance with ASCE 55. The provisions in Sections 3102.3 through 3102.6 shall apply.
|  | 3103.1.1 Conformance. | Temporary structures and uses shall conform to the structural strength, fire safety, means of egress, accessibility, light, ventilation and sanitary requirements of this code as necessary to ensure public health, safety and general welfare.
|  | 3103.1.2 Permit required. | Temporary structures that cover an area greater than 120 square feet (11.16 m2), including connecting areas or spaces with a common means of egress or entrance that are used or intended to be used for the gathering together of 10 or more persons, shall not be erected, operated or maintained for any purpose without obtaining a permit from the building official.
|  | 3104.7 Egress. | Access shall be provided at all times to a pedestrian walkway that serves as a required exit.
|  | 3104.8 Width. | The unobstructed width of pedestrian walkways shall be not less than 36 inches (914 mm). The total width shall be not greater than 30 feet (9144 mm).
|  | 3105.2 Design and construction. | Awnings and canopies shall be designed and constructed to withstand wind or other lateral loads and live loads as required by Chapter 16 with due allowance for shape, open construction and similar features that relieve the pressures or loads. Structural members shall be protected to prevent deterioration. Awnings shall have frames of noncombustible material, fire-retardant-treated wood, heavy timber complying with Section 2304.11, or 1-hour construction with combustible or noncombustible covers and shall be either fixed, retractable, folding or collapsible.
|  | 3105.3 Awnings and canopy materials. | Awnings and canopies shall be provided with an approved covering that complies with one of the following: 1. The fire propagation performance criteria of Test Method 1 or Test Method 2, as appropriate, of NFPA 701. 2. Has a flame spread index not greater than 25 when tested in accordance with ASTM E84 or UL 723. 3. Meets all of the following criteria when tested in accordance with NFPA 286: 3.1. During the 40 kW exposure, flames shall not spread to the ceiling. 3.2. Flashover, as defined in NFPA 286, shall not occur. 3.3. The flame shall not spread to the outer extremity of the sample on any wall or ceiling. 3.4. The peak heat release rate throughout the test shall not exceed 800 kW. Exception: The fire propagation performance and flame spread index requirements shall not apply to awnings in-stalled on detached one- and two-family dwellings.
|  | 3110.2 Vehicular gates intended for automation. | Vehicular gates intended for automation shall be designed, constructed and installed to comply with the requirements of ASTM F2200.
|  | 3110.3 Vehicular gate openers. | Vehicular gate openers, where provided, shall be listed in accordance with UL 325.
|  | 3111.1.1 Wind resistance. | Rooftop-mounted photovoltaic (PV) panel systems and solar thermal collectors shall be designed in accordance with Section 1609.
|  | 3111.1.2 Roof live load. | Roof structures that provide support for solar energy systems shall be designed in accordance with Section 1607.14.4.
|  | 3111.2 Solar thermal systems. | Solar thermal systems shall be designed and installed in accordance with this section, the International Plumbing Code, the International Mechanical Code and the International Fire Code. Where light-transmitting plastic covers are used, solar thermal collectors shall be designed in accordance with Section 2606.12.
|  | 3111.2.1 Equipment. | Solar thermal systems and components shall be listed and labeled in accordance with ICC 900/SRCC 300 and ICC 901/SRCC 100.
|  | 3111.3 Photovoltaic solar energy systems. | Photovoltaic solar energy systems shall be designed and installed in accordance with this section, the International Fire Code, NFPA 70 and the manufacturer’s installation instructions.
|  | 3111.3.1 Equipment. | Photovoltaic panels and modules shall be listed and labeled in accordance with UL 1703 or with both UL 61730-1 and UL 61730-2. Inverters shall be listed and labeled in accordance with UL 1741. Systems connected to the utility grid shall use inverters listed for utility interaction.
|  | 3111.3.2 Fire classification. | Rooftop-mounted photovoltaic (PV) panel systems shall have a fire classification in accordance with Section 1505.9. Building-integrated photovoltaic (BIPV) systems installed as roof coverings shall have a fire classification in accordance with Section 1505.8.
|  | 3111.3.3 Building-integrated photovoltaic (BIPV) systems. | BIPV systems installed as roof coverings shall be designed and installed in accordance with Section 1507.
|  | 3111.3.4 Access and pathways. | Roof access, pathways and spacing requirements shall be provided in accordance with Section 1205 of the International Fire Code.
|  | 3111.3.5 Ground-mounted photovoltaic systems. | Ground-mounted photovoltaic systems shall be designed and installed in accordance with Chapter 16 and the International Fire Code.
|  | 3111.3.5.1 Fire separation distances. | Ground-mounted photovoltaic systems shall be subject to the fire separation distance requirements determined by the local jurisdiction.
|  | 3112.1 General. | The provisions of this section shall apply to greenhouses that are designed and used for the cultivation, maintenance, or protection of plants.
|  | 3112.2 Accessibility. | Greenhouses shall be accessible in accordance with Chapter 11.
|  | 3112.3 Structural design. | Greenhouses shall comply with the structural design requirements for greenhouses in Chapter 16.
|  | 3112.4 Glass and glazing. | Glass and glazing used in greenhouses shall comply with Section 2405.
|  | 3112.5 Light-transmitting plastics. | Light-transmitting plastics shall be permitted in lieu of plain glass in greenhouses and shall comply with Section 2606.
|  | 3112.6 Membrane structures. | Greenhouses that are membrane structures shall comply with Section 3102.
|  | 3112.6.1 Plastic film. | Plastic films used in greenhouses shall comply with Section 3102.3.
|  | 3113.1.1 Compliance. | A newly constructed relocatable building shall comply with the requirements of this code for new construction. An existing relocatable building that is undergoing alteration, addition, change of occupancy or relocation shall comply with Chapter 14 of the International Existing Building Code.
|  | 3113.2 Supplemental information. | Supplemental information specific to a relocatable building shall be submitted to the authority having jurisdiction. It shall, as a minimum, include the following in addition to the information required by Section 105:
|  | 3113.3 Manufacturer’s data plate. | Each relocatable module shall have a data plate that is permanently attached on or adjacent to the electrical panel, and shall include the following information:
|  | 3113.4 Inspection agencies. | The building official is authorized to accept reports of inspections conducted by approved inspection agencies during off-site construction of the relocatable building, and to satisfy the applicable requirements of Sections 110.3 through 110.3.12.1.
|  | 3114.2 Flood resistance. | Public-use restrooms on publicly owned lands in flood hazard areas shall comply with the requirements of ASCE 24, except for elevation requirements, and shall comply with all of the following criteria: 1. The building footprint is not more than 1,500 square feet (139 m2). 2. Located, designed and constructed to resist the effects of flood hazards and flood loads to minimize flood dam-age from a combination of wind and water loads associated with the base flood. 3. Anchored to prevent flotation, collapse or lateral movement resulting from hydrodynamic and hydrostatic loads, including the effects of buoyancy during conditions of the base flood. 4. Constructed of flood-damage-resistant materials. 5. Where enclosed by walls, the walls have flood openings. 6. Mechanical and electrical systems are located above the base flood elevation. 7. Plumbing fixtures and plumbing connections are located above the base flood elevation. 8. An emergency plan, approved by the jurisdiction, is submitted to the building official and includes building de-sign documents specifying implementation of protection measures prior to the onset of flooding conditions. Exceptions: 1. Minimum necessary electric equipment required to address health, life safety and electric code requirements is permitted below the base flood elevation in accordance with ASCE 24 provisions for electric elements in-stalled below the minimum elevations. 2. Plumbing fixtures and connections are permitted below the base flood elevation provided that the fixtures and connections are designed and installed to minimize or eliminate infiltration of floodwaters into the sanitary sewage system and discharges from sanitary sewage systems into floodwaters.
|  | 3115.2 Construction documents. | The construction documents shall contain information to verify the dimensions and establish the physical properties of the steel components and wood floor components of the intermodal shipping container, in addition to the information required by Sections 107 and 1603.
|  | 3115.3 Intermodal shipping container information. | Intermodal shipping containers shall bear an existing data plate containing the following information as required by ISO 6346 and verified by an approved agency. A report of the verification process and findings shall be provided to the building owner.
|  | 3115.4 Protection against decay and termites. | Wood structural floors of intermodal shipping containers shall be protected from decay and termites in accordance with the applicable provisions of Section 2304.12.1.1.
|  | 3115.5 Under-floor ventilation. | The space between the bottom of the floor joists and the earth under any intermodal shipping container, except spaces occupied by basements and cellars, shall be provided with ventilation in accordance with Section 1202.4.
|  | 3115.6 Roof assemblies. | Intermodal shipping container roof assemblies shall comply with the applicable requirements of Chapter 15. Exception: Single-unit, stand-alone intermodal shipping containers not attached to, or stacked vertically over, other intermodal shipping containers, buildings or structures.
|  | 3115.7 Joints and voids. | Joints and voids that create concealed spaces between connected or stacked intermodal shipping containers at fire-resistance-rated walls, floor or floor/ceiling assemblies and roofs or roof/ceiling assemblies shall be protected by an approved fire-resistant joint system in accordance with Section 715.
|  | 3115.8 Structural. | Intermodal shipping containers that conform to ISO 1496-1 and are repurposed for use as buildings or structures, or as a part of buildings or structures, shall be designed in accordance with Chapter 16 and this section.
|  | 3115.8.1 Foundations. | Intermodal shipping containers repurposed for use as a permanent building or structure shall be supported on foundations or other supporting structures designed and constructed in accordance with Chapters 16 through 23.
|  | 3115.8.1.1 Anchorage. | Intermodal shipping containers shall be anchored to foundations or other supporting structures as necessary to provide a continuous load path for all applicable design and environmental loads in accordance with Chapter 16.
|  | 3115.8.2 Welds. | New welds and connections shall be equal to or greater than the original connections.
|  | 3115.8.3 Structural design. | The structural design for the intermodal shipping containers repurposed for use as a building or structure, or as part of a building or structure, shall comply with Section 3115.8.4 or 3115.8.5.
|  | 3115.8.4 Detailed design procedure. | A structural analysis meeting the requirements of this section shall be provided to the building official to demonstrate the structural adequacy of the intermodal shipping containers. Exception: Intermodal shipping containers designed in accordance with Section 3115.8.5.
|  | 3115.8.4.1 Material properties. | Structural material properties for existing intermodal shipping container steel components shall be established by material testing where the steel grade and composition cannot be identified by the manufacturer’s designation as to manufacture and mill test.
|  | 3115.8.4.2 Seismic design parameters. | The seismic force-resisting system shall be designed and detailed in accordance with one of the following:
|  | 3115.8.4.3 Allowable shear value. | The allowable shear values for the intermodal shipping container corrugated steel sheet panel side walls and end walls shall be demonstrated by testing and analysis accordance with Section 104.11. Where penetrations are made in the side walls or end walls designated as part of the lateral force-resisting system, the penetrations shall be substantiated by rational analysis.
|  | 3115.8.5 Simplified structural design of single-unit containers. | Single-unit intermodal shipping containers conforming to the limitations of Section 3115.8.5.1 shall be permitted to be designed in accordance with the simplified structural design provisions of Section 3115.8.5.2.
|  | 3115.8.5.1 Limitations. | The use of Section 3115.8.5 is subject to the following limitations:
|  | 3115.8.5.2 Simplified structural design. | Where permitted by Section 3115.8.5.1, single-unit, stand-alone intermodal shipping containers shall be designed using the following assumptions for the corrugated steel shear walls:
|  | 3115.8.5.3 Allowable shear. | The allowable shear for the corrugated steel side walls (longitudinal) and end walls (transverse) for wind design and seismic design using the coefficients of Section 3115.8.5.2 shall be in accordance with Table 3115.8.5.3, provided that all of the following conditions are met: | See BC31 Tables and Figures

## BC32
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
3201.1 Scope. | The provisions of this chapter shall govern the encroachment of structures into the public right-of-way. | 3201.1 Scope. | The provisions of this chapter shall govern the encroachment of structures into the public right-of-way.
3201.1.1 Encroachments removable. | All encroachments permitted beyond the street line by the provisions of this chapter shall be constructed so that they may be removed at any time without endangering the structural safety or fire safety of the building except that footings as permitted under Section 3202.1.1 of this code need not be removable.
3201.2 Measurement. | The projection of any structure or portion thereof shall be the distance measured horizontally from the lot line to the outermost point of the projection. | 3201.2 Measurement. | The projection of any structure or portion thereof shall be the distance measured horizontally from the lot line to the outermost point of the projection.
3201.3 Other laws. | The provisions of this chapter shall not be construed to permit the violation of other laws regulating the use and occupancy of public property. | 3201.3 Other laws. | The provisions of this chapter shall not be construed to permit the violation of other laws or ordinances regulating the use and occupancy of public property.
3201.4 Drainage. | Drainage water collected from a roof, awning, canopy or marquee, other than canvas and flexible mate­rial, and condensate from mechanical equipment shall not flow over a public walking surface. | 3201.4 Drainage. | Drainage water collected from a roof, awning, canopy or marquee, and condensate from mechanical equipment shall not flow over a public walking surface.
3201.3.1 Restrictions on construction and projections on certain streets, parkways, boardwalks and beaches. | Notwithstanding the provisions of this chapter, it shall be unlawful to build, erect, or make areaways, steps or other encroachments or projections prohibited by Sections 19-131, 19-132, 19-135, 18-109, 18-112 and 18-113 of the Administrative Code.
3202.1 Encroachments below grade. | Encroachments below grade shall comply with Sections 3202.1.1 through 3202.1.6. | 3202.1 Encroachments below grade. | Encroachments below grade shall comply with Sections 3202.1.1 through 3202.1.3.
3201.5 Permission revocable. | Any permission, expressed or implied, permitting the construction of encroachments within the area of the street under the provisions of this chapter shall be revocable, except footings as permitted under Section 3202.1.1.
3201.6 Existing projections. | Any part of a building that projects beyond a street line on January 1, 1938, may be maintained as constructed until its removal is directed in accordance with applicable law.
3202.1.3 Areaways. | Areaways shall be protected by grates, guards or other approved means, subject to approval by the Commissioner of the Department of Transportation. | 3202.1.3 Areaways. | Areaways shall be protected by grates, guards or other approved means.
3201.7 Alteration of existing encroachments. | Alterations to existing encroachments beyond the street line may be permitted in whole or in part, provided that such alterations conform with the requirements of this chapter.
3201.7.1 Fences, guards and railings. | Elements of existing fences, guards and railings shall not be increased in height, thickness, spacing or opacity. Exceptions: 1. Fences, guards and railings that are required to comply with other requirements of this code, including Chapters 10 and 16. 2. Buildings or structures designated by the Landmarks Preservation Commission, where such fences, guards or railings are approved by the Landmarks Preservation Commission.
3201.8 Definitions. | The following terms are defined in Chapter 2:
3201.9 Department of Transportation approval. | Any encroachment into the public right-of-way that exceeds the limitation provided for in this chapter shall require the approval of the Department of Transportation.
3202.1.1 Footings. | Exterior wall and column footings may be constructed to project beyond the street line not more than 12 inches (305 mm), provided that the top of the footing is not less than 8 feet (2438 mm) below the ground or sidewalk level. Foundation walls required to support permitted projections may be constructed to project not more than the permitted projection beyond the street line.
3202.1.1.1 Footings for temporary barriers or shields in flood hazard areas or shaded X-Zones. | In flood hazard areas or shaded X-Zones, continuous footings for the support and attachment of temporary, removable dry floodproofing barriers or shields may be constructed to project beyond the street line not more than 12 inches (305 mm) both at grade and below grade.
3202.1.2 Vaults. | Vaults may be permitted in accordance with the New York City Charter and Title 19 of the Administrative Code. Such vaults shall comply with the provisions of this code and other applicable laws and rules.
3202.1.4 Tunnels between buildings. | Tunnels connecting buildings and projecting beyond street lines may be constructed subject to the approval of the Commissioner of the Department of Transportation. Such tunnels shall comply with the provisions of this code and other applicable laws and regulations.
3202.1.5 Sidewalk supports. | Exterior foundation walls are permitted to be constructed with a ledge that projects beyond the street line not more than 4 inches (102 mm) to support sidewalk construction, provided that:
3202.1.6 Insulation. | Insulation required to comply with the New York City Energy Conservation Code shall be permitted to encroach into the public right of way not more than 6 inches (152 mm) beyond the face of the structural element being insulated.
3202.2 Encroachments above grade. | Encroachments into the public right-of-way above grade shall be prohibited except as provided for in Sections 3202.2.1 through 3202.2.5.
3202.2.1 Encroachments subject to the area limitations. | Encroachments that are subject to area limitations are those elements listed in Sections 3202.2.1.1 through 3202.2.1.9, generally of an architectural character, that form an integral part of the building facade. The aggregate area of all such elements constructed to extend beyond the street line shall not exceed 10 square feet (0.93 m2) within any 10 feet (3048 mm) by 10 feet (3048 mm) square area of wall. The area of any such projection shall be measured at that vertical plane, parallel to the wall, in which the area of the projection is greatest. This plane of measurement may be at the street line, the line of maximum projection or any point in between. For the purpose of measuring the projected area of a balcony, air spaces of less than 6 inches (152 mm) between closely spaced railing or guards elements shall contribute to the area of the projection. Exceptions: 1. The aggregate area of all elements subject to area limitations that includes a balcony or associated railings and brackets shall not exceed 24 square feet (2.2 m2) in any 240 square foot (22.3 m2) area on a given story. 2. The aggregate area of elements on existing buildings or structures designated by the Landmarks Preservation Commission as landmarks or within historic districts shall not be limited provided that such elements are approved by the Landmarks Preservation Commission.
3202.2.1.1 Entrance details. | Entrance details, includ­ing steps and doors when fully open, may be constructed to project beyond the street line not more than 18 inches (457 mm). Entrance steps that project beyond the street line shall be guarded at each end by railings at least 3 feet (914 mm) high or by other members of the entrance detail providing equivalent protection.
3202.2.1.2 Architectural details. | Details such as cor­nices, eaves, bases, sills, headers, band course, opening frames, rustications, applied ornament or sculpture, grilles, windows when fully open, air conditioning units, and other similar elements may be constructed: 1. To project not more than 4 inches (102 mm) beyond the street line when less than 10 feet (3048 mm) above the ground or sidewalk level. 2. To project not more than 10 inches (254 mm) beyond the street line when more than 10 feet (3048 mm) above the ground or sidewalk level. Exceptions: 1. Replacement or restoration of historical architectural details that are, or were: 1.1. located more than 10 feet (3048 mm) above the sidewalk and that project more than 10 inches (254 mm), on existing buildings or structures designated by the Landmarks Preservation Commission, may be permitted provided they do not exceed the historic projections and provided that they are approved by the Landmarks Preservation Commission; or 1.2. located 10 feet (3048 mm) or less above the sidewalk, and that project more than 4 inches (102 mm), on existing buildings or structures designated by the Landmarks Preservation Commission, may be permitted provided they do not exceed the historic projections and provided that they are approved by the Landmarks Preservation Commission, and further provided that if the projection exceeds 18 inches (457 mm), the applicant demonstrates to the Department of Transportation’s satisfaction that the replacement or restoration will not adversely impact the use of the public right of way. 2. New architectural details on new or existing buildings, additions or structures subject to the jurisdiction of the Landmarks Preservation Commission, that are more than 10 feet (3048 mm) above the sidewalk and that project more than 10 inches (254 mm) and no more than 3 feet (914 mm), may be permitted provided that the Landmarks Preservation Commission finds that the proposed detail is appropriate to the historic character of the historic district or landmarked building, structure or site.
3202.2.1.3 Balconies. | Balconies, including railings and supporting brackets, no parts of which are less than 10 feet (3048 mm) above the ground or sidewalk level, may be constructed to project not more than 2 feet 6 inches (762 mm) beyond the street line. When permitted by the provisions of this code, fire escapes that are part of a required exit may be constructed to project not more than 4 feet 6 inches (1372 mm) beyond the street line provided no part, including any movable ladder or stair, is lower than 10 feet (3048 mm) above the ground or sidewalk level when not in use.
3202.2.1.4 Marquees. | Marquees may be constructed to project beyond the street line provided that they comply with Section 3106 and Sections 3202.2.1.4.1 through 3202.2.1.4.5.
3202.2.1.4.1 Height. | Marquees shall receive structural support only from the building and shall be at least 10 feet (3048 mm) above the ground level or sidewalk.
3202.2.1.4.2 Projection. | Marquees shall project no closer to the curb line than 2 feet (610 mm).
3202.2.1.4.3 Thickness. | Marquees shall be no thicker nor shall the fascia be higher than 3 feet (914 mm) when measured vertically from its lowest to its highest point.
3202.2.1.4.4 Dimensions. | Dimensions shall include all decoration but shall exclude any tension supports suspending the marquee from the wall.
3202.2.1.4.5 Occupancy restrictions. | Marquees may be erected on:
3202.2.1.4.6 Change of occupancy. | When the occupancy or use of a building with a marquee is changed to an occupancy or use for which a projecting marquee is not permitted, the marquee shall be removed. Exception: For buildings subject to the jurisdiction of the Landmarks Preservation Commission, Section 3202.2.1.4.6 shall not apply when the Landmarks Preservation Commission makes a determination that the removal of the marquee would be inappropriate to the architectural character of the building or historic district.
3202.2.1.4.7 Other agency approvals. | An applicant wishing to erect a marquee shall provide proof that the Commissioners of the Departments of Transporta­tion, Consumer Affairs, and Environmental Protection have not permitted the use of a space or structure on or under the sidewalk beneath the proposed marquee in such a manner that the construction of the proposed marquee shall interfere with the removal or repair of any such permitted use or structure.
3202.2.1.5 Light fixtures. | Light fixtures that are sup­ported entirely from the building may be constructed to project not more than 2 feet (610 mm) beyond the street line, provided no part of the fixture is less than 8 feet (2438 mm) above the ground or sidewalk level.
3202.2.1.6 Flagpoles. | Flagpoles that are supported entirely from the building may be constructed to project not more than 18 feet (5486 mm) beyond the street line, but not closer than 2 feet (610 mm) to the curb line, provided that no part of the flagpole is less than 15 feet (4572 mm) above the ground or sidewalk level.
3202.2.1.7 Wall signs. | Wall signs may be constructed to project not more than 12 inches (305 mm) beyond the street line when conforming to the requirements of this code and Section H111 of Appendix H.
3202.2.1.8 Projecting signs. | All permitted projecting signs may be constructed to project not more than 10 feet (3048 mm) beyond the street line, but not closer to the curb line than 2 feet (610 mm), when conforming to the requirements of this code and Section H112 of Appendix H, and provided that no part of the sign is less than 10 feet (3048 mm) above the ground or sidewalk level. Exceptions: Permanent projecting signs are prohibited on buildings in the areas indicated below: 1. Borough of Manhattan. 1.1. Projecting signs. No permanent projecting sign shall be erected on any building on: 1.1.1. 5th Avenue between Washington Square north and 110th Street; 1.1.2. 34th Street between Park Avenue and 7th Avenue; 1.1.3. Madison Avenue between 23rd Street and 96th Street; 1.1.4. 57th Street between Lexington Avenue and Broadway; 1.1.5. Vanderbilt Avenue between 42nd Street and 47th Street; 1.1.6. Park Avenue between 32nd Street and 40th Street; 1.1.7. Park Avenue between 45th Street and 96th Street; 1.1.8. 33rd Street between Lexington Avenue and 5th Avenue; 1.1.9. 35th through 41st Streets between Lexington Avenue and 5th Avenue; 1.1.10. 43rd through 56th Streets between Lexington Avenue and 5th Avenue; 1.1.11. 58th Street between Lexington Avenue and 5th Avenue; 1.1.12. 60th Street between Lexington Avenue and 5th Avenue; 1.1.13. Nassau Street between Wall Street and Frankfort Street; or 1.1.14. John Street between Broadway and William Street. 1.2. Illuminated projecting signs. No permanent illuminated projecting sign shall be erected on any building on: 1.2.1. 72nd Street between Central Park West and River Drive. 2. Borough of Brooklyn. 2.1. Projecting signs. No permanent projecting sign shall be erected on any building on: 2.1.1. Fulton Street between Flatbush Avenue and Joralemon Street and Willoughby Street. 2.2. Illuminated projecting signs. No per¬manent illuminated projecting sign shall be erected on any building on: 2.2.1. Fulton Street between Flatbush Avenue and Prospect Street and Henry Street; 2.2.2. Washington Street between Myrtle Avenue and Prospect Street; 2.2.3. Court Street between Fulton Street and Livingston Street; 2.2.4. Pierrepont Street between Fulton Street and Clinton Street; 2.2.5. Montague Street between Court Street and Clinton Street; 2.2.6. Remsen Street between Court Street and Clinton Street; or 2.2.7. Joralemon Street between Court Street and Clinton Street.
3202.2.1.9 Sun control devices. | Sun control devices constructed in accordance with Section 3105 and supported entirely from the building may project beyond the street line not more than 2 feet 6 inches (762 mm), provided that no part of the sun control device is less than 8 feet (2438 mm) above the ground or sidewalk level. Any portion of a sun control device that is located over a sidewalk vault and is more than 10 inches (254 mm) beyond the street line and less than 40 feet above the ground or sidewalk shall be removable or retractable to less than 10 inches (254 mm) beyond the street line.
3202.2.2 Encroachments not subject to area limitations.
3202.2.2.1 Ramps. | When a building erected prior to December 6, 1969, is altered to provide access to individuals who use wheelchairs, ramps constructed to provide such access may, with the approval of the commissioner, project beyond the street line for a distance of not more than 44 inches (1118 mm). Ramps shall comply with the applicable provisions of Chapter 11.
3202.2.2.2 Bridges between buildings. | Bridges connecting buildings and projecting beyond street lines may be permitted in accordance with applicable law. Such bridges shall be of a construction class that is at least equal to the higher class of the two buildings connected and shall otherwise comply with the provisions of this code and other applicable laws and rules.
3202.2.2.3 Flood shield supports. | In flood hazard areas or shaded X-Zones, permanent attachments to building façades necessary for the support and attachment of temporary, removable dry floodproofing barriers or shields may be constructed to project beyond the street line for a distance of not more than 6 inches (152 mm).
3202.2.2.4 Curb cuts. | The lowering of any curb or the change of grade of any sidewalk for the purpose of providing a driveway across such curb or sidewalk shall be constructed in accordance with the specifications prescribed in Section 406.10.
3202.2.2.4.1 Curb cut removal. | Vehicular access curb cuts that can no longer serve as vehicular access across a curb or sidewalk, including where an existing building served by such a curb cut is demolished, shall be removed and the curb and sidewalk shall be restored in accordance with standards of the Department of Transportation. The commissioner may order such removal and restoration. The commissioner shall limit the length of any curb cut for the purpose of providing a driveway across such curb or sidewalk, when in the opinion of the commissioner the actual use or intended use of such driveway would endanger the public. Where the vehicular use of such driveway, in the opinion of the commissioner is dangerous to the public, the commissioner shall order the owner to discontinue use of such driveway and restore the curb and sidewalk in accordance with standards of the Department of Transportation. Upon the failure of the owner to comply with any of the orders provided for in Section 3202.2.2.4, in such cases where the restoration of such curb cuts are needed to facilitate department of transportation work, the commissioner may inform the commissioner of transportation of such failure to comply and may request the cooperation of the commissioner of transportation acting under his or her authority pursuant to Section 2903(b)(7) of the New York City Charter in the enforcement of this section.
3202.2.3 Awnings. | Awnings constructed in accordance with Section 3105 and supported entirely from the building may project beyond the street line as follows: | 3202.2.3 Awnings. | The vertical clearance from the public right-of-way to the lowest part of any awning, including valances, shall be not less than 7 feet (2134 mm).
3202.2.3.1 Store front awnings. | Store front awnings may project beyond the street line not more than 8 feet (2438mm), provided no part of the awning is less than 8 feet (2438 mm) above the ground or sidewalk level, except for a flexible valance which may be not less than 7 feet (2134 mm) above the ground or sidewalk level, and provided that the awning box or cover does not project more than 12 inches (305 mm).
3202.2.3.2 Awnings over windows or doors. | Awnings over windows or doors may project beyond the street line not more than 5 feet (1524 mm), provided that no part of the awning is less than 8 feet (2438 mm) above the ground or sidewalk level.
3202.2.4 Fire department connections, caps or plugs. | Fire department connection swivels, caps and plugs including test headers shall be permitted to project beyond the street line as provided for in NFPA 14, as amended by Appendix Q of this code.
3202.2.5 Exterior wall covering systems for prior code buildings. | For prior code buildings, exterior insulation and associated cladding systems (i.e. rain screens, EIFS, etc.) may be applied to the entire facade of a building provided such exterior wall covering system is needed to comply with the requirements of the New York City Energy Conservation Code and does not project more than 8 inches (203 mm) beyond the street line. Exterior wall coverings shall comply with Chapter 14. Exceptions: 1. A veneer may be applied to the entire facade of a building erected before December 6, 1968, provided such veneer does not project more than 4 inches (102 mm) beyond the street line. 2. Exterior wall covering systems projecting not more than 10 inches (254 mm) beyond the street line shall be permitted to cover the façade of a prior code building provided they are located more than 10 feet (3048 mm) above grade and are necessary to comply with the New York City Energy Conservation Code. 3. The department may approve exterior wall covering systems projecting not more than 12 inches (305 mm) beyond the street line provided they are necessary to comply with the New York City Energy Conservation Code, are substantiated with engineering calculations demonstrating need and practical difficulty, and provided that the applicant demonstrates to the Department of Transportation’s satisfaction that the projection of the wall covering system will not adversely impact the use of the public right of way.
3202.3 Temporary encroachments. | Encroachments of temporary nature shall comply with Sections 3202.3.1 through 3202.2.3.
3202.3.1 Sidewalk cafés. | Enclosures for sidewalk cafés, where permitted by the Commissioner of the Department of Consumer Affairs pursuant to applicable law and constructed in compliance with Section 3111, may be constructed beyond the street line.
3202.3.2 Temporary storm enclosures. | Construction of temporary storm enclosures must comply with the requirements of this code, including the fire-resistance rating of the building to which it is appurtenant, and Chapter 11. Such enclosures may be permitted during the period between November 15 and the following April 15 and must be removed at the end of this period.
3202.3.2.1 Temporary storm enclosures for eating and drinking establishments. | Provided a minimum clear unobstructed sidewalk width of 5 feet is maintained, temporary storm enclosures for eating and drinking establishments with a projection of not more than 25 square feet (2.32 m2) in area and door maneuvering clearances complying with Chapter 11, and related reference standards, including Section 404 (Doors and Doorways) of ICC A117.1, may be permitted.
3202.3.2.2 Temporary storm enclosures for other establishments. | Temporary storm enclosures projecting not more than 18 inches (457 mm) beyond the street line may be permitted at other establishments.
3202.3.3 Temporary flood shields, stairs and ramps in flood hazard areas and shaded X-Zones. | In flood hazard areas and shaded X-Zones, temporary flood shields, stairs and ramps shall comply with Sections G308.9 and G308.10 of Appendix G of the New York City Building Code and shall be permitted in accordance with plans approved by the department subject to the following conditions:
|  | 3202.1.1 Structural support. | A part of a building erected below grade that is necessary for structural support of the building or structure shall not project beyond the lot lines, except that the footings of street walls or their supports that are located not less than 8 feet (2438 mm) below grade shall not project more than 12 inches (305 mm) beyond the street lot line.
|  | 3202.1.2 Vaults and other enclosed spaces. | The construction and utilization of vaults and other enclosed spaces below grade shall be subject to the terms and conditions of the applicable governing authority.
|  | 3202.2 Encroachments above grade and below 8 feet in height. | Encroachments into the public right-of-way above grade and below 8 feet (2438 mm) in height shall be prohibited except as provided for in Sections 3202.2.1 through 3202.2.3. Doors and windows shall not open or project into the public right-of-way.
|  | 3202.2.1 Steps. | Steps shall not project more than 12 inches (305 mm) and shall be guarded by approved devices not less than 3 feet (914 mm) in height, or shall be located between columns or pilasters.
|  | 3202.2.2 Architectural features. | Columns or pilasters, including bases and moldings, shall not project more than 12 inches (305 mm). Belt courses, lintels, sills, architraves, pediments and similar architectural features shall not project more than 4 inches (102 mm).
|  | 3202.3 Encroachments 8 feet or more above grade. | Encroachments 8 feet (2438 mm) or more above grade shall comply with Sections 3202.3.1 through 3202.3.4.
|  | 3202.3.1 Awnings, canopies, marquees and signs. | Awnings, canopies, marquees and signs shall be constructed so as to support applicable loads as specified in Chapter 16. Awnings, canopies, marquees and signs with less than 15 feet (4572 mm) of clearance above the sidewalk shall not extend into or occupy more than two-thirds the width of the sidewalk measured from the building. Stanchions or columns that support awnings, canopies, marquees and signs shall be located not less than 2 feet (610 mm) in from the curb line.
|  | 3202.3.2 Windows, balconies, architectural features and mechanical equipment. | Where the vertical clearance above grade to projecting windows, balconies, architectural features or mechanical equipment is more than 8 feet (2438 mm), 1 inch (25 mm) of encroachment is permitted for each additional 1 inch (25 mm) of clearance above 8 feet (2438 mm), but the maximum encroachment shall be 4 feet (1219 mm).
|  | 3202.3.3 Encroachments 15 feet or more above grade. | Encroachments 15 feet (4572 mm) or more above grade shall not be limited.
|  | 3202.3.4 Pedestrian walkways. | The installation of a pedestrian walkway over a public right-of-way shall be subject to the approval of the applicable governing authority. The vertical clearance from the public right-of-way to the lowest part of a pedestrian walkway shall be not less than 15 feet (4572 mm).
|  | 3202.4 Temporary encroachments. | Where allowed by the applicable governing authority, vestibules and storm enclosures shall not be erected for a period of time exceeding 7 months in any 1 year and shall not encroach more than 3 feet (914 mm) nor more than one-fourth of the width of the sidewalk beyond the street lot line. Temporary entrance awnings shall be erected with a clearance of not less than 7 feet (2134 mm) to the lowest portion of the hood or awning where supported on removable steel or other approved noncombustible support.

## BC33
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
3301.1 Scope. | The provisions of this chapter shall govern the conduct of all construction or demolition operations with regard to the safety of the public and property. For regulations relating to the safety of persons employed in construction or demolition operations, OSHA standards shall apply. | 3301.1 Scope. | The provisions of this chapter shall govern safety during construction and the protection of adjacent public and private properties.
3301.1.1 Responsibility for safety. | Nothing in this chapter shall be construed to relieve persons engaged in construction or demolition operations from complying with other applicable provisions of law, nor is it intended to alter or diminish any obligation otherwise imposed by law on any party engaged in a construction or demolition operation, including but not limited to the owner, construction manager, general contractor, sub contractors, material men, registered design professionals, or other party to engage in sound design and engineering, safe construction or demolition practices, including but not limited to debris removal, and to act in a reasonable and responsible manner to maintain a safe construction or demolition site.
3301.1.2 Fire code. | In addition to the requirements of this chapter, construction or demolition operations shall also be conducted in conformance with the New York City Fire Code.
3301.1.3 Manufacturer specifications. | See Section 3301.6.1.
3301.1.4 Sizes. | All sizes and dimensions prescribed in this chapter are minimum requirements, unless otherwise specified. Lumber sizes are nominal or commercial except where stated otherwise.
3301.2 Safety measures and standards. | Contractors, construction managers, and subcontractors engaged in construction or demolition operations shall institute and maintain all safety measures required by this chapter and provide all equipment or temporary construction installations necessary to safeguard the public and property affected by such contractor’s operations.
3301.3 Site safety managers, coordinators and construction superintendents. | A site safety manager or site safety coordinator must be designated and present at the construction or demolition of a major building in accordance with Section 3310. A construction superintendent is required for the construction or demolition of buildings as identified in Section 3301.13.3.
3301.4 Inspection. | Structures, temporary construction installations, materials, operations, and equipment shall be inspected as required by this code, and records of such inspections shall be maintained as required by this code.
3301.4.1 Inspection of equipment where the code does not specifically require an inspection. | Where this code does not specifically require an inspection, any equipment, except hand tools, that would affect the safety of the public and property when operated shall be inspected by a competent person designated by the contractor using the equipment before the equipment is used at the site and on a periodic basis thereafter throughout the duration of the job. The results of the inspection shall be documented in an inspection checklist signed and dated by the competent person who performed the inspection.
3301.5 Unsafe conditions. | Any structure, temporary construction installation, material, operation, or equipment found to be defective or unsafe, and posing a risk to the public and property, shall be immediately secured and corrected, or removed from the site.
3301.6 Manufacturer specifications, design, and capacity. | The permit holder, or where there is no permit holder, the contractor or other entity causing the work to be performed, shall ensure compliance with manufacturer specifications, design documents, and capacity restrictions in accordance with Sections 3301.6.1 through 3301.6.5 and other applicable sections of the code. Where there is a discrepancy between a manufacturer specification, design document, capacity restriction, or other applicable code section, the more stringent requirement shall apply.
3301.6.1 Manufacturer specifications. | During construction or demolition operations, structures, building systems or components, temporary construction installations, materials, and equipment shall be installed, removed, and utilized in accordance with the specifications of their manufacturer, where such specifications exist.
3301.6.2 Design requirements. | Whenever design is required by this chapter, the design shall be in accordance with the requirements of this code. This requirement does not alleviate any other design requirements imposed by law or the manufacturer.
3301.6.3 Designer. | Where design is required by this chapter, the design shall be executed by or under the supervision of a registered design professional, who shall cause his or her seal and signature to be affixed to such documents that may be required for the work Exception: Where this chapter specifically indicates that the design may be executed by another individual.
3301.6.4 Capacity. | No structure, building system or component, temporary construction installation, material, or equipment, including any partially or fully completed element or section, shall be utilized in excess of its capacity.
3301.6.5 Design documents. | Whenever design is required by this chapter, the design shall be indicated in plans and specifications and other written, graphic and pictorial documents that are prepared or assembled for describing the design, location, physical characteristics, and other elements of the project. Design documents shall be complete and of sufficient clarity to indicate the location and entire nature and extent of the work proposed, and shall show in detail that the work conforms to the provisions of this code and other applicable laws and rules.
3301.7 Documents to be maintained on site. | Where this chapter requires documents, including but not limited to construction documents, submittal documents, shop drawings, inspection reports, logs, checklists, meeting records, pre-construction surveys, designation letters, site safety plans, fire safety and evacuation plans, tenant protection plans, occupant protection plans, or monitoring plans, copies of such documents shall be maintained at the site for the duration of the job and made available to the commissioner upon request. Copies of required construction documents or other design drawings shall also be maintained by the permit holder and the designer. Copies of required inspection records, including but not limited to reports, logs, or checklists, shall also be maintained by the permit holder and the entity that performed the inspection. Copies of required plans shall also be maintained by the permit holder and the entity that developed the plan. Copies of all other documents required by this chapter shall also be maintained by the permit holder.
3301.7.1╪ Other obligations. | Where this chapter requires documents to be maintained by another specified entity, such documents shall be maintained by such specified entity.
3301.7.2 Manufacturer specifications. | Where compliance with manufacturer specifications is required by this chapter, copies of such manufacturer specifications shall be available at the site and made available to the commissioner upon request. Manufacturer specifications that can be readily downloaded from the manufacturer’s website or that are stored in an electronic format acceptable to the commissioner shall satisfy the requirements of this section. A serial number, make and model number, or other similar identification shall be maintained in a legible condition on the item for which the manufacturer specification is required such that the identification can be used to match the item to the manufacturer specification. Exception: Where this chapter specifically requires that the manufacturer specifications for a specific item be physically maintained at the site, downloadable or electronically formatted manufacturer specifications will not satisfy the accessibility and availability requirements of this section.
3301.8 Incidents and damage to adjoining property. | The department shall be notified immediately by the permit holder, or a duly authorized representative, of any incident at a construction or demolition site, or of any damage to adjoining property caused by construction or demolition activity at the site. Where required by Section 3301.13.11 or Section 3310.8.2.1, incidents or damage to adjoining property shall instead be reported by the construction superintendent or the site safety manager or coordinator.
3301.8.1 Additional notifications. | Nothing in this section shall diminish or relieve other notification requirements imposed by this chapter, including but not limited to, notifications by the site safety manager, site safety coordinator, concrete safety manager, or hoisting machine operator.
3301.8.2 Use and tampering prohibited. | Following an incident, no person shall permit any of the following without the permission of the commissioner, or without a lawful order from the New York city police or fire department: 1. Use or operation of any equipment or structure damaged or involved in the incident; or 2. Removal or alteration of any equipment, structure, material, or evidence related to the incident. Exception: Immediate emergency procedures taken to secure structures, temporary construction installations, operations, or equipment that pose a continued imminent danger or to facilitate assistance for persons who are trapped or who have sustained bodily injury.
3301.9 Signs at a construction or demolition site. | Signs shall be posted at a construction or demolition site in accordance with Sections 3301.9.1 through 3301.9.8. It is the responsibility of the permit holder for the underlying construction or demolition work, or where there are no active permits, the building owner, to ensure such signs are posted and maintained at the site in accordance with Sections 3301.9.1 through 3301.9.8, and to ensure that such signs are updated in a timely fashion to reflect any revised information.
3301.9.1 Fence project information panel. | Where a site is enclosed with a fence in accordance with Section 3307.7, a project information panel meeting the requirements of Sections 3301.9.1.1 through 3301.9.1.6 shall be posted. Required project information panels shall be in place throughout the duration that the fence remains at the site. Exception: Project information panels at government-owned sites or at sites with government funding may be modified in accordance with department rule.
3301.9.1.1 Project information panel content. | Project information panels shall contain the following information: 1. A rendering, elevation drawing, or zoning diagram of the building exterior that does not contain logos or commercially recognizable symbols; 2. A title stating “Work in Progress:” and specifying the intended type(s) of zoning use(s) (e.g. Residential, Commercial, Manufacturing, Retail, Office, Hospital, School); 3. Anticipated project completion date; 4. The corporate name, address, and telephone number of the owner of the property; 5. Website address or phone number to contact for project information; 6. The corporate name and telephone number of the general contractor, or for a demolition site, the demolition contractor; 7. The statement, in both English and Spanish, “TO ANONYMOUSLY REPORT UNSAFE CONDITIONS AT THIS WORK SITE, CALL 311.”; and 8. A copy of the primary project permit, with accompanying text “To see other permits issued on this property, visit: www.nyc.gov/buildings.” The permit shall be laminated or encased in plastic covering to protect it from the elements or shall be printed directly onto the project information panel. Exception: A rendering, elevation drawing, or zoning diagram of the building exterior is not required for demolition projects.
3301.9.1.2 Posting of project information panels. | A project information panel shall be posted on the fence on each perimeter fronting a public thoroughfare. Where such perimeter is more than 150 feet (45 720 mm) in length, a project information panel shall be posted at each corner. Such panels shall be posted on the fence at a height of 4 feet (1219 mm) above the ground, with such distance measured from the ground to the bottom edge of the panel.
3301.9.1.3 Project information panel material. | Project information panels shall be constructed out of a durable and weatherproof material such as vinyl, plastic, or aluminum, and such material shall be flame retardant in accordance with NFPA 701 or listed under UL 214.
3301.9.1.4 Project information panel specifications. | Project information panels shall be 6 feet (1829 mm) wide and 4 feet (1219 mm) high, with the content required by Section 3301.9.1.1 arranged in accordance with Figures 3301.9.1.4(1) and 3301.9.1.4(2). The content required by Section 3301.9.1.1, Items 2 through 7, shall be written in the Calibri font or similar sans serif font style, with letters a minimum of 1 inch (25 mm) high, as measured by the upper case character. Such letters shall be white, on a blue background, with such blue color of a shade matching Pantone 296, or RGB 15, 43, 84, or CMYK 100, 88, 38, 35. Exceptions: 1. The dimensions for a project information panel posted in conjunction with a demolition project shall be 2 feet 4 inches (711 mm) wide and 4 feet (1219 mm) high, in accordance with Figure 3301.9.1.4(1). 2. For construction sites with a street frontage less than 60 feet (18 288 mm), the dimensions for a project information panel, other than that posted in conjunction with a demolition project, shall be 55 inches (1397 mm) wide and 36.5 inches (927 mm) high, in accordance with Figure 3301.9.1.4(3).
3301.9.1.5 Updating content. | When content required by Section 3301.9.1.1 changes, the project information panel shall be updated.
3301.9.1.6 Maintenance of project information panels. | Project information panels shall be maintained so that the panel remains legible, securely attached, and free of sharp edges, protruding nails, or similar hazards. Content required by Section 3301.9.1.1 shall not be obscured by panel attachments, including but not limited to grommets or grommet holes.
3301.9.2 Sidewalk shed parapet information panel. | Where a sidewalk shed is installed, a sidewalk shed parapet information panel meeting the requirements of Sections 3301.9.2.1 through 3301.9.2.6 shall be posted. Required sidewalk shed parapet information panels shall be in place throughout the duration that the sidewalk shed remains at the site.
3301.9.2.1 Sidewalk shed parapet information panel content. | Sidewalk shed parapet information panels shall contain the following information and be arranged in accordance with Figure 3301.9.2.1:
3301.9.2.2 Posting of sidewalk shed parapet information panels. | Sidewalk shed parapet information panels shall be posted on the parapet that runs along the long axis of the sidewalk shed. Where a sidewalk shed extends along multiple street frontages, not including incidental extensions at a street corner, a parapet information panel shall be posted along each long axis. Such sidewalk shed parapet information panel:
3301.9.2.3 Sidewalk shed parapet information panel material. | Sidewalk shed parapet information panels shall be constructed out of a durable and weatherproof material such as vinyl, plastic, or aluminum, and such material shall be flame retardant in accordance with NFPA 701 or listed under UL 214.
3301.9.2.4 Sidewalk shed parapet information panel specifications. | Sidewalk shed parapet information panels shall be 3 feet (914 mm) high and 6 feet (1829 mm) wide, with the content required by Section 3301.9.2.1 arranged in accordance with Figure 3301.9.2.1. The sign shall have a white background. The content required by Section 3301.9.2.1 must be written in Calibri font or similar sans serif font style, and such letters shall be blue, with such blue color a shade matching Pantone 296, or RGB 15, 43, 84, or CMYK 100, 88, 38, 35.
3301.9.2.5 Updating content. | When content required by Section 3301.9.2.1 changes, the sidewalk shed parapet information panel shall be updated.
3301.9.2.6 Maintenance of sidewalk shed parapet information panels. | Sidewalk shed parapet information panels shall be maintained so that the panel remains legible, securely attached, and free of sharp edges, protruding nails, or similar hazards. Content required by Section 3301.9.2.1 shall not be obscured by sign attachments, including but not limited to grommets or grommet holes.
3301.9.3 Reserved.
3301.9.4 Reserved.
3301.9.5 Other temporary signs required by law. | Other temporary signs required by law to be displayed at a construction or demolition site shall be posted within the site, readily visible to workers, and shall not be posted in any location readily visible to the public unless otherwise required by law.
3301.9.6 Obscured lawful signs. | When a protective structure constructed in accordance with Section 3307 obscures from view a lawful and existing sign, a temporary sign may be posted on such protective structure. The temporary sign shall comply with the following requirements:
3301.9.7 Other signs prohibited. | Except as specified by Sections 3301.9.1 through 3301.9.6 or as otherwise authorized by law, no sign, information, pictorial representation, or any business or advertising message shall be posted on any construction or demolition equipment or temporary construction installation, including but not limited to, protective structures.
3301.9.8 Illuminated signs prohibited. | No illuminated business or advertising sign shall be permitted on any construction or demolition equipment or temporary construction installation, including but not limited to, protective structures.
3301.10 Reserved.
3301.11 Site safety orientation and refresher. | Each permit holder at a site that requires a site safety manager, site safety coordinator, or construction superintendent shall ensure that each construction or demolition worker employed or otherwise engaged at such site by the permit holder or performing subcontracted work for or on behalf of such permit holder receives a site safety orientation and refresher in accordance with the requirements of Sections 3301.11.1 through 3301.11.5.
3301.11.1 Site safety orientation. | Each worker employed or otherwise engaged at such site by the permit holder or performing subcontracted work for or on behalf of such permit holder shall receive a site safety orientation before such worker commences any construction or demolition work at such site.
3301.11.2 Site safety refresher. | Each worker employed or otherwise engaged at such site by the permit holder or performing subcontracted work for or on behalf of such permit holder shall receive a site safety refresher if such worker (i) has performed construction or demolition work at such site for one year or more and (ii) one year or more has elapsed since such worker received a site safety orientation or refresher with respect to such site.
3301.11.3 Site safety orientation and refresher to be conducted by qualified person. | Site safety orientations and refreshers required by this section shall be conducted by a qualified person designated by the permit holder. Such qualified person shall have the ability to communicate with each worker who takes part in such orientation or refresher.
3301.11.4 Site safety orientation and refresher content. | Site safety orientations and refreshers required by this section shall include a review of safety procedures at such site and any hazardous activities to be performed at such site. In addition, information pertaining to the site safety training required by Section 3321 shall be made available to each worker in the designated citywide languages, as such term is defined in Section 23-1101 of the Administrative Code, and any other language as may be required by rule of the department, in a form and manner established by the department.
3301.11.5 Records. | A record of all orientations conducted for the site shall be maintained by the permit holder and kept at the site. Such record shall include for each such orientation or refresher:
3301.12 Pre-shift safety meetings. | Each permit holder at a site that requires a site safety manager, site safety coordinator, or construction superintendent shall ensure that each construction or demolition worker employed or otherwise engaged at such site by the permit holder or performing subcontracted work for or on behalf of such permit holder takes part in a safety meeting at the beginning of such worker’s shift, but before such worker commences any construction or demolition work in such shift, in accordance with the requirements of Sections 3301.12.1 through 3301.12.3. Exception: Where other sections of this code or rules promulgated thereunder specify pre-task or pre-shift meetings for specific types of work, those requirements shall instead apply.
3301.12.1 Pre-shift safety meeting to be conducted by a competent person. | Pre-shift safety meetings shall be conducted at the beginning of each worker’s shift, but before such worker commences any construction or demolition work in such shift, by a competent person designated by the permit holder, or where so authorized by the permit holder, by a competent person designated by the subcontractor. Such competent person shall have the ability to communicate with each worker who takes part in such meeting.
3301.12.2 Pre-shift safety meeting content. | The pre-shift safety meeting shall include a review of activities and tasks to be performed during the shift, including specific safety concerns or risks associated with fulfilling such work.
3301.12.3 Records. | The permit holder shall maintain, for each worker, a record of one pre-shift safety meeting per week. Such record shall include for each such meeting:
3301.13 Scope. | This section sets forth requirements for construction superintendents at certain construction or demolition sites.
3301.13.1 Site safety plan. | For jobs that require the designation of a primary construction superintendent pursuant to Section 3301.13.3, a site safety plan that meets the applicable requirements of Article 110 of Chapter 1 of Title 28 of the Administrative Code shall be kept on site and made available to the department upon request. Prior to the commencement of work, the permit holder must submit a statement to the department attesting that the site safety plan meets the requirements of Article 110 of Chapter 1 of Title 28 of the Administrative Code and coordinates with the scope of work intended. Exception: For a major building subject to the provisions of Section 3310, the site safety plan requirements of Section 3310.3 shall apply.
3301.13.2 Definitions. | For the purposes of this section, the following terms shall have the following meanings:
3301.13.3 Designation of primary construction superintendent. | The permit holder shall designate a primary construction superintendent who shall carry out all duties and responsibilities assigned to the construction superintendent by this chapter and rules promulgated by the commissioner, and notify the department of such designation, prior to the commencement of work, for the following types of jobs: 1. The construction of a new building; 2. The full demolition of an existing building; 3. An alteration to an existing building that involves one or more of the following: 3.1 A vertical enlargement; 3.2 A horizontal enlargement; 3.3 The alteration or demolition of more than 50 percent of the gross floor area of the building during the course of work over any 12-month period; 3.4 The removal of one or more floors during the course of work over any 12-month period; 3.5 Work that requires a special inspection for underpinning; or 3.6 Work that requires a special inspection for the protection of sides of excavations; or 4. Other jobs that pose an enhanced risk to the public and property, as determined by the commissioner. Exception: A construction superintendent is not required for work that solely involves a 1-, 2-, or 3-family building, or an accessory use to such building, provided the permit holder for such work is registered as a general contractor in accordance with Article 418 of Chapter 4 of Title 28 of the Administrative Code.
3301.13.4 Change of designation. | The permit holder must immediately notify the department of any permanent change to the primary construction superintendent.
3301.13.5 Alternate construction superintendent. | In the event the primary construction superintendent is temporarily unable to perform their duties, an alternate construction superintendent, designated by the permit holder, must act in place of the primary construction superintendent and carry out all duties and responsibilities assigned to the construction superintendent by this chapter and rules promulgated by the commissioner. In the event that an alternate construction superintendent will be acting in place of the primary construction superintendent for a period longer than two consecutive weeks, the permit holder must notify the department of such circumstance.
3301.13.6 Limitations on the designation of primary or alternate construction superintendents. | An individual may only be designated as a primary or alternate construction superintendent for that number of jobs for which he or she can adequately perform all required duties. No individual may be designated as the primary construction superintendent on more than ten jobs. Exceptions: 1. If one of the jobs for which the construction superintendent is designated as a primary construction superintendent is on a building that meets the definition of a major building, the individual may only be designated as the primary construction superintendent for that job and may not serve as the primary construction superintendent for any other job. 2. Notwithstanding exception 1, beginning on June 1, 2022, no individual may be designated as the primary construction superintendent for more than five jobs. 3. Notwithstanding exception 1, beginning on January 1, 2024 or a later date established by the department, provided that such date is not later than January 1, 2025, no individual may be designated as the primary construction superintendent for more than three jobs. 4. Notwithstanding exception 1, beginning on January 1, 2026 or a later date established by the department, provided that such date is not later than January 1, 2027, no individual may be designated as the primary construction superintendent for more than one job. 5. A construction superintendent designated as the primary construction superintendent at a job site may serve as a non-primary construction superintendent at another job site, provided there is no work requiring the presence of such individual occurring at the job site for which the individual has been designated as the primary construction superintendent. 6. Subject to the approval of the commissioner, a construction superintendent may serve as the primary construction superintendent for multiple non-major building jobs located on the same lot or on contiguous lots.
3301.13.7 Duties of construction superintendents. | The duties of a construction superintendent shall include: 1. Acting in a reasonable and responsible manner to maintain a safe job site and ensure compliance with this chapter and any rules promulgated thereunder at each job site for which the construction superintendent is responsible; 2. To the extent that a registered design professional or special inspection agency is not responsible, the construction superintendent must ensure compliance with the approved documents at each job site for which the construction superintendent is responsible; 3. Fulfilling the duties of a superintendent of construction assigned by Chapter 1 of Title 28 of the Administrative Code at each job site for which the construction superintendent is responsible; and 4. Visiting each job site for which the construction superintendent is responsible each day when active work is occurring; or, beginning January 1, 2026 or a later date established by the department, provided that such date is not later than January 1, 2027, where Section 3301.13.6 requires the construction superintendent to be dedicated to one job, being present at the job site for which the construction superintendent is responsible during all times when active work is occurring. Exception: The construction superintendent is not required to be present at the site during the following activities, provided no other work is in progress: 1. Surveying that does not involve the disturbance of material, structure, or earth; 2. Use of a hoist exterior to the building to transport personnel only; 3. Use of a hoist that is fully enclosed within the perimeter of the building to transport personnel or material; 4. Work limited to finish troweling of concrete floors; 5. Work limited to providing the site with temporary heat, light, or water; or 6. Truck deliveries to the site, provided the delivery occurs within the site while the gate is closed and flagpersons are provided to direct traffic while the truck is entering and exiting the site; 7. Painting; or 8. Landscaping that does not that does not involve the disturbance of material, structure, or earth.
3301.13.8 Inspection by the construction superintendent. | Each time the construction superintendent visits a job site for which he or she is responsible, the construction superintendent must inspect all areas and floors where construction or demolition work, and ancillary activity, is occurring, and: 1. Verify work is being conducted in accordance with sound construction/demolition practices; 2. Verify compliance with the approved documents; and 3. Verify compliance with this chapter and any rules promulgated thereunder. Exception: Where a site safety manager or coordinator has been designated for the job in accordance with Section 3310, the construction superintendent does not need to perform the inspections required by this section. Site safety inspections shall be performed by the site safety manager or coordinator in accordance with Section 3310.
3301.13.9 Correcting unsafe conditions. | In the event the construction superintendent discovers work or conditions at a job site for which he or she is responsible that are not being conducted in accordance with sound construction/demolition practices, not in compliance with approved documents, or not in compliance with this chapter and any rules promulgated thereunder, the construction superintendent must take all appropriate action to correct the unsafe work or condition, including but not limited to immediately notifying the person or persons responsible for creating the unsafe work or condition, and ordering the person or persons to correct the unsafe work or condition, to cease operations, or to leave the job site. Where unsafe work or an unsafe condition relates to an item which a registered design professional or special inspection agency is responsible for implementing or verifying, the construction superintendent must also notify the responsible registered design professional or special inspection agency of the unsafe work or condition. All such unsafe conditions, work, notices, orders, and corrective action must be recorded in the log required by Section 3301.13.13.
3301.13.10 Notification of conditions to the department. | The construction superintendent must immediately notify the department when he or she discovers, at any job site for which the construction superintendent is responsible, any of the conditions listed in Section 3310.8.2.1. Notification to the department does not relieve the construction superintendent of their obligations under Section 3301.13.9. Exception: Where a site safety manager or coordinator has been designated for the job in accordance with Section 3310, the construction superintendent does not need to provide the notification required by this section. Notifications shall be made by the site safety manager or coordinator in accordance with Section 3310.
3301.13.11 Reporting of incidents and damage to adjoining property. | The construction superintendent must immediately notify the department of any incident at any job site for which the construction superintendent is responsible, or any damage to adjoining property caused by construction or demolition activity at the job site. Exception: Where a site safety manager or coordinator has been designated for the job in accordance with Section 3310, the construction superintendent does not need to provide the notification required by this section. Notifications shall be made by the site safety manager or coordinator in accordance with Section 3310.
3301.13.12 Competent person. | The construction superintendent must designate a competent person for each job site for which the construction superintendent is responsible and ensure such competent person is present at the designated job site at all times active work occurs when the construction superintendent is not at the site. The designation of a competent person does not alter or diminish any obligation imposed upon the construction superintendent. The competent person must carry out orders issued by the construction superintendent; be able to identify unsanitary, hazardous or dangerous conditions; take prompt corrective measures to eliminate such conditions; immediately report to the construction superintendent incidents at the job site or any damage to adjoining property caused by construction or demolition activity at the job site; and be able to effectively communicate workplace instructions and safety directions to all workers at the site. Exception: Beginning January 1, 2026 or a later date established by the department, provided that such date is not later than January 1, 2027, where Section 3301.13.6 requires the construction superintendent to be dedicated to one job, the designation of a competent person is not authorized. In the event the primary construction superintendent cannot be present at the job site while active work is occurring, an alternate construction superintendent shall act on behalf of the primary construction superintendent in accordance with Section 3301.13.5.
3301.13.13 Log. | The construction superintendent must maintain a log at each job site for which the construction superintendent is responsible. Such log must be made available to the commissioner upon request. The construction superintendent must complete such log prior to departing the job site, or, where the job occurs on a building that meets the definition of a major building, by the end of the day. Each day’s log entry must be signed and dated by the construction superintendent. Such log must contain, at a minimum, the following information:
3301.13.14 Reserved.
3301.13.15 Reserved.
3301.13.16 Obligation of others. | Nothing in this section is intended to alter or diminish any obligation otherwise imposed by law on others, including but not limited to, the owner, permit holder, construction manager, general contractor, contractor, materialman, architect, engineer, land surveyor, site safety manager, site safety coordinator, concrete safety manager, or other party involved in a construction project to engage in sound engineering, design, and construction practices, and to act in a reasonable and responsible manner to maintain a safe job site.
3301.13.17 Licensing of construction superintendents. | No person shall perform the duties and responsibilities of a construction superintendent, including but not limited to serving as a primary construction superintendent or as an alternate construction superintendent, unless such person is licensed as a construction superintendent in accordance with Article 428 of Title 28 of the Administrative Code.
3301.13.18 Release of the construction superintendent. | The department may release the construction superintendent from the job when the construction superintendent demonstrates, to the satisfaction of the commissioner, that the job is substantially complete.
3301.13.19 Weekly safety meeting. | The construction superintendent shall, for each job site for which the construction superintendent is responsible, lead a safety meeting with the designated representative of the general contractor, construction manager, and each subcontractor to ascertain that all contractors and subcontractors are complying with the applicable provisions of this chapter, the site safety plan, and the tenant or occupant protection plan. Where a site safety manager or coordinator has been designated for the job in accordance with Section 3310, the site safety manager or coordinator shall also attend the meeting. Such meeting shall occur at least once a week while active work is occurring.
3301.14 Contractor shall inform personnel. | General contractors and subcontractors shall state to their directly employed personnel at the construction or demolition site, prior to such directly employed person commencing work at the site, that they are to follow all safety regulations at all times and that they are required to obey and implement all orders and directives issued by the general contractor/subcontractor, the general contractor’s/subcontractor’s designee, the construction superintendent, and the worker’s direct supervisor relating to safety requirements. Where a site safety manager or coordinator is required, the general contractor or subcontractor shall also state to their directly employed personnel at the site, prior to such directly employed person commencing work at the site, that the site safety manager or coordinator is responsible for monitoring compliance with laws and rules governing site safety; and shall inform their supervisory personnel at the site, prior to such supervisor commencing work at the site, of the name and responsibilities of the site safety manager or coordinator.
3302.1 Definitions. | The following terms are defined in Chapter 2:
3303.1 Scope. | Sites shall be safeguarded and maintained in accordance with the provisions of this section to protect the public and property.
3303.2 Utilities. | Utilities at a site shall meet the requirements of Sections 3303.2.1 through 3303.2.6.
3303.2.1 Existing services. | The location of all existing utilities and service lines shall be determined and adequate measures taken, or devices provided, to safeguard the public and property before such utilities are disturbed.
3303.2.2 Maintaining essential services. | See Section 3303.9.
3303.2.3 Electrical work. | All temporary electrical equipment and wiring shall meet the requirements of the New York City Electrical Code, and shall be maintained in compliance with such requirements. Portions of permanent electrical installations may be used for temporary operations provided the requirements of the New York City Electrical Code are met.
3303.2.3.1 Temporary lighting for construction sites. | Temporary lighting for construction sites shall use high-efficacy lamps with the following minimum efficacies:
3303.2.4 Sanitary facilities. | Sanitary facilities shall be provided during construction or demolition activ­ities in accordance with the New York City Plumbing Code.
3303.2.5 Removing, relocating, or interrupting services. | If any utility is to be removed, relocated, or have its service interrupted, the utility company or city agency affected shall be notified at least 72 hours in advance.
3303.2.6 Disconnecting, capping, and certifications. | Prior to the removal of any service, the utility connection shall be disconnected and capped, and certifications to that effect issued by the representative utility company shall be filed with the department.
3303.3 Watchperson. | Where an individual building being constructed or demolished has a footprint of between 5,000 square feet (1524 m2) and 40,000 square feet (12 192 m2), a competent watchperson shall be on duty at the site during all hours when operations are not in progress, from the time when the foundation is poured to when all work has concluded and the certificate of occupancy or temporary certificate of occupancy has been issued. Where the building has a footprint of more than 40,000 square feet (12 192 m2), at least one additional watchperson shall be on duty for each additional 40,000 square feet (12 192 m2) of building footprint, or fraction thereof. The watchperson shall be familiar with emergency notification procedures to the Fire Department, shall possess a valid security guard registration with the State of New York, shall hold a valid watchperson certificate from the Fire Department, and shall have completed a course that is at least 10-hours in length and approved by OSHA in construction industry safety and health. Exceptions: 1. Where the square footage of the building footprint requires two or more watchpersons, the number of watchpersons may be reduced, subject to the approval of the commissioner, where: 1.1. A video monitoring system is in place, or where the layout of the building allows a continuous line of sight across the entire building; and 1.2. At least one watchperson is provided. 2. The building is being actively monitored in accordance with a fire safety and evacuation plan approved by the Fire Department in accordance with the New York City Fire Code.
3303.4 Housekeeping. | Housekeeping at a site shall be in accordance with Sections 3303.4.1 through 3303.4.11.
3303.4.1 Slipping and tripping hazards. | Slipping and tripping hazards in areas used by the public shall be minimized in accordance with Sections 3303.4.1.1 and 3303.4.1.2.
3303.4.1.1 Maintenance of public areas. | All areas used by the public shall be maintained free from ice, snow, grease, debris, equipment, materials, projections, tools, or other items, substances, or conditions that may constitute a slipping, tripping, or other hazard.
3303.4.1.2 Location of hose lines, wires, ropes, pipes, chains and conduits. | Hose lines, wires, ropes, pipes, chains, and conduits shall be located so that they will not constitute a tripping hazard to the public. Where it is necessary to carry such across sidewalks, or any public way, they shall either be suspended at least 8 feet (2438 mm) above ground or, if left on the ground, suitable chamfered planks or a pedestrian bridge shall be provided to cover such.
3303.4.2 Containers. | Sufficient containers, including but not limited to waste dumpsters, debris boxes, and skip boxes, shall be available for the storage of all debris or waste. Such containers shall comply with the following requirements: 1. Containers shall be made of metal, flame-retardant plastic, or other noncombustible material. 2. Containers with wheels shall be secured at the end of the workday by rope, cable, or chocking at the wheels in order to prevent movement. 3. Containers shall not be placed at the edge of an unenclosed perimeter at any time, except when being moved from the floor or building. 4. Containers holding debris or waste shall be covered at the end of the workday and at any time when full to near the rim. However, containers need not be covered when they are empty and not in use, or while stored in a fully enclosed space at the end of the workday and not full to near the rim. Exception: Combustible debris shall not be permitted to accumulate and shall be removed from the site in accordance with Section 3303.5.1.
3303.4.3 Reserved.
3303.4.4 Control of debris. | Control of debris during construction and demolition work shall include the measures specified in Sections 3303.4.4.1 through 3303.4.4.3.
3303.4.4.1 Daily cleaning. | All areas of the construction or demolition site shall be cleaned of debris at least daily.
3303.4.4.2 Cleaning near unenclosed perimeters. | Areas that are at least 10 feet (3048 mm) from an unenclosed perimeter, as measured in all directions from the unenclosed perimeter, shall be cleaned of debris periodically throughout the day. Exception: In locations where unenclosed perimeter protection has been temporarily removed, the requirements of Section 3308.10 shall apply.
3303.4.4.3 Securing debris that cannot be removed by the end of the shift. | Debris that cannot be removed from the site by the end of the shift shall be: 1. Placed in containers meeting the requirements of Section 3303.4.2; or 2. Secured overnight to protect the public and property and shall be removed from the site or placed in containers meeting the requirements of Section 3303.4.2 at the beginning of the next shift. For demolition operations, debris stored overnight on grade or earth, and neatly piled to prevent dislodgement, tipping, or spillage, shall be considered to be in compliance with this section. Exception: Combustible debris shall not be permitted to accumulate and shall be removed from the site in accordance with Section 3303.5.1.
3303.4.5 Storage and safeguarding of materials and equipment during construction or demolition. | Material and equipment located at a site during construction or demolition operations shall comply with Sections 3303.4.5.1 and 3303.4.5.2.
3303.4.5.1 Open and exposed areas. | Material or equipment located on a working deck, unenclosed floor, roof, ground area, or similar exposed area shall be secured or otherwise safeguarded to prevent dislodgement by wind, vibration, accidental impact, or other means.
3303.4.5.2 Storage near unenclosed perimeters. | When not being used, material or equipment shall be stored at least 10 feet (3048 mm) from all unenclosed perimeters, as measured in all directions from the unenclosed perimeter. Material or equipment shall also be secured or safeguarded in accordance with the requirements of Section 3303.4.5.1. Exceptions: Provided the material or equipment is secured against dislodgement by wind, vibration, accidental impact, or other means, in lieu of the 10-foot (3048 mm) set back distance: 1. Material or equipment that weighs 750 pounds (340.2 kg) or more may be stored at least 5 feet (1524 mm) from the unenclosed perimeter. 2. Where the gross floor area is less than 1,000 square feet (93 m2), material or equipment, regardless of weight, may be stored at least 5 feet (1524 mm) from the unenclosed perimeter. 3. Where located on a floor that is at or above the level of the horizontal safety netting in accordance with Section 3308, material or equipment may be stored at least 2 feet (610 mm) from the unenclosed perimeter. 4. Material related to concrete operations may overhang the unenclosed perimeter of the building or structure, provided: 4.1. The material is banded with a minimum of two equally spaced bands to prevent dislodgement; 4.2. The material is braced and secured in place by positive means as indicated on the site safety plan, or where there is no site safety plan, in accordance with drawings prepared by a registered design professional; 4.3. The material overhangs by no more than one-third of its length; 4.4. The material is stored in an area designated on the site safety plan, or where there is no site safety plan, in an area designated on drawings prepared by a registered design professional; 4.5. Such designated area is broom swept and cleared of all materials, equipment, and debris prior to the temporary removal of the vertical netting and placement of overhanging material in the designated area; 4.6. The perimeter of such designated area, except for the perimeter along the unenclosed perimeter, is protected by vertical netting meeting the requirements of Section 3308.5 or an alternative system acceptable to the commissioner; 4.7. Horizontal safety netting meeting the requirements of Section 3308.6 is provided at a level not more than two stories or 30 feet (9144 mm) below the overhanging material, whichever is less, with such nets in place for the full time the material is overhanging, except that the nets may be pulled in at the immediate time the material is being hoisted or lowered where such nets would conflict with the hoisting or lowering operation; and 4.8. The material is relocated on the next workday.
3303.4.6 Storage of combustible material and equipment. | Storage of combustible material and other material and equipment that may present a fire hazard shall comply with the New York City Fire Code.
3303.4.7 Storage near sidewalks, walkways, and pathways. | Material stored adjacent to a sidewalk, walkway, or pathway that remains open to the public shall not be piled higher than 3 feet (914 mm), or where a solid fence or barrier is provided, to within one foot (305 mm) of the top of such fence or barrier. For the purposes of this section, the term “adjacent to” shall be any area that is within a horizontal distance that is equal to or less than the vertical height of the piled material. Exception: Material stored within a dumpster or similar solid container, provided such material is not piled above the top of such dumpster or container.
3303.4.8 Machinery. | All exposed, electrically charged, moving or otherwise dangerous parts of machines and construction or demolition equipment shall be located, guarded, shielded, or barricaded so as to prevent contact by the public.
3303.4.9 Internal combustion-powered equipment. | In addition to the requirements of this chapter, the use of internal combustion-powered equipment shall comply with the New York City Fire Code.
3303.4.10 Stairs, hallways, and other means of egress. | Stairs, hallways, pathways, and other means of egress, including but not limited to ladders used to facilitate access to a working level, shall not be encumbered by debris, material, or equipment.
3303.4.11 Daily inspection of housekeeping. | A daily inspection shall be made by a competent person to verify compliance with the housekeeping requirements of Sections 3303.4.1 through 3303.4.10. If the building is a major building, the occurrence of this inspection shall be noted in the site safety log. If the building is not a major building but requires a construction superintendent, the occurrence of this inspection shall be noted in the construction superintendent’s log.
3303.5 Removal of material and debris. | Material and debris shall be removed in a manner that prevents injury or damage to the public or property.
3303.5.1 Removal of combustible debris. | Combustible debris shall not be permitted to accumulate, and shall be removed from the site at reasonable intervals in accordance with the requirements of the New York City Fire Code.
3303.5.2 Dropping or throwing prohibited. | No material, debris, or equipment shall be intentionally dropped or thrown from a building or structure.
3303.5.3 Clogging. | Precautions shall be taken to prevent concrete or mortar washings, sand, grit, or any other material that would cause clogging from entering a sewer, drain, vault, or subsurface structure. Concrete washout water shall also meet the requirements of Section 3303.15.
3303.5.4 Air pollution. | The provisions of the Air Pollution Control Code shall apply in order to prevent dust from becoming airborne.
3303.5.5 Chutes. | Chutes used in association with the removal of materials shall comply with Sections 3303.5.5.1 through 3303.5.5.5.
3303.5.5.1 Enclosures. | Chute enclosures shall comply with the following requirements:
3303.5.5.2 Chute construction. | Chute construction shall comply with the following requirements:
3303.5.5.3 Chute construction where the chute is over 75 feet in height, or utilized in Group I occupancy. | Chutes that exceed 75 feet (22 860 mm) in height, or that are used in an occupied building where the main use or dominant occupancy is in Group I, shall either:
3303.5.5.4 Supports. | All structural supports of material chutes shall be of noncombustible material.
3303.5.5.5 Design and permit. | No chute shall be installed until a permit has been issued by the commissioner on the basis of drawings prepared by a registered design professional. Exception: Design and permit is not required for a chute that meets all of the following criteria: 1. The chute is installed on the exterior of a building or structure at a height of 40 feet (12 192 mm) or less above the level of the adjoining ground; 2. The chute is a manufactured product and is installed in accordance with the manufacturer’s specifications; and 3. The chute does not attach to or impart a load on a scaffold.
3303.6 Escape hatches. | Where portable fuel fired heaters or other heating equipment are used to provide temporary heating during the placing of concrete for a floor, an escape hatch shall be provided. The escape hatch shall be located as near to the center of the building or structure as practical. Exceptions: 1. An escape hatch is not required where either the concrete placement floor or heating floor is the ground floor. 2. An escape hatch is not required provided at least one permanent stairway is available for use on the floor where the concrete is being placed and the stair shaft is enclosed from the top of the floor where concrete is being placed to at least the top of the heating floor with either its permanent construction, a temporary smoke proof 1-hour fire rated assembly, or a 1-hour fireproof tarp wrapped tightly around the stair shaft so that no smoke can penetrate.
3303.6.1 Required ladders and shields. | The escape hatch shall be constructed with at least two fixed, vertical ladders enclosed in a solid non-combustible shield. The ladders shall extend from a distance of 3 feet (914 mm) above the floor where the concrete is being placed to at least the story below the heating floor, or to the ground floor, whichever is less. The solid non-combustible shield shall enclose the ladders on all sides from the top of the floor where the concrete is being placed to at least the top of the heating floor. The inside dimensions between faces of the shield shall be not less than 3 feet 8 inches (1118 mm). Exception: Extension ladders may be utilized where the horizontal dimension between the faces of the shields is equal to or greater than one-quarter the height of the shaft.
3303.6.2 Shield space and decking. | Any gap between the shield and the perimeter of the opening in the floor under construction and also between the shield and the perimeter of the opening in the heating floor shall be decked over with 2-inch (51 mm) or heavier planking covered with ply­wood or sheet metal so as to make the decking smoke tight. At the termination of the ladders, the opening in the floor shall be covered completely with 2-inch (51 mm) planking or other material of equivalent strength.
3303.7 Fire prevention and fire protection. | Firefighting equipment, fire fighting access at the construction or demolition site, and the conduct of all construction or demolition operations affecting fire prevention and fire fighting shall comply with the New York City Fire Code and the provisions of Sections 3303.7.1 through 3303.7.7.
3303.7.1 Water supply. | A water supply for fire protection shall be provided in accordance with the New York City Fire Code.
3303.7.1.1 Large footprint construction. | For a building that has a footprint of 100,000 square feet (30 480 m2) or more, regardless of the height of the building, and the building is substantially enclosed, permanent or temporary fire hydrants available for fire department use shall be provided during the course of construction:
3303.7.2 Fire extinguishers. | Fire extinguishers shall be provided in accordance with the New York City Fire Code.
3303.7.3 Smoking. | Smoking shall be prohibited at all construction and demolition sites. No smoking signs shall be posted at the site in accordance with the provisions of the New York City Fire Code.
3303.7.4 Sprinkler systems. | Existing sprinkler systems in buildings undergoing an alteration or demolition shall comply with the requirements of Section 3303.7.4.1 through 3303.7.4.3.
3303.7.4.1 Sprinklers during alteration. | Existing sprinkler systems in buildings undergoing an alteration shall be maintained in accordance with Section 3303.9, except as provided in Section 3303.7.4.3. The red paint required pursuant to Section 903.6 shall be maintained during any alteration operation.
3303.7.4.2 Sprinklers during demolition. | When existing sprinkler systems with fire department hose connections are present in buildings undergoing full or partial demolition, such systems shall be maintained as a nonautomatic sprinkler system, except as provided in Section 3303.7.4.3. When demolition starts, the sprinkler risers shall be capped immediately below the floor being demolished so as to maintain the sprinkler system on all lower floors for Fire Department use. Cutting and capping of sprinklers during demolition work shall be performed only by a licensed master plumber or licensed master fire suppression piping contractor who has obtained a permit for such work. Fire department hose connections shall be kept free from obstruction and shall be marked by a metal sign reading “Sprinkler Connection” and by a red light at night. The red paint required pursuant to Section 903.6 shall be maintained during any demolition operations.
3303.7.4.3 Removal of damaged sprinklers. | Requests for a variance from the sprinkler requirements of this section shall be limited to requests to remove a damaged or inoperable sprinkler system or a portion of such system in connection with demolitions or gut rehabilitations. Applications for construction document approvals for such requests shall be filed with the department by a registered design professional in accordance with the following procedure:
3303.7.5 Standpipe systems. | Standpipe systems shall meet the requirements of Section 3303.8.
3303.7.6 Floor numbering and floor elevation. | During new building construction, a vertical or horizontal enlargement, or a demolition operation that results in the removal of one or more floors in a building that is greater than 420 feet (128 m) in height above grade, or in any building, regardless of height, with non-sequential floor numbers, the following shall be provided:
3303.7.7 Special provisions for Type IV construction. | In addition to the fire prevention and fire protection requirements imposed by this code, the New York City Fire Code, and other applicable law, the following provisions shall also apply during the construction of structures categorized as Type IV construction by Chapter 6 of this code.
3303.7.7.1 Interior exit stair enclosures. | Notwithstanding the requirements of Section 3303.11, no wooden structural components shall be installed until the permanent stairs and interior exit stair enclosures have been constructed to a height of at least two floors above the topmost working deck, or to their full height, and enclosed with their permanent fire protected rated material. A temporary or permanent self-closing door that meets the requirements of Section 715 shall be installed at each level as soon as a walkable surface is in place at that floor level. Openings in the interior exit stair enclosures at levels where a walkable surface has not been placed shall be protected with guardrails that meet the requirements of Section 3308.7. The top of the interior exit stair enclosure, if not permanently enclosed, shall be covered with a tarp or other temporary weather protection. The stair shall be provided with temporary or permanent handrails. Permanent signs, markings, or anti-slip materials in the stairs are not required during construction.
3303.7.7.2 Standpipes. | A permanent or temporary standpipe system meeting the requirements of Sections 905 and 3303.8 shall be provided in each interior exit stair enclosure and kept in a state of readiness at all times for use by firefighting personnel, even if the site does not otherwise trigger the standpipe requirements of Section 3303.8, Item 1. The standpipe system shall be in place prior to the installation of wooden structural components and shall serve all levels where the interior exit stair enclosure has been constructed. No standpipe shall be considered to be in a state of readiness unless it is painted red in accordance with the provisions of Section 905.11. The standpipe system shall be maintained as a dry system and provided with an air pressurized alarm system in accordance with Section 3303.8.1. Where the building will not be provided with a permanent standpipe at the end of construction, the temporary standpipe system shall be removed once the sprinkler system for the building has been signed off.
3303.7.7.3 Progressive installation of enclosures and fire protection elements. | Fire-rated enclosures (e.g. corridors, fire compartmentalization, fire-rated doors), noncombustible exterior walls, heat detectors required by Section 3303.7.7.5, and sprinkler systems, if required for the building, shall be installed as soon as practical, and in no case shall they lag more than two floors below the topmost walkable surface. Sprinkler systems shall be temporary or permanent and shall be maintained as a dry system during construction. Openings in the façade for hoists or material loading platforms are permitted provided the opening is covered at the end of the shift with a flame resistant tarp made tight so that no smoke can penetrate.
3303.7.7.4 Temporary protection of structural connections. | Where a structural connection between a girder and column is not provided with its permanent fire-rated enclosure or protection, it shall be protected by a temporary 1-hour rated enclosure or protection. Such temporary enclosure or protection shall be installed as soon as practical after the connection has been made, and no later than by the end of the shift.
3303.7.7.5 Heat detectors. | Heat detectors shall be provided throughout the site. Such detectors shall send alerts to a dedicated monitoring location, either at the site or at a remote location that is monitored continuously, including days, nights, weekends, and holidays. The monitor shall be familiar with emergency contact procedures, the locations of heat detectors at the site, and shall be able to alert the New York City Fire Department as necessary and provide the fire department with the location of any heat detector that has been activated.
3303.7.7.6 Watchperson. | A watchperson meeting the requirements of Section 3303.3 shall be on duty during all times specified by Section 3303.3, even if the building has a footprint of less than 5,000 sq ft (1524 m2).
3303.7.7.7 Site safety orientation and refresher. | The site safety orientation and refresher required by Section 3301.11 shall contain instruction on site specific fire hazards, fire safety safeguards, and fire safety procedures.
3303.7.7.8 Pre-shift safety meetings. | The pre-shift safety meetings required by Section 3301.12 shall contain instruction on fire hazards, fire safety safeguards, and fire safety procedures applicable to the individual worker.
3303.7.7.9 Chutes. | Chutes shall comply with the requirements of Section 3303.5.5.3 even if the building does not otherwise meet the trigger thresholds of Section 3303.5.5.3.
3303.7.7.10 Doors. | Except when required to facilitate the active passage of personnel, material, debris, or equipment, fire rated doors shall be kept closed at all times, and all other doors shall be closed during non-working hours.
3303.7.7.11 Control of saw dust and combustible debris. | Sawdust shall be vacuumed as operations proceed. Combustible debris, including but not limited to sawdust and scrap lumber, shall be removed from the site as required by Section 3303.5.1.
3303.7.7.12 Storage of lumber. | During non-working hours, lumber shall be stored on the ground or street, or shall be stored in a fully enclosed room meeting its permanent fire rating. No more than 1920 ft3 (54.37 m3) of lumber shall be stored at the site at any one time. Exception: Columns may be stored on the topmost working deck provided they are to be installed at the start of the next shift.
3303.8 Standpipe systems during construction, alteration or demolition. | During construction, alteration or demolition operations, standpipe systems shall comply with the following:
3303.8.1 Air pressurized alarm system for dry standpipe systems during construction or demolition operations. | Dry standpipe systems utilized during construction or demolition operations shall be provided with an air pressurized alarm system as set forth in Items 1 through 5 below. The provisions of NFPA 14, Chapter 12, as modified in Appendix Q, shall also apply.
3303.8.2 Free from obstruction. | Fire department hose connections shall be kept free from obstruction and shall be marked by a metal sign reading, “Standpipe Connection” and by a red light at night.
3303.8.3 Use of standpipes for purposes other than supplying water for firefighting. | Standpipes may be used for a purpose other than to supply water for firefighting operations, including but not limited to supplying water or compressed air for construction or demolition operations, subject to the approval of the Fire Department and provided at least one standpipe riser is maintained at all times for firefighting operations. Where the standpipe is used to supply water for construction or demolition operations and freezing conditions may occur, the standpipe shall be completely drained after use to prevent freezing.
3303.9 Elements to be maintained in existing buildings. | Required means of egress, existing structural elements, fire protection devices, and sanitary safeguards shall be maintained at all times during construction or demolition operations in existing buildings. Required means of egress shall not be obstructed in any manner that would destroy the full effectiveness of such means of egress. Exception: Where adequate alternate provisions are provided in accordance with the requirements of this code, or where the element is temporarily or permanently disconnected, removed, or demolished in accordance with the requirements of this code and of the agency or authority having jurisdiction to temporarily or permanently disconnect, remove, or demolish such element. Such alternative means, disconnection, removal, or demolition shall be shown on the approved plans. Fire protection systems, including but not limited to sprinklers, standpipes, and fire alarms, shall only be taken out of service in accordance with the requirements of the New York City Fire Code.
3303.10 Operations in occupied buildings. | When construction or demolition activity occurs in an occupied building, barricades, signs, drop cloths, and other protective means shall be installed and maintained as necessary to provide reasonable protection for the occupants against hazard and nuisance. Such protective means shall be indicated on an occupant protection plan, or where a tenant protection plan is required by Section 3303.10.1, on a tenant protection plan.
3303.10.1 Tenant protection plan. | In buildings containing any occupied dwelling units, including newly constructed buildings that are partially occupied where work is still ongoing within the building, all alteration, construction, or partial demolition work shall be performed in accordance with a tenant protection plan as required by Article 120 of Title 28 of the Administrative Code.
3303.10.2 Inspections of tenant protection plan. | The owner shall notify the department in writing at least 72 hours prior to the commencement of any work requiring a tenant protection plan. The department shall conduct an inspection of 10 percent of such sites within seven days after the commencement of such work to verify compliance with the tenant protection plan. The department shall conduct follow up inspections of such sites every 180 days until such construction is completed to verify compliance with the building code and tenant protection plan. Thereafter, the department shall conduct an inspection within 10 days of receipt of a complaint concerning such work.
3303.10.3 Enforcement of tenant protection plan. | If work is not being performed in accordance with the tenant protection plan, the commissioner may issue a stop work order pursuant to Section 28-207.2 of the Administrative Code.
3303.11 Stairs during construction or demolition. | Stairs shall meet the requirements of Section 3303.11.1 through 3303.11.3 during construction or demolition work.
3303.11.1 Existing stairs. | Stairs in an existing building undergoing alteration or a partial demolition shall be maintained in accordance with Section 3303.9. Stairs in a building undergoing a full demolition shall comply with Section 3306.9.9.
3303.11.2 Stairs during building construction or enlargements. | During new building construction or the enlargement of an existing building, stairs shall be provided at all locations where a permanent stair will be required and shall serve all floors. At least one of the provided stairs must be of permanent construction for its full length; in all other locations, the stairs may be of temporary or permanent construction. Exceptions: 1. Where a floor is open to the public, all stairs required for egress from the floor must be of their permanent construction from that floor to the ground level. 2. Stairs are not required where the floor is closed to the public and the floor is less than 4 stories or 40 feet (12 192 mm) below the topmost working deck, whichever is less. 3. During the construction or enlargement of a building whose primary structural system consists of structural steel, where it is not feasible to provide one or more permanent stairs to serve all floors that are at least 4 stories or 40 feet (12 192 mm) below the topmost working deck, whichever is less, all stairs shall be of their permanent construction up to the level of the topmost completed steel floor, and temporary stairs, acceptable to the commissioner, shall be brought up in all locations to serve all remaining floors that are at least 4 stories or 40 feet (12 192 mm) below the topmost working deck, whichever is less. At a minimum, the temporary stairs shall be made of non-combustible material, be equipped with adequate handrails, be provided with landings that are level with the adjoining floor, and have riser height and tread depths that are uniform, within ¼ inch (6 mm), for each flight of stairs.
3303.11.3 Lighted and kept free of obstructions. | All stairs in a building undergoing construction or demolition shall be lighted at all times, and shall be kept free of equipment, debris, and material in accordance with Section 3303.4.10.
3303.12 Elevators and hoists during construction or demolition. | Elevators and hoists shall meet the requirements of Sections 3303.12.1 through 3303.12.5 during construction or demolition work.
3303.12.1 Publicly accessible floors. | Existing elevators serving publicly accessible floors in a building undergoing construction or demolition work shall be maintained in accordance with Section 3303.9.
3303.12.2 Floors closed to the public. | When required by Sections 3303.12.2.1 through 3303.12.2.4, floors closed to the public in a new or existing building undergoing construction or demolition work shall be served by, at least, either: 1. An elevator provided with Phase I and Phase II recall meeting the requirements of Chapter 30, which shall be kept in readiness at all times for Fire Department use; or 2. A hoist meeting the requirements of Section 3318, which shall be available at all times for Fire Department use. Exception: An elevator or hoist is not required during the course of construction or demolition of a building that does not require a permanent elevator.
3303.12.2.1 Initial installation of an elevator or hoist during the construction or enlargement of a building whose height will exceed 75 feet. | During the construction or enlargement of a building, once the topmost working deck exceeds 75 feet (22 860 mm) in height above the lowest level of the ground, all floors that are closed to the public and within 40 feet (12 192 mm) above the lowest level of the ground shall be served by an elevator or hoist meeting the requirements of this section. Where this measurement lands between floors, the measurement shall be rounded such that the elevator or hoist is brought up to serve the higher floor.
3303.12.2.2 Increasing the height of the elevator or hoist during the construction or enlargement of a building. | During the construction or enlargement of a building, when the topmost working deck exceeds 75 feet (22 860 mm) in height above the lowest level of the ground and subsequent to complying with Section 3303.12.2.1, all floors that are closed to the public and that are at least 4 stories or 48 feet (14 630 mm) below the topmost working deck, whichever is less, or for a building whose primary structural system consists of structural steel, at least 4 stories or 64 feet (19 507 mm) below the topmost working deck, whichever is less, shall be served by an elevator or hoist meeting the requirements of this section. However, no more than two weeks after the topmost working deck has become a walkable floor, a hoist or elevator meeting the requirements of this section shall be brought up to serve all remaining floors in the building that are closed to the public.
3303.12.2.3 During demolition. | During the demolition of a building where one or more floors are removed from the building, all floors in the building that are closed to the public and that are more than 7 stories or 75 feet (22 860 mm) below the topmost working deck, whichever is less, shall be served by an elevator or hoist meeting the requirements of this section.
3303.12.2.4 Other instances. | During the alteration of a building that would require a permanent elevator and where the scope of work does not constitute an enlargement or involve the removal of one or more floors from the building, all floors in the building that are closed to the public shall be served by an elevator or hoist meeting the requirements of this section.
3303.12.3 Deep excavations. | Where the proposed lowest level of a building with a footprint of 10,000 square feet (929 m2) or greater is constructed at a depth greater than 75 feet (22 860 mm), a hoist meeting the requirements of Section 3318 shall be available at all times for Fire Department use once the foundation is in place and the first elevated slab has been erected. The hoist shall serve the level at grade and all stories below grade. Exception: Subject to the approval of the commissioner, alternate means available at all times for Fire Department use, including but not limited to a vehicular ramp, shall be provided.
3303.12.4 Converting elevators. | Where an existing elevator is converted from passenger or freight use, the department shall be notified in accordance with the requirements of Chapter 30.
3303.12.5 Hoist travel. | If the travel of the hoist cannot be increased or decreased to fulfill the requirements of this section due to inclement weather, it shall be increased by the end of the next working day.
3303.12.6 Stretcher accommodation. | Where a hoist is provided, it must be capable of accommodating two standing individuals and a stretcher that is 84 inches in length by 24 inches in width (2134 mm by 610 mm).
3303.13 Interrupted or abandoned and discontinued operations. | Where construction or demolition work has been interrupted or abandoned and discontinued, the owner of the site shall ensure the site is secured, protected, and maintained to safeguard the public and property, and that the site is in compliance with the requirements of Sections 3303.13.1 through 3303.13.3.
3303.13.1 Fencing. | A fence meeting the requirements of Section 3307.7 shall be maintained throughout the duration of time that operations at the site are interrupted or abandoned and discontinued.
3303.13.2 Safety monitoring plan. | Where work has been interrupted or abandoned and discontinued for a period of at least three months, a safety monitoring plan satisfactory to the commissioner shall be prepared by a qualified person on behalf of the owner of the property and submitted to the department by the owner. Such safety monitoring plan shall be specific to the site, shall identify safeguards to be instituted and maintained to secure the site, and shall specify monitoring to be performed during the duration of suspension of work. The owner of the property shall be responsible for ensuring compliance with such plan.
3303.13.3 Filling and grading. | Where work has been interrupted or abandoned and discontinued for a period of at least three months, all open excavations shall be filled and graded to eliminate all steep slopes, holes, obstructions or similar sources of hazard. Fill shall consist of clean, noncombustible material. The final surface shall be graded in such a manner as to drain the lot, eliminate pockets in the fill, and prevent the accumulation of water without damaging any foundations on the premises or on adjoining property. Exception: Filling and grading is not required for abandoned, discontinued, or interrupted excavations that are: 1. Secured in accordance with Section 3303.13.2, and 2. Inspected periodically by an engineer to verify continued stability of the excavation, with a record of such inspections signed, sealed, and dated by the engineer.
3303.14 Water conditions. | The requirements of Sections 3303.14.1 through 3303.14.5 shall be followed to control the accumulation of water.
3303.14.1 Drainage. | No condition shall be created as a result of construction or demolition operations that will interfere with natural surface drainage. Water courses, drainage ditches, etc., shall not be obstructed by debris, refuse, waste building materials, earth, stones, tree stumps, branches, or other objects that may interfere with surface drain­age or cause the impoundment of surface waters.
3303.14.2 Protection of foundations. | Provision shall be made to prevent the accumulation of water or water damage to any foundations on the premises or to adjoining property.
3303.14.3 Drainage of excavations. | All excavations shall be drained, and the drainage shall be maintained as long as the excavation continues or remains. Where necessary, pumping shall be used, provided proper permits are obtained from the New York City Department of Environmental Protection.
3303.14.4 Clogging. | The requirements of Section 3303.5.3 shall apply.
3303.14.5 Dewatering. | The contractor or other entity performing the soil or foundation work shall dewater the site, as needed, for the progress of the work, and shall take all necessary measures to prevent settlement, slope failure, and damage to buildings, structures, and property affected by the dewatering operations.
3303.14.5.1 Dewatering plan. | Where dewatering is performed to drawdown or control the level of the water table, the dewatering operation shall proceed in accordance with a site specific plan developed by a registered design professional. The dewatering plan must incorporate all the conditions and findings identified in the geotechnical report required by Section 1803.6, the evaluation analysis required by Section 1817, and the preconstruction survey required by Section 3309.4.3. At a minimum, the plan shall indicate:
3303.15 Concrete washout water. | Concrete washout water shall not be allowed to enter any sewer, catch basin, drain, or body of water or to leach into the ground.
3303.15.1 Collection and containment. | All concrete washout water shall be collected and contained in or on the concrete mixer truck or in pre-manufactured watertight containers specifically designed and fabricated for the purpose of collecting and containing concrete washout water on-site. Such containers shall be of sufficient quantity and size to accommodate all rinsing operations required on-site so as not to delay the timely return of concrete ready mix trucks to the concrete plant and shall be protected from breach or overflow at all times.
3303.15.2 Location. | Rinsing operations and concrete washout water containers shall not be located less than 30 feet from any sewer, drain, catch basin, or body of water without the written approval of the commissioner.
3303.15.3 Disposal. | Collected concrete washout water shall be transported off site for treatment and disposal or contained on site until completely evaporated. Any hardened concrete remaining after evaporation shall be disposed of, reused or recycled.
3303.16 Worker sheds, contractor sheds, contractor offices, and similar structures. | Worker sheds, contractor sheds, contractor offices, and similar structures shall:
3303.16.1 Permit required. | No worker shed, contractor shed, contractor office, or similar structure shall be installed until a permit for the shed or office has been issued by the commissioner in accordance with the requirements of Chapter 1 of Title 28 of the Administrative Code. Exception: A permit is not required for a worker shed, contractor shed, contractor office, or similar structure that does not exceed 1 story in height and 120 square feet (36.58 m2) in area, and further provided that the shed, office, ╪ or similar structure is located more than 30 feet (9144 mm) from another shed, or office, or similar structure.
3303.16.2 Utility hookups. | No electrical, plumbing, or other utility hook up shall be made to a worker shed, contractor shed, contractor office, or similar structure until a permit for the hookup has been issued by the commissioner in accordance with the requirements of Chapter 1 of Title 28 of the Administrative Code. Where required by Chapter 4 of Title 28 of the Administrative Code, the utility hookup must be made by or under the direct and continuing supervision of a licensed individual.
3304.1 Scope. | The provisions of this section shall apply to all soil and foundation work, including but not limited to drilling or excavations made for the purposes of taking earth, sand, gravel, rock, or other material, as well as to soil and foundation work related to accessory uses such as garages, pools, and decks, and also to the underpinning or bracing of buildings or structures, in order to safeguard the public and property from such work. In addition to the requirements of this section, the applicable sections of Chapter 18 shall also apply to soil and foundation work. Exceptions: This section shall not apply to: 1. Soil or foundation work not related to the underpinning or bracing of an existing building or structure, and which is performed in connection with utility or infrastructure work occurring within a public right of way, including but not limited to the construction, alteration, maintenance, repair, or demolition of bridges, streets, sidewalks, highways, railroads, subways, water tunnels, or utility lines. 2. Soil or foundation work on cemetery grounds for burials. 3. Soil or foundation work performed within an industrial or commercial quarry, plant, or yard and not related to the construction or demolition of a building or structure on the property of such quarry, plant, or yard.
3304.1.1 Measurements. | The depth of all soil and foundation work shall be measured from the level of the adjacent ground surface to the lowest point of the soil and foundation work. The height of all soil and foundation work shall be measured from the level of the adjacent ground surface to the highest point of the soil and foundation work. Where soil and foundation work occurs within a basement or cellar, the soil and foundation work shall be measured from the level of the adjacent slab.
3304.1.2 Safety of the public and property. | Soil and foundation work shall be performed and, as necessary, supported, in a manner to prevent injury to the public, damage to property, or collapse, subsidence, or uncontrolled loss of earth or rock.
3304.2 Permit. | A permit shall be obtained prior to the commencement of soil or foundation work when required by Chapter 1 of Title 28 of the Administrative Code.
3304.3 Notification. | Prior to the commencement of soil or foundation work, notification shall be provided as follows.
3304.3.1 Notification of the department. | No soil or foundation work within the property line shall commence unless the permit holder, or where there is no permit holder the person causing the soil or foundation work to be made, notifies the department, via phone or electronically, at least 24 hours, but no more than 48 hours prior to the commencement of such work. The notification shall state the date that such soil or foundation work is to commence and include a “Call before you dig” confirmation number verifying compliance with the notification requirements of Section 3304.3.7. Should the notification date fall on a weekend or official holiday, the permit holder, or where there is no permit holder the person causing the soil or foundation work to be made, shall notify the department on the last business day before the commencement date. In the event that the soil or foundation work does not begin on the date provided in the notification to the department, the permit holder, or where there is no permit holder the person causing the soil or foundation work to be made, shall notify the department of its cancellation not more than 24 hours prior to but no later than the date for which the soil or foundation work was scheduled. Should the cancellation date fall on a weekend or an official holiday, the permit holder, or where there is no permit holder the person causing the soil or foundation work to be made, shall notify the department on the next business day after the intended commencement date. The permit holder, or where there is no permit holder the person causing the soil or foundation work to be made, shall notify the department of a new intended commencement date pursuant to the provisions above. Exceptions: Notification to the department is not required for the following: 1. Hand excavation work that extends less than 5 feet (1524 mm) in depth and is 2 feet (610 mm) or more from an existing footing or foundation. This exception shall not apply to any hand excavation work performed anywhere in existing or demolished basements or cellars that adjoin existing foundations. 2. Excavations for a geotechnical investigation that do not exceed 10 feet (3048 mm) in length, width, or diameter, and that are conducted under the supervision of a registered design professional. 3. Emergency work performed by the Department of Housing Preservation and Development (HPD) or other agency as directed by the commissioner or work on unsafe buildings performed by HPD or other agency pursuant to a precept. 4. Soil or foundation work related to gardening or landscaping work, provided no excavation occurs to a depth of 5 feet or greater (1524 mm); and either: 4.1. The excavation occurs more than 5 feet (1524 mm) from all footings and foundations; or 4.2. Where the excavation occurs within 5 feet (1524 mm) or less from a footing or foundation, such excavation does not occur below the level of the footing or foundation. 5. Soil or foundation work related to the pouring of a slab or pavement, provided no excavation to a depth greater than 2 feet (610 mm) occurs in conjunction with such work. 6. Where notification is required by Section 3306.3, separate notification for the removal of a foundation is not required.
3304.3.2 Notification of adjoining property owners. | When an excavation to a depth of 5 feet to 10 feet (1524 mm to 3048 mm) is to be made within 10 feet (3048 mm) of an adjacent footing or foundation, or when any excavation over 10 feet (3048 mm) is to be made anywhere on a site, the person causing the excavation to be made shall provide written notice to the owners of the adjoining property not less than 10 days prior to the scheduled starting date of the excavation. The written notice shall provide a description of the work to be performed, the timeframe and schedule, the contact information of the person causing the excavation to be made, and the contact information of the department. Exception: Notification is not required where the excavation is set back from the edge of the adjacent footing or foundation or adjoining property by a ratio of 2 horizontal to 1 vertical, as measured from the deepest point of the excavation.
3304.3.3 Notification to the Department of Environmental Protection. | When­ever soil or foundation work, for any purpose, is proposed to a depth greater than 50 feet (15 240 mm) in the borough of the Bronx or on or north of 135th Street in the borough of Manhattan, or greater than 100 feet (30 480 mm) is proposed in the borough of Brooklyn, Queens, or Staten Island or south of 135th Street in the borough of Manhattan, the owner of the premises, engineer, architect or contractor shall notify the New York City Department of Environmental Protection prior to commencement of such activity in accordance with Section 24-367 of the Administrative Code and any rules promulgated thereunder. The issuance of any permit or approval by the department shall not relieve the applicant, owner, engineer, architect or contractor of the obligation to comply with any notification or permitting requirements of the New York City Department of Environmental Protection. Whether or not a permit is required from the department for work, including but not limited to drilling for borings or geothermal wells, the owner of the premises, engineer, architect or contractor shall still comply with the notification and permitting requirements of the New York City Department of Environmental Protection.
3304.3.4 Excavations requiring permit from the New York State Department of Environmental Conservation. | Whenever soil or foundation work is planned deeper than 500 feet (152 m) below grade, a permit may be required from the New York State Department of Environmental Conservation. The issuance of any permit or approval by the department shall not relieve the applicant of the obligation to comply with any approval or permitting requirements of the New York State Department of Environmental Conservation. Whenever any drilling for borings or geothermal wells is planned, the owner of the premises or the contractor shall notify the New York State Department of Environmental Con­servation prior to commencement of such activity to determine if a permit is necessary.
3304.3.5 Notification and approval of the New York City Transit Authority, the Metropolitan Transportation Authority, and the Port Authority of New York and New Jersey. | Whenever an excavation of any depth is proposed within 200 feet (60 960 mm) of any facility, infrastructure, or property under the jurisdiction of the New York City Transit Authority, the Metropolitan Transportation Authority, or the Port Authority of New York and New Jersey, including but not limited to rail and subway lines, stations, station entrance and access points, bridges, tunnels, bus depots, access roads, fan plants, pump rooms, substations, shops and yards, duct lines, and easements, an approval shall be obtained from such authority having jurisdiction. The owner of the premises or the contractor shall notify the authority having jurisdiction prior to commencement of any such activity. The issuance of any permit or approval by the department shall not relieve the applicant of the obligation to comply with any approval requirements of the New York City Transit Authority, the Metropolitan Transportation Authority, or the Port Authority of New York and New Jersey.
3304.3.6 Notification and permit requirements of the New York City Fire Department. | Soil or foundation work that is to be done with the use of explosives shall also be subject to the notification and permit requirements set forth in the New York City Fire Code.
3304.3.7 Call before you dig notification. | “Call before you dig” notification shall be provided in accordance with the requirements of 16 NYCRR Part 753. The notification must address all street frontages associated with the soil and foundation work.
3304.4 Protection of sides of excavations. | The sides of excavations shall be protected in accordance with the requirements of Sections 3304.4.1 through 3304.4.6.
3304.4.1 Support of excavation construction documents. | Means of supporting excavations, including related or resulting embankments, rock faces, and soil slopes, shall be indicated on construction documents. Such means of supporting excavations shall be installed and maintained in accordance with the construction documents. The construction documents shall be prepared by a registered design professional who has demonstrated knowledge or experience in the design of retaining structures or bracing systems for the support of excavation. Where the excavation exceeds 20 feet (6096 mm) in depth, the registered design professional shall be a New York State licensed professional engineer. Exceptions: Construction documents indicating the means of supporting the excavation are not required if: 1. The excavation meets the conditions specified in Items 1.1 through 1.4: 1.1. Is less than 5 feet (1524 mm) in depth; 1.2. Occurs above the level of the water table; 1.3. Occurs more than 5 feet (1524 mm) from all streets, sidewalks, tunnels, railroad tracks, public right of ways, and retaining walls; and 1.4. Occurs either: 1.4.1. More than 5 feet (1524 mm) from all footings and foundations; or 1.4.2. When within 5 feet (1524 mm) or less from a footing or foundation, does not extend below the level of the footing or foundation. 2. The excavation meets the conditions specified in Items 2.1 through 2.3: 2.1. Occurs more than 5 feet (1524 mm) from all footings, foundations, streets, sidewalks, tunnels, railroad tracks, public right of ways, and retaining walls; 2.2. Does not exceed 20 feet (6096 mm) in depth; and 2.3. Either: 2.3.1. The slope of the excavation does not exceed 1.5 horizontal to 1 vertical (34 degrees measured from the horizontal), with no benching allowed; or 2.3.2. A registered design professional determines the soil type, and the excavation is properly sloped or benched for the soil type in accordance with the requirements of Section 3304.4.2. Determination of the soil type shall be based upon a site specific evaluation, and documentation of the determination, signed and sealed by the registered design professional, shall be kept at the site. 3. A trench box is utilized in accordance with the manufacturer’s specifications, provided a physical copy of the manufacturer specifications are available onsite. 4. It is a trench that complies with Table 3304.4.1, including all notes to the table. 5. The excavation is performed in conjunction with the installation or removal of an exterior in-ground pool, provided such pool is an accessory to a one-or two-family home, is limited to 400 square feet (121.92 square meters) in area, and further provided that the distance from the edge of the pool to any building, structure, or lot line is greater than the depth of the deepest portion of the pool. 6. Where demolition drawings are required by Section 3306.5, separate support of excavation construction documents for the removal of the foundation are not required, provided the details required for a support of excavation drawing are instead shown on the demolition drawings. |  |  | See BC33 Tables and Figures
3304.4.1.1 Content of support of excavation construction documents. | Support of excavation construction documents shall, at a minimum:
3304.4.1.2 Geotechnical analysis and relevant reports. | The support of excavation construction documents shall be developed based upon site specific testing and analysis performed by a registered design professional who has demonstrated knowledge or experience in geotechnical evaluation. The support of excavation construction documents must incorporate all the conditions and findings identified in the geotechnical report required by Section 1803.6, the evaluation analysis required by Section 1817, and the preconstruction survey required by Section 3309.4.3.
3304.4.2 Limitation on sloping and benching. | Where sloping or benching is utilized to support an excavation, the slope or bench step shall be appropriate for conditions at the site, including but not limited to soil type, environmental conditions, and surcharge loads. In no case shall the maximum slope or bench step for an excavation that is 5 feet (1524 mm) or greater in depth exceed the values specified in Table 3304.4.2. For layered soil conditions, the most restrictive value among the soil types present at the excavation location shall be utilized unless otherwise specified by the registered design professional and indicated on the construction documents required by Section 3304.4.1. Exception: The limitations of Table 3304.4.2 shall not apply to excavations made in Class 1a, 1b, or 1c rock, as classified by Chapter 18, provided the geotechnical report required by Section 1803.6 substantiates the safety of the proposed slope, cut, or bench step, and further provided that the resulting slope, cut, or bench step, as well as any supplemental support of the rock face, is indicated on the construction documents required by Section 3304.4.1. |  |  | See BC33 Tables and Figures
3304.4.3 Fence. | Every site with an excavation shall be enclosed with a fence that meets the requirements of Section 3307.7.
3304.4.4 Guardrail system. | All open edges of an excavation that are 6 feet (1829 mm) or greater in depth shall be protected by a guardrail system meeting the requirements of Sections 3308.7.1 through 3308.7.5, or by a solid enclosure at least 3 feet 6 inches (1067 mm) high. For the purpose of a guardrail system installed in accordance with this section to protect the open edge of an excavation, the term “floor” in Sections 3308.7.1 through 3308.7.5 shall mean “ground.” Exceptions: 1. A toeboard is not required where the sheeting, shoring, bracing, or any other support of excavation extends at least 3½ inches (89 mm) above the top of the excavation. 2. guardrail system or a solid enclosure is not required where access to the adjoining area is precluded. 3. A guardrail system or a solid enclosure is not required where side slopes are three horizontal by one vertical (33-percent slope) or flatter. 4. In lieu of a guardrail system, wells, pits, excavation shafts, or similar excavations may be protected by an adequate cover capable of supporting, without failure, at least twice the weight of persons, equipment, and materials that may be imposed on the cover at any one time, or where located in roadways and vehicular aisles, at least twice the maximum axle load of the largest vehicle expected to cross over the cover. The cover shall be secured when installed so as to prevent accidental displacement by the wind, equipment, or persons, and shall be color coded or marked with the word "HOLE" or "COVER" to provide warning of the hazard. 5. The edges of ramps shall be protected in accordance with Section 3315.
3304.4.4.1 Openings. | To provide necessary openings for intermittent operations, one or more sections of the guardrail system or solid enclosure may be hinged or supported in sockets. When supported in sockets, rails shall be so constructed that they cannot be jolted out. A button or hook may be used to hold the guardrail system or solid enclosure in a fixed position. As an alternative to hinged or socketed sections, substantial chains or ropes may be used to guard such openings in such guardrail system or solid enclosure. Where so used, the chains or ropes shall meet the tautness and height requirements as the rails of a standard guardrail system.
3304.4.5 Placing of soil or foundation work equipment and excavated material. | Excavated material and superimposed loads, including but not limited to equipment and trucks used for soil or foundation work, shall not be placed closer to the edge of the excavation than a distance equal to one and one-half times the depth of such excavation unless the sides of the excavation have been sloped or sheet piled (or sheeted) and shored to withstand the lateral force imposed by such superimposed loads, or the registered design professional has determined the side of the excavation can adequately support the load imposed, with such support or determination shown on construction documents required by Section 3304.4.1. In the case of open excavations with side slopes, the edge of excavation shall be taken as the top of the slope.
3304.4.6 Installation of protection. | Required protection for the sides of the excavation shall be installed as the excavation advances. The placement of permanent structures or fill in areas requiring support of excavation shall not begin until the support of excavation has been completed for such areas.
3304.5 Inspections. | Soil and foundation work shall be inspected in accordance with the requirements of Sections 3304.5.1 and 3304.5.2.
3304.5.1 Rainstorms. | All sides or slopes of excavations or embankments shall be inspected after rainstorms, or any other hazard-increasing event, and safe conditions shall be restored.
3304.5.2 Special inspections. | Special inspections shall be performed in accordance with Chapter 17.
3304.6 Retaining walls. | The requirements of Article 305 of Title 28 of the Administrative Code, as well as Sections 1806 and 3309 of the building code shall apply as applicable.
3304.7 Access. | Every excavation shall be provided with at least one safe means of ingress and egress that is kept available at all times. For a trench that has a depth of 4 feet (1219 mm) or greater, and with a width of 15 feet (4572 mm) or less, as measured between the soil, forms, or structure at the bottom of the trench, one or more stairways, ladders, ramps, or other safe means of ingress and egress shall be located in the trench so as to require no more than 25 feet (7620 mm) of lateral travel.
3304.8 Drainage. | The requirements of Section 3303.14 shall apply.
3304.9 Utilities. | The requirements of Section 3303.2 shall apply.
3304.10 Dewatering. | The requirements of Section 3303.14 shall apply.
3304.11 Underpinning requirements. | The requirements of Section 1814 and Section 3309 shall apply.
3304.12 Slurry. | Where slurry is utilized to support an excavation, trench, or drilled or bored hole, slurry mix proportions and installation procedures shall be provided by a registered design professional on signed and sealed design and installation procedures. The installation procedures shall account for all imposed loads, including those from the earth, adjacent structures, and adjacent equipment. Where construction documents are required for the support of excavation by Section 3304.4.1, slurry mix proportions, slurry installation procedures, and slurry parameters necessary for stability, including but not limited to viscosity, unit weight, fluid loss, sand content, and pH, shall be indicated on such construction documents. The use of slurry to support excavations shall be subject to special inspection in accordance with Chapter 17.
3305.1 Scope. | Materials shall be placed and installed in accordance with the requirements of this section and in a manner such that the safety of the public and property will not be endangered.
3305.1.1 Handling and storing materials. | Materials to be placed or installed shall be handled and stored in such a manner as to prevent damage to the material, including but not limited to:
3305.1.2 Rigging. | The requirements of Section 3316.9 and rules promulgated by the commissioner shall apply to the conduct of all rigging operations.
3305.2 Structural steel assembly. | Structural steel assembly shall be in accordance with the requirements of AISC 360 and the requirements of Chapter 22 and Sections 3305.2.1 through 3305.2.8 of this code.
3305.2.1 Shop drawings. | The requirements of Section 2205.3.1 shall apply.
3305.2.2 Field connections. | The requirements of Section 2205.3.2 shall apply.
3305.2.3 Repair of damage. | Any damage to protective coatings shall be repaired prior to the application of fireproofing, the placement of concrete around the steel, or any other action that would otherwise conceal the steel. Any loss of section, bends, crimps or other evidence of permanent deformations shall be repaired by methods approved by the registered design professional of record or the piece shall be rejected.
3305.2.4 Open web steel joists. | The placement and installation of open web steel joists shall comply with the requirements of Sections 3305.2.4.1 through 3305.2.4.3.
3305.2.4.1 Attached to support structure. | Open web steel joists shall be attached to the support structure, at least at one end on both sides of the seat, immediately upon placement in the final erection position and before additional joists are placed. Exception: Open web steel joists that have been pre-assembled into panels with bridging shall be attached to the structure at each panel corner with sufficient bolted or welded connections before the hoisting cables are released.
3305.2.4.2 Connection to bays. | Connections of individual open web steel joists to steel structures in bays of 40 feet (12 192 mm) or more shall be fabricated to allow for field bolting of connections during erection. Exception: Open web steel-joists that have been pre-assembled into panels.
3305.2.4.3 Landing and placing loads. | The landing and placing of loads on open web steel joists shall be in accordance with the following requirements:
3305.2.5 Reserved.
3305.2.6 Erection of trusses. | Trusses shall be braced or guyed, as necessary, for the safety of the structure.
3305.2.7 Erection of frames. | Structural frames shall be properly braced with shores, guyed cables, turnbuckles, or other devices, as necessary, for the safety of the structure.
3305.2.8 Permanent flooring and steel erection in tiered buildings. | The permanent floors of such buildings or other structures shall be installed as soon as possible as the erection of structural steel members progresses. In no case shall there be more than eight stories, floors or equivalent levels or 120 feet (36 576 mm), whichever is less, between the working deck and the uppermost permanent floor. Exception: Where otherwise designed, in accordance with the approved construction documents, by the registered design professional of record.
3305.3 Concrete formwork. | Concrete formwork shall be in accordance with the requirements of Sections 3305.3.1 through 3305.3.7.
3305.3.1 General requirements. | The design, fabrication and erection of forms shall comply with the requirements of Sections 3305.3.1.1 through 3305.3.1.6.
3305.3.1.1 Safe support of loads. | Formwork, including all related braces, shoring, framing, and auxiliary construction, shall be proportioned, erected, supported, braced, and maintained so that it will safely support all vertical and lateral loads that might be applied until such loads can be sup­ported by the permanent construction.
3305.3.1.2 Vertical and lateral loads. | Vertical and lateral loads shall be carried to the ground by the formwork system, by the new construction after it has attained adequate strength for that purpose, or by existing structures. Forms and their supports shall be designed so as not to damage previously placed structures.
3305.3.1.2.1 Use of existing structures to support vertical or lateral loads. | The use of existing structures to support vertical or lateral loads imposed by concrete construction operations shall require an evaluation by a registered design professional of the adequacy of the existing structure to support the loads to be imposed. The registered design professional shall prepare design drawings documenting the findings of the evaluation, indicate the location of formwork elements, and the interface between the formwork and the existing structure. Concrete operations that utilize a stay form adjacent to a party wall, that place concrete against insulation in a seismic gap, or that utilize similar methods shall be assumed to impose a load on an existing structure, and shall always require an evaluation by a registered design professional in accordance with the requirements of this section.
3305.3.1.3 Bracing. | Forms shall be properly braced or tied together so as to maintain position and shape, and shall conform to the sizes and shapes of members as shown on the design drawings.
3305.3.1.4 Ramps, runways and platforms. | Ramps, runways, and platforms utilized in connection with concrete placement shall comply with Section 3315.
3305.3.1.5 Design. | Concrete formwork shall be designed in accordance with Section 3305.3.2.
3305.3.1.6 Forms for prestressed and post-tensioned concrete. | Forms for prestressed and post-tensioned concrete members shall be designed and constructed to permit movement of the member without damage during application of the prestressing or post-tensioning forces, or during installation of the prestressing steel.
3305.3.2 Design of concrete formwork. | Design of formwork, including but not limited to forms, proprietary formwork products, shores, and shoring foundations, shall comply with ACI 318, Section 26.11, and the requirements of Sections 3305.3.2.1 through 3305.3.2.8 of this code.
3305.3.2.1 Design drawings. | Site-specific formwork design drawings prepared by a registered design professional shall be required in the following cases: 1. For concrete formwork in a structure classified as a major building; 2. Wherever the shore or form height exceeds 14 feet (4267 mm); 3. Wherever the total vertical load on the forms exceeds 150 pounds per square foot (732 kg/m2); 4. Wherever power buggies are used; 5. Wherever multi-stage shores are used; 6. Wherever the slab thicknesses or beam heights equal or exceed 10 inches (254 mm); 7. Wherever there are concentrated loads exceeding 2000 pounds (907 kg) imposed on the formwork; or 8. Wherever there are loads imposed on existing structures in accordance with Section 3305.3.1.2.1. Exception: Design drawings prepared by a registered design professional are not required for formwork installed in conjunction with slabs supported directly on grade or footings where such slab or footing does not impart any load on an adjacent structure.
3305.3.2.2 Vertical loads. | Vertical loads shall include the total dead and live loads. Dead load shall include the weight of the formwork plus the weight of the reinforcement and fresh concrete. Live load shall allow for the weight of the workers and equipment, with allowance for impact, but in no case shall be less than 20 pounds per square foot (98 kg/m2).
3305.3.2.3 Lateral concrete pressure. | Design of forms, ties and bracing shall satisfy the minimum lateral pressures of fresh concrete specified in Table 3305.3.2.3. Maximum rate of placement shall be shown on the design drawings. |  |  | See BC33 Tables and Figures
3305.3.2.4 External loads. | Braces and shores shall be designed to resist all external loads, including, but not limited to, wind, cable tensions, inclined supports, dumping of concrete, and starting and stopping of equipment. In no case shall the assumed value of lateral load acting in any direction at each floorline be less than 100 plf applied along the edge or 2 percent of total dead load of the floor, whichever is greater. Except for foundation walls that are poured against a rigid backing, wall forms shall be designed for a minimum lateral load of 10 pounds per square foot (49 kg/m2), and bracing for wall forms shall be designed for a lateral load of at least 100 pounds per linear foot (148.8 kilograms per linear meter) of wall, applied at the top. The lateral load acting on walls greater than 14 feet (4267 mm) high shall be determined by analysis of conditions applicable to the site and building.
3305.3.2.5 Special loads. | The formwork shall be designed for any special conditions of construction likely to occur, such as asymmetrical placement of concrete, impact of machine-delivered concrete, uplift and concentrated loads.
3305.3.2.6 Shoring and bracing. | Shoring and bracing shall comply with Sections 3305.3.2.6.1 through 3305.3.2.6.4.
3305.3.2.6.1 Approval. | When patented or commercial devices that are not susceptible to design are used for shoring, bracing, or splicing, they shall be approved by the commissioner.
3305.3.2.6.2 Splices. | Splices shall develop the full strength of the spliced members.
3305.3.2.6.3 Bracing. | Where shore height exceeds 10 feet (3048 mm), or when necessary to provide structural stability, diagonal bracing shall be provided. Struts, anchored into masonry or to panel joints of adjacent braced bays may be used to prevent buckling of individual members not supported by the diagonal bracing, but bracing an entire tier of shores with struts without diagonal bracing shall be prohibited unless the system can be demonstrated to be braced by other rigid construction.
3305.3.2.6.4 Unbraced length of shores. | The unbraced length of shores shall not exceed the maximum length determined in accordance with the requirements of this code for the structural material used.
3305.3.2.7 Foundations. | Foundations for shores more than 10 feet (3048 mm) high and supported on the ground shall be designed by a registered design professional.
3305.3.2.8 Settlement. | Formwork shall be so constructed that vertical adjustments can be made to compensate for take-up and settlements. Wedges, jacks or other positive means shall be provided for this purpose.
3305.3.3 Formwork inspection and observation. | Formwork shall be inspected and observed in accordance with the requirements of Sections 3305.3.3.1 through 3305.3.3.3.
3305.3.3.1 Inspection by contractor. | Formwork, including shores, reshores, braces and other supports, shall be inspected prior to placement of reinforcing steel to verify the adequacy and proper installation of the formwork, and where construction documents and form design drawings are provided, that the formwork conforms to the construction documents and form design drawings. Subsequently, during and after concreting, periodic inspections shall be performed to detect incipient problems, and the elevations, camber, and vertical alignment of formwork systems shall be inspected using tell-tale devices. Such inspections shall be performed by a qualified person designated by the contractor; nothing shall prohibit the concrete safety manager from performing such inspection where so designated. The results of such inspections shall be documented in an inspection report signed and dated by the qualified person who performed the inspection. The names of the persons responsible for such inspections and the foreman in charge of the formwork shall be posted in the field office.
3305.3.3.2 Formwork observation. | In addition to the inspections by the contractor required pursuant to Section 3305.3.3.1, visual observations of the formwork for the general conformance with the design intent shall be performed by: 1. The formwork designer; 2. An employee of the formwork designer under his or her direct supervision; 3. A registered design professional retained by the formwork designer; or 4. An employee of such retained registered design professional under the direct supervision of such retained registered design professional. Exceptions: Formwork observation pursuant to Section 3305.3.3.2 shall not be required for: 1. Formwork that does not require design drawings pursuant to Section 3305.3.2.1; and 2. One- two- and three-family dwellings and accessory uses to such buildings.
3305.3.3.2.1 Intervals. | Formwork shall be observed at intervals permitting observation of representative configurations throughout the project duration. The formwork designer shall maintain a log of such observations at the construction site. At a minimum, observations shall be made:
3305.3.3.2.2 Discrepancies from the formwork design. | Where the individual performing the formwork observation pursuant to Section 3305.3.3.2 discovers a discrepancy from the formwork design, such discrepancy shall be immediately brought to the attention of the concrete contractor. The concrete contractor shall be responsible for correcting the discrepancy. In addition, the site safety manager, site safety coordinator, and concrete safety manager, as applicable, shall be notified of discrepancies from the formwork design that relate to site safety. Follow-up observations to confirm corrective action has been taken shall be made by the formwork designer or his or her qualified designee pursuant to Section 3305.3.3.2.
3305.3.3.2.3 Hazardous formwork conditions. | Where an observed formwork condition hazardous to life, safety, or health is not immediately corrected by the responsible contractor, the formwork designer or his or her qualified designee pursuant to Section 3305.3.3.2 shall immediately report such hazardous formwork condition and such failure to correct the hazardous formwork condition to the commissioner.
3305.3.3.3 Special inspection. | The requirements of Chapter 17 shall apply.
3305.3.4 Construction. | Concrete formwork, including but not limited to forms, shores, and shoring foundations, shall be constructed in conformance with the design drawings, where such drawings are required by Section 3305.3.2.1, and shall also be constructed to comply with the requirements of Sections 3305.3.4.1 through 3305.3.4.5.
3305.3.4.1 Field-constructed lap splices. | Field-constructed lap splices, other than approved devices, shall not be used more often than for every other shore under slabs or for every third shore under beams and shall develop the full strength of the members. Such spliced shores shall be uni­formly distributed throughout the work. Splices shall not be located near the midheight of the shores unless lateral support is provided, nor midway between points of lateral support.
3305.3.4.2 Vertical shores. | Vertical shores incorporated in multi-stage shores shall be set plumb and in alignment with lower tiers so that loads from upper tiers are transferred directly to the lower tiers, or adequate transfer members shall be provided. Provision shall be made to transfer the lateral loads to the ground or to completed construction of adequate strength. Vertical shores shall be so erected that they cannot tilt, and shall have firm bearing. Inclined shores and the bearing ends of all shores shall be braced against slipping or sliding. The bearing surfaces shall be cut square and have a tight fit at splices.
3305.3.4.3 Runways. | Runways for moving equipment shall be provided with struts or legs as required and shall be sup­ported directly on the formwork or structural member and not on the reinforcement.
3305.3.4.4 Unsafe conditions. | Any unsafe condition or necessary adjustment revealed by inspection shall be remedied immediately. If, during construction, any weakness develops and the formwork shows any undue settlement or distortion, the work shall be stopped, the affected construction removed if permanently damaged, and the formwork strengthened.
3305.3.4.5 Formwork interconnection. | Horizontal formwork deck panels and beam formwork shall be positively connected to all formwork support systems. Connections located within 16 feet (4877 mm) from the building perimeter shall be installed continuously throughout the day as the formwork is installed and shall be in place prior to the end of the shift.
3305.3.5 Removal of forms and shoring. | The removal of forms and shoring shall comply with the requirements of Sections 3305.3.5.1 through 3305.3.5.6.
3305.3.5.1 Removal schedule. | Before starting construction, the contractor shall develop a procedure and schedule for removal of shores and installation of reshores and for calculating the loads transferred to the structure during the process.
3305.3.5.1.1 Data and analysis. | The structural analysis and concrete strength data used in planning and implementing form removal and reshoring shall be furnished by the registered design professional responsible for the removal schedule to the commissioner when so requested.
3305.3.5.1.2 Support and removal. | No construction loads shall be supported on, nor any shoring removed from, any part of the structure under construction except when that portion of the structure in combination with the remaining forming and shoring system has sufficient strength to support safely its weight and the loads placed thereon.
3305.3.5.1.3 Concrete strength. | Sufficient strength shall be demonstrated by structural analysis of the proposed loads, the strength of the forming and shoring system, and concrete strength data. Concrete strength data shall be based on tests of field-cured cylinders. As an alternative, the concrete strength is permitted to be estimated using the maturity method performed in accordance with ASTM C1074, provided that the strength is at least 500 psi (3447.38 kPa) higher than the specified compressive strength necessary for formwork or shoring removal, as applicable. Other procedures for evaluating concrete strength are also permitted when approved by the commissioner.
3305.3.5.2 Construction loads. | No construction loads exceeding the combination of superimposed dead load plus specified live load shall be supported on any unshored portion of the structure under construction, unless analysis indicates adequate strength to support such additional loads.
3305.3.5.3 Prestressed members. | Form supports for prestressed concrete members shall not be removed until sufficient prestressing has been applied to prestressed members to carry their dead load, anticipated construction loads, and prestress transfer forces.
3305.3.5.4 Manner of removal. | Forms shall be removed in such a manner as to ensure the complete safety of the public and property.
3305.3.5.5 Shores support. | Where the structure as a whole is supported on shores, beam and girder sides, columns and similar vertical forms may be removed after the concrete is sufficiently hard to withstand damage from the removal. In no case shall the supporting forms or shoring be removed until the members have acquired sufficient strength to safely support their weight and the load thereon.
3305.3.5.6 Control tests. | The results of control tests, including concrete cylinder specimens pre­pared in accordance with ASTM C 31, cast-in-place cores, or other device that will produce test specimens representative of the condition of the concrete in place, of suitable size and proportions, and approved by the registered design professional of record shall be evidence that the concrete has attained sufficient strength or the strength as may be specified on the drawings.
3305.3.6 Reshoring. | Reshoring shall be provided to support the construction where forms and shores are stripped before the concrete has attained sufficient strength to support the superimposed loads due to construction above. Reshoring shall comply with Sections 3305.3.6.1 through 3305.3.6.8.
3305.3.6.1 Reshores limitations. | Reshores shall comply with the requirements of Sections 3305.3.6.1.1 through 3305.3.6.1.7.
3305.3.6.1.1 Secureness of reshores. | Reshores of wood or metal shall be screw adjusted or jacked and locked and wedged to make them secure. Reshores shall not be jacked or screwed so tightly that they preload the floor below or remove the normal deflection of the slab above.
3305.3.6.1.2 Reshores in proximity to unenclosed perimeters. | Reshores within 10 feet (3048 mm) of an unenclosed perimeter of a building shall be secured to prevent them from falling off the building.
3305.3.6.1.3 Wedges. | Wedges shall not be used within 10 feet (3048 mm) of the façade or at such other locations as determined by the commissioner.
3305.3.6.1.4 Stresses. | In no case shall shores be so located as to alter the pattern of stresses determined in the original structural analysis or to induce tensile stresses where reinforcing bars are not provided.
3305.3.6.1.5 Angle to surface. | Reshores shall be perpendicular to the surface that they are supporting.
3305.3.6.1.6 Adjusting devices. | Adjusting devices shall not be used if heavily rusted, bent, dented, rewelded or having broken weldments or other defects.
3305.3.6.1.7 Metal shoring and accessory parts. | Metal shoring and accessory parts shall be fully operative when in use.
3305.3.6.2 Site safety provisions. | Reshoring shall comply with the requirements of Sections 3305.3.6.2.1 through 3305.3.6.2.3.
3305.3.6.2.1 Emergency. | Extra shores or material and equipment that might be needed in an emergency shall be furnished.
3305.3.6.2.2 Stripping. | Care shall be taken while stripping is underway to ensure that material does not fall off the building.
3305.3.6.2.3 Building materials. | Building materials shall be properly piled and tied or contained.
3305.3.6.3 Bracing. | Lateral bracing shall be provided during reshoring operations, and reshores shall be located as close as practical to the same position on each floor to provide continuous support from floor to floor.
3305.3.6.4 Reshoring beam and girder construction. | Where reshoring of beam and girder construction is required, the forms shall not be removed from more than one girder at a time, and the girder shall be reshored before any other supports are removed. After the supporting gird­ers are reshored, the form shall be removed from one beam with its adjacent slabs and the beam shall be reshored before any other supports are removed. Slabs spanning 10 feet (3048 mm) or more shall be reshored along the centerline of the span.
3305.3.6.5 Reshoring flat slabs. | Where reshoring of flat-slab construction is required, the formwork cannot be stripped until the concrete has acquired sufficient strength to safely support its weight and the load thereon, or temporary preshores are provided supporting the slab at intervals of no more than 8 feet (2438 mm) on center to be replaced by reshores prior to placing concrete on the floor above. Reshores must be installed and remain in place until the concrete reaches full or sufficient strength to sustain the superimposed loads to which the concrete will be subjected.
3305.3.6.6 Stripping operation. | Debris generated as a result of stripping operations shall be immediately contained and removed at reasonable intervals. Stripping operations on concrete structures shall not be performed more than three stories below the story being formed.
3305.3.6.7 Prestressed construction. | Solid safety shields shall be provided at end anchorages of prestressing beds, or where necessary, for protection against breakage of prestressing strands, cables, or other assemblies during prestressing or casting operations.
3305.3.6.8 Reshoring schedule. | A signed and sealed reshoring schedule shall be provided and maintained at the construction site whenever reshoring is employed. Exception: A separate reshoring schedule is not required when the required reshoring information is covered on the approved construction documents prepared by the applicant of record.
3305.3.7 Alternate methods. | The contrac­tor may submit alternate methods of stripping, shoring, reshoring, and strength control for approval by the registered design professional of record, subject to review by the commis­sioner.
3305.4 Precast concrete construction. | Precast concrete members shall be adequately braced and supported during erection to ensure proper alignment and structural integrity until permanent connections are completed.
3305.4.1 Cracking or deflections. | Any cracking or deflections inconsistent with the design drawings observed during handling shall be subject to assessment by a registered design professional prior to erection.
3305.4.2 Design of temporary shores. | Temporary shores shall be designed by a registered design professional.
3305.5 Aluminum erection. | In addition to the requirements of Section 2002, the erection of aluminum used for structural purposes shall comply with the requirements of Sections 3305.5.1 through 3305.5.4.
3305.5.1 Reserved.
3305.5.2 Temporary bracing. | Temporary bracing shall be provided to support all loads imposed upon the framework during construction that are in excess of those for which the framework was designed.
3305.5.3 Temporary connections. | As erection progresses, the work shall be securely bolted or welded to resist all dead loads, wind, and erection stresses.
3305.5.4 Alignment. | The structure shall be properly aligned before riveting, permanent bolting, or welding is performed.
3305.6 Masonry erection. | The requirements of Section 2104.5 shall apply.
3305.7 Wood construction. | The requirements of Section 2304 shall apply.
3305.8 Cold-formed steel light-frame construction. | The installation of cold-formed steel light-frame construction, the installation of decking on cold-formed steel light-frame construction, as well as the use of such framing and decking during construction or demolition operations shall be in accordance with the requirements of AISI S240 and the following sections. The design of cold-formed steel light-frame construction and decking on cold-formed steel light-frame construction shall meet the requirements of Chapter 22.
3305.8.1 Cutting, notching, and splicing. | Cutting, notching, and splicing of cold-formed steel structural members shall be performed only in accordance with specifications as indicated on drawings, including but not limited to erection drawings, approved by a registered design professional.
3305.8.2 Uniform bearing surface. | A uniform bearing surface shall be provided under cold-formed steel structural members. In no case shall the gap between the bottom track and the uniform bearing surface exceed ¼ of an inch (6.4 mm). Leveling shall be subject to the approval of a registered design professional and shall be achieved through the use of either load bearing shims or grout.
3305.8.3 Corrosion protection. | The following precautions shall be taken to prevent corrosion of cold-formed steel structural members:
3305.8.4 Screw connections. | Screw fasteners in cold-formed steel structural members shall extend through the steel connection with a minimum of three exposed threads.
3305.8.4.1 Stripped screws in direct tension prohibited. | Stripped screws in direct tension shall not be permitted.
3305.8.4.2 Stripped screws in shear connections. | Stripped screws in shear connections shall only be permitted if the number of stripped screw fasteners does not exceed 25% of the total number of fasteners in the connection.
3305.8.5 In-line framing. | Each joist, rafter, truss, and structural wall stud (above or below) shall be aligned vertically in accordance with the limits depicted in Figure B1.2.3-1 of AISI S240. Exception: The alignment tolerance depicted in Figure B1.2.3-1 of AISI S240 shall not be required to be met when a structural load distribution member is specified in accordance with the approved construction documents.
3305.8.6 Joists, decking, and shoring and bracing. | Joists, temporary decking, permanent decking, and shoring and bracing for joists and decking shall be installed in accordance with the requirements of Section 3305.8.6.1 through 3305.8.6.9.
3305.8.6.1 Installed as indicated on drawings. | Joists, temporary decking, permanent decking, and shoring and bracing for joists and decking shall be installed as indicated on drawings, including but not limited to erection drawings, approved by a registered design professional. Such drawings shall be specific to the site and shall, at a minimum, indicate the following details:
3305.8.6.2 Lateral bracing of floor joists. | Floor joists shall be laterally braced. Types of bracing to maintain structural integrity include but are not limited to steel straps screwed to top and bottom flanges, bridging between joists, web reinforcement, cross bracing, diagonal strap bracing, wall anchorage or any other details as specified on the approved drawings.
3305.8.6.3 Ceiling joists and roof trusses. | Ceiling joists and roof trusses shall be installed in accordance with one of the following:
3305.8.6.4 Account for all loads during construction. | Framing and decking, whether temporary or permanent, shall be designed to sustain all anticipated loads to be imposed by construction activity, including construction loads, concentrated loading caused by material delivery and loads generated by the movement of material and equipment.
3305.8.6.5 Bracing and shoring for temporary loading areas. | Bracing and shoring shall be provided for all temporary loading areas and shall be designed to support the maximum load allowed in the temporary loading area. In no case shall the required shoring be designed for a construction load of less than 100 psf. Bracing and shoring shall ultimately bear upon permanent structure or earth capable of sustaining the loads transmitted. The design shall also specify the criteria for the removal of any temporary bracing or shoring.
3305.8.6.6 Floor joists to be braced prior to installation of decking. | No decking or section of decking shall be placed on a joist until the joist has been fully installed and braced in accordance with Sections 3305.8.5 and 3305.8.6.
3305.8.6.7 Placing loads on cold-formed steel. | Loads shall be placed on cold-formed steel in accordance with section 3305.8.7.
3305.8.6.8 Removal or modification of temporary shoring and bracing. | No temporary shoring or bracing shall be removed until the cold-formed steel special inspector required by Chapter 17 has verified the shoring or bracing is no longer required in accordance with item number 10 of Section 3305.8.6.1. Modifications to temporary shoring or bracing shall be verified by the special inspector. In addition to the documentation required by Chapter 17, the special inspector shall document the verification in accordance with the checklist required by Section 3305.8.8.
3305.8.6.9 Deviations. | Deviations from the drawings required by Section 3305.8.6.1 that are not immediately corrected shall be brought to the attention of the registered design professional who prepared the drawings.
3305.8.7 Placing loads on cold-formed steel. | The placing of loads during construction or demolition work on cold-formed steel framing or on decking on cold-formed steel framing shall be in accordance with the requirements of Sections 3305.8.7.1 through 3305.8.7.6.
3305.8.7.1 System in place. | No person, material, or equipment shall be permitted on any joist, temporary decking or permanent decking, until all members, fasteners, shoring and bracing have been installed as indicated on the drawings required by Section 3305.8.6.1.
3305.8.7.2 Maximum loads. | Loading shall not exceed that as indicated on the drawings required by Section 3305.8.6.1.
3305.8.7.3 Placed as indicated on plans. | Construction loads shall only be placed in areas and to the extent as indicated on the drawings required by Section 3305.8.6.1.
3305.8.7.4 Marking the temporary loading area. | Temporary loading areas shall be clearly marked on the deck by spray paint or equivalent means. The markings shall indicate the boundaries of the loading area and the maximum loads allowed in the temporary loading area as specified in the drawings required by Section 3305.8.6.1.
3305.8.7.5 Verification by special inspector. | No construction load shall be placed on a floor or portion of a floor until the temporary or permanent decking for the floor or such portion is in place and the cold-formed steel special inspector required by Chapter 17 has verified compliance with Section 3305.8.6, including but not limited to the drawings required by Section 3305.8.6.1. At a minimum, this special inspection shall be performed at least once for each floor. In addition to the documentation required by Chapter 17, the special inspector shall document the verification in accordance with the checklist required by Section 330586.8.
3305.8.7.6 Verification inspection by a competent person. | Immediately prior to the placement of any person, material or equipment on a section of cold-formed steel framing for the first time, or on a section of decking on cold-formed steel framing for the first time, a competent person designated by the construction superintendent, or where the project does not require a construction superintendent, a competent person designated by the permit holder, shall determine that the structure is ready to receive the person, material or equipment by performing an inspection that:
3305.8.7.6.1 Record of designation of competent person. | The designation of the competent person required by Section 3305.8.7.6 shall be recorded in the construction superintendent’s log required by Section 3301.13.13, or where the project does not require a construction superintendent, the designation of the competent person shall be documented in the form of a notarized letter on the letterhead of the permit holder. The record letter shall state the name and contact information of the competent person, the date of designation and shall be signed and dated by the permit holder, the competent person and the person who designated the competent person.
3305.8.7.6.2 Record of inspection. | The results of the inspection shall be documented in accordance with the checklist required by Section 3305.8.8.
3305.8.7.6.3 Does not diminish responsibility. | The designation of a competent person does not alter or diminish any obligation imposed upon the construction superintendent or the permit holder to maintain a safe site and ensure compliance with the requirements of this code.
3305.8.8 Inspection checklist. | The results of the verification inspections required by Sections 3305.8.6.8, 3305.8.7.5 and 3305.8.7.6 shall be documented on a verification inspection checklist signed and dated by the person who performed the inspection. The verification inspection checklist shall be developed by the designer who prepared the drawings required by Section 3305.8.6.1.
3306.1 Scope. | All full demolition and partial demolition operations shall be performed in accordance with the requirements of this section so that the safety of the public and property will not be endangered by demolition operations.
3306.2 Protection of pedestrians and adjoining property. | Demolition operations shall not commence until the applicable pedestrian and adjoining property protection is in place as required by Sections 3307, 3308, and 3309. In addition, safety zones and measures to prevent access shall be implemented as required by Sections 3306.2.1 and 3306.2.2.
3306.2.1 Preventing access. | The permit holder, or where there is no permit holder, the person causing the demolition work to be performed, shall institute and maintain measures to prevent persons other than workers from entering areas where demolition work is occurring, debris is stored, or equipment is located.
3306.2.2 Safety zone for exterior demolition. | Where demolition work occurs on the exterior of a building, the permit holder, or where there is no permit holder, the person causing the demolition work to be performed, shall institute and maintain a safety zone around the site to prevent persons other than workers from entering such safety zone. Where the safety zone precludes access to the entire demolition site, it shall be considered to satisfy the requirements of Section 3306.2.1. Exception: A safety zone is not required for the following types of work. Relief from the safety zone requirements does not grant relief from applicable pedestrian and adjoining property protection required by Sections 3307, 3308, and 3309, nor from the requirements of Section 3306.2.1. 1. Demolition work whose scope is limited to a minor alteration or ordinary repair, and is accomplished without any mechanical demolition equipment, other than handheld devices. 2. Work whose scope is limited to the alteration, maintenance, or repair of a façade, and which does not constitute a façade recladding as defined in rules promulgated by the commissioner, and is accomplished without any mechanical demolition equipment, other than handheld devices. 3. Demolition work accomplished without any mechanical demolition equipment, other than handheld devices, provided the entire exposure where demolition work is to occur is covered by either: 3.1. A supported scaffold with netting and guardrails in accordance with Section 3314.8; or 3.2. A site specific engineered enclosure system in accordance with Section 3309.17.
3306.2.2.1 Approval of the commissioner. | Where a safety zone is required by Section 3306.2.2, it shall be approved by the commissioner.
3306.2.2.2 Size of safety zone for mechanical demolition. | Where mechanical demolition equipment, other than handheld devices, is to be used for the full or partial demolition of a building, the safety zone shall be equal to or greater than half the height of the building to be demolished; such safety zone may be reduced by the same ratio as the building is being demolished.
3306.3 Notification. | The permit holder shall notify the department and adjoining property owners prior to the commencement of full and partial demolition operations in accordance with Sections 3306.3.1 and 3306.3.2. Exceptions: 1. Notification to the department or adjoining property owners is not required for partial demolition operations limited to the interior components of a building provided no mechanical demolition equipment, other than handheld devices, are used. 2. Notification to the department or adjoining property owners is not required for partial demolition that occurs on the exterior of a building, provided such work is a minor alteration or ordinary repair, and is accomplished without any mechanical demolition equipment, other than handheld devices.
3306.3.1 Notification of the department. | The permit holder shall notify the department via phone or electronically at least 24 hours, but no more than 48 hours prior to the commencement of such work. If the notification date falls on a weekend or official holiday, the permit holder shall notify the department on the last business day before the commencement date.
3306.3.2 Notification of adjoining property owners. | Adjoining property owners shall be notified of upcoming demolition operations in writing not less than 10 days prior to the scheduled starting date of the demolition. The written notice shall provide a description of the work to be performed, the timeframe and schedule, and contact information of the person causing the demolition work and of the department. Demolition or removal work that is to be done with the use of explosives shall also be subject to the notification requirements set forth in the New York City Fire Code.
3306.4 Mechanical demolition equipment. | Where mechanical demolition equipment, other than handheld devices, is to be used in the full or partial demolition of a building or structure, or is to be used within a structure to remove debris or move material, approval of the commissioner for the use of the mechanical demolition equipment must be obtained prior to the commencement of demolition operations. Exception: Approval of the commissioner is not required where the structure has been demolished to grade and mechanical equipment, located on the ground or a slab on grade, is utilized to remove the slab or foundation of the structure or to remove debris or move material.
3306.5 Submittal documents for demolition. | Full and partial demolition operations shall be conducted in accordance with submittal documents. Such submittal documents shall comply with Sections 3306.5.1 through 3306.5.7. Exceptions: Section 3306.5 shall not apply to: 1. Demolitions performed as emergency work pursuant to Section 28-215.1 of the Administrative Code when such work is monitored by a qualified person with experience in demolition operations who is employed by the city agency that has been directed to perform or arrange for the performance of such work. If the department or such city agency determines that there is a need for supervision of the work by a registered design professional, such city agency shall retain a registered design professional or cause a registered design professional to be retained to supervise the demolition operations. 2. The full demolition of a detached one-, two-, or three-family dwelling, or both halves of a semi-detached one-, two-, or three-family dwelling, or a detached accessory structure to a one-, two-, or three-family dwelling, provided such dwelling or accessory structure is three stories or fewer in height, and also provided that the demolition is to be accomplished without any mechanical demolition equipment, other than handheld devices. 3. The full demolition of a fully detached building that is three stories or fewer and with a floor area of 5,000 square feet (464.5 m2) or less per story, provided such demolition is to be accomplished without any mechanical demolition equipment, other than handheld devices. 4. The removal, with mechanical demolition equipment, of the remaining slab or foundation of a structure described in exemption 2 or 3 above once the structure has been demolished to grade, or the removal of landscaping elements, on grade parking or driveways, or pools that are accessory to a structure described in exemption 2 or 3 above, provided during all such removal work the mechanical demolition equipment is located on the ground or a slab on grade. 5. Partial demolition operations accomplished without any mechanical demolition equipment, other than handheld devices, provided such work is a minor alteration or ordinary repair. 6. Demolition operations that do not require a permit.
3306.5.1 Required documents. | Submittal documents shall be approved by the department before demolition work begins. Such submittal documents shall be signed, sealed, and submitted by a registered design professional and shall contain, at a minimum, the following:
3306.5.1.1 Submittal documents for full or partial demolition using mechanical equipment other than handheld. | Submittal documents for full or partial demolition using mechanical equipment other than handheld shall be signed, sealed and submitted by a registered design professional.
3306.5.2 Maintenance of submittal documents. | The approved set of submittal documents shall be kept at the site at all times and be accessible for inspection in accordance with Section 3301.7. It shall be a violation of this code to use mechanical equipment, whether handheld or other than handheld, to perform full or partial demolitions unless the approved submittal documents required by Section 3306.5.1 are available for inspection. Failure to make submittal documents available on site may result in the issuance of a stop work order.
3306.5.3 Filing requirements. | Where submittal documents are required in connection with full or partial demolition in accordance with Section 3306.5, applications shall be filed by the registered design professional in accordance with Article 104 of Chapter 1 of Title 28 of the Administrative Code and shall be approved prior to issuance of the work permit.
3306.5.4 Assessment of structure to be demolished. | Submittal documents required by Section 3306.5 shall be based upon an assessment of the structure where demolition operations are to occur. The assessment shall be performed by a registered design professional. The assessment shall, at a minimum, consist of an interior and exterior physical inspection of the structure where demolition operations are to occur, in which all areas to be demolished are accessed during the inspection. The results of the assessment shall be documented in an assessment report prepared by the person who performed the assessment. If the assessment was performed by a registered design professional other than the registered design professional who prepares the submittal documents, the report shall be provided to the registered design professional who prepares the submittal documents.
3306.5.5 Assessment of adjoining structures. | Where a bearing masonry or wood framed building shares a party wall or party foundation with a building that is to undergo a full demolition, a demolition performed in conjunction with work that meets the requirements of Section 101.4.5 of Title 28 of the Administrative Code, a demolition that results in the demolition of more than 50 percent of the gross floor area of the building during the course of work over any 12-month period, or a demolition that results in the removal of one or more floors during the course of work over any 12-month period, the submittal documents required by Section 3306.5 shall be based upon an assessment of such bearing masonry or wood framed building. The assessment shall be performed by a registered design professional. The assessment shall, at a minimum, consist of an interior and exterior visual inspection of the structure where demolition operations are to occur. The results of the assessment shall be documented in an assessment report prepared by the person who performed the assessment. If the assessment was performed by a registered design professional other than the registered design professional who prepares the submittal documents, the report shall be provided to the registered design professional who prepares the submittal documents.
3306.5.6 Review of pertinent plans and records. | Submittal documents required by Section 3306.5 shall be based upon a review of all pertinent plans and records of the structure where demolition operations are to occur. In addition, where a building is to undergo a full demolition, a demolition performed in conjunction with work that meets the requirements of Section 101.4.5 of Title 28 of the Administrative Code, a demolition that results in the demolition of more than 50 percent of the gross floor area of the building during the course of work over any 12-month period, or a demolition that results in the removal of one or more floors during the course of work over any 12-month period, the submittal documents shall further be based upon a review of all pertinent plans and records of all adjoining structures. The review shall be performed by the registered design professional who prepares the submittal documents.
3306.5.7 Incorporate all other relevant reports. | The demolition submittal documents must incorporate all the conditions and findings identified in the geotechnical report when such report is required by Section 1803.6, the evaluation analysis when such analysis is required by Section 1817, the assessment reports required by Section 3306.5.4 and 3306.5.5, and the preconstruction survey when such survey is required by Section 3309.4.3.
3306.6 Special inspection. | Demolition shall be subject to special inspection in accordance with Chapter 17.
3306.7 Demolition of weakened structures. | Where a structure to be demolished has been partially wrecked or weakened by fire, flood, explosion, age, or other causes, it shall be shored or braced to the extent necessary to permit orderly full demolition or partial demolition without collapse. The necessary measures to ensure a safe demolition shall be determined by the owner’s registered design professional and shall be approved by the commissioner. Exception: Shoring or bracing are not required for the full demolition of a building, subject to the approval of the commissioner, provided: 1. The demolition is conducted with mechanical demolition equipment, other than handheld devices; and 2. No demolition operation occurs, or equipment is located, within the structure of the building.
3306.8 Demolition sequence. | Any structural member that is being dismembered shall not support any load other than its own weight. No wall, chimney, or other structural part shall be left in such condition that it may collapse or be toppled by wind, vibration or any other cause. The method of removal of any structural member shall not destabilize remaining members. All handling and movement of material or debris shall be controlled such that it will not develop unaccounted impact loads on the structure.
3306.8.1 Structural steel, reinforced concrete, and heavy timber buildings. | Structural steel, reinforced concrete, and heavy timber buildings, or portions thereof, shall be demolished column length-by-column length and tier-by-tier. Structural members shall be chained or lashed in place to prevent any uncontrolled swing or drop. Exception: Where the design applicant who prepared the submittal documents required by Section 3306.5 has demonstrated the adequacy of alternate means of demolition through plans, calculations, or the establishment of safety zones, as appropriate, the commissioner may accept such alternative means of demolition.
3306.8.2 Masonry buildings with wooden floors. | Demolition of masonry buildings with wooden floors shall comply with the following requirements:
3306.9 Safeguards. | Demolition shall be conducted in accordance with the requirements of Sections 3306.9.1 through 3306.9.16.
3306.9.1 Utilities and service lines. | The requirements of Section 3303.2 shall apply.
3306.9.2 Party wall exits, fire exits. | The requirements of Section 3303.9 shall apply.
3306.9.3 Dust. | Dust producing operations shall be wetted down to the extent necessary to control the dust.
3306.9.4 Water accumulation. | The requirements of Section 3303.14 shall apply.
3306.9.5 Temporary elevators and standpipe systems. | The requirements of Sections 3303.8 and 3303.12 shall apply.
3306.9.6 Sprinkler systems. | The requirements of Section 3303.7.4 shall apply.
3306.9.7 Use of explosives. | The use of explosives in demolition operations shall conform to the requirements and limi­tations imposed by the New York City Fire Code and Section 3312.
3306.9.8 Hazards to be removed. | Prior to the commencement of demolition operations, hazards shall be removed in accordance with Sections 3306.9.8.1 through 3306.9.8.4.
3306.9.8.1 Combustible content. | Prior to the commencement of demolition operations, the area authorized to be demolished by the work permit shall be thoroughly cleaned of combustible content and debris, including but not limited to building contents and exterior finishes, down to the structural elements.
3306.9.8.2 Asbestos. | Prior to the commencement of demolition operations, all asbestos shall be removed from the area authorized to be demolished by the department work permit, and certification to that effect shall be filed with the department and the Department of Environmental Protection. Such asbestos removal shall be in accordance with Section 28-106 of the Administrative Code and rules promulgated by the commissioner of the Department of Environmental Protection.
3306.9.8.3 Glass. | Prior to the commencement of demolition operations, all glass located in the area authorized to be demolished by the work permit, including but not limited to glass in windows, doors, skylights, and fixtures, shall be removed. Exception: Demolition operations relating to the alteration, maintenance, or repair of a façade.
3306.9.8.4 Steam and fuel. | Prior to the commencement of demolition operations, all pipes, tanks, boilers, or similar devices containing steam or fuel and located in the area authorized to be demolished by the work permit shall be purged of such steam or fuel. Exception: Pipes, tanks, boilers, or similar devices containing steam or fuel located in the area authorized to be demolished by the work permit and which will not be disturbed during the course of the demolition operation may, in lieu of being purged, be safeguarded so as to prevent their being damaged during the course of demolition operations.
3306.9.9 Stairs. | All enclosed vertical shafts and stairs shall be maintained enclosed at all floors except the topmost floor being demolished, and all work on the topmost floor shall be completed before stair and shaft enclosures on the floor below are disturbed. All hand rails and banisters shall be left in place until actual demolition of such floor is in progress.
3306.9.10 Floors. | The safeguards of Sections 3306.9.10.1 through 3306.9.10.3 shall apply to demolition operations involving floors.
3306.9.10.1 Bearing partitions and headers. | No bearing partition shall be removed from any floor until the floor framing system on the floor above has been removed and lowered. All header beams and headers at stair openings and chimneys shall be carefully examined and, where required, shall be shored from the cel­lar floor through successive floors. All operations shall be continually monitored by a qualified person designated by the permit holder as the work progresses to detect any hazards that may develop.
3306.9.10.2 Floor openings not to aggregate more than 25 percent of the gross floor area. | Openings in any floor shall not aggregate more than 25 percent of the area of that floor unless it can be shown by submission from a registered design professional to the satisfaction of the commissioner that larger openings will not impair the stability of the structure.
3306.9.10.3 Covering of floor openings. | Floor openings used for the removal of debris shall comply with Section 3306.9.12.1. Every opening not used for the removal of debris in any floor shall be clearly marked and solidly planked over by planking not less than 2 inches (51 mm) in thickness, or equivalent solid material, laid close.
3306.9.11 Storage of material. | Material shall not be stored on catch platforms, working platforms, floors, or stairways of any structure, except that any one floor of a building to be demolished may be used for the temporary storage of material when such floor can be evaluated by a registered design professional and proven to be of adequate strength to support one and one-half times the load to be superimposed. Such evaluation by the registered design professional shall be maintained by the permit holder and made available to the department upon request.
3306.9.11.1 Avoid interference. | Storage spaces shall not interfere with access to any stairway or passageway, and suitable barricades shall be provided so as to prevent material from sliding or rebounding into any space accessible to the public. All material shall be safely stored or piled in such storage locations in a manner that will not overload any part of the structure or create any hazard.
3306.9.11.2 Examination of connections. | Before any material is stored on any floor, the existing flooring adjacent to bearing walls, shear walls, beams and columns shall be removed and the connections of the floor framing system to the bearing walls, shear walls, beams and columns shall be carefully examined by a competent person designated by the permit holder to ascertain their condition and adequacy to support such material. If the connections are found to be in poor condition or inad­equate to support the stored material, no material shall be deposited on the floor until these connections are shored from the cellar floor through each successive floor or otherwise strengthened to safely support such material.
3306.9.11.3 Removal of floor slabs for storage. | In buildings of noncombustible construction, floor slabs to an elevation of not more than 25 feet (7620 mm) above the legally established curb level may be removed to provide temporary storage for debris, provided that:
3306.9.11.4 Cellar or basement storage. | Debris stored in the cellar or basement shall not be piled above the level of the adjacent exterior grade unless the demolition contractor provides sheet-piling, shoring, bracing, or such other means necessary to insure the stability of the walls and to prevent any wall from collapsing due to horizontal loading created by the debris as determined by a registered design professional. Where debris is stored against a party wall, the requirements of Section 3306.9.11.5 shall also apply.
3306.9.11.5 Examination of party walls. | Party walls shall be carefully examined by a competent person designated by the permit holder to ascertain the condition and adequacy of the party wall prior to the placement of any material that will impose a load upon such party wall. If the party wall is to be found to be in poor condition or inadequate to support the stored material, no material shall be deposited on the floor until the party wall is shored or otherwise strengthened as determined by a registered design professional to safely support such material.
3306.9.12 Removal of material. | Debris, bricks, and similar material shall be removed through openings in the floors of the structure, or by means of chutes, buckets, or hoists that comply with the provisions of this chapter.
3306.9.12.1 Floor openings used for the removal of debris. | Every opening in a floor used for the removal of debris shall be tightly enclosed with a shaftway, extending from floor to floor, with such shaftway enclosed with: 1. Planking not less than 2 inches (51 mm) in thickness, or equivalent solid material; or 2. Where the opening is used for the removal of noncombustible material, wire mesh may be utilized in lieu of planking, provided such mesh is not less than number 18 gauge wire mesh, with openings in the wire no longer than ½ inch (13 mm), and also provided that the wire mesh is securely attached, in accordance with drawings developed by a registered design professional, to the shaftway so that the wire mesh enclosure in any location does not deflect more than 2 inches (51 mm) when a force of at least 200 pounds (890 n) is applied along any horizontal portion of such wire mesh enclosure. Exceptions: 1. In buildings not more than six stories or 75 feet (22 860 mm) in height, whichever is less, a shaftway is not required. Instead openings in the floor shall be clearly marked and solidly planked over while not in use by planking not less than 2 inches (51 mm) in thickness, or equivalent solid material, and laid close. 2. A shaftway is not required at the working deck. Instead, openings in the working deck shall be clearly marked and solidly planked over while not in use by planking not less than 2 inches (51 mm) in thickness, or equivalent solid material, laid close.
3306.9.12.1.1 Temporary removal of protection. | Wherever a shaftway or planking required by Section 3306.9.12.1 has been temporarily removed to permit debris removal, the floor opening shall be protected by a guardrail system that meets the requirements of Sections 3308.7.1 through 3308.7.5. Such protection required by Section 3306.9.12.1 shall be promptly replaced in posi­tion upon the ceasing of such work at the end of each workday.
3306.9.12.2 Protection of wall openings. | In any buildings more than 25 feet high (7620 mm), any window or other exterior wall opening that is within 20 feet (6096 mm) of a floor opening used for the passage of debris from levels above shall be solidly boarded up or otherwise substantially covered, unless such window or opening is so located as to preclude the possibility of any person being injured by material that may fall from such window or opening.
3306.9.12.3 Chutes. | Chutes used in association with the removal of materials shall comply with Section 3303.5.5.
3306.9.13 Rodent extermination. | A licensed exterminator shall effectively treat the premises for rodent extermination as per the requirements of the Department of Health and Mental Hygiene. Exception: Partial demolition operations.
3306.9.14 Chimneys. | Where brick or masonry chimneys cannot be safely toppled or dropped, all materials shall be dropped down on the inside of such chimneys.
3306.9.15 Partitions. | Partitions required for the stability of the structure or required for egress, as identified in the submittal documents required by Section 3306.5, shall be clearly marked prior to the commencement of demolition operations. Such partitions shall not be removed until a competent person designated by the permit holder has determined the demolition sequence, as identified in the submittal documents, has reached the point the partitions can be safely removed, and authorizes their removal.
3306.9.16 Temporary weather protection. | Temporary weather protection shall be installed and maintained by the demolition contractor, as necessary, to protect building systems or elements that may be susceptible to exposure to the weather during periods where the permanent weather protection has been breached, diminished, or is not yet in place. Such building systems or elements include, but are not limited to, walls, party walls, roofs, areas of missing brick, loose lain brick, and exposed electrical conduit.
3306.10 Removal of foundations and slabs. | Where a building, or any portion, has been demolished to grade, the floor slab or foundation of such building, or portion, shall be removed and the site backfilled to grade. Exceptions: 1. Cellar floors may remain provided the cellar floor slab is broken up to the extent necessary to provide ground drainage and prevent accumulation of water, and also provided that all fixtures or equipment that would cause voids in the fill are removed. 2. Where portions of a foundation, underpinning, or similar elements, other than a cellar floor, are to remain and be covered with backfill, a waiver approved by the commissioner shall be obtained. Drawings prepared by a registered design professional depicting the remaining buried structure shall be submitted with the waiver request. 3. Where a floor slab or foundation is to remain and not be backfilled, a waiver approved by the commissioner shall be obtained. Such request for waiver shall be accompanied by a statement and drawings prepared by a registered design professional demonstrating the necessity for retaining the existing floor slab or foundation for future construction or site remediation, as well as demonstrating positive cellar drainage to an approved place of disposal.
3306.10.1 Evaluation of fill on adjoining foundations. | Where the installation of fill will impart a load on an adjoining foundation, a registered design professional shall evaluate the foundation prior to the placement of the fill. If necessary, sheeting, shoring, or bracing shall be provided as indicated by the registered design professional.
3306.11 Completion of demolition operations. | All work required for structural stability and permanent waterproofing of adjacent buildings must be completed prior to demolition sign-off.
3306.12 Monitoring of adjoining structures during demolition. | Where a bearing masonry or wood framed building shares a party wall or party foundation with a building that is to undergo a full demolition, a demolition performed in conjunction with work that meets the requirements of Section 101.4.5 of Title 28 of the Administrative Code, a demolition that results in the demolition of more than 50 percent of the gross floor area of the building during the course of work over any 12-month period, or a demolition that results in the removal of one or more floors during the course of work over any 12-month period, such bearing masonry or wood framed building shall be monitored during the demolition operation. The monitoring shall be in accordance with a monitoring plan prepared or accepted by the registered design professional who prepared the submittal documents in accordance with Section 3306.5. The monitoring plan shall be acceptable to the commissioner and shall include but not be limited to, the monitoring frequency, reporting requirements for the monitoring program, anticipated movement and settlement thresholds, and procedures to be implemented when thresholds are exceeded.
3306.13 Additional monitoring required by the commissioner. | When, in the opinion of the commissioner, a demolition operation poses a potential hazard to an adjacent building, elevations of the building under demolition or the adjacent building, or both, shall be recorded or other monitoring procedures shall be implemented by a registered design professional at intervals of 24 hours or less as determined by the commissioner to ascertain if movement has occurred.
3307.1 Scope. | Pedestrians shall be protected during construction or demolition activities as required by this section and by the Department of Transportation.
3307.2 Streets, including bicycle lanes and sidewalks, as well as walkways and pathways. | Streets, including bicycle lanes and sidewalks, as well as walkways and pathways, either within the public way or within a site, shall meet the requirements of Sections 3307.2.1 through 3307.2.6, and the requirements of the Department of Transportation.
3307.2.1 Obstruction of streets, including bicycle lanes and sidewalks. | The requirements of the Department of Transportation shall apply with regard to the closing of streets, including bicycle lanes and sidewalks, or to the obstruction of any part thereof.
3307.2.2 Temporary public walkway in the street. | Where authorized by the Department of Transportation, a temporary walkway open to the public may be provided in the street in front of the site. Such temporary walkway shall be protected in accordance with the requirements of the Department of Transportation. Department of Transportation authorization is required where a temporary walkway and a temporary or permanent bicycle lane will share the same space.
3307.2.3 Temporary public walkway within the site. | Where authorized by the commissioner, a temporary walkway open to the public may be provided through a site that is otherwise fenced and closed to the public. Such temporary walkway shall be:
3307.2.4 Pathways. | Where a means of ingress/egress to a building or structure remains open to the public during the course of construction or demolition, an adequate pathway shall be provided between such means of ingress/egress and the sidewalk, or in lieu of the sidewalk, the temporary public walkway provided in accordance with Section 3307.2.2.
3307.2.5 Foot bridges. | Where foot bridges are utilized as part of a sidewalk, walkway, or pathway, they shall be provided with guardrails for the entire length, and shall have cleats to prevent slipping. Where planks are used to pave the walkway of the foot bridge, the planks shall be laid close and securely fastened to prevent displacement. Planks shall be of uniform thickness, and all exposed ends of ramps shall be provided with beveled fillers to eliminate tripping hazards.
3307.2.6 Requirements for sidewalks, temporary walkways, foot bridges, and pathways. | Sidewalks, walkways, foot bridges, and pathways that remain open to the public shall be accessible and shall be provided with: 1. A continuous clear path, free of obstruction, at least 5 feet (1524 mm) in width; 2. A durable walking surface capable of supporting all imposed loads and in no case shall the design live loads be less than 150 pounds per square foot (732.4 kg/m2); 3. Mirrors at locations where a pedestrian’s or bicyclist’s view is obstructed, including but not limited to blind corners, blind turns, and points where fencing or similar barriers project into a sidewalk, temporary walkway, foot bridge, or pathway; 4. For a temporary walkway or foot bridge where there is a change in elevation along the walkway or foot bridge, a ramp with a running slope not steeper than one unit vertical in 12 units horizontal (8-percent slope) with a level landing at least 5 feet long at the top and bottom of each run, and if there is a total rise greater than 6 inches (152 mm), handrails; and 5. For a temporary walkway or foot bridge where the running slope of such walkway or foot bridge is steeper than one unit vertical in 20 units horizontal (5-percent slope) and there is a total rise greater than 6 inches (152 mm), handrails. Exception: Where it is not possible to provide the continuous clear path to the extent required by Item 1 above, the sidewalk, temporary walkway, or pathway shall be kept open to the extent required by the Department of Transportation, and shall also comply with applicable provisions of ICC A117.1, the ADA Accessibility Guidelines for Buildings and Facilities and/or the ADA Accessibility Guidelines for Pedestrian Facilities in the Public Right-of-Way, as applicable.
3307.3 Sidewalk sheds and fences. | Sidewalk sheds shall be provided as required by Section 3307.6. Fences shall be provided as required by Section 3307.7.
3307.4 Warning signs, personnel, and barriers. | Warning signs, personnel, or barriers shall be provided to protect the public from hazards generated by construction or demolition activity in or adjacent to a public way as set forth in Sections 3307.4.1 through 3307.4.7.
3307.4.1 Obstructions and openings. | Obstructions or openings located in a public way shall be marked and guarded by barriers, flags, or signs in accordance with the requirements of the Department of Transportation.
3307.4.2 Dangerous areas. | In areas where special danger to the public exists, including but not limited to vehicle entrances and exits, hoisting areas, points of storage of explosives or highly flammable material, blasting areas, or discharge ends of chutes, descriptive warning signs shall be provided in accordance with the requirements of the Department of Transportation.
3307.4.3 Vehicular traffic. | Whenever any work is being performed over, on, or in close proximity to a highway, street, or similar public way, control and protection of traffic shall be provided by barriers, signals, signs, flagperson, or other devices, equipment, and personnel in accordance with the requirements of the Department of Transportation.
3307.4.4 Areas open to persons other than workers. | A flagperson shall be provided whenever intermittent operations are conducted on, or adjacent to, areas open to use by persons other than workers, or when dangerous operations, such as blasting, may affect such areas. Where required by the Department of Transportation, designated personnel shall also be provided in addition to flag persons.
3307.4.5 Additional signs. | In addition to the requirements of this section, information panels and signs shall also be provided as required by Section 3301.9.
3307.4.6 Prohibited signs. | See Section 3301.9.
3307.4.7 Work or storage zones. | Where work or storage related to the construction or demolition of a building or structure is occurring adjacent to a sidewalk shed or equivalent overhead protection, and such work or storage area is not contained within the enclosed and fenced area of the site as specified in Section 3307.7, fencing, barriers, or netting complying with items 1, 2, or 3 of this section shall be provided to separate the sidewalk, walkway, foot bridge, or pathway from the work or storage area.
3307.5 Watchperson and flagperson. | Watchpersons shall be provided as required by Section 3303.3. Flagpersons shall be provided as required by Section 3307.4.
3307.6 Sidewalk sheds. | Sidewalk sheds shall be provided as required by this section to protect pedestrians from construction or demolition operations.
3307.6.1 Permit. | No sidewalk shed shall be installed without a permit in accordance with the requirements of Chapter 1 of Title 28 of the Administrative Code.
3307.6.2 Where required. | A sidewalk shed shall be installed and maintained to protect all sidewalks, walkways, and pathways within the property line of a site, and all public sidewalks that abut the property, as follows: 1. When such sidewalk, walkway, or pathway is to be located immediately below a scaffold, mast climber, or chute. The sidewalk shed shall be installed prior to the installation of such equipment and shall not be removed until such equipment has been dismantled and/or removed from the area being protected; 2. When a structure higher than 40 feet (12 192 mm) or greater is to be constructed, and the sidewalk, walkway, or pathway is within a perpendicular distance from the new structure that is equal to or less than half the height of the new structure. The sidewalk shed shall be installed when the structure reaches the planned height of the shed. Such shed shall not be removed until the structure is enclosed, all exte¬rior work has been completed and the sash is glazed above the second story, the façade has been cleaned down, and all exterior chutes, scaffolds, mast climbers, and hoisting equipment have been dismantled and removed from the site; 3. When a portion of a façade over 40 feet (12 192 mm) above curb level is to be constructed, altered, maintained, or repaired, or a vertical or horizontal enlargement is to occur at a height over 40 feet (12 192 mm) above curb level, and the sidewalk, walkway, or pathway is within a perpendicular distance from the structure that is equal to or less than half the height of such façade work or vertical or horizontal enlargement. The sidewalk shed shall be installed prior to the commencement of work at a height greater than 40 feet (12 192 mm) above curb level. Such shed shall not be removed until the building is enclosed, all exte¬rior work has been completed and the sash is glazed above the second story, the façade has been cleaned down, and all exterior chutes, scaffolds, mast climbers, and hoisting equipment have been dismantled and removed from the site; or 4. When a structure higher than 25 feet (7620 mm) is to undergo a full demolition, or when exterior partial demolition, other than that performed in conjunction with the construction, alteration, maintenance, or repair of a façade, is to occur at a height greater than 25 feet (7620 mm) above curb level, and the sidewalk, walkway, or pathway is within a perpendicular distance from the structure that is equal to or less than half the height of the demolition work. The sidewalk shed shall be installed prior to the commencement of demolition work. Such shed shall remain in place until the building has been razed to the height of the shed, or where the building is not being fully demolished, until all demolition work has been completed and all exterior chutes, scaffolds, mast climbers, and hoisting equipment have been dismantled and removed from the site. Exceptions: Except where specifically required by the commissioner to protect the public from unique hazards at the site, sidewalk sheds are not required for: 1. Sidewalks, walkways, and pathways, or portions thereof, that are closed to the public. 2. Temporary walkways in accordance with Section 3307.2.3 that are provided with lighting and overhead protection equivalent to that afforded by a sidewalk shed. 3. Inspections, including a façade inspection, provided no work occurs during the inspection. 4. Sign hanging occurring by or under the direct and continuing supervision of a licensed sign hanger. 5. Window washing. 6. Work confined to the roof of an existing building, provided that: 6.1 The edge of the roof is enclosed to a height of 42 inches (1067 mm) with a solid parapet; 6.2 Such parapet is of sufficient strength to resist accidental impact during construction; 6.3 The work does not exceed the height of the parapet or is set back from the edge of the roof at a distance that is equal to or greater than half the height of the work; and 6.4 No work occurs on the parapet itself, and no material is placed or stored on the parapet during the course of the work. 7. Subject to the approval of the commissioner, work of limited scope and duration provided that: 7.1 During the course of the work the area immediately under the work zone is temporarily closed to the public by means of barriers, cones, or caution tape, and flagpersons are provided to direct pedestrian traffic; 7.2 At the end of the day the façade of the building is left in a safe condition and fully enclosed; and 7.3 There is compliance with Section 3307.2.1. 8. Locations where a cantilevered platform has been installed, provided that: 8.1 The cantilevered platform is approved by the commissioner; 8.2 The cantilevered platform provides overhead protection equivalent to a sidewalk shed; and 8.3 The cantilevered platform is installed below the level of work to be performed, excluding work performed at the first story. 9. Areas along an exposure that are located more than 5 feet (1524 mm) beyond those required for compliance with Item 1 of Section 3307.6.2, provided that: 9.1 The work is limited to the alteration, maintenance, or repair of a façade, and does not constitute a façade recladding as defined in rules promulgated by the commissioner; and 9.2 The entire exposure where façade work is to occur is covered by either: 9.2.1 A supported scaffold with netting and guardrails in accordance with Section 3314.8; or 9.2.2. A site specific engineered enclosure system in accordance with Section 3309.17.
3307.6.3 Area to be protected. | The decking of the sidewalk shed shall extend: 1. The full length of the area that falls within the zone specified in Section 3307.6.2, plus an additional 5 feet (1524 mm) beyond such length, or to within 18 inches (457 mm) of the curb line, whichever is less; or where the sidewalk shed is installed to protect against an unenclosed façade, work, or equipment that is greater than 100 feet (30 480 mm) above the ground, the decking of the sidewalk shed shall extend the full length of the area that falls within in the zone specified in Section 3307.6.2, plus an additional 20 feet (6096 mm) on both ends beyond such length, or to within 18 inches (457 mm) of the curb line, whichever is less. 2. The full width of the sidewalk, walkway, or pathway that falls within the zone specified in Section 3307.6.2, except for a clearance to avoid existing obstructions, not to exceed 18 inches (457 mm) along the curb. Exceptions: 1. Where it is not possible to bring the deck tightly against the face of an abutting building, structure, or fence, the deck shall be brought to within 1 inch (25 mm) of the face of such building, structure, or fence, with the resulting gap sealed or covered by material of sufficient manner and strength capable of trapping falling debris. 2. Openings in the deck to avoid tree trunks and branches, provided such opening is brought as close to the tree as practical without damaging the tree.
3307.6.4 Design and construction of sidewalk sheds. | Sidewalk sheds shall be designed and constructed in accordance with the requirements of Sections 3307.6.4.1 through 3307.6.4.11.
3307.6.4.1 Design required. | All sidewalk sheds shall be designed by a registered design professional. The sidewalk shed design shall be detailed on plans developed by the registered design professional. The plans shall be specific to the site and shall, at a minimum, include a plan view and an elevation view, with full dimensions, detailing:
3307.6.4.2 Design loads. | All sidewalk sheds shall be designed as a heavy duty sidewalk shed to carry a live load of at least 300 pounds per square foot (1464.7 kg/m2). However, where the shed is installed to protect from work performed at a height of less than 100 feet (30 480 mm) above the ground, the sidewalk shed may be designed as a light duty sidewalk shed to carry a live load of at least 150 pounds per square foot (732.4 kg/m2), provided that no item is stored or placed upon the shed.
3307.6.4.2.1 Wind and other loads. | The effect of wind and other loads on the sidewalk shed, and any item placed or attached on or to the shed, shall be considered in the design in accordance with Chapter 16.
3307.6.4.2.2 Storage. | Storage on sidewalk sheds shall be as follows:
3307.6.4.3 Materials. | Sidewalk sheds shall be constructed out of wood, steel, or other material possessing equivalent strength and suitability.
3307.6.4.4 Vertical members and beams. | Vertical members and beams of the sidewalk shed shall conform with the following:
3307.6.4.5 Deck. | The deck of the sidewalk shed shall conform with the following:
3307.6.4.6 Parapet. | A vertical parapet at least 3 feet 6 inches (1067 mm) high, but no more than 4 feet (1219 mm) high, as measured from the deck of the sidewalk shed, shall be constructed along all edges of the sidewalk shed. Such parapet shall consist of galvanized wire screen not less than No. 16 steel wire gauge with a ½ inch (13 mm) mesh. Parapets shall be securely attached to the shed with braced uprights. Parapet braces shall be made of metal. Temporary removal of a portion of the parapet is permitted for the handling of material, provided the parapet is immediately restored at the end of the handling operation. Exceptions: 1. A parapet is not required along the edge of the sidewalk shed that abuts a building or structure. 2. A parapet is not required along the edge of a sidewalk shed that abuts an area that is closed to the public. 3. Where the sidewalk shed is installed in conjunction with the full or partial demolition of a building or structure, other than work limited to a façade project, the parapet shall consist of plywood or other equivalent solid material. 4. Where a sign, including a parapet information panel, is installed on a sidewalk shed, the parapet backing for the sign may consist of plywood or other equivalent solid material.
3307.6.4.7 Height. | The passageway under the shed shall have a mini­mum clear ceiling height of 8 feet (2438 mm). Exception: Lights that extend no more than 8 inches (203 mm) below the level of the deck shall be excluded from the clear ceiling height measurement.
3307.6.4.8 Lighting. | Sidewalk shed lighting shall be in conformance with the following:
3307.6.4.9 Avoid interference. | Sidewalk sheds shall be installed and located so to not unreasonably obstruct, either visually or physically, traffic, curb cuts, curb ramps, vehicular access points, street lighting poles, traffic lights or signs, fire hydrants, fire department connections, water sampling stations, bus shelters, or other street furniture, trees, adjacent show windows, means of ingress/egress, subway entrances, or access points to vaults, manholes, or other underground structures.
3307.6.4.10 Founding. | Sidewalk shed founding shall be in accordance with the following:
3307.6.4.11 Color. | Sidewalk sheds erected on or after July 1, 2013, shall meet the following color requirements: 1. Solid parapet panels shall be hunter green. 2. Mesh parapet panels shall be hunter green or metallic gray. 3. Portions of parapet panel framing members visible to the public shall be hunter green. This includes side and back portions of such parapet panel framing members that may be visible through mesh panels. 4. Vertical members, cross bracing, and other metallic components shall be hunter green or metallic gray. Exception: Sidewalk sheds that are of a model whose prototype won a design competition recognized by the city may be white in color.
3307.6.5 Installation, adjustment, maintenance, repair, use, inspection, and removal of sidewalk sheds. | Sidewalk sheds shall be installed, adjusted, maintained, repaired, used, inspected, and removed in accordance with the following requirements.
3307.6.5.1 Safe condition. | Sidewalk sheds shall be maintained in a safe condition and used in a manner that eliminates hazards to the public. Any hazardous conditions or defects discovered with the sidewalk shed shall immediately be brought to the attention of the permit holder for the shed.
3307.6.5.2 Supervision of installation, adjustment, repair, and removal. | The installation, adjustment, repair, or removal of a sidewalk shed shall be performed under the supervision of a competent person designated by the permit holder for the sidewalk shed.
3307.6.5.3 Responsibility for maintenance and use. | Sidewalk sheds shall be maintained and used by the general contractor, or where there is no general contractor, the contractor causing the work to be performed, or where there is no active work, the building owner.
3307.6.5.4 Storage or placement of items. | No item shall be stored or placed upon a sidewalk shed unless such shed has been designed for such storage or placement in accordance with Section 3307.6.4.2.2. Where such shed has been so designed, items shall be stored or placed only in the area designated on the drawings for storage. Any item placed or stored upon a sidewalk shed shall be secured in a manner to prevent dislodgement, displacement by wind, and shall be distributed so as not to exceed the design limits of the sidewalk shed.
3307.6.5.5 Cleaning. | The decks of sidewalk sheds shall be broom swept and cleaned of material daily while active work is occurring at the site.
3307.6.5.6 Sharp edges. | Where located in an area that could pose a danger to the public, bolts and screws without a cap, and sharp edges, shall be protected to prevent injury to the public.
3307.6.5.7 Installation inspection. | Upon completion of the installation of a sidewalk shed, the shed shall be inspected by a qualified person designated by the designer, the permit holder for the shed, or a third party acceptable to both the designer and the permit holder to verify that the sidewalk shed is in a safe condition and has been installed in accordance with drawings and the requirements of this chapter.
3307.6.5.8 Periodic inspection. | A periodic inspection of the sidewalk shed shall be performed six months following the last installation, adjustment, or repair inspection required by Section 3307.6.5.7 or 3307.6.5.9, or where no such inspection has occurred within six months, six months following the last periodic inspection. The periodic inspection shall be performed by a qualified person designated by the designer, the permit holder for the shed, or a third party acceptable to both the designer and the permit holder to verify that the sidewalk shed is in a safe condition and is in compliance with drawings and the requirements of this chapter.
3307.6.5.9 Inspection following an adjustment or repair. | Following a repair or adjustment at a site, the sidewalk shed shall be inspected by a qualified person designated by the designer, the permit holder for the shed, or a third party acceptable to both the designer and the permit holder to verify the adequacy of the repair or adjustment and to verify the sidewalk shed is in a safe condition and is in compliance with drawings and the requirements of this chapter.
3307.6.5.10 Daily inspection. | Sidewalk sheds shall be visually inspected daily by a person designated by the general contractor, or where there is no general contractor, the contractor causing the work to be performed, or where there is no active work, by the building owner to verify compliance with Items 1 through 5 of this section. 1. The lights are functioning; 2. No brace or rail is hanging unattached at one or more ends; 3. No portions of the support structure are disconnected; 4. No section of parapet is missing; and 5. All legs remain on their support and are supported to the ground, and any wood blocking is free of visible rot. Exception: The inspections for a scaffold suspended or supported above a sidewalk shed shall be in accordance with Section 3314.
3307.6.5.11 Inspection reports. | The results of an inspection required by Sections 3307.6.5.7 through 3307.6.5.10 shall be recorded in an inspection report that is prepared, signed, and dated by the person who performed the inspection. In lieu of compliance with the requirements of Section 3301.7, copies of the inspection reports required by Sections 3307.6.5.7 through 3307.6.5.10 shall be maintained at the site by the general contractor, or where there is no general contractor, the contractor causing the work to be performed, or where there is no active work, by the building owner.
3307.6.5.12 Discovery of defects. | Defects discovered during the course of performing an inspection required by Sections 3307.6.5.7 through 3307.6.5.10 shall immediately be brought to the attention of the permit holder for the shed.
3307.6.5.13 Notification of removal. | The permit holder for the shed shall notify the department no more than two business days following the complete removal of a sidewalk shed.
3307.6.5.14 Signage. | Only signage, including parapet information panels, allowed by Section 3301.9, and indicated on the sidewalk shed design drawings in accordance with Section 3307.6.4.1, shall be installed on the sidewalk shed. Sidewalk shed signage shall only be installed, adjusted, maintained, repaired, and removed by the permit holder for the shed or an entity authorized by the permit holder.
3307.7 Fences. | All sites where a new building is being constructed, or a building is being demolished to grade, shall be enclosed with a fence. Fences shall also be installed to fully or partially enclosed sites, as necessary, where there exists an open excavation, an unenclosed portion of a building accessible at grade, or other hazard to the public. Such fences shall be at least 8 feet (2438 mm) high, built solid for their entire length, out of wood or other suitable material, and shall be returned at the ends to the extent necessary to effectively close off the site. Exceptions: 1. The commissioner may approve the use of a chain link fence to: (i) Secure a site where work has been interrupted or abandoned and discontinued, and a registered design professional has certified that all construction or demolition equipment and material that pose a hazard to the safety of the public and property have been removed from the site or safely secured. Prior to the resumption of work, the chain link fence shall be replaced by a solid fence meeting the requirements of this section. (ii) Secure portions of a site where a one-, two-, or three-family building that is 40 feet (12 192 mm) or less in height, or a commercial building 40 feet (12 192 mm) or less in height, is being constructed or demolished and such building is setback at least 15 feet (4572 mm) from sidewalks or spaces accessible to the public and 5 feet (1524 mm) from adjoining buildings or structures. 2. Chain link fence shall be installed and maintained to secure a site where work has been discontinued for not less than two continuous years after a registered design professional has certified that all construction or demolition equipment and material that pose a hazard to the safety of the public and property have been removed from the site or safely secured. Prior to the resumption of work, the chain link fence shall be replaced by a solid fence meeting the requirements of this section.
3307.7.1 Location of fence. | Where the fence is installed to fully enclose a site, the fence shall be constructed along the inside edge of the sidewalk or walkway and along the edges of the property line. Where a fence is installed to partially enclose a site, the fence shall be installed as necessary to prevent public access to any excavation or unenclosed portion of the building accessible at grade. Fences shall be installed and located so to not unreasonably obstruct, either visually or physically, traffic, curb cuts, curb ramps, vehicular access points, street lighting poles, traffic lights or signs, fire hydrants, fire department connections, water sampling stations, bus shelters, or other street furniture, trees, means of ingress/egress, or access points to vaults, manholes, or other underground structures. Exceptions: 1. Fences may encroach onto the sidewalk in accordance with Department of Transportation requirements. 2. A fence is not required to be installed along the party wall of an adjoining property, provided no material is stored along such wall during the course of work.
3307.7.2 Gates. | Gates shall be sliding or shall swing into areas not accessible to the public, and shall be provided only where required for access to the site or to facilitate the work. Gates shall consist of the same material and construction as the rest of the fence. Gates shall be kept closed at all times except during actual loading and unloading operations, when individuals or vehicles are actively entering or leaving the site, or as needed to facilitate active work around the gate. Exception: Where approved by the commissioner, chain link gates may be utilized in a solid fence.
3307.7.3 Viewing panels. | Viewing panels shall be provided in solid fences erected on or after July 1, 2013, at a rate one for every 25 linear feet (7.6 m) per frontage, with a minimum of one per frontage. Viewing panels shall be 12 inches by 12 inches (305 by 305 mm) in size and shall be blocked with nonfrangible acrylic paneling or equivalent material. The top of the viewing panel shall be located no more than 6 feet (1829 mm) above the level of the ground, and the bottom of the viewing panel shall be located no less than 3 feet (914 mm) above the level of the ground.
3307.7.4 Chain link fences or gates. | Where a chain link fence or gate is utilized, the following requirements shall apply:
3307.7.5 Design of fences. | Fence installations shall be designed by a registered design professional. The effect of wind on the fence shall be considered in the design in accordance with Chapter 16. Exception: Fences installed in connection with the construction or demolition of a one-, two-, or three-family building that is 40 feet (12 192 mm) or less in height.
3307.7.6 Installation and removal of fences. | Fences required by this section shall be installed prior to the commencement of work. Such required fences shall not be removed until:
3307.7.7 Condition of fences. | All fences and related windscreens or netting shall be installed, adjusted, repaired, and maintained in a sound condition, free of protruding or loose nails, wood, or metal, and with posts in an upright position restrained to prevent the fence from leaning or overturning.
3307.7.8 Inspection of fences. | Fences and related windscreens or netting shall be visually inspected at least once a week, or where a sidewalk shed is installed at the site, daily, by a person designated by the general contractor, or where there is no general contractor, the contractor causing the work to be performed, or where there is no active work, by the building owner to verify the fence and related windscreens or netting remains in a safe condition in accordance with Section 3307.7.7.
3307.7.8.1 Inspection reports. | The results of the inspection shall be recorded in an inspection report that is prepared, signed, and dated by the person who performed the inspection. In lieu of compliance with the requirements of Section 3301.7, copies of the inspection report shall be maintained at the site by the general contractor, or where there is no general contractor, the contractor causing the work to be performed, or where there is no active work, by the building owner.
3307.7.8.2 Discovery of defects. | Defects discovered during the course of performing the inspection shall immediately be brought to the attention of the permit holder for the fence.
3307.7.9 Color. | Fences erected on or after July 1, 2013, shall be painted hunter green. Exception: Where the sidewalk shed installed at the site is of a model whose prototype won a design competition recognized by the city, the fence may be painted the same color as the shed.
3307.8 Maintaining Department of Transportation pedestrian and bicyclist protection in place. | Notwithstanding other provisions of law, pedestrian and bicyclist protection required by the Department of Transportation shall be maintained in place and kept in good order for the entire length of time pedestrians and/or bicyclists may be endangered.
3307.9 Removing protection at conclusion of work. | Public property shall be left in as good a condition following the completion of the construction or demolition work as it was before such work was commenced. Except where otherwise required by this code, the owner or the owner’s agent shall, upon the completion of the construction or demolition work, immediately remove all sidewalk sheds, fences, guard rails, temporary walkways, material, and other obstructions in or adjacent to the public way.
3307.10 Facilitating city work. | In the event a duly authorized city agency must repair, maintain, or install city property, including but not limited to intersection control signs, electrical equipment, traffic signals, lane markings, sewer and water manholes, bus shelters, street lighting, other street furniture, or fire hydrants, at a location where pedestrian protection required by this chapter is located, such pedestrian protection shall be removed as directed by the department of buildings as long as the removal is deemed to be safe and, if necessary, suitable appropriate pedestrian protection that does not interfere with the work of such city agency is installed.
3308.1 Scope. | Protection shall be provided along unenclosed perimeters as required by this section and rules promulgated by the commissioner, including but not limited to safety netting systems, guardrail systems, cocoon systems, climbing formwork, and enclosure panels. Except where this section authorizes the temporary removal of unenclosed perimeter protection, no work shall occur, nor shall materials be stored on any level where required unenclosed perimeter protection is not installed.
3308.2 Permit. | A permit is required for the installation of unenclosed perimeter protection. Exceptions: A permit is not required for: 1. Vertical safety netting systems that are in accordance with Sections 3308.5; 2. Horizontal safety netting systems that are in accordance with Section 3308.6; or 3. Guardrail systems that are in accordance with Section 3308.7.
3308.3 Design and documentation of unenclosed perimeter protection. | Unenclosed perimeter protection shall be designed and provided with documentation in accordance with Sections 3308.3.1 through 3308.3.5. Exception: The requirements of Sections 3308.3.1, and 3308.3.3 through 3308.3.5, shall not apply to guardrail systems. The requirements of Section 3308.7 shall apply to guardrail systems.
3308.3.1 Design. | Unenclosed perimeter protection shall be designed by a registered design professional to meet temporary loads, including but not limited to wind, as prescribed in Chapter 16. The registered design professional shall take the supporting structure into account when designing the installation and shall include details of connections, anchorages, and supports. The minimum loads for vertical net cables required by Section 3308.5.3 need not be added to wind loads in determining the maximum lateral force, but in no event shall the maximum design load for the cables be less than that required by Section 3308.5.3. A reduction in the surface area due to the openings in vertical or horizontal net fabric or partially enclosed perimeter panel is permitted provided that the force at design wind speed is derived from manufacturers’ test data or other testing or methods acceptable to the commissioner.
3308.3.2 Site safety plans. | Details of the unenclosed perimeter protection shall also be shown on the site safety plan, where such plan is required by this chapter.
3308.3.3 Make and model. | The make and model of unenclosed perimeter protection, along with the connections and supports, shall be acceptable to the registered design professional responsible for the design of the unenclosed perimeter protection in accordance with Section 3308.3.1. The make and model, along with acceptance of the make and model by such registered design professional, shall be indicated as a note on the drawings, or in the form of a signed, sealed, and dated letter from such registered design professional that is kept with the drawings.
3308.3.4 Flame retardant. | Vertical and horizontal safety netting used for unenclosed perimeter protection shall be flame retardant in accordance with NFPA 701. Documentation of such shall be provided by the manufacturer and shall be noted on the drawings by the registered design professional responsible for the design of the safety netting systems in accordance with Section 3308.3.1, or shall be recorded by such registered design professional in the form of a signed, sealed, and dated letter from such registered design professional, with such letter kept with the drawings.
3308.3.5 Tensile strength. | The tensile strength for the structural net utilized in connection with a horizontal safety netting system shall be noted on the drawings by the registered design professional responsible for the design of the safety netting systems in accordance with Section 3308.3.1, or shall be recorded by such registered design professional in the form of a signed, sealed, and dated letter from such registered design professional, with such letter kept with the drawings. Where required by Section 3308.6.3, the strength shall be confirmed by testing; the results of the test shall be documented in the form of a signed, sealed, and dated letter from the registered design professional responsible for the design of the safety netting systems in accordance with Section 3308.3.1. Such letter shall be kept with the drawings.
3308.4 Responsibility and supervision. | The permit holder for the project, or where a permit is required by Section 3308.2, the holder of such permit, shall be responsible for complying with the requirements of Section 3308. A competent person designated by such responsible permit holder shall supervise the installation, reinstallation, adjustment, maintenance, repair, and temporary or permanent removal of all unenclosed perimeter protection, along with any support, connection, or component. The inspection of unenclosed perimeter protection shall be conducted in accordance with the requirements of Section 3308.9.3.
3308.5 Vertical safety netting systems. | Vertical safety netting shall be installed, maintained, and provided along all unenclosed perimeters. Exceptions: 1. Vertical safety netting is not required for: 1.1. The story at grade, provided it is less than 6 feet (1829 mm) above the level of the adjoining ground or structure; or 1.2. The working deck; or 1.3. Any story in concrete construction where the formwork has not been stripped, provided such floor is no more than four stories or 40 feet (12 192 mm) below the working deck, whichever is less; or 1.4. Any story in steel construction where the concrete slab has not been placed, provided that no work, other than steel erection or metal deck placement, is occurring on that story. 2. Vertical safety netting is not required at a location where a supported scaffold has been installed provided the scaffold is decked even with the building at such level where the unenclosed perimeter exists, with no gap between the scaffold deck and the building deck greater than 3 inches (76 mm), and also provided that the scaffold is provided with netting and guardrails in accordance with Section 3314.8. 3. Vertical safety netting is not required to protect an unenclosed window opening, provided such window opening is enclosed with a sill not less than 3 feet 6 inches (1067╪ mm) in height. 4. Vertical safety netting is not required for a building whose final height will be no more than 4 stories or 40 feet (12 192 mm) in height, whichever is less. 5. Vertical safety netting is not required for a minor alteration or ordinary repair. 6. Vertical safety netting is not required at a location where an equivalent alternative system acceptable to the commissioner, including but not limited to cocoon systems, climbing formwork, or enclosure panels, has been installed.
3308.5.1 Openings. | The largest opening area for debris netting when used vertically shall not be larger than 1 square inch (645 mm2), with no opening larger than 1 inch (25 mm) in the vertical or horizontal dimensions and 1 ½ inch (38 mm) in any other dimension.
3308.5.2 Height. | Where required, vertical safety netting shall extend to cover all openings in the unenclosed perimeter to a height of at least 60 inches (1524 mm) above the floor or, where installed at the roof level, the roof.
3308.5.3 Cables. | Vertical safety netting shall be secured to noncorrosive wire cable capable of withstanding a load of at least 200 pounds (90.7 kg) applied in any direction except upward. The cables shall be located at a height of 60 inches (1524 mm), 42 inches (1067 mm), 21 inches (533 mm), and 0 inches (0 mm) above the level of the floor or, where installed at the roof level, the roof. Where the vertical safety netting extends above 60 inches (1524 mm) in height, a cable shall also be placed at the top of the netting, with intermediate cables between the 60 inch (1524 mm) cable and the top cable as needed to satisfy the design requirements of Section 3308.3. Exceptions: In lieu of a cable: 1. At 60 inches (1524 mm) or above, a toprail made of wood, pipe, or structural angle meeting the requirements of Section 3308.7.3. 2. At 42 inches (1067 mm) and 21 inches (533 mm), midrails made of wood, pipe, or structural angle meeting the requirements of Section 3308.7.3. 3. At 0 inches (0 mm), a toeboard meeting the requirements of Sections 3308.7.2 and 3308.7.3, provided the net is secured to the toeboard.
3308.5.3.1 Zero cable. | Zero cables shall be secured to the deck and be maintained in contact with the deck such that debris cannot accumulate nor pass beneath the cable.
3308.5.4 Taut systems. | Where the vertical safety netting relies upon a taut system, the net and cables shall be maintained taut. A positive tensioning system such as a turnbuckle shall be provided to keep the cable taut.
3308.5.5 Friction connections. | Wood installations that utilize a friction connection are not permitted.
3308.5.6 Temporary removal. | The requirements of Section 3308.10 shall apply.
3308.5.6.1 Supplemental requirement for removal of toeboard or zero cable. | The toeboard or zero cable may be temporarily removed to facilitate the placement and curing of a concrete floor slab, provided no other work occurs on such floor, and provided an alternative measure is utilized to secure the bottom of the netting as close to the deck as practical.
3308.5.7 Permanent removal. | Vertical safety netting systems may be removed from floors where the façade has been installed and all such openings in the façade, including for windows, have been permanently enclosed to a height of at least 60 inches (1524 mm) above the floor. Vertical safety netting systems may be removed from the roof where the final parapet or guardrail has been installed.
3308.6 Horizontal safety netting systems. | Horizontal safety netting shall meet the requirements of Sections 3308.6.1 through 3308.6.4.
3308.6.1 Where required. | Horizontal safety netting shall be installed and maintained as follows.
3308.6.1.1 During construction. | When, during the course of new building construction, or during the vertical or horizontal enlargement of an existing building, the topmost walkable floor reaches a height of six stories or 75 feet (22 860 mm), whichever is less, above the level of the ground or an adjoining roof, horizontal safety netting shall be provided at a level not more than two stories or 30 feet (9144 mm), whichever is less, below: 1. In concrete structures: the stripping floor; or 2. In steel structures: at the topmost story where the concrete floor slab has been placed. Exception: When tarpaulins encase one or more floors immediately below the finished concrete floor in order to maintain temporary heat, the horizontal netting may be located no more than three floors below the finished concrete floor.
3308.6.1.2 During demolition. | When the demolition of the exterior walls or the roof of a building occurs at a height greater than six stories or 75 feet (22 860 mm), whichever is less, horizontal safety netting shall be provided at a level not more than two stories or 30 feet (9144 mm), whichever is less, below the story from which the exterior walls and roof are being removed. Exception: Demolition of exterior walls only for the purposes of the alteration, maintenance, or repair of a façade shall be in accordance with Section 3308.6.1.3.
3308.6.1.3 During façade alteration, maintenance, or repair. | Where unique hazards associated with the alteration, maintenance, or repair of a façade exist to the public and property, horizontal safety netting shall be provided as required by the commissioner.
3308.6.1.4 Alternative systems. | Alternative systems may be used in lieu of horizontal safety netting in accordance with the requirements of Sections 3308.6.1.4.1 or 3308.6.1.4.2.
3308.6.1.4.1 Supported scaffold alternative. | Horizontal safety netting is not required at a location where a supported scaffold has been installed provided the scaffold is decked even with the building at the level where the horizontal safety net would otherwise be required to be installed and all levels above where the horizontal nets would otherwise be required, with no gap between the scaffold deck and the building deck greater than 3 inches (76 mm), and also provided that the scaffold is provided with netting and guardrails in accordance with Section 3314.8.
3308.6.1.4.2 Other alternative systems. | Horizontal safety netting is not required at a location where an equivalent alternative system acceptable to the commissioner, including but not limited to cocoon systems or climbing formwork, covers the full height of the unenclosed perimeter at and above all levels where horizontal nets are required.
3308.6.1.5 Hoisting area. | Where approved by the commissioner, horizontal safety netting may be omitted in designated crane, derrick, or hoisting areas.
3308.6.1.6 Temporary removal. | The requirements of Section 3308.10 shall apply.
3308.6.1.7 Permanent removal. | Horizontal safety netting systems may be permanently removed as follows:
3308.6.2 Horizontal safety netting systems requirements. | Horizontal safety netting systems shall meet the requirements of Sections 5, 6.3, 6.4, 6.5, 6.6, 7, 8, 10.1, 10.4, 10.5, 10.6, 10.7, 11, and 13 of ANSI/ASSP A10.11, as modified as follows.
3308.6.2.1 Personnel net. | Throughout the standard, the term “personnel net” shall be amended to read “structural net.”
3308.6.2.2 Should and shall. | Throughout the standard, the term “should” shall be amended to read “shall.”
3308.6.2.3 Entanglement. | The phrase, “and to minimize entanglement of the persons head, arms, and legs when arresting the fall,” shall be deleted from Section 6.3 of ANSI/ASSP A10.11.
3308.6.2.4 Arresting a fall. | The phrase “when arresting a fall,” shall be deleted from Section 6.4 of ANSI/ASSP A10.11.
3308.6.2.5 Size of debris net openings. | Section 6.6 of ANSI/ASSP A10.11 shall be amended by adding a new sentence at the end of the section, as follows, “However, in no case shall the largest opening area for debris netting when used horizontally be larger than ½ square inch (323 mm2), with no opening larger than ½ inch (13 mm2) in the vertical or horizontal dimensions and ¾ inch (19 mm) in any other dimension.”
3308.6.2.6 Projection of nets. | The phrase, “as to capture falling personnel” in Section 10.6 of ANSI/ASSP A10.11 shall be amended to read “as to capture falling material.”
3308.6.2.7 Supports. | The phrase, “or personnel” in Section 10.7 of ANSI/ASSP A10.11 shall be amended to read, “or material.”
3308.6.2.8 Inspection. | Section 11.1 of ANSI/ASSP A10.11 shall be deleted in its entirety and replaced with the following, “Horizontal safety netting systems shall be inspected in accordance with Section 3308.9.3.”
3308.6.2.9 Dates tested. | The phrase “Dates inspected” in Item 5 of Section 11.4 of ANSI/ASSP A10.11 shall be amended to read “Dates tested”.
3308.6.2.10 Moving. | Section 11.4 of ANSI/ASSP A10.11 shall be amended to add a new Item 9, which shall read, “Dates nets were moved to a higher or lower level.”
3308.6.2.11 Cleaning. | Section 13.2 of ANSI/ASSP A10.11 shall be deleted and replaced with the following: “Horizontal safety netting shall not be used for storing material. Horizontal netting shall be cleaned, at least daily, to remove any items that fall into the nets.”
3308.6.3 Tensile strength test. | The tensile strength of netting mesh and/or twine of a structural net utilized in conjunction with a horizontal safety netting system shall be confirmed by testing in accordance with ASTM D 5034 or ASTM D 5035. The testing criteria shall be developed by the registered design professional who designed the safety netting system in accordance with Section 3308.3. Such testing shall occur prior to the installation of the net at the site for any net that has previously been used, and for any net that has been installed at the site for two years and every two years thereafter. Nets that do not meet the specified tensile strength as required by Section 3308.3.5 shall not be utilized or shall be replaced.
3308.6.4 Identification of nets. | Structural netting shall be identified in accordance with Section 7 of ANSI/ASSP A10.11. Debris netting shall be identified by a letter or other documentation from the manufacturer stating the description and model. The identification for structural netting and debris netting shall be kept at the site until the netting is removed.
3308.7 Guardrail system. | A guardrail system shall be installed, maintained, and provided along all unenclosed perimeters. Exceptions: A guardrail system is not required at: 1. The story at grade, provided that it is less than 6 feet (1829 mm) above the level of the adjoining ground or structure. 2. Locations where vertical safety netting is installed in accordance with Section 3308.5. 3. Locations where a supported scaffold has been installed provided the scaffold is decked even with the building at such level where the unenclosed perimeter exists, with no gap between the scaffold deck and the building deck greater than 3 inches (76 mm), and also provided that the scaffold is provided with netting and guardrails in accordance with Section 3314.8. 4. Locations where an equivalent alternative system acceptable to the commissioner, including but not limited to cocoon systems, climbing formwork, or enclosure panels, has been installed.
3308.7.1 Components. | Guardrail systems shall include a toprail, midrail, toeboard, and posts.
3308.7.2 Height of railings and toeboard. | Toprails, midrails, and toeboards shall be located as follows: 1. The top of the toprail shall be located at a height of 39 to 45 inches (991 and 1143 mm) above the floor. 2. The midrail shall be located at a height approximately midway between the toprail and the floor, or where more than one midrail is utilized, each shall be located equidistant from each other, the floor, and the toprail. 3. The toeboard shall be at least 3 ½ inches (89 mm) high and shall be installed so that there is not more than a ¼ inch (6 mm) gap between the floor and the bottom of the toeboard. Exception: When conditions warrant, the height of the toprail may exceed the 45-inch (1143 mm) height provided additional midrails are installed so that there is no vertical gap larger than 24 inches (610 mm) between any toeboard, midrail, or toprail.
3308.7.3 Dimensions and materials. | Toprails, midrails, toeboards, and posts shall have the following dimensions and be constructed out of the following materials: 1. Toprails shall, at a minimum, consist of: 1.1. 2 inch by 4 inch (51 mm by 102 mm) 1500 foot pounds per square inch (1.05 kgf/mm2╪) fiber (stress grade) construction grade lumber; 1.2. 1 ½ inch (38 mm) nominal diameter (Schedule 40) pipe; 1.3. 2 inch by 2 inch by ⅜th inch (51 mm by 51 mm by 10 mm) structural angle; or 1.4. ¼ inch (6 mm) diameter noncorrosive wire cable made of mild plow steel. 2. Midrails shall, at a minimum, consist of: 2.1. 1 inch by 6 inch (25 mm by 152 mm) 1500 foot pounds per square inch (1.05 kgf/mm2╪) fiber (stress grade) construction grade lumber; 2.2. 1 ½ inch (38 mm) nominal diameter (Schedule 40) pipe; 2.3. 2 inch by 2 inch by ⅜th inch (51 mm by 51 mm by 10 mm) structural angle; or 2.4. ¼ inch (6 mm) diameter noncorrosive wire cable made of mild plow steel. 3. Toeboards shall, at a minimum, consist of: 3.1. 1 inch by 4 inch (25 mm by 102╪ mm) lumber; or 3.2. Metal plank at least 3½ inches (89 mm) high. 4. Toprails, midrails, and toeboards shall be securely fastened to upright posts spaced not more than 8 feet (2438 mm) apart. Such posts shall, at a minimum, consist of: 4.1. 2 inch by 4 inch (51 mm by 102 mm) 1500 foot pounds per square inch (1.05 kgf/mm2╪) fiber (stress grade) construction grade lumber; 4.2. 1½ inch (38mm) nominal diameter (Schedule 40) pipe; 4.3. 2 inch by 2 inch by ⅜ inch (51 mm by 51 mm by 10 mm) structural angle; or 4.4. A building column. Exceptions: 1. Guardrail systems designed by a registered design professional capable of withstanding, without failure: 1.1. A force of at least 200 pounds (890 N) applied within 2 inches (51 mm) of the top edge, in any outward or downward direction, at any point along the top edge. Where the force is applied in a downward direction, the top edge shall not deflect more than 6 inches (152 mm) and in no case to a height less than 39 inches (991 mm) above the floor; and 1.2. A load of at least 50 pounds (222 N) applied in any downward or horizontal direction at any point along the toeboard. 2. Posts supporting wire cable toprails and midrails, as well as the toeboards utilized in connection with such wire cable toprails and midrails, may be spaced more than 8 feet (2438 mm) apart provided that the posts are spaced such that where a force of 200 pounds (890 N) is applied in a downward direction along the top edge, the top edge shall not deflect more than 6 inches (152 mm) and in no case to a height less than 39 inches (991 mm) above the floor.
3308.7.4 Horizontal gap. | The guardrail system shall be installed so that there exists no horizontal gap larger than 1 inch (25 mm) as measured along the perimeter of the building from the edge of the guardrail system to any building column or façade.
3308.7.5 Tensioning system. | When made of wire cable, toprails and midrails shall be provided with a positive tensioning system, such as a turnbuckle, to keep the cable taut.
3308.7.6 Dislodgement. | Guardrail systems shall be secured to prevent dislodgement by impact or wind.
3308.7.7 Temporary removal. | The requirements of Section 3308.10 shall apply.
3308.7.8 Permanent removal. | Guardrail systems installed to protect unenclosed perimeters may be removed where vertical safety netting systems meeting the requirements of Section 3308.5 have been installed.
3308.8 Modifications. | The commissioner may, based upon a written request from a registered design professional, modify the requirements for unenclosed perimeter protection in accordance with Section 28-103.3 of the Administrative Code.
3308.9 Unenclosed perimeter protection inspection, use, adjustment, maintenance, and repair. | Unenclosed perimeter protection shall be inspected, used, adjusted, maintained, repaired, and replaced in accordance with the design drawings, manufacturer specifications, and the requirements of this code. Where there is a discrepancy, the stricter standard shall apply.
3308.9.1 Safe condition. | Unenclosed perimeter protection shall be maintained in a safe condition and used in a manner that eliminates hazards to the public and property. Any hazardous conditions or defects discovered with such shall immediately be brought to the attention of the responsible permit holder under Section 3308.4.
3308.9.2 Precautions. | Precautions shall be taken to prevent unenclosed perimeter protection from being damaged by sunlight, abrasion, sand, rust, welding, cutting operations, chemicals, and airborne contaminants, where such systems are susceptible to damage by such.
3308.9.3 Inspections. | Unenclosed perimeter protection shall be inspected for compliance with this code, manufacturer specifications, and required drawings at least daily, as well as before and after each removal and restoration in accordance with Section 3308.10.3, and after each impact loading event, installation, reinstallation, adjustment, maintenance, or repair of the unenclosed perimeter protection or any part or component of such. Where the job requires a site safety manager or coordinator in accordance with Section 3310, the inspection shall be performed by the site safety manager or coordinator, and a written record of such inspection maintained as part of the site safety log. Where the job does not require a site safety manager or coordinator, the inspection shall be performed by a competent person designated by the permit holder in accordance with Section 3308.4, with a record of such inspection prepared, initialed, and dated by such competent person.
3308.9.4 Removing from service. | Unenclosed perimeter protection showing signs of mildew, corrosion, wear, tears, breaks, frays, damage, or deterioration that may substantially affect the strength of such shall be immediately removed from service.
3308.9.5 Repair. | Repairs to unenclosed perimeter protection shall be in accordance with the specifications of the manufacturer of such and shall provide the original manufacturer factor of safety, or where manufacturer specifications do not exist, shall be repaired in accordance with specifications developed by the registered design professional responsible for the design of the unenclosed perimeter protection in accordance with Section 3308.3.1. Exception: Structural nets and debris nets shall not be repaired.
3308.9.6 Vacuum cleaning. | Areas in the vicinity of operations related to the installation, reinstallation, adjustment, maintenance, repair, temporary removal, or permanent removal of unenclosed perimeter protection systems that produce or typically produce small debris shall be vacuumed as the operation progresses. Examples of operations that produce small debris include, but are not limited to, the installation or removal of fasteners for a vertical netting system, chipping to expose curtain wall clips, preparation of the slab to install or receive exterior walls, and chopping or core drilling at perimeter for mechanical risers. Vacuum equipment shall be tethered or otherwise secured to prevent the equipment from falling.
3308.10 Temporary removal of unenclosed perimeter protection. | Unenclosed perimeter protection, or portions thereof, may be temporarily removed in the immediate area where active loading or unloading operations are occurring, or to the extent necessary to facilitate active work at the perimeter, including but not limited to inspections or the relocation of unenclosed perimeter protection to a higher level, provided there is compliance with the following items:
3308.10.1 Restoring unenclosed perimeter protection. | Unenclosed perimeter protection shall be reinstalled immediately following the end of the active loading or unloading operation or active work at the perimeter, or at the end of the shift, whichever occurs sooner. Immediately prior to restoring a guardrail system, vertical netting system, or equivalent alternative system, areas in the vicinity of the edge shall be vacuumed, and other areas to a distance of at least 10 feet (3048 mm), in all directions from the area where the unenclosed perimeter protection is removed, shall be broom-swept. Vacuum equipment shall be tethered or otherwise secured to prevent the equipment from falling. Exceptions: 1. Where material overhangs overnight in accordance with Section 3303.4.5.2, guardrails shall be reinstalled the next work day immediately following the relocation of the material. 2. Where a toeboard or zero cable has been temporarily removed to facilitate the placement and curing of a concrete floor slab, the toeboard or zero cable shall be reinstalled as soon as practical.
3308.10.2 Competent person. | The competent person designated in accordance with Section 3308.4 shall supervise the temporary removal and reinstallation of unenclosed perimeter protection, including all ancillary activities, such as preparing the area for the removal of the unenclosed perimeter protection, and shall ensure compliance with the requirements of Section 3308.10.
3308.10.3 Inspection. | An inspection shall be performed immediately prior to the removal of unenclosed perimeter protection to verify compliance with the provisions of Section 3308.10. An inspection shall be performed immediately prior to restoring a guardrail system, vertical netting system, or equivalent alternative system to verify compliance with the cleaning provisions of Section 3308.10.1. An inspection shall be performed immediately after unenclosed perimeter protection is restored to verify compliance with this code, manufacturer specifications, and required drawings. These inspections shall be performed by the site safety manager, site safety coordinator, or competent person in accordance with Section 3308.9.3, and recorded in accordance with Section 3308.9.3.
3309.1 Protection required. | Adjoining public and private property, including persons thereon, shall be protected from damage and injury during construction or demolition work. Protection must be provided for footings, foundations, party walls, chimneys, skylights and roofs. Provisions shall also be made to control water run-off and erosion during construction or demolition activities. Where the New York City Department of Environmental Protection has issued a stormwater construction permit for a covered development project, such run-off and erosion controls shall be installed and maintained in accordance with the rules of the Department of Environmental Protection and this code.
3309.1.1 Notification. | Where a construction or demolition project will require access to adjoining property in accordance with this section, written notification shall be provided to the adjoining property owner at least 60 calendar days prior to the commencement of work. Such notification shall describe the nature of work, estimated schedule and duration, details of inspections or monitoring to be performed on the adjoining property, protection to be installed on the adjoining property, and contact information for the project. Where no response is received, a second written notification shall be made no more than 45 calendar days, and not less than 30 calendar days, prior to the commencement of work.
3309.2 License to enter adjoining property. | The responsibility of affording any license to enter adjoining property shall rest upon the owner of the adjoining property involved; and in case any tenant of such owner fails or refuses to permit the owner to afford such license, such failure or refusal shall be a cause for the owner to dispossess such tenant through appropriate legal proceedings for recovering possession of real property. Nothing in this chapter shall be construed to prohibit the owner of the property undertaking construction or demolition work from petitioning for a special proceeding pursuant to Section 881 of the Real Property Actions and Proceedings Law.
3309.3 Physical examination. | When permission to enter upon adjoining property has been obtained, a physical examination of such property shall be conducted by the person causing the construction or demolition operations prior to the commence­ment of the operations and at reasonable periods during the progress of the work. Observed conditions shall be recorded by the person causing the construction or demolition operations, and such records shall be made available to the department upon request.
3309.4 Soil or foundation work affecting adjoining property. | Whenever soil or foundation work occurs, regardless of the depth of such, the person who causes such to be made shall, at all times during the course of such work and at his or her own expense, preserve and protect from damage any adjoining structures, including but not limited to footings and foundations, provided such person is afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect the adjoining buildings and property, and to perform such work thereon as may be necessary for such purpose. If the person who causes the soil or foundation work is not afforded a license, such duty to preserve and protect the adjacent property shall devolve to the owner of such adjoining property, who shall be afforded a similar license with respect to the property where the soil or foundation work is to be made.
3309.4.1 Additional safeguards during excavation. | The following additional requirements shall apply during excavation:
3309.4.2 Support of party walls. | Where a party wall will be affected by excavation, regardless of the depth, the person who causes the excavation to be made shall preserve such party wall at his or her own expense so that it shall be, and shall remain, in a safe condition. Where an adjoining party wall is intended to be used by the person causing an excavation to be made, and such party wall is in good condition and sufficient for the uses of the existing and proposed buildings, it shall be the duty of such person to protect such party wall and support it by proper foundations, so that it shall be and remain practically as safe as it was before the excavation was commenced.
3309.4.3 Preconstruction survey. | No excavation work to a depth of 5 feet to 10 feet (1524 mm to 3048 mm) within 10 feet (3048 mm) of an adjacent building, or an excavation over 10 feet (3048 mm) anywhere on the site shall commence until the person causing an excavation to be made has documented the existing conditions of all adjacent buildings in a preconstruction survey. In addition to the preconstruction survey, a geotechnical report in accordance with Section 1803.6, and an evaluation analysis in accordance with Section 1817, shall be prepared when required by Chapter 18.
3309.4.4 Monitoring. | During the course of excavation work the following shall be monitored in accordance with Section 3309.16: 1. Buildings that are within a distance from the edge of the excavation that is equal to or less than the maximum depth of the excavation. 2. Historic structures that are contiguous to or within a lateral distance of 90 feet (27 432 mm) from the edge of the lot where an excavation is occurring. Exception: Monitoring is not required for excavations to a depth of five feet (1523 mm) or less, provided: 1. The excavation occurs more than 5 feet (1524 mm) from all footings and foundations; or 2. Where the excavation occurs within five feet (1524 mm) or less from a footing or foundation, such excavation does not occur below the level of the footing or foundation.
3309.4.5 Potential hazard. | When, in the opinion of the commissioner, a potential hazard exists as a result of soil or foundation work, elevations of the adjacent buildings shall be recorded or other monitoring procedures shall be implemented by a registered design professional at intervals of 24 hours or less as determined by the commissioner to ascertain if movement has occurred.
3309.5 Underpinning or alternate methods of support of buildings and adjacent property. | Whenever underpinning or an alternate method of support of buildings and adjacent property is required to preserve and protect an adjacent property from construction, demolition, or excavation work, the person who causes such work shall, at his or her own expense, underpin or otherwise support the adjacent building and property provided such person is afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect the adjoining buildings and property, and to perform such work thereon as may be necessary for such purpose. If the person who causes the construction, demolition, or excavation work is not afforded a license, such duty to preserve and protect the adjacent property shall devolve to the owner of the adjoining property, who shall be afforded a similar license with respect to the property where the construction, demolition, or excavation is to be performed.
3309.6 Subsurface operations affecting adjacent properties. | Whenever subsurface operations, other than excavation or fill, are conducted that may impose loads or movements on adjoining property, including but not limited to the driving of piles, compaction of soils, or soil solidification, the effects of such operations on adjoining property and structures shall be monitored in accordance with Section 3309.16. Exception: Monitoring during underpinning or alternate methods of support of buildings and adjacent property shall be in accordance with Section 1817.
3309.6.1 Change in ground water level. | Where placement of a foundation will cause changes in the ground water level under adjacent buildings, the effects of such changes on the stability and settlement of the adjacent foundations shall be investigated and provision shall be made to prevent damage to such buildings.
3309.6.2 Potential hazard. | When, in the opinion of the commissioner, a potential hazard exists as a result of subsurface operations, elevations of the adjacent buildings shall be recorded by a registered design professional at intervals of 24 hours or less as determined by the commissioner to ascertain if movement has occurred.
3309.7 Retaining structures. | The requirements of Article 305 of Chapter 3 of Title 28 of the Administrative Code shall apply to the regulation of retaining structures.
3309.8 Adjoining walls. | When any construction or demolition operation exposes or breaches an adjoining wall, including load bearing and nonload-bearing walls as well as party walls and non party walls, the person causing the construction or demolition operation shall, at his or her own expense, perform the following:
3309.9 Weatherproof integrity of adjoining buildings. | Where the waterproof integrity of an adjoining wall or building has been impaired due to construction or demolition opera­tions, the person causing the construction or demolition opera­tions shall, at his or her own expense, provide all necessary measures to permanently waterproof the adjoining wall or building in order to establish or restore the weatherproof integrity of such adjoining wall or building. This shall include, but is not limited to:
3309.10 Protection of roofs. | Whenever any building is to be constructed or demolished above the roof of an adjoining building, it shall be the duty of the person causing such work to protect from damage at all times during the course of such work and at his or her own expense the roof, skylights, other roof outlets, and equipment located on the roof of the adjoining building, and to use every reasonable means to avoid interference with the use of the adjoining building during the course of such work, provided such person causing such work is afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect the adjoining building and per­form such work thereon as may be necessary for such purpose; otherwise, the duty of protecting the roof, skylights, other roof outlets, and equipment on the roof of the adjoining building shall devolve upon the owner of such adjoining building. Adjoining roof protection shall be secured to prevent dislodgement by wind. Where construction or demolition work occurs at a height of at least 48 inches (1219 mm) above the level of the adjoining roof, adjoining roof protection shall consist of 2 inches (51 mm) of flame-retardant foam under 2 inches (51 mm) of flame-retardant wood plank laid tight and covered by flame-retardant plywood, or shall consist of equivalent protection acceptable to the commissioner, and shall cover all areas of the adjoining roof that are within a horizontal distance from the building being constructed or demolished equal to the height of the highest working level of the building being constructed or demolished, to a maximum of 20 feet (6096 mm), or to a greater maximum when ordered by the commissioner due to a unique hazard at the site. Exceptions: 1. Adjoining roof protection is not required along an exposure where a site specific engineered enclosure system that is acceptable to the commissioner and meets the requirements of Section 3309.17 has been installed to cover the entire exposure where work is occurring. 2. Where vents, equipment, or similar obstructions are present on the roof, the roof protection shall be elevated to avoid interreference, or an equivalent elevated system, designed by a registered design professional, shall be installed. 3. Occupiable spaces on an adjoining roof, such as a roof terrace, observation deck, rooftop bar, or residential balcony, that will not be closed during the work, shall instead be protected in accordance with Section 3309.13.
3309.11 Protection of trees. | No trees outside the property line within the public right-of-way shall be disturbed or removed without the permission of the commissioner of the department of parks and recreation. Protection meeting the requirements of the department of parks and recreation shall be provided for all such trees, and written notification shall also be made to the department of parks and recreation at least 48 hours prior to commencement of such work.
3309.11.1 Deleterious, caustic, or acid materials. | No deleterious, caustic, or acid materials shall be dumped or mixed within 10 feet (3048 mm) of any tree within the public right-of-way, nor shall salt for the removal of ice or snow be applied when runoff will drain to a tree within the public right-of-way. Exceptions: 1. Mixing, delivery, or placement of concrete from a concrete mixer or concrete truck. 2. Application of de-icing materials as necessary to prevent slipping and tripping hazards in areas accessible to the public during periods where freezing conditions are to be encountered.
3309.12 Protection of chimneys. | Any person having the duty to alter or maintain chimneys of any adjoining building under and pursuant to the provisions of this code, the New York City Mechanical Code, the New York City Fuel Gas Code, or other applicable laws and rules shall be afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect such adjoining building and perform such work thereon as may be necessary for such purpose; otherwise, such duty shall devolve upon the owner of such adjoining building.
3309.13 Protection of adjoining equipment and spaces. | Whenever a building is constructed or demolished, it shall be the duty of the person causing such work to protect from damage, at all times during the course of such work and at his or her own expense, all mechanical, electrical, and similar equipment on the adjoining property, and to protect all publicly accessible spaces on the adjoining property, and also to use every reasonable means to avoid interference with the use of such equipment and spaces during the course of such construction or demolition work, provided such person causing such work is afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect the adjoining property and perform such work thereon as may be necessary for such purpose; otherwise, the duty of protecting such adjoining equipment and spaces shall devolve upon the owner of such adjoining property. Adjoining equipment and space protection shall be secured to prevent dislodgement by wind. Where the construction or demolition work requires a site safety plan in accordance with Section 3301.13 or 3310 and access to the equipment or space is not precluded, adjoining equipment and space protection shall be designed to provide a level of overhead protection equivalent to that provided by a sidewalk shed in accordance with Section 3307, and shall cover all adjoining equipment or spaces that are within a horizontal distance from the building being constructed or demolished equal to the height of the highest working level of the building being constructed or demolished, to a maximum of 20 feet (6096 mm), or to a greater maximum when ordered by the commissioner due to a unique hazard at the site. Exceptions: 1. Equipment on an adjoining roof shall be protected in accordance with Section 3309.10. 2. Adjoining equipment and space protection is not required along an exposure where a site specific engineered enclosure system, acceptable to the commissioner, and meeting the requirements of Section 3309.17, has been installed to cover the entire exposure where work is occurring.
3309.14 Protection of windows. | Whenever exterior construction or demolition work occurs, and such work results in an unenclosed perimeter, it shall be the duty of the person causing such work to protect from damage, at all times during the course of such work and at his or her own expense, all windows on adjoining private property that face such work and are 20 feet (508 mm) or less from an unenclosed perimeter, provided such person causing such work is afforded a license in accordance with the requirements of Section 3309.2 to enter and inspect the adjoining property and perform such work thereon as may be necessary for such purpose; otherwise, the duty of protecting the adjoining windows shall devolve upon the owner of such adjoining building. Where the window provides required means of natural lighting, natural ventilation, or egress, such protection shall not be allowed to interfere with such required means. Exceptions: Window protection is not required for: 1. Minor alterations and ordinary repairs. 2. Work performed on a one-, two- or three-family detached house or accessory use to such. 3. Locations where the unenclosed perimeter of the building under construction or demolition is protected along the entire exposure by vertical netting that meets the requirements of Section 3308.5, supported scaffolding provided with guardrails and netting in accordance with Section 3314.8, or an equivalent alternative system acceptable to the commissioner.
3309.15 Modifications and alternate methods. | The commissioner may, in accordance with Section 28-103.3 of the Administrative Code, and based upon a written request from a registered design professional, modify the requirements for adjoining property protection required by this section, including but not limited to authorizing the installation or use of alternative methods of surveying, monitoring, inspection, or protection.
3309.16 Monitoring plan. | Where monitoring is required by Section 3309, such monitoring shall be in accordance with a monitoring plan developed by a registered design professional and acceptable to the commissioner. The monitoring plan shall be specific to the structures to be monitored and operations to be undertaken, and shall specify the scope and frequency of monitoring, acceptable tolerances, and reporting criteria for when tolerances are exceeded. Monitoring plans shall also comply with the applicable requirements of Chapter 18 and Sections 3303, 3304, and 3306.
3309.17 Site specific engineered enclosure system. | Site specific engineered enclosure systems authorized by this section shall meet the following requirements:
3310.1 Scope. | This section shall apply to: 1. The construction of a new major building; 2. The vertical or horizontal enlargement of a major building; 3. The full or partial demolition of a major building; 4. The alteration, maintenance, or repair of a façade of a major building, provided the building is more than 14 stories or 200 feet (60 960 mm) in height, whichever is less, and also provided the façade work requires a sidewalk shed to be installed; and 5. Any construction or demolition work, including the alteration, maintenance, or repair of a façade, in a building so designated by the commissioner. Exception: The requirements of this section shall not apply to partial demolition operations limited to the interior components of a major building, provided no mechanical demolition equipment, other than handheld devices, are used.
3310.1.1 Applicability of other laws. | Nothing contained herein shall diminish or supersede any other applicable city, state, or federal regulation. Nothing in this section shall relieve persons engaged in construction or demolition work of their obligations under this chapter, including but not limited to Sections 3301.1 and 3301.2, or from complying with other applicable provisions of law.
3310.2 Major buildings. | See the definition of “Major building” in Chapter 2.
3310.3 Site safety plan. | No permit shall be issued for the type of work listed in Section 3310.1 until a site safety plan that meets the requirements of Article 110 of Chapter 1 of Title 28 of the Administrative Code has been approved by the department.
3310.4 Site safety monitoring program. | For a project that requires a site safety plan, the general contractor shall enact and maintain a site safety monitoring program to implement such site safety plan. The site safety monitoring program shall, at a minimum, comply with Sections 3310.5 through 3310.10. Exception: Subject to the approval of the commissioner, a site safety monitoring program may be waived, reduced, or modified in accordance with Section 3310.11.
3310.5 Site safety manager or coordinator to be designated. | A primary site safety manager shall be designated by the owner, agent, construction manager, or general contractor. Where more than one site safety manager is to serve at the site, all such entities shall agree to designate one such site safety manager as the primary site safety manager, or where there is only one site safety manager, such manager shall automatically be designated as the primary site safety manager. The primary site safety manager shall carry out all duties and responsibilities assigned to the site safety manager or coordinator by this chapter and rules promulgated by the commissioner, and shall be certified by the department in accordance with Article 402 of Chapter 4 of Title 28 of the Administrative Code. Exceptions: 1. A site safety coordinator, certified by the department in accordance with the requirements of Article 403 of Chapter 4 of Title 28 of the Administrative Code, may be designated in lieu of a site safety manager for the construction, vertical or horizontal enlargement, or full or partial demolition of a major building, provided such building: 1.1. Is less than 15 stories or 200 feet (60 960 mm) in height, whichever is less; and 1.2. Has a building footprint of 100,000 square feet (30 480 m2) or less. 2. Façade or roof projects that comply with Section 3310.12.
3310.5.1 Notification to the department of the primary manager or coordinator. | The department shall be notified of the primary site safety manager or coordinator prior to the commencement of work. In the event that an alternate site safety manager or coordinator will be acting in place of the primary site safety manager or coordinator for a period longer than two consecutive weeks, the department must be so notified. Any permanent change of the primary site safety manager or coordi­nator requires immediate notification to the department.
3310.5.2 Presence at the site. | For the construction or alteration of a building, the site safety manager or coordinator shall be present at the site during all times while active work is occurring and through all phases of work, beginning with excavation and continuing until the building is enclosed and the sidewalk shed removed. Exceptions: 1. The site safety manager or coordinator is not required to be present at the site during the following activities, provided no other work is in progress; 1.1 Surveying that does not involve the disturbance of material, structure, or earth; 1.2 Use of a hoist exterior to the building to transport personnel only; 1.3 Use of a hoist that is fully enclosed within the perimeter of the building to transport personnel or material; 1.4 Work limited to finish troweling of concrete floors; 1.5 Work limited to providing the site with temporary heat, light, or water; 1.6 Truck deliveries to the site, provided the delivery occurs within the site while the gate is closed and flagpersons are provided to direct traffic while the truck is entering and exiting the site. 1.7 Painting; or 1.8 Landscaping that does not involve the disturbance of material, structure, or earth. 2. Subject to the approval of the commissioner, the requirement for a site safety manager, or where a site safety coordinator is authorized by this code, a site safety coordinator, may be waived entirely, or reduced to a part time basis with such part time basis determined by the commissioner, in accordance with Section 3310.11.
3310.5.3 Alternate site safety manager or coordinator. | Where the primary site safety manager or coordinator is unable to be at the site, an alternate site safety manager or coordinator shall act in place of the primary site safety manager or coordinator and carry out all duties and responsibilities assigned to the site safety manager or coordinator by this chapter and rules promulgated by the commissioner. Such shall be recorded in the site safety log as required by Section 3310.8.4.2, and where required by Section 3310.5.1 notification shall be provided to the department.
3310.5.4 Limitation on primary site safety manager or coordinator serving at another site. | No site safety manager or coordinator designated as the primary site safety manager or coordinator at a site shall serve as a site safety manager or coordinator at any other site. Exceptions: 1. A site safety manager or coordinator designated as the primary site safety manager or coordinator at a site may serve as a non-primary site safety manager or coordinator at another site, provided there is no work requiring the presence of such individual in accordance with Section 3310.5.2 occurring at the site for which the individual has been designated as the primary site safety manager or coordinator. 2. A site safety manager may be designated as the primary site safety manager for two or more sites, provided all sites meet the criteria set forth in Section 3310.12.
3310.6 Reserved.
3310.7 Contractor shall inform personnel. | The requirements of Section 3301.14 shall apply.
3310.8 Site safety manager’s and coordinator’s duties. | The site safety manager or coordinator shall monitor compliance with the site safety plan, the tenant or occupant protection plan, and the requirements of this chapter and any rules promogulated thereunder by performing the duties required by Sections 3310.8.1 through 3310.8.5 and by performing all other safety duties assigned by the owner or general contractor to meet legal requirements.
3310.8.1 Meetings. | The meeting requirements of Section 3301.13.18 shall apply.
3310.8.2 Notification of violations. | In the event the site safety manager or coordinator discovers a violation of this chapter or any rules promogulated thereunder, the site safety plan, or the tenant or occupant protection plan, he or she shall immediately notify the person or persons responsible for creating the violation, whether these persons are employed by the general contractor or by subcontractors. If the site safety manager or coordinator is unable to obtain the cooperation of these persons in correcting the violation, he or she shall immediately inform the direct supervisor of the person or company responsible for creating the violation and request that the supervisor order the necessary corrective action. If such supervisor is not present at the site or is otherwise unavailable, or if informing the direct supervisor does not result in the violation being corrected, the site safety manager or coordinator shall notify the construction superintendent, or if the job does not require a construction superintendent, any other supervisory personnel of the permit holder or any other responsible manager or officer of the permit holder. All such violations and corrective work shall be recorded in the daily log.
3310.8.2.1 Notification of conditions to the department. | The site safety manager or coordina­tor shall immediately notify the department directly if he or she discovers any of the following conditions in the routine performance of the job:
3310.8.2.1.1 Responsibility. | Upon proper notification to the department of the existence of any of the above-noted circumstances, any responsibility the site safety manager or coordinator has under this code arising out of, relating to, or as a result of the existence of that circumstance, shall cease.
3310.8.2.1.2 Notification of construction superintendent. | For a job that requires a construction superintendent, upon notification of the above conditions to the department, the site safety manager or coordinator shall notify the construction superintendent of the condition and that notification has been made to the department.
3310.8.3 Inspections. | Site safety inspections shall be performed and documented as required by Sections 3310.8.3.1 through 3310.8.3.4.
3310.8.3.1 Spot checks. | The safety manager or coordinator shall personally perform spot checks of the site on a regular basis throughout the day for compliance with the site safety plan, the tenant or occupant protection plan, the requirements of this chapter, and any rules promulgated thereunder.
3310.8.3.2 Enumerated inspections. | The following inspections shall be performed by the site safety manager or coordinator, or by one or more individuals designated by the site safety manager or coordinator and certified as a site safety manager or coordinator in accordance with Chapter 4 of Title 28 of the Administrative Code:
3310.8.3.3 Delegation. | Nothing in this code shall be read to prohibit the site safety manager from delegating enumerated inspections to an individual certified as a site safety coordinator at a site where a primary site safety manager is required; however, the site safety manager or coordinator may not delegate their general responsibility to perform spot checks of the site throughout the day. Delegation does not relieve the site safety manager or coordinator from the responsibility to ensure such inspections are adequately performed.
3310.8.3.4 Record of inspections. | A record of all such inspections shall be maintained by such site safety manager or coordinator in the site safety log in accordance with Section 3310.8.4.
3310.8.4 Site safety log. | A site safety log shall be maintained and kept at the site. The log, or where there is more than one log, the logs in total, shall, at a minimum, contain the following information:
3310.8.4.1 Recording inspections in the site safety log. | Inspections shall be recorded by the end of the day by the site safety manager or coordinator who performed the inspection. The site safety log, or where there is more than one log, each individual log, shall be completed and signed by the site safety manager or coordinator, and if the inspection is performed by another individual, by the site safety manager or coordinator who performed the inspection. Exception: Where a part time site safety manager or coordinator is approved by the commissioner in accordance with Section 3310.11, the site safety manager or coordinator shall sign the log when he or she arrives at the site and leaves the site, and all entries in the site safety log shall be completed and signed prior to leaving the site.
3310.8.4.2 Recording change in site safety manager or coordinator. | If at any point during the day an alternate site safety manager or coordinator acts as the primary site safety manager, this shall be noted in the log, and the alternate site safety manager shall log in. If a site safety manager or coordinator is relieved of his or her responsibilities at the site, or a site safety manager or coordinator leaves the site for any reason, this shall be indicated in the site safety log, and another site safety manager or coordinator shall assume the duties of such relieved or absent site safety manager or coordinator by signing in.
3310.8.4.3 Review and signature by the construction superintendent. | Prior to the start of the subsequent work day, the previous day’s entries in the site safety log shall be reviewed by the construction superintendent, and an entry shall be made in the site safety log, signed and dated by the construction superintendent, that he or she has reviewed all of the previous day’s entries.
3310.8.5 Permit log. | Any equipment brought onto the job that requires permits, as well as a description of the equipment, where it is to be located, permit number, issue and expiration date of the permit, and certificate of inspection, if required, shall be entered on a separate permit log that shall be maintained at the site by the site safety manager or coordinator and kept at the site.
3310.8.6 Reserved.
3310.9 Additional site safety personnel. | The following additional personnel shall be employed to oversee concrete operations at a major building and such other classes of buildings or operations as the commissioner may designate by rule. These personnel shall coordinate directly with the site safety manager or coordinator. In all instances, the site safety manager or coordinator retains responsibility for ensuring compliance with the provisions of Section 3310 of this code and all applicable rules, and for signing the site safety log. The name and contact information of the additional site safety personnel shall be recorded in the site safety log.
3310.9.1 Concrete safety manager. | A concrete safety manager shall be designated by the concrete contractor at those sites where the concrete portion of the project involves the pouring of a minimum of 2,000 cubic yards of concrete or such lesser amount as the commissioner may determine by rule. Concrete safety managers shall have five years of experience in concrete operations and shall have satisfactorily completed, within the five calendar years prior to registration, a thirty hour course approved by the commissioner that is sufficient to qualify the individual as a competent person under OSHA standards to oversee concrete operations, including such topics as formwork design, construction and stripping operations, rebar handling, and rigging. Concrete safety managers shall register with the department in the same manner as construction superintendents, and shall provide evidence of meeting the eligibility requirements set forth herein. No person shall perform the duties of a concrete safety manager without being registered as such with the department. The commissioner shall promulgate rules establishing the duration that such registration shall be valid and the requirements for renewal of the registration. The concrete safety manager shall be present during all concrete operations. For purposes of this section, “concrete operations” shall mean the pouring of concrete and the construction and stripping of concrete forms and related activities as specified by the commissioner.
3310.10 Orientation and training. | All workers employed at a major building site shall receive orientation and training as required by this section and Section 3321.
3310.10.1 Orientation. | The requirements of Section 3301.11 shall apply.
3310.11 Modifications to the site safety monitoring program. | The commissioner may, based upon a written request from a registered design professional, waive, reduce, or modify the requirements for the site safety monitoring program for a job of a limited scope or duration in accordance with Section 28-103.3 of the Administrative Code.
3310.12 Façade projects. | Where authorized in accordance with rules promulgated by the commissioner for a project whose scope is limited to the alteration, maintenance, or repair of a façade or roof, the inspection, documentation, reporting, and other activities required by Sections 3310.5 through 3310.9 may instead be assigned to a qualified person. The qualified person shall also perform all other duties assigned by rules promulgated by the commissioner. The qualified person shall work under the direct and continuing supervision of a site safety manager, or a licensed master or special rigger, and shall meet all training and experience prerequisites established by rules promulgated by the commissioner.
3311.1 Scope. | Explosive powered tools, including but not limited to powder-actuated tools and projectile tools, used in connection with the construction or demolition of a building or structure shall be in accordance with the requirements of this section.
3311.2 Projectile tools. | Projectile tools shall comply with the requirements of Sections 3311.2.1 through 3311.2.3.
3311.2.1 Basic requirements. | Design and construction of the tool must be such as to safely retain all internal pressures that may occur during its operation. The discharge mechanism shall be such that the projectile cannot be discharged by dropping the tool. The discharge mechanism shall be such that the discharge of each projectile shall be dependent on a separate and distinct act by the operator, and all safety features shall be durable.
3311.2.2 Maintenance. | Every projectile tool shall be properly maintained. No such tool shall be used if any part necessary to retain internal pressures or to prevent accidental discharge of a projectile is not in sound and operable condition.
3311.2.3 Operation. | The operation of projectile tools shall comply with the following:
3311.3 Explosive powered tools. | The provisions of ANSI A10.3, as modified in Section 3311.4, shall apply to explosive powered tools, including but not limited to powder-actuated tools. The storage, handling and use of explosives shall also comply with the New York City Fire Code and Section 3307.4.2.
3311.4 Modifications to ANSI A10. | 3. The text of ANSI A10.3 shall be modified as indicated in Sections 3311.4.1 through 3311.4.12.
3311.4.1 ANSI A10. | 3, Section 4.2.2. Delete Sections 4.2.2.2, 4.2.2.3 and 4.2.2.4 in their entirety and modify Sec­tion 4.2.2.1 to read as follows:
3311.4.2 ANSI A10. | 3, Section 4.2.3. Delete Sections 4.2.3.2, 4.2.3.3 and 4.2.3.4 in their entirety and modify Sec­tion 4.2.3.1 to read as follows:
3311.4.3 ANSI A10. | 3, Section 4.3. Delete Section 4.3 in its entirety.
3311.4.4 ANSI A10. | 3, Section 5.5. Add a new section 5.5 to read as follows:
3311.4.5 ANSI A10. | 3, Section 7.9. Add the following sentence at the beginning of Section 7.9:
3311.4.6 ANSI A10. | 3, Section 9.4. Add a new section 9.4 to read as follows:
3311.4.7 ANSI A10. | 3, Section 10.3.1. Add a new Section 10.3.1 to read as follows:
3311.4.8 ANSI A10. | 3, Section 10.6. Add a new section 10.6 to read as follows:
3311.4.9 ANSI A10. | 3, Section 11.4.1. Add a new section 11.4.1 to read as follows:
3311.4.10 ANSI A10. | 3, Section 11.6. Add a new Section 11.6 to read as follows:
3311.4.11 ANSI A10. | 3, Section 12. Delete Section 12 in its entirety and add a new Section 12 to read as follows:
3311.4.12 ANSI A10. | 3, Section 13. Add a new Section 13 to read as follows:
3312.1 General. | All handling, transporting, and use of explosives, as defined by the New York City Fire Code, shall comply with the New York City Fire Code and Sec­tion 3307.4.2. The use of explosives is strictly prohibited unless the written consent of the commissioner and the Fire Department is obtained. Exception: Explosive powered or projectile tools that comply with Section 3311.
3313.1 General. | The transportation, handling, storage, instal­lation, connection, ventilation, and use of all volatile flamma­ble oils, flammable and combustible mixtures, compressed gases, and other hazardous materials shall comply with the New York City Fire Code, and shall also be safeguarded
3314.1 Scope. | Scaffolds utilized in conjunction with the construction or demolition of a building or structure shall be erected and maintained in accordance with the requirements of this section so that the safety of public and property will not be endangered by falling material, debris, or equipment, or by collapse of the scaffold. Exceptions: 1. The requirements of this section shall not apply to window washing equipment permanently anchored to the building and subject to the jurisdiction of the New York State Department of Labor. However, this exemption shall not apply when such equipment is used for activities other than window washing. 2. Mast climbers are only required to comply with the requirements of Section 3314.19.
3314.1.1 Height. | For the purposes of this section, the height of a scaffold shall be measured from the base of the scaffold to the top of the uppermost vertical member of the scaffold, with any temporary structure, but not any permanent structure, on which the scaffold rests included in the height measurement.
3314.2 Permit. | Prior to the installation and use of a scaffold, the contractor or licensee who is to install the scaffold, or a designated representative of the installer, shall obtain a permit for such scaffold. The permit requirements of this section are independent of the design requirements of Section 3314.3. Sections 3314.3.1 through 3314.3.4 may require a scaffold to be designed even if Section 3314.2 does not require a permit for such scaffold. Exceptions: 1. A permit is not required for a two-point, single tier, suspended scaffold suspended from a parapet using C-hooks. 2. A permit is not required for a suspended scaffold provided Items 2.1 through 2.3 are complied with: 2.1. The scaffold is installed and used in conjunction with a construction, alteration, or demolition project that holds a valid permit from the department for such project; 2.2. The site is closed to the public and enclosed with a fence in accordance with Section 3307.7; and 2.3. The installation, use, and removal of the scaffold is confined within the site or over an area protected by sidewalk sheds or roof protection. 3. A permit is not required for a single tier nonadjustable suspended scaffold whose platform is 40 square feet (3720 mm2) or less in size. 4. A permit is not required for a supported scaffold, provided Items 4.1 through 4.6 are complied with: 4.1 The scaffold is not an outrigger scaffold (thrust out); 4.2 No hoisting equipment with a manufacturer’s rated capacity greater than 2,000 pounds (907 kg) will be located on the scaffold; 4.3 The scaffold will not be loaded, or designed to be loaded, in excess of 75 pounds per square foot (366.15 kg/m2) (e.g. a light duty scaffold, a medium duty scaffold, or a heavy duty scaffold); 4.4 The scaffold is less than 40 feet (12 192mm) in height; 4.5 Side-arm or end-arm scaffold brackets are used exclusively for the support of workers; and 4.6 Where the scaffold has a height-to-base ratio (including outriggers supports, if used) of more than four to one (4:1), it is restrained in accordance with Section 3314.9.1.
3314.3 Design. | Scaffolds shall be designed in accordance with Sections 3314.3.1 through 3314.3.4. The design requirements of this section are independent of the permit requirements of Section 3314.2. Sections 3314.3.1 through 3314.3.4 may require a scaffold to be designed even if Section 3314.2 does not require a permit for such scaffold.
3314.3.1 Supported scaffolds and outrigger scaffolds (thrust out). | Supported scaffolds and outrigger scaffolds (thrust out) shall be designed by a registered design professional. Where the scaffold is to be located upon a sidewalk shed, the requirements of Section 3307.6.4.2.2 shall also apply. Exception: Design is not required for a supported scaffold, provided Items 1 through 6 are complied with: 1. The scaffold is not an outrigger scaffold (thrust out); 2. No hoisting equipment with a manufacturer’s rated capacity greater than 2,000 pounds (907kg) will be located on the scaffold; 3. The scaffold will not be loaded, or designed to be loaded, in excess of 75 pounds per square foot (366.15 kg/m2) (e.g. a light duty scaffold, a medium duty scaffold, or a heavy duty scaffold); 4. The scaffold is less than 40 feet (12 192mm) in height; 5. Side-arm or end-arm scaffold brackets are used exclusively for the support of workers; and 6. Where the scaffold has a height-to-base ratio (including outriggers supports, if used) of more than four to one (4:1), it is restrained in accordance with Section 3314.9.1.
3314.3.2 Suspended scaffolds. | Suspended scaffolds shall be designed by a registered design professional. Exceptions: 1. Design is not required for a single tier nonadjustable suspended scaffold whose platform is 40 square feet (3720 mm2) or less in size. 2. In lieu of a registered design professional, a two-point, single tier, suspended scaffold may be designed by a licensed rigger provided Items 2.1 and 2.2 are complied with and either Items 2.2.1 or 2.2.2 are complied with: 2.1. The scaffold or scaffold outrigger beam or suspension member support structure is not anchored to the building or structure, other than tiebacks; and 2.2. The scaffold will not be loaded, or designed to be loaded, in excess of 75 pounds per square foot (366.15 kg/m2); and either 2.2.1. The scaffold utilizes c-hooks; or 2.2.2. The distance from floor or roof on which the support structure is located to the top of the outrigger beam or suspension member support structure is less than 15 feet (4572 mm). 3. In lieu of a registered design professional or a licensed rigger, a two-point, single tier, suspended scaffold meeting the requirements of Item 2 of these exceptions that is used exclusively for sign hanging work may be designed by a licensed sign hanger.
3314.3.3 Drawings. | Where design is required by this section, the drawings shall be specific to the site and shall, at a minimum, include a plan view and an elevation view, with full dimensions, detailing:
3314.3.4 Loads imposed. | Where a supported scaffold requiring design in accordance with Section 3314.3.1 imparts a load on a temporary or permanent structure, including but not limited to a sidewalk shed, roof, setback, or vault, the design drawings required by Section 3314.3.3 shall either be:
3314.4 Installation, inspection, repair, maintenance, adjustment, use, and removal of scaffolds. | Scaffolds shall be installed, inspected, repaired, maintained, adjusted, used, and removed in accordance with the specifications of the manufacturer, where such specifications exist, and the requirements of Sections 3314.4.1 through 3314.4.8.
3314.4.1 Installation and removal. | Scaffolds shall be installed and removed in accordance with the requirements of Sections 3314.4.1.1 through 3314.4.1.5. Where modifications to the base structure are required to support the scaffold, the scaffold shall not be installed until such modifications have been completed.
3314.4.1.1 Supervision of suspended scaffold installation and removal. | Suspended scaffolds shall be installed and removed by or under the direct and continuing supervision of a licensed rigger. Exceptions: In lieu of direct and continuing supervision by a licensed rigger: 1. The installation and removal of a suspended scaffold utilized exclusively for sign hanging work may be performed by or under the direct and continuing supervision of a licensed sign hanger. 2. The installation and removal of a suspended scaffold may be supervised by a competent person designated by the scaffold permit holder, or where there is no scaffold permit holder, designated by the scaffold controlling entity, provided such scaffold is installed and removed in conjunction with: 2.1. The construction of a new building; 2.2. The full demolition of an existing building; 2.3. The vertical or horizontal enlargement of an existing building; or 2.4. The alteration, maintenance, or repair of a façade of a major building where a site safety plan is required by Section 3310.3. 3. The lateral relocation of a wheel or track mounted scaffold and tiebacks may be supervised by a competent person designated by the scaffold controlling entity, provided the design developed by the registered design professional allows for such relocation, and also provided such lateral relocation occurs without the addition or removal of any part, component, attachment, counterweight, anchorage, or connection to the base building or structure, other than tie-backs so long as such tie-backs are placed as designated on the approved plan.
3314.4.1.2 Supervision of supported scaffold installation and removal. | The installation and removal of a supported scaffold shall be supervised by a competent person designated by the contractor installing or removing the scaffold.
3314.4.1.3 Supervisor to be present at the site. | The licensee or competent person supervising the installation or removal of a scaffold shall be present at the site during all installation and removal work and shall have the ability to communicate with all individuals involved in the installation or removal work. Where only one person is installing or removing a scaffold, such person shall be deemed to be the supervisor present at the site and must have the qualifications and training required by this chapter to serve as a supervisor for such work. Exception: The licensed rigger or sign hanger does not have to be present at the site, provided a suspended scaffold foreman is present at the site during all installation and removal work and provided such suspended scaffold foreman has the ability to communicate with all individuals involved in the installation or removal work.
3314.4.1.4 Training. | All individuals involved in the installation or removal of a supported scaffold or an adjustable suspended scaffold, including the person supervising such work, shall have been trained as required by Section 3314.4.5.
3314.4.1.5 Notification of adjustable suspended scaffold installation and removal. | Prior to the initial installation of the adjustable suspended scaffold at a site, and prior to the final removal of the adjustable suspended scaffold at a site, the department shall be notified at least 24 hours, but not more than 48 hours, prior to such installation or removal. Should the notification date fall on a weekend or official holiday, the notification shall be made on the last business day before the commencement date of the installation or removal. Such notification:
3314.4.2 Use of scaffolds. | Scaffolds shall be used in accordance with the requirements of Sections 3314.4.2.1 through 3314.4.2.5.
3314.4.2.1 Supervision of suspended scaffold use. | Suspended scaffolds shall be used by or under the direct and continuing supervision of a licensed rigger. Exceptions: 1. In lieu of direct and continuing supervision by a licensed rigger, the use of a suspended scaffold utilized exclusively for sign hanging work may be performed by or under the direct and continuing supervision of a licensed sign hanger. 2. In lieu of direct and continuing supervision by a licensed rigger, the use of a suspended scaffold may be supervised by a competent person designated by the scaffold controlling entity, provided such scaffold is used in conjunction with: 2.1. The construction of a new building; 2.2. The full demolition of an existing building; 2.3. The vertical or horizontal enlargement of an existing building; or 2.4. The alteration, maintenance, or repair of a façade of a major building where a site safety plan is required by Section 3310.3. 3. Where a scaffold is used by or under the direct and continuing supervision of a licensed rigger, a registered design professional who is not in the direct employ of the licensee or business of the licensee may ride on a suspended scaffold to perform inspections provided the registered design professional: 3.1. Does not perform construction, maintenance, repair, or demolition work from the scaffold; 3.2. Does not operate the scaffold; and 3.3. Is familiar with the use of the scaffold, safety equipment, and emergency procedures. 4. Where a scaffold is used by or under the direct and continuing supervision of a licensed rigger, a specialty crew who is not in the direct employ of the licensee or business of the licensee may use the suspended scaffold, provided: 4.1. The work requires a specialty trade, including but not limited to work with hazardous materials or chemicals; 4.2. The crew is in accordance with rules promulgated by the commissioner; and 4.3. The members of the crew are approved by the commissioner.
3314.4.2.2 Supervision of supported scaffold use. | The use of a supported scaffold shall be supervised by a competent person designated by the scaffold controlling entity.
3314.4.2.3 Installer who is not the scaffold controlling entity. | Where the contractor or licensee that installed the scaffold is not the scaffold controlling entity, the installer shall have no supervisory responsibility for the use of the scaffold.
3314.4.2.4 Supervisor to be present at the site. | The licensee or competent person supervising the use of a scaffold shall be present at the site during all times the scaffold is in use and shall have the ability to communicate with all individuals using the scaffold; however, such supervisor does not need to be on the scaffold. Exception: The licensed rigger or sign hanger does not have to be present at the site, provided a suspended scaffold foreman is present at the site during all times the scaffold is in use and provided such suspended scaffold foreman has the ability to communicate with all individuals using the scaffold. Such suspended scaffold foreman does not need to be on the scaffold.
3314.4.2.5 Training. | All individuals using a supported scaffold or an adjustable suspended scaffold, including the person supervising such use, shall have been trained as required by Section 3314.4.5.
3314.4.3 Inspections. | Scaffolds shall be inspected in accordance with the requirements of Sections 3314.4.3.1 through 3314.4.3.6.
3314.4.3.1 Inspection prior to the installation of a suspended scaffold. | Prior to the installation of a suspended scaffold, all suspended scaffold support devices, including but not limited to outrigger beams and C-hooks, along with the support surface/structure upon which they rest (e.g. roof, parapet), shall be inspected by a qualified person. The qualified person shall: 1. Where the installation or removal occurs under the direct and continuing supervision of a licensed rigger or sign hanger, be designated by such licensee; or 2. Where the installation or removal does not occur under the direct and continuing supervision of a licensed rigger or sign hanger, be designated by the designer of the scaffold. Exception: An inspection is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.4.3.1.1 Special provision for parapet clamps. | Where parapet clamps are to be utilized, the qualified person who inspects the support surface/structure as required by Section 3314.4.3.1 shall be a registered design professional. The registered design professional shall confirm, based on the inspection and evaluation of the support surface/structure, that the support surface/structure is capable of supporting the loads to be imposed, including any eccentric load introduced by the parapet clamp.
3314.4.3.1.2 Documentation of parapet clamp inspection and evaluation. | Documentation of the inspection and evaluation required by Section 3314.4.3.1.1 shall be included with the installation inspection report required by Section 3314.4.3.2.1. Such documentation shall be signed, sealed, and dated by the registered design professional that performed the inspection and evaluation.
3314.4.3.2 Installation inspection for suspended scaffolds. | Upon completion of the installation of a suspended scaffold, the scaffold, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold shall be inspected prior to use to verify that they are in a safe condition and, where design is required, installed in accordance with the design drawings. The individual performing the inspection shall have completed the training required by Section 3314.4.5.3 and shall be: 1. Where the scaffold was designed by a licensed rigger or sign hanger, or installed by or under the direct and continuing supervision of a licensed rigger or sign hanger: 1.1. The licensee; or 1.2. A suspended scaffold foreman; or 2. Where the scaffold was not designed by a licensed rigger or sign hanger, or installed by or under the direct and continuing supervision of a licensed rigger or sign hanger: 2.1. The scaffold designer; 2.2. An employee of the scaffold designer under his or her direct supervision; 2.3. A registered design professional retained by the scaffold designer; or 2.4. An employee of such retained registered design professional under the direct supervision of such retained registered design professional. Exceptions: An installation inspection is not required for: 1. A nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed; or 2. The lateral relocation of a wheel or track mounted scaffold and tiebacks, provided the design developed by the registered design professional allows for such relocation, and also provided such lateral relocation occurs without the addition or removal of any part, component, attachment, counterweight, anchorage, or connection to the base building or structure, other than tie-backs. Following such lateral relocation, the scaffold, and any re-installed tie-back, shall be inspected and documented under the requirements of Section 3314.4.3.4.
3314.4.3.2.1 Installation inspection report. | The results of the inspection shall be documented in an installation inspection report signed and dated by the person who performed the inspection. The scaffold shall not be used until it has passed such inspection and the installation inspection report has been completed. Exception: An installation inspection report is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.4.3.3 Installation inspection for supported scaffolds. | Upon completion of the installation of a supported scaffold, the scaffold, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold, shall be inspected prior to use to verify that they are in a safe condition and, where design is required, installed in accordance with the design drawings. Such inspection shall be performed by a qualified person who has completed the training required by Section 3314.4.5.1 and who is designated by the designer, the installer, or a third party acceptable to both the designer and the installer. The results of the inspection shall be documented in an installation inspection report signed and dated by the person who performed the inspection. The scaffold shall not be used until it has passed such inspection and the installation inspection report has been completed. Exceptions: 1. Where additional components or attachments are installed to an existing supported scaffold, or where existing deck planking or guardrails are relocated to a different level or location, the installation inspection and installation inspection report shall be limited to such components or attachments and related anchorages. 2. An inspection and report is not required for a supported scaffold that, pursuant to Section 3314.3.1, is not required to be designed.
3314.4.3.4 Pre-shift inspection for a suspended scaffold. | Suspended scaffolds shall be inspected prior to each shift, and after any occurrence which could affect a scaffold’s structural integrity, in accordance with a pre-shift inspection checklist that meets the requirements of Section 3314.4.3.4.2. The scaffold shall not be used until it has passed such inspection and the results have been documented on the checklist. The checklist shall be kept at the site by the scaffold controlling entity. Exception: A pre-shift inspection is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.4.3.4.1 Responsibility for performing the inspection and signing the checklist. | The inspection required by Section 3314.4.3.4 shall be performed by, and the checklist required by Section 3314.4.3.4.2 shall be signed and dated by, the licensee, suspended scaffold foreman, or competent person who is onsite and responsible for supervising the scaffold under the provisions of Section 3314.4.2.4. Such individual shall have completed the training required by Section 3314.4.5.3.
3314.4.3.4.2 Pre-shift inspection checklist contents. | The pre-shift inspection checklist shall be based on the manufacturer requirements for the inspection of the scaffold, where such requirements exist, and shall, at a minimum, include an inspection prior to each shift to verify the scaffold, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold, remain in a safe condition for use, and shall also include a comprehensive inspection following high winds. Such checklist shall be: 1. Where the scaffold was designed by a licensed rigger or sign hanger, or installed by or under the direct and continuing supervision of a licensed rigger or sign hanger, developed by the licensee; or 2. Where the scaffold was not designed by a licensed rigger or sign hanger, or installed by or under the direct and continuing supervision of a licensed rigger or sign hanger, developed by the registered design professional who designed the scaffold. Exception: A pre-shift inspection checklist is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.4.3.5 Pre-shift inspection for a supported scaffold. | Prior to each shift, and after any occurrence which could affect a scaffold’s structural integrity, the supported scaffold shall be inspected by the competent person supervising the use of the scaffold in accordance with Section 3314.4.2.2 to verify the scaffold, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold, remain in a safe condition for use. Such competent person shall have completed the training required by Section 3314.4.5.2. The results of the inspection shall be documented in a pre-shift inspection report signed and dated by the person who performed the inspection. The scaffold shall not be used until it has passed such inspection and the pre-shift inspection report has been completed. Exception: An inspection report is not required for a supported scaffold that is not required to be designed under Section 3314.3.1.
3314.4.3.6 Inspection following a site repair or adjustment. | Following a repair or adjustment to a scaffold at a site, the portion adjusted or repaired shall be inspected by the person who supervised the adjustment or repair in accordance with Sections 3314.4.6 or 3314.4.7 to verify the adequacy of such adjustment or repair. A description of the adjustment or repair, and the results of the inspection, shall be recorded, signed, and dated by such supervisor and kept with the inspection report required by Sections 3314.4.3.4 or 3314.4.3.5. The scaffold shall not be used until it has passed such inspection and the results of the inspection have been documented. Exceptions: 1. The scaffold may be used prior to the inspection where authorized in accordance with Section 3314.4.4.7. 2. An inspection and report is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.4.4 Safeguards. | The safeguards required by Sections 3314.4.4.1 through 3314.4.4.12 shall be observed at all times.
3314.4.4.1 Safe working order. | Scaffolds, including all components of and attachments to the scaffold, and all supports and anchorages of the scaffold, shall be provided to the site in a safe working order by their respective owner, with no known hazardous conditions, defective repairs, or maintenance problems that could compromise the safety of the public and property. All scaffolds shall be kept in a safe condition at the site by the scaffold controlling entity. Every damaged or weakened scaffold shall be immediately repaired or secured and shall not be used until satisfactory repairs have been completed, and the scaffold is inspected under the provisions of Section 3314.4.3.
3314.4.4.2 Loads. | At no time shall a scaffold be loaded beyond the capacity of the scaffold or the ground or structure upon which it rests or is supported. Loads shall not be concentrated so as to cause stresses in excess of the allow­able values designated for the applicable material described in this code.
3314.4.4.3 Capacity. | Scaffolds shall meet the following capacity requirements.
3314.4.4.3.1 Scaffold and components. | Each scaffold, and its components, shall be capable of sup­porting, without failure, its own weight and at least four times the maximum intended load applied or transmitted to it. Where applicable, scaffolds and their connections to the building or structure shall be designed to meet the anticipated loads during construction or demolition work, including wind loads as prescribed in Chapter 16.
3314.4.4.3.2 Suspension rope on nonadjustable suspended scaffolds. | Each suspension rope, including connecting hardware, used on nonadjustable suspended scaffolds shall be capable of supporting, without failure, at least six times the maximum intended load applied or transmitted to the rope.
3314.4.4.3.3 Suspension rope on adjustable suspended scaffolds. | Each suspension rope, including connecting hardware, used on adjustable suspension scaffolds shall be capable of supporting, without failure, at least six times the maximum intended load applied or transmitted to that rope with the scaffold operating at the rated load of the hoist.
3314.4.4.3.4 Direct connections to roofs, floors, and counterweights. | Direct connections to roofs and floors, and counterweights used to balance adjustable suspension scaffolds, shall be capable of resisting at least four times the tipping moment imposed by the scaffold operating at the rated load of the hoist.
3314.4.4.4 Stable and secure. | The scaffold and all materials and equipment located on or used from the scaffold shall be kept stable and secure at all times to prevent the scaffold from losing balance, overturning, or collapsing, and to prevent any object from falling from the scaffold.
3314.4.4.5 Dislodgement. | Material and equipment susceptible to dislodgment shall not be stored on a scaffold while work is not being performed.
3314.4.4.6 Winds. | Where sustained winds or wind gusts at the site exceed 30 miles per hour, the installation, repair, maintenance, adjustment, use, operation, and removal of scaffolds located on the roof or setback of a building, exterior to a building or structure, on a working deck, or in an area with an unenclosed perimeter shall cease and the scaffold shall be secured. If the manufacturer or designer of the scaffold recommends work to cease at a lower wind speed, such recommendation shall instead apply. Wind speed shall be determined based on data from the nearest United States weather bureau reporting station, or an anemometer located at the site, freely exposed to the wind, and calibrated in accordance with ASTM D5096. No scaffold installation, repair, maintenance, adjustment, use, operation, or removal work shall commence where the weather forecast indicates the work will not be able to be safely completed and the scaffold secured before sustained winds or wind gusts exceed the thresholds established by this section.
3314.4.4.7 Use during installation, repairs, maintenance, adjustments, or removal. | Only personnel, materials, and uses authorized by the person responsible for supervising the installation, repair, maintenance, adjustment, or removal of a scaffold shall be located on and using the scaffold during such work.
3314.4.4.8 Noncombustible construction. | With the exception of the planking, the following scaffolds shall be constructed of noncombustible materials: 1. Exterior scaffolds exceeding 75 feet (22 860 mm) in height. 2. Interior scaffolds exceeding 21 feet (6401 mm) in height. 3. All scaffolds used in the alteration, repair, or partial demolition of buildings in Occupancy Groups I-1 to I-4.
3314.4.4.9 Capacity identification for suspended scaffolds. | Suspended scaffold motors shall contain a plate from the manufacturer of the motor indicating the rated load of the motor. Swaged attachments or spliced eyes on wire suspension ropes shall be tagged in accordance with the requirements of Section 3314.11.8. Identification required by this section shall be maintained so as to be legible during the life of the element. Missing or illegible identification shall be replaced by a qualified person in accordance with the requirements of the manufacturer of the component or the testing entity authorized by Section 3314.11.8.
3314.4.4.10 Prohibition on shore or lean-to scaffolds. | The use of shore or lean-to scaffolds is prohibited.
3314.4.4.11 Accumulation of debris. | Debris shall not be allowed to accumulate on platforms.
3314.4.4.12 Precautions while working around powerlines. | The clearance between scaffolds and power lines shall be as specified in Table 3314.4.4.12. Scaffolds shall not be erected, used, dismantled, altered, or moved such that they or any conductive material handled on them might come closer to exposed and energized power lines than as specified in Table 3314.4.4.12. Exception: Scaffolds and materials may be closer to power lines than specified in Table 3314.4.4.12 where such clearance is necessary for performance of work, and only after the utility company, or electrical system operator, has been notified of the need to work closer and the utility company, or electrical system operator, has deenergized the lines, relocated the lines, or installed protective coverings to prevent accidental contact with the lines. |  |  | See BC33 Tables and Figures
3314.4.5 Training. | Only those who are qualified to install, adjust, maintain, repair, use, or remove a scaffold, and are trained in accordance with the requirements of this section, shall perform such work or supervise such work. No person shall knowingly permit or cause an individual who does not have the experience and training required by this section to install, adjust, modify, repair, use, or remove a scaffold.
3314.4.5.1 Training for supported scaffold installers, adjusters, repairers, maintainers, or removers. | Workers who install, adjust, repair, maintain, or remove a supported scaffold that is 40 feet (12 192 mm) or more in height, including the person supervising such, shall, at a minimum, have completed a department-approved training program or course that is at least 32 hours long and shall complete a department-approved 8-hour refresher program or course every 4 years thereafter. Workers who install, adjust, repair, maintain, or remove a sidewalk shed that provides a base for a supported scaffold that is 40 feet (12 192 mm) or more in height, including the person supervising such, are subject to the above requirements. Exceptions: 1. The installation, adjustment, maintenance, repair, or removal of a supported scaffold performed by an employee of a public utility, including the person supervising such, where such supported scaffold is located within the interior of a structure owned or operated by such utility, and when such utility has a training safety program or course of not less than 32 hours for its employees who perform such scaffold work. 2. Where existing supported scaffold deck planking or guardrails are being relocated to a different level of the scaffold in accordance with the design, such may be performed by individuals who have completed the training required by Section 3314.4.5.2.
3314.4.5.2 Training for supported scaffold users. | Individuals who use a supported scaffold, including the person supervising such, shall, at a minimum, have completed a department-approved training program or course that is at least 4 hours long and, every four years thereafter, retake the 4-hour training program or course. Exceptions: 1. Employees of a public utility performing work while using a supported scaffold, including the person supervising such, provided that such employees are trained to be able to recognize the hazards associated with the type of supported scaffold being used and to understand the procedures to control those hazards. 2. A registered design professional who has not completed the training may use a supported scaffold to perform inspections provided the registered design professional does not perform construction, maintenance, repair, or demolition work from the scaffold. 3. The use of a stair tower/scaffold stairway/scaffold stair tower that is not connected to a scaffold work platform and is dedicated to providing temporary ingress or egress to the building or structure.
3314.4.5.3 Training for suspended scaffold supervisors. | Individuals who exercise supervisory responsibility in accordance with the requirements of Sections 3314.4.1 through 3314.4.4 for the installation, adjustment, repair, maintenance, use, or removal of a suspended scaffold shall, at a minimum, have completed a department-approved training program or course that is at least 32 hours long and, four years following completion of the 32-hour program or course, and every four years thereafter, complete a department-approved 8-hour refresher program or course. Exception: Individuals supervising the installation, adjustment, modification, repair, use, or removal of a single tier nonadjustable suspended scaffold whose platform is 40 square feet (3720 mm2) or less in size.
3314.4.5.4 Training for suspended scaffold installers, adjusters, repairers, maintainers, users, or removers. | Individuals who install, adjust, repair, maintain, use, or remove a suspended scaffold shall, at a minimum, have completed a department-approved training program or course that is at least 16 hours long and, four years following completion of the 16-hour program or course, and every four years thereafter, complete a department-approved 8-hour refresher program or course. Exceptions: 1. A registered design professional who has not completed the training may ride on a suspended scaffold to perform inspections provided the registered design professional does not perform construction, maintenance, repair, or demolition work from the scaffold, or operate the scaffold, and provided the registered design professional is familiar with the use of the scaffold, safety equipment, and emergency procedures. 2. Individuals who install, adjust, repair, maintain, use, or remove a single tier nonadjustable suspended scaffold whose platform is 40 square feet (3720 mm2) or less in size. 3. A person who possesses a valid challenge examination certificate issued prior to January 1, 2014, need not take a new 16-hour initial program or course but shall be required to complete the 8-hour refresher program or course every 4 years, beginning from the date of enactment of this code.
3314.4.5.5 Course providers. | Training programs or courses required by this section shall be conducted by a registered New York State Department of Labor apprenticeship training program or by an educational institution or school chartered, licensed or registered by the New York State Department of Education or by a provider approved by the department and presented by an instructor acceptable to the commissioner.
3314.4.5.6 Course curriculums. | All training programs or courses required by this section shall be based on the scaffold requirements of this chapter and shall include, but not be limited to, instruction on the type of scaffold the training covers and associated hazards, common causes of scaffold incidents and steps to avoid such incidents, scaffold components, scaffold connections to a structure, scaffold inspection, the maximum intended load and load-handling capacities of scaffolds, and the prevention of overload conditions. Curriculums for scaffold users shall be focused on the proper use of the scaffold. Curriculums for scaffold installers, adjusters, maintainers, repairers, and removers shall be focused on the proper execution of such work. Curriculums in excess of eight hours in length shall include a significant portion of hands-on training.
3314.4.5.7 Evaluation. | Successful completion of a training program or course that is more than 4 hours in length shall be based upon a written performance evaluation. For courses that are 16 hours or greater in length, successful completion shall also be based upon passage of a hands-on performance evaluation.
3314.4.5.8 Certificate card. | Successful completion of the training program or course shall be evidenced by a wallet size certificate card issued by the training provider and acceptable to the commissioner. Such certificate card shall be readily available to the commissioner upon request and shall contain, at a minimum, the name and photograph of the individual to whom it was issued, as well as any other information required pursuant to rules promulgated by the commissioner for a department approved training course.
3314.4.5.9 Grace period. | For individuals who fail to complete the required refresher program or course within any 4 year period, a refresher program or course shall be considered timely if completed within 1 year after the expiration date of the last previously completed initial or refresher program or course. During such period, such individual shall not perform or supervise any activity for which the lapsed training is required to perform or supervise such activity until such individual has successfully completed such refresher program or course. Where more than 1 year has lapsed, such individual shall be required to successfully recomplete the initial training program or course.
3314.4.6 Adjustments. | Scaffolds, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold installed at a site shall be adjusted under the supervision of a competent person designated by the contractor or licensee who installed the scaffold. Individuals who perform adjustments, and the person supervising such, shall be trained in accordance with Section 3314.4.5. Following the adjustment, the scaffold shall be inspected in accordance with Section 3314.4.3.6. Exception: Where a sidewalk shed provides the base for a supported scaffold, the sidewalk shed shall be adjusted in accordance with the requirements of Section 3307.6.
3314.4.7 Repairs. | Scaffolds, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold installed at a site shall be repaired under the supervision of a competent person designated by the equipment owner. Individuals who perform repairs, and the person supervising such, shall be trained in accordance with Section 3314.4.5. Following the repair, the scaffold shall be inspected in accordance with Section 3314.4.3.6. Exceptions: 1. Where a sidewalk shed provides the base for a supported scaffold, the sidewalk shed shall be repaired in accordance with the requirements of Section 3307.6. 2. Components and attachments may be replaced under the supervision of a competent person designated by the contractor or licensee who installed the scaffold.
3314.4.8 Maintenance. | Scaffolds, all components of and attachments to the scaffold, and all supports and anchorages of the scaffold installed at a site shall be maintained in a good condition by a qualified person designated by the scaffold controlling entity. Individuals maintaining a scaffold shall have been trained in accordance with Section 3314.4.5. Individuals who maintain an adjustable suspended scaffold hoist shall also have been trained and authorized by the manufacturer of the scaffold hoist. A description of the maintenance shall be recorded, signed, and dated by the person who performed the maintenance and kept with the inspection checklist or report required by Sections 3314.4.3.4 or 3314.4.3.5. Exceptions: 1. Where a sidewalk shed provides the base for a supported scaffold, the sidewalk shed shall be maintained in accordance with the requirements of Section 3307.6. 2. A description of the maintenance is not required for a nonadjustable suspended scaffold that, pursuant to Section 3314.3.2, is not required to be designed.
3314.5 Platform construction. | Platforms on all working levels of a scaffold shall be fully planked or decked between the front uprights and the guardrail system supports in accordance with Sections 3314.5.1 through 3314.5.7. Exception: Platforms used solely as walkways or used solely by workers installing or removing the scaffold shall be planked to the extent necessary to ensure the safety of the public and property.
3314.5.1 Platform spacing. | Each platform unit (e.g., scaffold plank, fabricated plank, fabricated deck, or fabricated platform) shall be installed so that the space between adjacent units and the space between the platform and the uprights is no more than 1 inch (25 mm) wide except where a qualified person can demonstrate that a wider space is necessary.
3314.5.2 Maximum span for wood plank. | All lumber used in scaffolds or their supports shall be at least equal in strength and quality to construction grade lumber in accordance with Section 2301. See Table 3314.5.2 for the maximum span for scaffold planks. |  |  | See BC33 Tables and Figures
3314.5.3 Minimum overhang. | The end of a platform shall extend over the centerline of its support a minimum of 6 inches (152 mm) unless cleated or otherwise restrained by hooks or equivalent means.
3314.5.4 Maximum cantilever. | The maximum cantilever shall be as follows.
3314.5.4.1 Ten feet or less. | The end of a platform 10 feet (3048 mm) or less in length shall not extend over the centerline of its support more than 12 inches (305 mm) unless the platform and its tiedown are designed by a qualified person or the platform has guardrails to prevent access to the cantilevered end.
3314.5.4.2 More than ten feet. | The end of a platform more than 10 feet (3048 mm) in length shall not extend over the centerline of its support more than 18 inches (457 mm) unless the platform and its tiedown are designed by a qualified person or the platform has guardrails to prevent access to the cantilevered end.
3314.5.5 Platform tiedown. | All platforms shall be tied down or otherwise positively restrained by hooks or equivalent means to prevent dislodgment in all directions.
3314.5.6 Platform deflection. | Platforms shall not deflect more than 1/60 of the span when loaded.
3314.5.7 Unsuitable platforms. | Unstable objects shall not be used as working platforms.
3314.6 Footings and anchorage. | The footings and anchorage for every scaffold shall be sound and rigid, capable of carrying the maximum load without settlement or deformation and secure against movement in any direction. Supports such as barrels, boxes, loose brick, loose stone, or other unstable materials shall not be used.
3314.6.1 Safe points of anchorage. | Safe points of anchorage include structural members of a building. Window washing anchors, window frames, mullions, handrails, standpipes, vents and other piping systems, electrical conduit, counterweights or similar elements shall not be used as anchors or braceback points. Exception: Window washing anchor points that are part of the base building structure may be utilized as an anchor or braceback point for a scaffold, subject to the approval of the commissioner. The anchor points shall be inspected by a registered design professional prior to use to verify their ability to support all loads imposed. At the end of the job, the anchor points shall be restored to their original condition, any damage repaired, and inspected by a registered design professional to verify such. A report verifying such restoration and inspection shall be prepared by the registered design professional and submitted to the department.
3314.6.2 Lifeline anchorage. | Vertical lifelines shall be fastened to a fixed safe point of anchorage and shall be independent of the scaffold. Horizontal lifelines shall only be utilized where the individual who designed the scaffold in accordance with Section 3314.3 has determined vertical lifelines are not feasible (for example, lower platforms of a multi-level suspended scaffold). Where utilized, horizontal lifelines shall be secured to two or more structural members of the scaffold, or they may be looped around both suspension and independent suspension lines (on scaffolds so equipped) above the hoist and brake attached to the end of the scaffold. Horizontal lifelines shall not be attached only to the suspension ropes. Vertical and horizontal lifelines shall be protected from sharp edges and abrasion.
3314.6.3 Lifelines and suspension ropes. | Vertical lifelines, tiebacks, and suspension ropes shall each be attached to a different point of anchorage.
3314.6.4 Scaffolds supported on structure. | Loads from supported and suspended scaffolds imposed on an existing roof or floor or similar structure shall:
3314.7 Outrigger beams. | Outrigger beams shall be made of structural metal or equivalent strength material and shall be restrained to prevent movement.
3314.7.1 Overhang. | The overhang of outrigger beams shall not exceed that specified by the design and the inboard length of beam shall be at least one and one-half times the outboard length unless otherwise designed by a registered design professional.
3314.7.2 Placement. | Outrigger beams shall be placed so that the suspension ropes will hang vertically.
3314.7.3 Outrigger beam end of suspension ropes. | Suspension ropes shall be securely fastened to the outrigger beams by steel shackles, thimbles, or equivalent means.
3314.7.4 Load end of wire suspension ropes. | The load end of wire suspension ropes shall be equipped with proper size thimbles and secured by eyesplicing or equivalent means. Where applicable, such equivalent means shall be in accordance with Section 3314.11.8.
3314.8 Guardrail system and debris netting. | The open sides and ends of scaffold platforms shall be provided with a guardrail system that meets the requirements of Section 3314.8.1 and debris netting that meets the requirements of Section 3314.8.2. Exceptions: 1. A guardrail system and debris netting are not required while the scaffold is being installed or removed but shall be in place before the scaffold is used. 2. A guardrail system and debris netting is not required along the edge of a scaffold facing a building or structure, provided the distance from the edge of the scaffold platform to the face of the building or structure is: 2.1. For an outrigger scaffold, 3 inches (76 mm) or less; 2.2. For a scaffold used in conjunction with plastering and lathing operations, 18 inches (457 mm) or less; or 2.3. For all other scaffolds, 14 inches (356 mm) or less. 3. Debris netting is not required for a scaffold where the scaffold is set back from all adjoining property and areas that remain open to the public at a distance that is equal to or greater than half the height of scaffold, except where the scaffold is installed to provide an alternative to demolition safety zones, sidewalk sheds, safety netting, or adjoining property protection in accordance with Sections 3306, 3307, 3308, 3309, or the scaffold is installed at the edge of an unenclosed perimeter in accordance with Section 3314.9.4. 4. Debris netting is not required for a scaffold that does not require a design in accordance with Section 3314.3, except where the scaffold is installed to provide an alternative to demolition safety zones, sidewalk sheds, safety netting, or adjoining property protection in accordance with Sections 3306, 3307, 3308, or 3309, or the scaffold is installed at the edge of an unenclosed perimeter in accordance with Section 3314.9.4. 5. A guardrail system and debris netting is not required for a supported scaffold whose topmost platform is 6 feet (1829 mm) or less above the level of the ground or floor, except as otherwise required by Section 3314.9.4.
3314.8.1 Guardrail system. | Where required by Section 3314.8, the guardrail system for a scaffold shall meet the requirements of Section 3308.7.1 through 3308.7.7. Exceptions: For the purposes of this section: 1. The term “floor” in Sections 3308.7.1 through 3308.7.7 shall mean “platform.” 2. The height of the toprail, as prescribed in Section 3308.7.2, may be as low as 38 inches (965 mm) in a guardrail system utilized in connection with a scaffold, and such toprail may deflect to a height of not less than 38 inches (965 mm) when designed in accordance with Exception 1 to Section 3308.7.3. 3. Alternate guardrail systems under Exception 1 to Section 3308.7.3 may be designed by the designer of the scaffold or the manufacturer of the scaffold to be capable of withstanding, without failure, a force of at least: 3.1. For toprails or equivalent members, a force applied in any downward or horizontal direction at any point along its top edge of at least 100 pounds (445 N) for guardrail systems installed on single-point adjustable suspended scaffolds or two-point adjustable suspended scaffolds, and at least 200 pounds (890 N for guardrail systems installed on all other scaffolds. 3.2. For midrails, screens, mesh, intermediate vertical members, solid panels, or equivalent members, a force applied in any downward or horizontal direction at any point along the midrail or other member of at least 75 pounds (333 N) for guardrail systems with a minimum 100 pound (445 N) toprail capacity, and at least 150 pounds (666 N) for guardrail systems with a minimum 200 pound (890 N) toprail capacity. 3.3. For toeboards, a force of at least 50 pounds (222 N) applied in any downward or horizontal direction at any point along the toeboard. 4. Where intermedi¬ate supports, such as ballisters or additional rails are used, they shall not be more than 19 inches (483 mm) apart.
3314.8.2 Debris netting. | Where required by Section 3314.8, the scaffold shall be enclosed with a debris netting consisting of a wire screen comprised of not less than number 18 gauge wire mesh, or equivalent synthetic netting that is flame retardant in accordance with NFPA 701, with openings in the wire or synthetic mesh no larger than ½ inch (13 mm) in the vertical or horizontal dimensions and ¾ inch (19 mm) in any other dimension. Such netting shall be securely attached to the scaffold and shall enclose all open sides, ends, and bottom of the scaffold for the full height of all platform levels where work is occurring. The effect of wind on the netting shall be accounted for in the design of the scaffold, where such design is required by Section 3314.3. Exceptions: 1. Netting is not required to protect the bottom of the scaffold platform provided the netting is securely fastened to the scaffold deck and the scaffold platform planks are laid tight or the deck of the scaffold is solid. 2. Where netting is provided on the upper level of a supported scaffold, or when provided on a suspended scaffold, the netting need only extend to the height of the toprail. 3. Where the scaffold is installed as an alternative to sidewalk sheds, vertical nets, or adjoining property protection in accordance with Sections 3307, 3308, and 3309 respectively, the netting shall enclose the scaffold for its full height.
3314.9 Supported scaffold. | Supported scaffolds shall meet the requirements of Sections 3314.9.1 through 3314.9.4.
3314.9.1 Height-to-base ratio. | A supported scaffold with a height-to-base ratio (including outriggers supports, if used) of more than four to one (4:1) shall be restrained from tipping by guying, tying, bracing or equivalent means as follows:
3314.9.2 Foundation. | Supported scaffold poles, legs, posts, frames and uprights shall bear on base plates and mud sills or other adequate firm foundation to distribute the weight of the scaffold into the ground, structure, or sidewalk shed upon which it rests. Unstable objects shall not be used to support scaffolds or platform units.
3314.9.3 Plumb. | Supported scaffold poles, legs, posts, frames, and uprights shall be plumb and braced to prevent swaying and displacement. The tolerance shall not exceed L/100, where L is the distance measured from the ground or grade elevation to the first cross brace or bottom of the first bearer or frame horizontal member.
3314.9.4 Supported scaffolds at the edge. | Supported scaffolds located on a floor, working deck, or roof and located within a distance from the edge of the roof or an unenclosed perimeter that is equal to or less than one and one-half times the height of the scaffold shall: 1. Be positively anchored or tied-back, and with all wheels or rollers secured by rope, cable, or chocking at the wheels in order to prevent movement; and 2. Have all sides of the scaffold facing an unenclosed perimeter or the edge of a roof within a distance that is equal to or less than one and one-half times the height of the scaffold provided with guardrails and debris netting in accordance with Section 3314.8; or 3. Have all material and equipment susceptible to dislodgement, and not being actively held by a person, secured in a manner to prevent dislodgement by wind or accidental impact. Exception: The above requirements shall not apply where vertical safety netting that meets the requirements of Section 3308.5, or an approved alternate system, extends to cover the full height and width of all unenclosed perimeters within a distance from the scaffold equal to or less than one and one-half times the height of the scaffold.
3314.10 Suspended scaffold. | Suspended scaffolds shall meet the requirements of Sections 3314.10.1 through 3314.10.14.
3314.10.1 Suspended elements to be kept vertical and parallel. | Suspended scaffolds shall be installed and used in such a manner that the ropes or similar suspension elements are vertical and/or in a plane parallel to the wall at all times. Exception: Ropes or similar suspension elements do not have to be vertical and/or in a plane parallel to the wall provided such occurs in accordance with design drawings prepared by a registered design professional. Such design drawings shall be based on an investigation of the support surface/structure (e.g. roof, parapet) and anchorage of the scaffold conducted by such registered design professional. A signed, sealed, and dated report prepared by the registered design professional documenting such investigation shall accompany the design drawings.
3314.10.2 Support. | All suspended scaffold support devices, such as outrigger beams, C-hooks, parapet clamps, and similar devices shall be supported by surfaces/structures (e.g. roof, parapet) capable of supporting at least four times the load imposed on them by the scaffold operating at the rated load of the hoist. The support shall be inspected prior to installation in accordance with the requirements of Section 3314.4.3.1.
3314.10.3 Outrigger beam location. | Outrigger beams shall be placed perpendicular to the face of the building or structure. Exception: Where a licensed rigger or registered design professional can demonstrate to the commissioner’s satisfaction that it is not possible to place an outrigger beam perpendicular to the face of the building or structure, the outrigger beam may be placed at a different angle, provided opposing angle tiebacks are used.
3314.10.4 Outrigger beam stabilization. | The inboard ends of the suspended scaffold outrigger beam shall be stabilized by bolts or other direct connections to the floor or roof deck, or they shall have their inboard ends stabilized by counterweights. Exception: Multipoint adjustable suspended scaffolds shall not be stabilized by counterweights.
3314.10.5 Outrigger beams secured by tiebacks. | Outrigger beams which are not stabilized by bolts or other direct connections to the floor or roof deck shall be secured by tiebacks.
3314.10.6 Outrigger beam installation. | Outrigger beams shall be installed with all bearing supports perpendicular to the beam centerline and shall set and maintain the web in a vertical position. The shackle or clevis with which the rope is attached to the outrigger beam shall be placed directly over the centerline of the stirrup.
3314.10.7 Counterweight material. | Only those items specifically designed as counterweights shall be used to counterweight scaffold systems. Counterweights shall be made of a nonflowable material. Sand, gravel and similar materials that can be easily dislocated shall not be used. Construction materials such as, but not limited to, masonry units and rolls of roofing felt, shall not be used as counterweights.
3314.10.8 Counterweight securement. | Counterweights shall be secured by mechanical means to the outrigger to prevent accidental dislodgment.
3314.10.9 Counterweight removal. | Counterweights shall not be removed from an outrigger beam until the scaffold is disassembled.
3314.10.10 Tiebacks. | Tiebacks shall be equivalent in strength to the suspension ropes. Tiebacks shall be secured to a structurally sound anchorage on the building or structure in accordance with Section 3314.6.
3314.10.11 Horizontal tieback location. | Horizontal tiebacks shall be installed perpendicular to the face of the building or structure, or opposing angle tiebacks shall be installed. Single tiebacks installed at an angle are prohibited.
3314.10.12╪ Support devices. | Suspended scaffold support devices, such as C-hooks, cornice hooks, roof hooks, roof irons, parapet clamps or other similar devices shall meet the following requirements:
3314.10.13 Securing suspended scaffolds. | At the end of the shift, and when otherwise required by Section 3314.4.4.6, the suspended scaffold shall be cleared of all equipment and material susceptible to dislodgement and shall be lowered to the street, sidewalk shed, or other location specified in the design drawings required by Section 3314.3.3, or shall be secured to the roof, building, or other structure in accordance with the design drawings required by Section 3314.3.3.
3314.10.14 Stand-off brackets prohibited. | The installation or use of a stand-off bracket is prohibited.
3314.11 Suspension rope. | Suspension ropes on suspended scaffolds shall meet the requirements of Section 3314.11.1 through 3314.11.8.
3314.11.1 Wraps of rope. | When winding drum hoists are used on a suspended scaffold, they shall contain not fewer than four wraps of the suspension rope at the lowest point of scaffold travel. When other types of hoists are used, the suspension ropes shall be long enough to allow the scaffold to be lowered to the level below without the rope end passing through the hoist, or the rope end shall be configured or provided with means to prevent the end from passing through the hoist.
3314.11.2 Repaired rope. | The use of repaired wire rope as suspension rope is prohibited.
3314.11.3 Rope replacement. | Ropes shall be replaced or removed if any of the following conditions exist, and as otherwise prescribed by rule of the department:
3314.11.4 Shielding. | Suspension ropes shall be shielded from heat-producing processes.
3314.11.5 Corrosive substances. | When acids or other corrosive substances are used on a scaffold, the ropes shall be shielded, treated to protect against corrosive substances, or made of a material that will not be damaged by the corrosive substance being used.
3314.11.6 Suspended scaffold welding precautions for arcing prevention. | Precautions shall be taken to prevent the possibility of arcing through the suspension wire rope during welding operations.
3314.11.6.1 Insulated thimble. | An insulated thimble shall be used to attach each suspension wire rope to its hanging support. Excessive suspension wire rope and any additional independent lines from grounding shall be insulated.
3314.11.6.2 Insulating material. | The suspension wire rope shall be covered with insulating material extending at least 4 feet (1219 mm) above the hoist. If there is a tail line below the hoist, it shall be insulated to prevent contact with the platform. The portion of the tail line that hangs free below the scaffold shall be guided or retained or both so that it does not become grounded.
3314.11.6.3 Protective covers. | Each hoist shall be covered with insulated protective covers.
3314.11.6.4 Grounding conductor. | In addition to a work lead attachment required by the welding process, a grounding conductor shall be connected from the scaf­fold to the structure. The size of the connector shall be at least the size of the welding process work lead, and this conductor shall not be in series with the welding process or the work piece.
3314.11.6.5 Disconnected grounding lead. | If the scaf­fold grounding lead is disconnected at any time, the welding machine shall be shut off or the welding lead shall be removed from the scaffold.
3314.11.6.6 Welding rod or lead. | An active welding rod or uninsulated welding lead shall not be allowed to make contact with the scaffold or its suspension system.
3314.11.7 Wire rope clips. | Wire rope clips used on suspended scaffolds shall be in accordance with Sections 3114.11.7.1 through 3314.11.7.4.
3314.11.7.1 Minimum number of clips to be installed. | Where wire clips are used on suspended scaffolds, there shall be a minimum of three wire rope clips installed a minimum of six rope diameters apart.
3314.11.7.2 Installed to manufacturer specifications. | The clips shall be installed according to the manufacturer’s specifications.
3314.11.7.3 Retightening of clips. | The clips shall be retightened to the manufacturer’s specifications after initial loading. Clips shall be inspected and retightened to the manufacturer’s specifications at the start of each work shift thereafter.
3314.11.7.4 U-bolt clips. | When U-bolt clips are used, the U-bolt shall be placed over the dead end of the rope and the saddle shall be placed over the live end of the rope. Exception: U-bolt clips shall not be used at the point of suspension.
3314.11.8 Swaged attachments or spliced eyes. | Swaged attachments or spliced eyes on wire suspension ropes shall not be used unless they are made by the wire rope manufacturer or a qualified person. Where swaged attachments or spliced eyes are made by a qualified person, a representative sample of the assembly shall be tested under the supervision of a licensed rigger or a registered design professional to confirm the assembly will supply the clamping force specified by the wire rope manufacturer or the manufacturer of the hardware. Swaged attachments or spliced eyes shall be provided with a tag by the wire rope manufacturer or the testing entity indicating the capacity of the assembly. Exception: J-bolts shall be designed by a manufacturer and installed in accordance with the manufacturer’s specifications.
3314.12 Wood pole scaffolds. | Wood pole scaffolds shall meet the requirements of Sections 3314.12.1 through 3314.12.9.
3314.12.1 Standard designs. | All wood pole scaffolds 40 feet (12 192 mm) high or less shall be constructed in accordance with the minimum nominal sizes and maximum spacings shown in Tables 3314.12.1 (1) through 3314.12.1 (6). Wood pole scaffolds more than 40 feet (12 192 mm) high shall be designed in accordance with Section 3314.3. |  |  | See BC33 Tables and Figures
3314.12.2 Erection and removal. | When a new working level is desired, the existing planks shall be left undisturbed until the new working level is framed. As the platform level is abandoned with the progress of the work, all members other than the planking, railing and toeboards shall be left intact. When removing a scaffold, the sequence of removing the members shall be the reverse of that used in erection.
3314.12.3 Materials and construction for wood pole scaffolds. | Wood pole scaffold materials and construction shall comply with the following requirements:
3314.12.4 Poles. | Wooden scaffold poles shall be plumb and the foot ends shall be secured against lateral movement. Where wood poles are spliced, the squared end of the upper section shall bear uniformly on the squared end of the lower section and the two ends shall be rigidly fastened together with two or more wood splice plates, each at least 4 feet (1219 mm) in length. The plates shall be placed at right angles to each other, shall overlap the abutting ends of the pole equally, and shall have a combined sectional area not less than 50 percent of the cross sectional area of the pole. Splicing of adjacent poles shall be staggered. Splices shall be close to ledgers, but so located as not to interfere with the fastenings.
3314.12.5 Bracing. | Wood pole scaffolds shall be braced and stayed to prevent movement away from the building. Diagonal or equivalent bracing shall be provided to prevent the poles from moving in a direction parallel to the building face and shall be so installed that every spliced section of every pole is braced to adjacent poles.
3314.12.6 Planking. | Planking shall comply with Items 1 through 3.
3314.12.7 Connections. | Ledgers shall not be spliced between poles but shall overlap the poles at each end by at least 4 inches (102 mm). Where ledgers lap each other, bearing-blocks attached to the pole shall be provided to support the ledger.
3314.12.7.1 Braces. | The ends of all wooden braces shall overlap the nailed fastenings by an amount sufficient to prevent the ends of the braces from splitting.
3314.12.8 Putlogs for single pole scaffolds. | All putlogs shall be set with the greater dimension vertical and shall be long enough to project beyond the outer edge of the poles by at least 12 inches (305 mm). Putlogs shall be supported on the ledger and located against the side of the poles and fastened to either the pole or the ledger. The other end of the putlog shall rest in the wall of the building, with at least a 4 inch (102 mm) bearing, and shall not be notched or cut down, except for light duty scaffolds, which may be notched or cut down to fit into a space made by the removal of a brick. In such cases, the notch shall be made on the top of the putlog just deep enough to permit it to be inserted in the hole in the wall.
3314.12.9 Bearers for independent pole scaffolds. | Bearers shall be set with their greater dimensions vertical, and shall be long enough to project over the ledgers beyond the outer row of poles by at least 12 inches (305 mm) and beyond the inner row of poles by at least 2 inches (51 mm). Bearers shall be supported on the ledgers, located against the sides of the poles and fastened to the ledgers.
3314.13 Fabricated frame scaffolds. | Fabricated frame scaffolds shall meet the requirements of Sections 3314.13.1 through 3314.13.3.
3314.13.1 Bracing. | Frames and panels shall be braced by cross, horizontal or diagonal braces or a combination thereof, which secure vertical members together laterally.
3314.13.2 Vertical joining. | Frames and panels shall be joined together vertically by coupling or stacking pins or equivalent means. Where uplift can occur, the frames or panels shall be locked together vertically by pins or equivalent means.
3314.13.3 Frame scaffold brackets. | Brackets used to support cantilevered loads shall be seated with side-brackets parallel to the frame and end-brackets at 90 degrees (1.57 rad) to the frames shall not be bent or twisted from these positions and shall be used only to support light duty loads of up to 25 pounds per square foot (122.05 kg/m2), unless the design provisions of Section 3314.3 have been met.
3314.14 Outrigger scaffolds (thrust out). | Outrigger scaffolds (thrust out) shall not be used for loading in excess of 50 pounds per square foot (244.1 kg/m2) (medium duty).
3314.14.1 Outrigger beams. | The fulcrum point of the beam shall rest on a secure bearing at least 6 inches (152 mm) in each horizontal dimension. The beam shall be secured against movement and shall be securely braced against tipping at both the fulcrum point and the inboard end.
3314.14.2 Inboard supports. | The inboard ends of outrigger beams shall be securely fixed to resist all vertical, horizontal and torsional forces. Pull-out tests for adhesive and expansions anchors, if used, shall be approved by the commissioner.
3314.15 Two-point adjustable suspended scaffolds. | Two-point adjustable suspended scaffolds shall meet the requirements of Sections 3314.15.1 through 3314.15.7.
3314.15.1 Width and support. | Two-point adjustable suspended platforms shall be at least 20 inches (508 mm) but not more than 36 inches (914 mm) in width unless designed by a registered design professional. Each end of the platform shall be supported by a stirrup or hanger that meets the requirements of Section 3315.15.2, and the platform shall be securely fastened thereto. Not more than two hangers or stirrups shall be used to support one scaffold.
3314.15.2 Hangers or stirrups. | Hangers or stirrups shall be of steel or wrought iron. Each such hanger shall be formed to properly fit the platform and the hoist mechanism. The hanger or stirrup shall be placed at least 6 inches (152 mm) but not more than 18 inches (457 mm) from the end of the platform. Exception: Alternative spacing from the end of the platform may be utilized where the manufacturer so specifies and such alternative spacing is indicated on design drawings developed by a registered design professional.
3314.15.3 Fiber suspension rope. | The use of fiber rope shall be limited to light duty two-point adjustable suspended scaffolds. Fiber rope shall be at least equivalent in strength and suitability to ¾-inch (19 mm) grade #1 unspliced manila rope.
3314.15.3.1 Corrosive substances. | Fiber rope susceptible to damage from corrosive substances shall not be permitted for or near any work involving the use of corrosive substances.
3314.15.3.2 Upper block. | Fiber rope shall not be used where the upper block is more than 100 feet (30 480 mm) or ten stories, whichever is less, above the ground or roof setback.
3314.15.3.3 Fit. | All blocks shall fit the size of rope they carry, and shall be constructed so as not to chafe the rope.
3314.15.4 Combination. | Two or more two-point adjustable suspended scaffolds shall not be combined into one by bridging the distance between them or by any other form of connection.
3314.15.5 Number of workers. | Not more than two people shall be permitted on one scaffold at one time except where the scaffold is designed to hold more. Written permission from the commissioner shall be required for more than two people on the scaffold.
3314.15.6 Device to raise, lower, and hold the scaffold. | Every two-point adjustable suspended scaffold shall be equipped with a device to raise, lower or hold the scaffold in position.
3314.15.7 Platforms. | The platforms of every two-point adjustable suspended scaffold shall be ladder-type, plank-type, beam-type, light-metal type, or another type acceptable to the commissioner.
3314.16 Corner and angle scaffolds. | Corner and angle scaffolds shall comply with the requirements of Sections 3314.16.1 through 3314.16.4.
3314.16.1 Motors. | As many motors as needed shall be provided to maintain the stability of the platform under all operating conditions.
3314.16.2 Maximum number of people. | The number of people allowed on a corner or angle scaffold shall not be more than the number of motors required to keep the scaffold stable, unless otherwise designed by a registered design professional.
3314.16.3 Additional information. | In addition to the information required by Section 3314.3, corner and angle scaffolds shall also contain load capacity and distribution charts and a certification from the registered design professional that he/she has reviewed the manufacturer’s design calculations and testing or prepared sufficient calculations of his/her own and found them to conform to this code.
3314.16.4 Inspection. | The equipment setting for corner and angle scaffolds shall be inspected by the department prior to its use. Additional inspection by the department shall be required each time the equipment is moved to a different position.
3314.17 Multiple-point adjustable suspended scaffolds. | Multiple-point adjustable suspended scaffolds shall comply with the following:
3314.18 Manually propelled, free-standing scaffolds. | All manually propelled free-standing scaffolds shall meet the following requirements:
3314.19 Mast climbers. | Mast climbers shall be designed, constructed, permitted, installed, adjusted, maintained, repaired, used, operated, inspected, and removed in accordance with rules promulgated by the commissioner.
3314.20 Public housing construction projects. | No scaffolding permit issued for construction projects on public housing developments provided by the New York city housing authority shall be renewed unless the commissioner determines that such scaffolding is being used as part of an ongoing construction project. The commissioner shall promulgate such rules and regulations as shall be necessary to implement the provisions of this section.
3315.1 Ramps and runways. | Ramps and runways (including elevated walkways) shall comply with the requirements of Sections 3315.1.1 through 3315.1.7, as well as rules promulgated by the commissioner.
3315.1.1 Construction. | All runways and ramps shall be constructed, braced and supported to resist lateral displacement and all vertical loads, including impact.
3315.1.2 For motor vehicle use. | Runways and ramps for the use of motor vehicles may consist of an earthfill or may be structurally supported. Such runways and ramps shall have a clear width of not less than 12 feet (3658 mm) with solid curbs or barriers at least 8 inches by 8 inches (203 mm by 203 mm) placed parallel to, and secured to, the sides of the runway or ramp. The flooring of structurally supported ramps shall consist of no smaller than 3-inch (76 mm) planking full size, undressed, or equivalent material, with spans designed for the loads to be imposed. Runways and ramps used by both motor vehicles and persons must also comply with requirements for runways and ramps used by persons. Runways and ramps dedicated exclusively to motor vehicles do not have to comply with requirements for runways and ramps used by persons.
3315.1.3 For use by persons. | Runways and ramps used by persons shall be at least 2 feet (610 mm) in clear width. Where used for wheelbarrows, handcarts, or hand-trucks, runways and ramps shall be at least 3 feet (914 mm) in clear width. Flooring shall consist of at least 2-inch (51 mm) planking spanning as permitted by Table 3314.5.2, laid close, butt-joined and securely fastened. |  |  | See BC33 Tables and Figures
3315.1.4 Slope limitations. | Ramps shall have a slope not steeper than one in four. If the slope is steeper than one in eight, the ramp shall be provided with cleats spaced not more than 14 inches (356 mm) apart and securely fastened to the planking to afford a foothold. Spaces in the cleats may be provided for the passage of the wheels of vehicles. The total rise of a continuous ramp used by persons carrying material or using wheelbarrows, hand-carts, or hand-trucks shall not exceed 12 feet (3658 mm) unless broken by horizontal landings at least 4 feet (1219 mm) in length.
3315.1.5 Guardrail required. | A guardrail meeting the requirements of Sections 3308.7.1 through 3308.7.7 shall be provided in any of the following circumstances:
3315.1.6 Netting required. | Where it is possible for the public to pass under, or next to, runways or ramps, the space between the top rail and the toeboard shall be enclosed with a wire screen comprised of not less than number 18 gauge wire mesh, or equivalent synthetic netting that is flame retardant in accordance with NFPA 701, with openings in the wire or synthetic mesh no larger than ½ inch (13 mm) in the vertical or horizontal dimensions and ¾ inch (19 mm) in any other dimension.
3315.1.7 Signage required. | At every access point to a runway or ramp, a sign shall be posted indicating whether the runway or ramp, or a portion thereof, is intended for use by motor vehicles or by persons.
3315.2 Platforms. | Platforms shall comply with the requirements of Sections 3315.2.1 through 3315.2.3.
3315.2.1 Planking. | Platforms shall have a floor consisting of at least 2-inch (51 mm) planking spanning as permitted by Table 3314.5.2. Planking shall be laid close and shall be butt-joined and securely fastened. Exceptions: 1. Where the platform is to be used to support loads in excess of 75 psf (366.2 kg/m2), or is intended for a use as specified in rules promulgated by the commissioner, the platform shall be designed by a registered design professional. 2. Where the platform is to be used by motorized equipment, including but not limited to trucks, power buggies, fork lifts, or scissor lifts, the platform shall be designed by a registered design professional. |  |  | See BC33 Tables and Figures
3315.2.2 Guardrail required. | A guardrail meeting the requirements of Sections 3308.7.1 through 3308.7.7 shall be provided in any of the following circumstances: 1. Where an unprotected side or edge is 6 feet (1829 mm) or more above the ground, floor, or other lower level; 2. Along any portion of the runway or ramp that abuts motor vehicle traffic; or 3. Along any portion of the runway or ramp where a person may thereby be exposed to harm from adjoining machinery, electrical equipment, or other hazardous equipment. For the purposes of Section 3315.2.2, the term “floor” in Sections 3308.7.1 through 3308.7.7 shall mean “platform.” Exception: In lieu of a guardrail, the side of the platform used for the loading or unloading of vehicles may be protected by a solid curb or barrier at least 8 inches by 8 inches (203 mm by 203 mm) for motor trucks or 4 inches by 4 inches (102 mm by 102 mm) for wheelbarrows and hand-trucks.
3315.2.3 Netting required. | Where it is possible for the public to pass under, or next to, platforms, the space between the top rail and the toeboard shall be enclosed with a wire screen comprised of not less than number 18 gauge wire mesh, or equivalent synthetic netting that is flame retardant in accordance with NFPA 701, with openings in the wire or synthetic mesh no larger than ½ inch (13 mm) in the vertical or horizontal dimensions and ¾ inch (19 mm) in any other dimension.
3315.3 Special requirements where motorized equipment is used. | Runways, ramps, platforms, and other surfaces upon which motorized equipment, including but not limited to trucks, power buggies, fork lifts, or scissor lifts, is operated shall also meet the following minimum requirements:
3316.1 Scope. | Hoisting equipment and material handling equipment shall meet and be used in accordance with the requirements of this section and rules promulgated by the commissioner. Material hoists and bucket hoists shall also meet the requirements of Section 3317, personnel hoists shall also meet the requirements of Section 3318, and cranes and derricks shall also meet the requirements of Section 3319. Certain material handling equipment listed in Section 3320 shall also meet the requirements of that section. Exceptions: The requirements of this section, as well as Sections 3317 through 3320, shall not apply to: 1. Scaffolds. Scaffolds shall comply with the requirements of Section 3314. However, hoisting equipment utilized on scaffolds shall be subject to the requirements of this section. 2. Mast climbers. Mast climbers shall comply with rules promulgated by the commissioner. However, hoisting equipment utilized on mast climbers shall be subject to the requirements of this section. 3. Elevators. Elevators shall comply with the requirements of Chapter 30. 4. Hoisting equipment and material handling equipment, including but not limited to cranes or derricks, used in industrial or commercial plants or yards, other than those used for the construction or demolition of the facility. 5. Hoisting equipment and material handling equipment on ships or barges, including but not limited to floating cranes, floating derricks, and cranes and derricks used on floating equipment. 6. An automotive wrecker, tow truck, or mechanic’s truck with a hoisting device when used to clear vehicular wrecks, haul vehicles, or used in activities related to the maintenance and repair of construction- or demolition-related vehicular equipment. However, this exception shall not apply to the use of such equipment to perform other tasks, including but not limited to hoisting earthwork equipment for the purpose of placing or extracting the earthwork equipment from an excavation. 7. Helicopters. Helicopter lifts shall require a permit from the fire department. 8. Tree trimming or tree removal equipment. However, this exception shall not apply to the use of hoisting equipment capable of lifting or lowering other loads, including but not limited to a crane utilized in conjunction with tree trimming or tree removal.
3316.2 Requirements. | Hoisting equipment and material handling equipment, including supports and runback structures, shall be installed, operated, used, and maintained to eliminate hazard to the public or to property.
3316.3 Notification of incidents involving hoisting equipment or material handling equipment. | The requirements of Section 3301.8 shall apply.
3316.3.1 Additional notification requirement for hoisting machines. | In addition to the requirements of Section 3301.8, the operator of a hoisting machine shall immediately notify the department, in a form and manner acceptable to the commissioner, of any incident involving the use of the hoisting machine, or of any damage to adjoining property caused by the use of the hoisting machine.
3316.4 Permit for power operated hoisting equipment. | No power operated hoisting equipment, including supports and runback structures, shall be installed until the equipment user has obtained a permit in accordance with the requirements of Chapter 1 of Title 28 of the Administrative Code. Exceptions: 1. A hoisting equipment permit is not required for equipment that is exempted from the requirements of Sections 3316.1 or 3319.1. 2. A hoisting equipment permit is not required for equipment, other than a crane, derrick, bucket hoist, material hoist, personnel hoist, or industrial rope access equipment, used exclusively to make deliveries to the site or service the site, and not used to perform construction or demolition work. 3. A hoisting equipment permit is not required for a power-operated, nonguided hoist with a maximum capacity of one ton or less and installed on new construction, or on alterations where the operation of the hoist is confined within the property and the site is pro¬tected in accordance with Section 3307. 4. A hoisting equipment permit issued under the provisions of this section is not required for cranes and derricks. Permits for cranes and derricks shall be in accordance with Section 3319.3.
3316.5 Design, installation, and inspection. | Hoisting equipment and material handling equipment, including supports and runback structures, shall be designed, installed, and inspected in accordance with the manufacturer’s specifications, the requirements of this code, and rules promul­gated by the commissioner. If there is a discrepancy, the stricter requirement shall be met.
3316.6 Rope inspection and replacement. | All ropes used in hoisting equipment and material handling equipment shall meet the inspection and replacement requirements specified in the manufacturer’s specifications, the requirements of this code, and rules promulgated by the commissioner. If there is a dis­crepancy, the stricter requirement shall be met.
3316.7 Operation. | Hoisting equipment and material handling equipment, including supports and runback structures, shall be operated in accordance with the manufacturer’s specifications, the requirements of this code, and rules promulgated by the commissioner. If there is a discrepancy, the stricter requirement shall be met.
3316.7.1 Operators and signalpersons. | Operators and signalpersons shall be qualified for the operation they perform. Only operators designated by the equipment user shall operate hoisting equipment and material handling equipment. Operators of hoisting machines shall be licensed where required by Article 405 of Title 28 of the Administrative Code. Signalpersons shall be trained or certified where required by Section 3316.9.2 of this code. Operators of hoisting equipment and material handling equipment shall familiarize themselves with manufacturer specifications and applicable plans for the hoisting equipment prior to operating the hoisting equipment at the site and whenever such specifications or plans are revised or amended.
3316.7.2 Use during installation, jumping, dismantling or alteration. | Personnel and building materials connected with or related to the building project shall not be moved by the hoisting equipment or material handling equipment while such equipment is being installed, jumped, dismantled, or altered.
3316.7.3 Preventing unauthorized operation. | It shall be unlawful to operate any hoisting equipment or material handling equipment that is not provided with a positive means for preventing the unauthorized operation of such equipment. The means whereby the equipment may be made inoperative shall be acceptable to the department.
3316.7.4 Securing equipment. | The operator of the hoisting equipment or material handling equipment shall park and secure the equipment at the end of the shift and as weather or site conditions otherwise warrant. The operator of the hoisting equipment or material handling equipment shall make the equipment inoperative before leaving the equipment.
3316.7.5 Loading. | Loading of hoisting equipment and material handling equipment shall be conducted in accordance with the following requirements:
3316.7.6 Refueling. | Refueling of hoisting equipment and material handling equip­ment shall be conducted in accordance with the following requirements:
3316.7.7 Work area control. | The equipment user shall provide and maintain measures, including but not limited to warning signs, barriers, or flagpersons, to prevent the public from coming into contact with or passing under hoisting equipment or material handling equipment. Exception: For cranes or derricks, the work area shall be controlled in accordance with rules promulgated by the commissioner.
3316.7.8 Wind and weather. | Hoisting equipment located on the roof or setback of a building, exterior to a building or structure, on a working deck, or in an area with an unenclosed perimeter, is subject to the following wind and weather restrictions. Exception: Cranes and derricks shall not be subject to the requirements of this section. Wind and weather restrictions for cranes and derricks shall be in accordance with the requirements of Section 3319.13 and rules promulgated by the commissioner.
3316.7.8.1 Start of work. | No operator of hoisting equipment shall start a pick when:
3316.7.8.2 In-service. | During picks it is the responsibility of the operator of the hoisting equipment to safely bring the pick to a stop and safely land the load when:
3316.7.8.3 Out-of-service. | At the end of the shift, or as weather conditions otherwise warrant, the operator of the hoisting equipment must properly park or secure the hoisting equipment for occurring or forecasted winds in accordance with the specifications of the manufacturer of the hoisting equipment and applicable plans.
3316.7.8.4 Assembly/disassembly. | The assembly/disassembly of hoisting equipment, including but not limited to the installation, jumping, or dismantling of the hoisting equipment, shall not begin when:
3316.7.8.5 Determining wind speed. | Wind speed shall be determined based on data from the nearest United States weather bureau reporting station, or an anemometer located at the site, freely exposed to the wind, and calibrated in accordance with ASTM D5096-02. Exception: For cranes and derricks, the requirements of Section 3319.13 shall apply.
3316.7.8.6 Assist equipment. | The requirements of Sections 3316.7.8.1 through 3316.7.8.5 shall also apply to assist equipment utilized in conjunction with the assembly/disassembly of hoisting equipment.
3316.8 Maintenance and repair. | Hoisting equipment and material handling equipment, including supports and runback structures, shall be maintained and repaired in compliance with the manufacturer’s specifications, the requirements of this code, and rules promulgated by the commissioner. If there is a discrepancy, the stricter requirement shall be met.
3316.9 Rigging. | The hoisting or lowering of any suspended article on the outside of any building in the city shall be performed in accordance with the requirements of Sections 3316.9.1 through 3316.9.3.
3316.9.1 Supervision. | The hoisting or lowering of any suspended article on the outside of any building in the city shall be performed by or under the direct and continuing supervision of a licensed rigger. Exceptions: 1. In lieu of a licensed rigger, the hoisting or lowering of a sign may be performed by or under the direct and continuing supervision of a licensed sign hanger. 2. Suspended scaffold operations shall meet the requirements of Section 3314. 3. In lieu of a licensed rigger, the hoisting or lowering of any suspended article on the outside of any building in the city may be performed by or under the supervision of a competent person designated by the contractor using the equipment provided the following conditions are met: 3.1 The hoisting or lowering occurs in conjunction with: 3.1.1 The construction of a new building; 3.1.2 The full demolition of an existing building; 3.1.3 The vertical or horizontal enlargement of an existing building; or 3.1.4 The alteration, maintenance, or repair of a façade of a major building where a site safety plan is required by Section 3310.3. 3.2 All individuals involved in the work are certified or trained in accordance with Section 3316.9.2, where such certification or training is required; 3.3 The hoisting or lowering does not meet the definition of industrial rope access; 3.4 The article being hoisted or lowered is not a boiler or tank; 3.5 The article being hoisted or lowered is not related to the assembly, jumping, or disassembly of a tower crane; and 3.6 Where the hoisting or lowering operation meets the definition of a critical pick, such critical pick is: 3.6.1 Performed in accordance with a plan developed by either a: 3.6.1.1 Licensed master rigger; or 3.6.1.2 Registered design professional who has demonstrated knowledge or experience with safe loads and computation thereof, types of rigging, size and strength of ropes, cables, blocks, and any other rigging equipment to be used during the critical pick; and 3.6.2 Immediately prior to the pick, onsite verification is made to ensure conformance with the plan by either: 3.6.2.1 The licensed master rigger who developed the plan; 3.6.2.2 The registered design professional who developed the plan; or 3.6.2.3 A registered design professional employed by and working under the direct supervision of the registered design professional who developed the plan. 4. Where the hoisting or lowering is performed under the direct and continuing supervision of a licensed rigger, a specialty crew who is not in the direct employ of the licensee or business of the licensee may be utilized, provided: 4.1 The work requires a specialty trade, including but not limited to work with hazardous materials or chemicals; 4.2 The crew is in accordance with rules promulgated by the commissioner; and 4.3 The members of the crew are approved by the commissioner.
3316.9.1.1 Supervisor. | The individual supervising the hoisting or lowering in accordance with Section 3316.9.1 shall:
3316.9.2 Certification or training. | All members of the rigging crew engaged in the hoisting or lowering of any suspended article on the outside of any building in the city, the supervisor of such individuals, and signalpersons communicating with such individuals, shall either: 1. Possess a valid certification for both rigging and signaling. The certification shall be acceptable to the commissioner and issued by a rigging and signaling certification program that is accredited by the National Commission for Certifying Agencies (NCCA) or the American National Standards Institute (ANSI). The certification shall be valid for a term of no more than five years before it has to be renewed and shall cover areas including, but not limited to, the inspection and use of rigging hardware, basic rigging techniques, signaling, and hazards associated with rigging. The certification for a supervisor shall, in addition to the foregoing, include calculations and problem solving with respect to rigging; or 2. Have completed an initial department-approved training course, and four years following the completion of the initial training course, and every four years thereafter, complete a department-approved refresher course. The courses shall be in accordance with the following: 2.1 The initial training course for members of the rigging crew, including signalpersons communicating with such crew, shall be, at a minimum, 16 hours long, with the refresher course, at a minimum, 8 hours long. The initial training course for a supervisor shall be, at a minimum, 32 hours long, with the refresher course, at a minimum, 16 hours long. 2.2 The training course shall be conducted by a registered New York State Department of Labor apprenticeship training program or by an educational institution or school chartered, licensed or registered by the New York State Department of Education or by a provider approved by the department and presented by an instructor acceptable to the commissioner. 2.3 Training courses and refresher courses shall cover areas including, but not limited to, the inspection and use of rigging hardware, basic rigging techniques, signaling, and hazards associated with rigging. The training course and refresher course for a supervisor shall, in addition to the foregoing, include calculations and problem solving with respect to rigging. The training course and refresher course, both for crew members and supervisors, shall include a significant portion of hands on training. 2.4 Successful completion of the initial training course and refresher course shall be based upon passage of a written and a practical exam. 2.5 Successful completion of the initial training course and refresher course shall be evidenced by a wallet size certificate card issued by the training provider and acceptable to the commissioner. Such certificate card shall be readily available to the commissioner upon request and shall contain, at a minimum, the following information: 2.5.1 The name of the individual to whom it was issued; 2.5.2 A photograph of the individual to whom it was issued; and 2.5.3 Any other information required pursuant to rules promulgated by the commissioner for a department approved training course. 2.6 For individuals who fail to complete the required refresher course within any 4 year period, a refresher course shall be considered timely if completed within 1 year after the expiration date of the last previously completed initial or refresher course. During such period, such individual shall not perform or supervise any activity for which the lapsed training is required to perform or supervise such activity until such individual has successfully completed such refresher course. Where more than 1 year has lapsed, such individual shall be required to successfully recomplete the initial training course. Exceptions: Training or certification is not required for: 1. Individuals working under the direct and continuing supervision of a licensed rigger or sign hanger. 2. The loading or unloading of a material delivery truck provided the material is loaded or unloaded only between the ground and the truck, or vice versa, and also provided that the material is not raised more than 12 feet (3658 mm) above the bed of the truck during the loading or unloading process. 3. The use of hoisting equipment that has a manufacturer’s rated capacity of 2,000 pounds (907 kg) or less. 4. The use of equipment that is exempted from the requirements of Section 3316.1 or Section 3319.1 of the building code. 5. The use of industrial rope access equipment, which shall instead meet the requirements of Section 3316.9.3.
3316.9.3 Industrial rope access. | Any person using industrial rope access methods to descend or ascend outside a building, including the individual supervising such, must be certified by either the Society of Professional Rope Access Technicians (“SPRAT”) or the Industrial Rope Access Trade Association (“IRATA”), or an equivalent acceptable to the department. Only hand tools, securely attached to a person, may be carried by such person during the use of industrial rope access methods. Any other tools or equipment must be separately hoisted or lowered.
3316.10 Special provisions for cableways. | The construction, installation, inspection, maintenance, and use of cableways shall be in accordance with rules promulgated by the commissioner.
3317.1 Scope. | Material hoists and bucket hoists shall meet and be used in accordance with the requirements of this section, Section 3316, and rules promulgated by the commissioner. Exception: Equipment that is exempted from the requirements of Section 3316.1.
3317.2 Permit. | Material hoists and bucket hoists shall require a permit in accordance with Section 3316.4.
3317.3 Design and inspection. | Material hoists, bucket hoists and their components shall be designed and inspected in accordance with rules promulgated by the commissioner.
3317.4 Construction. | Material hoists, bucket hoists and their components shall be constructed in compliance with the manufacturing specifications, the requirements of this code, and rules promulgated by the commissioner. If there is a discrepancy, the stricter requirement shall be met.
3317.5 Operation. | Notwithstanding any other provision of law, material hoists with a manufacturer’s capacity over one ton shall be operated only by persons holding a Class A or B hoisting machine operators license except during installation, jumping, dismantling or alteration operations.
3317.6 Making safety devices inoperative. | No person shall at any time make any required safety device or electrical protective device inoperative except when necessary during tests, inspections, and maintenance.
3318.1 Scope. | Personnel hoists shall meet and be used in accordance with the requirements of this section, Section 3316, and rules promulgated by the commissioner. Exception: Equipment that is exempted from the requirements of Section 3316.1.
3318.2 Permit. | Personnel hoists shall require a permit in accordance with Section 3316.4.
3318.3 Design and inspection. | Personnel hoists and their components shall be designed and inspected in accordance with rules promulgated by the commissioner.
3318.4 Construction. | Personnel hoists and their components shall be constructed in compliance with the manufacturer’s specifications, this code, and rules promulgated by the commissioner. If there is a discrepancy, the stricter requirement shall be met.
3318.5 Operation. | Personnel hoists and their components shall be operated in accordance with this code and rules pro­mulgated by the commissioner.
3318.6 Making safety devices inoperative. | No person shall at any time make any required safety device or electrical protective device inoperative except when necessary during tests, inspections and maintenance.
3319.1 Scope. | Cranes and derricks shall meet and be used in accordance with the requirements of this section, Section 3316, and rules promulgated by the commissioner. Exceptions: The requirements of this section shall not apply to: 1. Equipment that is exempted from the requirements of Section 3316.1. 2. Material delivery trucks when used to load and unload material, provided such material is loaded or unloaded only between the ground and the truck, or vice versa, and also provided that the material is not raised more than 12 feet (3658 mm) above the bed of the truck during the loading or unloading process. 3. Excavation or earth-moving equipment, including but not limited to power shovels, excavators, wheel loaders, backhoes, loader backhoes, and truck loaders. However, this exception shall not apply when such equipment is used to lift or lower a suspended load more than 12 feet (3658 mm) above the level of the ground. This exception further shall not apply to equipment designed primarily to lift or lower a suspended load, including but not limited to a mobile crane with a clamshell. 4. Excavation or earth-moving equipment equipped with a pile driving attachment. However, this exception shall not apply when such equipment is configured to lift or lower a suspended load not related to the pile driving operation. This exception further shall not apply to dedicated pile drivers, nor shall it apply to equipment designed primarily to lift or lower a suspended load, including but not limited to a mobile crane with a pile driving attachment. 5. Drilling equipment, including but not limited to augers, churn-drills, dedicated drilling rigs, and excavators equipped with a drilling attachment. However, this exception shall not apply when such equipment is configured to lift or lower a suspended load not related to the drilling operation. This exception further shall not apply to equipment designed primarily to lift or lower a suspended load, including but not limited to a mobile crane with a drilling attachment. 6. Digger derricks used in conjunction with the installation, alteration, maintenance, or removal of electric or telecommunication transmission/distribution lines and associated equipment. 7. Demolition equipment, including but not limited to vertical concrete chippers and high reach demolition equipment. However, this exception shall not apply when such equipment is configured to lift or lower a suspended load. This exception further shall not apply to equipment designed primarily to lift or lower a suspended load, including but not limited to a crane assisting with demolition operations. 8. Powered industrial trucks (forklifts). However, this exception shall not apply when such equipment is used to lift or lower a suspended load. 9. Aerial work platforms, including but not limited to vehicle-mounted aerial devices for lifting personnel, and self-propelled elevating work platforms. However, this exception shall not apply when such equipment is configured to both lift or lower a suspended load and function as an aerial work platform. This exception further shall not apply to equipment designed primarily to lift or lower a suspended load, including but not limited to a mobile crane equipped with a manbasket. 10. Concrete pumping equipment not capable of lifting or lowering any suspended loads. 11. Machinery that hoists by using a come-a-long or chainfall. 12. Roustabouts.
3319.2 Personnel. | Personnel shall comply with Sections 3319.2.1 through 3319.2.3.
3319.2.1 Hoisting machine operators. | The hoisting machine operator shall be licensed as required by Chapter 4 of Title 28 of the Administrative Code.
3319.2.2 Riggers. | Rigging work must be supervised in accordance with Section 3316.9.1 and where required, riggers must be licensed in accordance with Chapter 4 of Title 28 of the Administrative Code.
3319.2.3 Lift directors. | Lift directors shall be designated, and perform the duties assigned to them, in accordance with rules promulgated by the commissioner. Such duties shall include, but not be limited to, ensuring compliance with approved plans, traffic and pedestrian controls, and weather restrictions.
3319.3 Certificates required. | No owner, equipment user, or other person shall authorize or permit the use or operation of a crane or derrick that does not possess and/or is not in conformance with a certificate of approval, certificate of operation, and certificate of on-site inspection. The certificates are valid only if the conditions and statements contained in the approved application are complied with, and the crane or derrick is used or operated in conformance with the provisions of this code and the rules applicable thereto. Exceptions: The requirement for a certificate of approval, certificate of operation, and a certificate of on-site inspection shall not apply to the following: 1. Cranes or derricks performing an emergency use pursuant to the lawful order of the head of any department. 2. Cranes or derricks with a manufacturer’s rated capacity of 1 ton (907 kg) or less. 3. Mobile cranes, including jibs and any other extensions to the boom, not exceeding 50 feet (15 240 mm) in length and with a manufacturer’s rated capacity of 3 tons (2722 kg) or less. 4. Mobile cranes, including jibs and any other extensions to the boom, exceeding 50 feet (15 240 mm) but not exceeding 135 feet (41 148 mm) in length, and with a manufacturer’s rated capacity of 3 tons (2722 kg) or less, except that a certificate of operation, as pro¬vided for in Section 3319.5, shall be required. 5. Mobile cranes of a limited size and capacity, or performing a limited use, and exempted from the requirements for a certificate of approval, certificate of operation, or a certificate of on-site inspection in accordance with rules promulgated by the commissioner.
3319.4 Certificate of approval. | Certificates of approval shall comply with the following:
3319.5 Certificate of operation. | Certificates of operation shall comply with the following:
3319.6 Certificate of on-site inspection. | Certificates of on-site inspection shall comply with the following:
3319.7 Temporary certificates. | The commissioner may issue temporary certificates of approval, operation, or on-site inspection for any crane or derrick during the pendency of an application for the certificate and upon inspection, analysis, and testing as the commis­sioner may deem necessary. The commissioner may place appropriate restrictions on a crane or derrick operating under a temporary certificate, and may revoke such temporary certificates if the underlying application is denied.
3319.8 Special provisions for tower cranes. | Tower cranes shall comply with the requirements of Sections 3319.8.1 through 3319.8.8. Exceptions: The requirements of Sections 3319.8.1 through 3319.8.8 shall not apply to: 1. The installation of a tower crane foundation, anchor stool, and first mast section, provided such installations are in accordance with rules promulgated by the commissioner. 2. The assembly or disassembly of a self-erecting tower crane, provided the assembly/disassembly proceeds in accordance with rules promulgated by the commissioner.
3319.8.1 Plan for the erection, jumping, and dismantling of tower cranes. | An erection, jumping, and dismantling plan for tower cranes, other than truck and crawler mounted tower cranes, shall be submitted to the department by a licensed engineer. The plan must be prepared by a licensed engineer in conjunction with a licensed rigger and must be in compliance with the manufacturer’s recommendation for erection, jumping, or dismantling of the specific crane where such manufacturer’s recommendations exist. The plan must be filed with the certificate of on-site inspection application as required by Section 3319.3. No erection, jumping, or dismantling of a tower crane shall take place without the prior issuance of a certificate of on-site inspection by the cranes and derricks unit. The plan shall include the following:
3319.8.2 Safety coordination meeting. | The equipment user must hold a safety coordination meeting prior to the initial erection, as well as the dismantling or initial jump down, of a tower crane. No work related to the erection, jumping or dismantling of the tower crane may be performed without the safety coordination meeting having taken place. The following parties must be present at the safety coordination meeting:
3319.8.3 Pre-jump safety meeting. | The equipment user must coordinate a pre-jump safety meeting no more than 24 hours prior to each instance of a tower crane jump. No work related to the jumping of the tower crane may be performed without the pre-jump safety meeting having taken place. The following parties must be present at the pre-jump safety meeting:
3319.8.4 Department notification. | The equipment user shall notify the department at least 48 hours in advance of the erection, jumping, or dismantling of a tower crane. No work related to the erecting, jumping, or dismantling of the tower crane is to be performed without such notification having been given to the department. The notification shall include the following information:
3319.8.5 Safety coordination and pre-jump safety meeting topics. | The following topics are to be covered during safety coordination and pre-jump safety meetings:
3319.8.6 Meeting log. | The equipment user, or his or her designee, and/or the company erecting, jumping, or dismantling the tower crane shall keep a log on site and available to the department at all times that shall include:
3319.8.7 Inspection and certification by the engineer of record. | Prior to jumping a tower crane, the engineer of record for the crane must provide the department with a certified, signed, and sealed report stating that:
3319.8.8 Erection, jumping, and dismantling operations. | The erection, jumping, and dismantling operations for tower cranes shall be subject to the following requirements:
3319.9 Slings. | Slings shall be used in accordance with the following requirements and any rules promulgated by the commissioner.
3319.9.1 Use of synthetic slings in conjunction with tower crane erection, jumping, and dismantling. | Synthetic slings shall only be used in conjunction with tower crane erection, jumping, and dismantling if the manufacturer’s manual specifically states or recommends the use of synthetic slings. Synthetic slings shall not be used unless softening mechanisms have been applied to all sharp edges.
3319.9.2 Discarded rope. | Discarded rope shall not be used for slings.
3319.10 Worker training. | The training of workers engaged in the erection, jumping, or dismantling of a tower crane, including the licensed rigger and the rigger foreman, shall be in accordance with the requirements of Section 3319.10.1 and 3319.10.2. Exceptions: The requirements of this section shall not apply to: 1. The installation of a tower crane foundation, anchor stool, and first mast section. 2. The assembly or disassembly of a self-erecting tower crane, provided workers engaged in the assembly/disassembly operation have been trained in accordance with rules promulgated by the commissioner.
3319.10.1 Training Requirements. | All workers engaged in the erection, jumping, or dismantling of a tower crane, including the licensed rigger and the rigger foreman, shall have satisfactorily completed a department-approved training course of not less than thirty hours. Such course shall, at a minimum, include instruction on fall protection, crane assembly and disassembly, pre-lift planning, weights and materials, the use of slings, lifting/lowering loads, signaling and other proper means of communication with the crane operator, crane and hoist inspections, rigging requirements, and generally how to avoid incidents with cranes and hoists. The commissioner may by rule identify additional types of cranes for which such training is necessary. Any person who, within the three years prior to the effective date of this section, has successfully completed at least a thirty-hour training course need not take a second thirty-hour course, provided such person can provide to the department a dated certificate as set forth in this section evidencing completion of such a training course. Such person shall, however, take a department-approved eight-hour re-certification course within three years of the initial course and every three years thereafter. Successful completion of the training or re-certification course shall be evidenced by a dated certificate issued by the provider of the training or re-certification course. The certificate shall include such information as specified by the department by rule. The certificate, or a valid wallet card version thereof, shall be readily available to the commissioner upon request.
3319.10.1.1 Training providers. | Such training or refresher course shall be conducted (i) pursuant to a registered New York state department of labor training program, or (ii) by a provider approved by the department.
3319.10.2 Certification. | Prior to erecting, jumping, or dismantling the tower crane, or other crane type the commissioner specifies by rule, the master or tower crane rigger shall certify in the meeting log, described in Section 3319.8.6, that the rigger foreman and all other members of the “jumping crew” and back-up personnel have satisfactorily completed all training requirements.
3319.11 Crane location device. | No crane operation that requires a certificate of on-site inspection, and other such types of crane operations where identified in rules promulgated by the commissioner, shall commence unless the crane is equipped with a global positioning system, or other similar device, that is approved by the department and capable of transmitting the location of the crane to which it is attached to the department. Where no such system or device has been approved by the department, (i) no crane operation subject to the provisions of this section shall commence until after the department has been notified by the equipment user, in a form and manner approved by the commissioner, of the date upon which the crane will arrive at the site, and (ii) upon the conclusion of the work, the equipment user shall also notify the department, in a form and manner approved by the commissioner, of the date of the departure of the crane from the site. Exception: Crane operations that utilize tower cranes and require submission of an erection, jumping, and dismantling plan to the department by a licensed engineer.
3319.12 Crane event recorder. | No certificate of operation for a crane shall be issued or renewed on or after January 1, 2019, unless the crane is equipped with an event recorder that is supplied by the crane manufacturer, or by a dealer, distributor, vendor, or third-party authorized crane manufacturer. Exception: Cranes where the manufacturer certifies to the department that an event recorder cannot be installed on the crane due to a technological limitation.
3319.12.1 Data to be recorded. | At a minimum, the event recorder shall collect the following data:
3319.12.2 Data to be made available to commissioner upon request. | Data collected by the event recorder shall be made available to the commissioner upon request.
3319.13 Measuring wind. | Wind speed during crane or derrick operations shall be determined in accordance with the requirements of Table 3319.13. Options 1, 2, and 3 in Table 3319.13 shall be in accordance with the requirements of Sections 3319.13.1 through 3319.13.3, respectively. |  |  | See BC33 Tables and Figures
3319.13.1 Option 1: Anemometer on the crane or derrick. | An anemometer provided by the crane or derrick manufacturer, or an entity acceptable to such manufacturer, and installed at the top of the boom or at the location specified by such manufacturer. The anemometer must measure a 3-second gust wind. A real time display of the anemometer must be available to the hoisting machine operator in the crane cab or at the operator’s station. Such anemometer is to be considered an operational aid and must be checked prior to each shift as required by department rules. Exception: Where the manufacturer is no longer in business, or the manufacturer or an entity acceptable to such manufacturer is unable to provide the anemometer, the anemometer may be approved by the department.
3319.13.2 Option 2: Anemometer at the site. | An anemometer located at a high point of the site approximate to the height and location of the crane or derrick boom/jib, freely exposed to the wind, and calibrated in accordance with ASTM D5096-02. The anemometer must measure a 3-second gust wind. A real time display of the anemometer must be available to the hoisting machine operator at the operator’s station, or a person designated by the hoisting machine operator must be provided to monitor the display and alert the hoisting machine operator when measurements near, meet, or exceed the thresholds specified in the approved wind action plan. Such anemometer is to be considered an operational aid and must be checked prior to each shift as required by department rules.
3319.13.3 Option 3: Nearest weather station. | The most recent gust wind speed reported at the nearest National Weather Service weather station. The equipment user must establish a system to ensure the hoisting machine operator is notified when reported wind gusts near, meet, or exceed the thresholds specified in the approved wind action plan. An acceptable system may include engaging a metrological service to provide a text or similar alert to a person designated by the equipment user when wind thresholds are neared, met, or exceeded, and have such designated person notify the hoisting machine operator.
3319.14 Age limitations for cranes. | Only cranes having an age of less than 25 years from the manufacture date may be used in New York City. Notwithstanding the provisions of Section 3319.5, the certificate of operation for a crane with an age greater than 25 years from the manufacture date shall be deemed to have expired. Exceptions: 1. A crane with an age of 25 years or greater from the manufacture date that is (i) in use on a project on January 1, 2019 or (ii) not in use on January 1, 2019, but for which an application for a certificate of on-site inspection has been approved as of January 1, 2019, may continue to be used until completion of the project for which it is being used or the project for which such certificate of onsite inspection was issued. 2. Where a crane with an age of less than 25 years from the manufacture date at the time the department approved the application for a certificate of on-site inspection is being used on a project and will reach an age of 25 years or greater from the manufacture date during such project, such crane may be used for the duration of that project or until it reaches 28 years of age, whichever occurs earlier. 3. The commissioner may approve the use of a crane with an age of 25 years or greater from the manufacture date for up to a maximum of five years, not to exceed 30 years from the manufacture date, when records as required by rule of the department are deemed sufficient by the commissioner to establish that such crane meets the manufacturer’s standards for use. 4. This section shall not apply to equipment used for pile driving or clamshell work.
3320.1 Scope. | Conveyors, trucks, power buggies, lift and fork trucks, hand propelled vehicles, mixing machines, and jacks shall meet and be used in accordance with the requirements of this section, Section 3316, and rules promulgated by the commissioner. Exception: Equipment that is exempted from the requirements of Section 3316.1.
3320.2 Reserved.
3320.3 Reserved.
3320.4 Reserved.
3320.5 Conveyors. | Conveyors shall meet the requirements of Sections 3320.5.1 through 3320.5.3.
3320.5.1 Walkways. | Walkways along belt conveyors or bucket conveyors shall be kept free of materials and, where 5 feet (127 mm) or more above the ground, shall be provided with a guardrail system that meets the requirements of Sections 3308.7.1 through 3308.7.7 along the outside of the walkway. The guardrail system may be omitted on the side toward the belt if the walkway is located adjacent to the conveyor.
3320.5.2 Trippers. | Where trippers are used to control dis­charge, a device for throwing the belt or bucket drive into neutral shall be installed at each end of the runway.
3320.5.3 Spillage. | Where conveyor belts cross any traveled way, trays shall be installed to catch spillage and overhead protection shall be provided for persons or traffic passing beneath.
3320.6 Trucks. | Trucks shall meet the requirements of Sections 3320.6.1 and 3320.6.2.
3320.6.1 Maintenance. | All parts and accessories of trucks shall be kept in repair. Brakes shall be maintained so that the vehicle with full load may be held on any grade that may be encountered on the job. Provision shall be made for the immediate application of wheel blocks to trucks traversing ramps steeper than one in ten.
3320.6.2 Loading. | Trucks shall not be loaded beyond the manufacturer’s rated capacity, nor beyond the legal load limit, where applicable. The loads shall be trimmed before the truck is set in motion to prevent spillage. Loads that project beyond the sides of the truck, or that may be dislodged in transit, shall be removed or securely lashed in place.
3320.7 Power buggies. | Power buggies shall meet the requirements of Sections 3320.7.1 and 3320.7.2.
3320.7.1 Responsibilities of employers and workers. | Employers and workers shall have the following responsi­bilities regarding power buggies:
3320.7.2 Operation and construction. | Power buggies shall be operated and constructed in accordance with the requirements of Sections 3320.7.2.1 through 3320.7.2.4.
3320.7.2.1 Brakes. | Every power buggy shall be provided with brakes and tire surfaces capable of bringing it to a full stop within 25 feet (635 mm) on a level surface that is similar to the one on which it will be used and at full rated load and maximum design speed. Brakes shall be capable of being fixed in engagement to hold the full load stationary on a 25 percent grade.
3320.7.2.2 Accidental starting. | All movement controls of every power buggy shall be so arranged or shielded that they cannot be inadvertently engaged or the buggy accidentally set in motion.
3320.7.2.3 Parking on grades. | No power buggy shall be left unattended on any grade sufficiently steep to cause it to coast if free of engine and brake resistance.
3320.7.2.4 Use on ramps, runways and platforms. | Power buggies shall not be used on ramps, runways, or platforms that do not meet the requirements of Section 3315.
3320.8 Lift and fork trucks. | Lift and fork trucks shall meet the requirements of Sections 3320.8.1 through 3320.8.4.
3320.8.1 Load capacity. | A metal plate with readily legible etched or stamped figures giving the capacity rating in pounds shall be attached to every lift or fork truck.
3320.8.2 Maintenance. | All parts and accessories of lift or fork trucks shall be kept in repair and with brakes adequate to maintain the fully loaded vehicle on any grade that may be encountered on the job.
3320.8.3 Loading. | No lift or fork truck shall be loaded beyond its capacity rating. No hand-operated pallet truck loaded so that any point on the load is at a greater height than 4 feet 6 inches (114 mm) above the floor shall be moved by pushing unless handled by two persons.
3320.8.4 Prohibited use. | No lift or fork truck shall be in motion when the loaded forks are elevated higher than nec­essary to clear obstructions, except as may be required for positioning, picking up, or depositing the load.
3320.9 Hand propelled vehicles. | Hand propelled vehicles shall be constructed and braked to withstand the loads to be carried and shall be maintained in repair. Vehicles with loose parts shall not be used.
3320.10 Mixing machines. | Where the public may have access to the working area near charging skips, guardrails or other adequate protection in accordance with the New York City Department of Transportation shall be erected to enclose the area under the raised skip and the mixing machine. Each time before raising or lowering the charging skip, the operator shall ascertain that no one is in the danger zone.
3320.11 Jacks. | Jacks shall meet the requirements of Sections 3320.11.1 through 3320.11.5.
3320.11.1 Marking. | The rated capacity of every jack shall be legibly marked in a prominent location on the jack by casting or stamping. The manufacturer shall designate the intended supporting point of the load and the maximum permissible length of lever and force applied.
3320.11.2 Overtravel to be limited. | Every jack shall, where practicable, be provided with a positive stop to pre­vent overtravel; otherwise an indicator to clearly show overtravel shall be provided on the jack.
3320.11.3 Maintenance. | Lubrication and operation of jacks shall be in accordance with the recommendations of the manufacturer.
3320.11.4 Foundations. | Jacks shall rest on a firm, level foundation adequate to support the load.
3320.11.5 Blocking required. | When the object has been lifted to the desired height, blocking or cribbing shall be immediately placed under it if the jack does not have built-in safety devices such as stop-rings, locknuts or place-in cylin­der sleeves.
|  | 3301.2 Storage and placement. | Construction equipment and materials shall be stored and placed so as not to endanger the public, the workers or adjoining property for the duration of the construction project.
|  | 3301.2.1 Structural and construction loads. | Structural roof components shall be capable of supporting the roof-covering system and the material and equipment loads that will be encountered during installation of the system.
|  | 3302.1 Alterations, repairs and additions. | Required exits, existing structural elements, fire protection devices and sanitary safeguards shall be maintained at all times during alterations, repairs or additions to any building or structure. Exceptions: 1. Where such required elements or devices are being altered or repaired, adequate substitute provisions shall be made. 2. Maintenance of such elements and devices is not required where the existing building is not occupied.
|  | 3302.2 Manner of removal. | Waste materials shall be removed in a manner that prevents injury or damage to persons, adjoining properties and public rights-of-way.
|  | 3302.3 Fire safety during construction. | Fire safety during construction shall comply with the applicable requirements of this code and the applicable provisions of Chapter 33 of the International Fire Code.
|  | 3303.1 Construction documents. | Construction documents and a schedule for demolition shall be submitted where required by the building official. Where such information is required, work shall not be done until such construction documents or schedule, or both, are approved.
|  | 3303.2 Pedestrian protection. | The work of demolishing any building shall not be commenced until pedestrian protection is in place as required by this chapter.
|  | 3303.3 Means of egress. | A horizontal exit shall not be destroyed unless and until a substitute means of egress has been provided and approved.
|  | 3303.4 Vacant lot. | Where a structure has been demolished or removed, the vacant lot shall be filled and maintained to the existing grade or in accordance with the ordinances of the jurisdiction having authority.
|  | 3303.5 Water accumulation. | Provision shall be made to prevent the accumulation of water or damage to any foundations on the premises or the adjoining property.
|  | 3303.6 Utility connections. | Service utility connections shall be discontinued and capped in accordance with the approved rules and the requirements of the applicable governing authority.
|  | 3303.7 Fire safety during demolition. | Fire safety during demolition shall comply with the applicable requirements of this code and the applicable provisions of Chapter 33 of the International Fire Code.
|  | 3304.1 Excavation and fill. | Excavation and fill for buildings and structures shall be constructed or protected so as not to endanger life or property. Stumps and roots shall be removed from the soil to a depth of not less than 12 inches (305 mm) below the surface of the ground in the area to be occupied by the building. Wood forms that have been used in placing concrete, if within the ground or between foundation sills and the ground, shall be removed before a building is occupied or used for any purpose. Before completion, loose or casual wood shall be removed from direct contact with the ground under the building.
|  | 3304.1.1 Slope limits. | Slopes for permanent fill shall be not steeper than one unit vertical in two units horizontal (50-percent slope). Cut slopes for permanent excavations shall be not steeper than one unit vertical in two units horizontal (50-percent slope). Deviation from the foregoing limitations for cut slopes shall be permitted only upon the presentation of a soil investigation report acceptable to the building official.
|  | 3304.1.2 Surcharge. | Fill or other surcharge loads shall not be placed adjacent to any building or structure unless such building or structure is capable of withstanding the additional loads caused by the fill or surcharge. Existing footings or foundations that can be affected by any excavation shall be underpinned adequately or otherwise protected against settlement and shall be protected against lateral movement.
|  | 3304.1.3 Footings on adjacent slopes. | For footings on adjacent slopes, see Chapter 18.
|  | 3304.1.4 Fill supporting foundations. | Fill to be used to support the foundations of any building or structure shall comply with Section 1804.6. Special inspections of compacted fill shall be in accordance with Section 1705.6.
|  | 3305.1 Facilities required. | Sanitary facilities shall be provided during construction, remodeling or demolition activities in accordance with the International Plumbing Code.
|  | 3306.1 Protection required. | Pedestrians shall be protected during construction, remodeling and demolition activities as required by this chapter and Table 3306.1. Signs shall be provided to direct pedestrian traffic. | See BC33 Tables and Figures
|  | 3306.2 Walkways. | A walkway shall be provided for pedestrian travel in front of every construction and demolition site unless the applicable governing authority authorizes the sidewalk to be fenced or closed. A walkway shall be provided for pedestrian travel that leads from a building entrance or exit of an occupied structure to a public way. Walkways shall be of sufficient width to accommodate the pedestrian traffic, but shall be not less than 4 feet (1219 mm) in width. Walkways shall be provided with a durable walking surface. Walkways shall be accessible in accordance with Chapter 11 and shall be designed to support all imposed loads, and the design live load shall be not less than 150 pounds per square foot (psf) (7.2 kN/m2).
|  | 3306.3 Directional barricades. | Pedestrian traffic shall be protected by a directional barricade where the walkway extends into the street. The directional barricade shall be of sufficient size and construction to direct vehicular traffic away from the pedestrian path.
|  | 3306.4 Construction railings. | Construction railings shall be not less than 42 inches (1067 mm) in height and shall be sufficient to direct pedestrians around construction areas.
|  | 3306.5 Barriers. | Barriers shall be not less than 8 feet (2438 mm) in height and shall be placed on the side of the walkway nearest the construction. Barriers shall extend the entire length of the construction site. Openings in such barriers shall be protected by doors that are normally kept closed.
|  | 3306.6 Barrier design. | Barriers shall be designed to resist loads required in Chapter 16 unless constructed as follows:
|  | 3306.7 Covered walkways. | Covered walkways shall have a clear height of not less than 8 feet (2438 mm) as measured from the floor surface to the canopy overhead. Adequate lighting shall be provided at all times. Covered walkways shall be designed to support all imposed loads. The design live load shall be not less than 150 psf (7.2 kN/m2) for the entire structure. Exception: Roofs and supporting structures of covered walkways for new, light-frame construction not exceeding two stories above grade plane are permitted to be designed for a live load of 75 psf (3.6kN/m2) or the loads imposed on them, whichever is greater. In lieu of such designs, the roof and supporting structure of a covered walkway are permitted to be constructed as follows: 1. Footings shall be continuous 2-inch by 6-inch (51 mm by 152 mm) members. 2. Posts not less than 4 inches by 6 inches (102 mm by 152 mm) shall be provided on both sides of the roof and spaced not more than 12 feet (3658 mm) on center. 3. Stringers not less than 4 inches by 12 inches (102 mm by 305 mm) shall be placed on edge upon the posts. 4. Joists resting on the stringers shall be not less than 2 inches by 8 inches (51 mm by 203 mm) and shall be spaced not more than 2 feet (610 mm) on center. 5. The deck shall be planks not less than 2 inches (51 mm) thick or wood structural panels with an exterior exposure durability classification not less than 23/32 inch (18.3 mm) thick nailed to the joists. 6. Each post shall be knee braced to joists and stringers by members not less than 2 inches by 4 inches (51 mm by 102 mm); 4 feet (1219 mm) in length. 7. A curb that is not less than 2 inches by 4 inches (51 mm by 102 mm) shall be set on edge along the outside edge of the deck.
|  | 3306.8 Repair, maintenance and removal. | Pedestrian protection required by this chapter shall be maintained in place and kept in good order for the entire length of time pedestrians are subject to being endangered. The owner or the owner’s authorized agent, on completion of the construction activity, shall immediately remove walkways, debris and other obstructions and leave such public property in as good a condition as it was before such work was commenced.
|  | 3306.9 Adjacent to excavations. | Every excavation on a site located 5 feet (1524 mm) or less from the street lot line shall be enclosed with a barrier not less than 6 feet (1829 mm) in height. Where located more than 5 feet (1524 mm) from the street lot line, a barrier shall be erected where required by the building official. Barriers shall be of adequate strength to resist wind pressure as specified in Chapter 16.
|  | 3307.1 Protection required. | Adjoining public and private property shall be protected from damage during construction, remodeling and demolition work. Protection shall be provided for footings, foundations, party walls, chimneys, skylights and roofs. Provisions shall be made to control water runoff and erosion during construction or demolition activities. The person making or causing an excavation to be made shall provide written notice to the owners of adjoining buildings advising them that the excavation is to be made and that the adjoining buildings should be protected. Said notification shall be delivered not less than 10 days prior to the scheduled starting date of the excavation.
|  | 3307.2 Excavation retention systems. | Where a retention system is used to provide support of an excavation for protection of adjacent structures, the system shall conform to the requirements in Sections 3307.2.1 through 3307.2.3.
|  | 3307.2.1 Excavation retention system design. | Excavation retention systems shall be designed by a registered design professional to provide vertical and lateral support.
|  | 3307.2.2 Excavation retention system monitoring. | The retention system design shall include requirements for monitoring of the system and adjacent structures for horizontal and vertical movement.
|  | 3307.2.3 Retention system removal. | Elements of the system shall only be removed or decommissioned where adequate replacement support is provided by backfill or by the new structure. Removal or decommissioning shall be performed in such a manner that protects the adjacent property.
|  | 3308.1 Storage and handling of materials. | The temporary use of streets or public property for the storage or handling of materials or of equipment required for construction or demolition, and the protection provided to the public shall comply with the provisions of the applicable governing authority and this chapter.
|  | 3308.1.1 Obstructions. | Construction materials and equipment shall not be placed or stored so as to obstruct access to fire hydrants, standpipes, fire or police alarm boxes, catch basins or manholes, nor shall such material or equipment be located within 20 feet (6096 mm) of a street intersection, or placed so as to obstruct normal observations of traffic signals or to hinder the use of public transit loading platforms.
|  | 3308.2 Utility fixtures. | Building materials, fences, sheds or any obstruction of any kind shall not be placed so as to obstruct free approach to any fire hydrant, fire department connection, utility pole, manhole, fire alarm box or catch basin, or so as to interfere with the passage of water in the gutter. Protection against damage shall be provided to such utility fixtures during the progress of the work, but sight of them shall not be obstructed.
|  | 3309.1 Where required. | Structures under construction, alteration or demolition shall be provided with not fewer than one approved portable fire extinguisher in accordance with Section 906 and sized for not less than ordinary hazard as follows:
|  | 3309.2 Fire hazards. | The provisions of this code and the International Fire Code shall be strictly observed to safeguard against all fire hazards attendant upon construction operations.
|  | 3310.1 Stairways required. | Where building construction exceeds 40 feet (12 192 mm) in height above the lowest level of fire department vehicle access, a temporary or permanent stairway shall be provided. As construction progresses, such stairway shall be extended to within one floor of the highest point of construction having secured decking or flooring.
|  | 3310.2 Maintenance of means of egress. | Means of egress and required accessible means of egress shall be maintained at all times during construction, demolition, remodeling or alterations and additions to any building. Exception: Existing means of egress need not be maintained where approved temporary means of egress systems and facilities are provided.
|  | 3311.1 Where required. | In buildings required to have standpipes by Section 905.3.1, not fewer than one standpipe shall be provided for use during construction. Such standpipes shall be installed prior to construction exceeding 40 feet (12 192 mm) in height above the lowest level of fire department vehicle access. Such standpipes shall be provided with fire department hose connections at locations adjacent to stairways complying with Section 3310.1. As construction progresses, such standpipes shall be extended to within one floor of the highest point of construction having secured decking or flooring.
|  | 3311.2 Buildings being demolished. | Where a building is being demolished and a standpipe exists within such a building, such standpipe shall be maintained in an operable condition so as to be available for use by the fire department. Such standpipe shall be demolished with the building but shall not be demolished more than one floor below the floor being demolished.
|  | 3311.3 Detailed requirements. | Standpipes shall be installed in accordance with the provisions of Chapter 9. Exception: Standpipes shall be either temporary or permanent in nature, and with or without a water supply, provided that such standpipes conform to the requirements of Section 905 as to capacity, outlets and materials.
|  | 3312.1 Completion before occupancy. | In buildings where an automatic sprinkler system is required by this code, it shall be unlawful to occupy any portion of a building or structure until the automatic sprinkler system installation has been tested and approved, except as provided in Section 111.3.
|  | 3312.2 Operation of valves. | Operation of sprinkler control valves shall be permitted only by properly authorized personnel and shall be accompanied by notification of duly designated parties. When the sprinkler protection is being regularly turned off and on to facilitate connection of newly completed segments, the sprinkler control valves shall be checked at the end of each work period to ascertain that protection is in service.
|  | 3313.1 Where required. | An approved water supply for fire protection, either temporary or permanent, shall be made available as soon as combustible building materials arrive on the site, on commencement of vertical combustible construction, and on installation of a standpipe system in buildings under construction, in accordance with Sections 3313.2 through 3313.5. Exception: The fire code official is authorized to reduce the fire-flow requirements for isolated buildings or a group of buildings in rural areas or small communities where the development of full fire-flow requirements is impractical.
|  | 3313.2 Combustible building materials. | When combustible building materials of the building under construction are delivered to a site, a minimum fire flow of 500 gallons per minute (1893 L/m) shall be provided. The fire hydrant used to provide this fire flow supply shall be within 500 feet (152 m) of the combustible building materials, as measured along an approved fire apparatus access lane. Where the site configuration is such that one fire hydrant cannot be located within 500 feet (152 m) of all combustible building materials, additional fire hydrants shall be required to provide coverage in accordance with this section.
|  | 3313.3 Vertical construction of Types III, IV and V construction. | Prior to commencement of vertical construction of Type III, IV or V buildings that utilize any combustible building materials, the fire flow required by Sections 3313.3.1 through 3313.3.3 shall be provided, accompanied by fire hydrants in sufficient quantity to deliver the required fire flow and proper coverage.
|  | 3313.3.1 Fire separation up to 30 feet. | Where a building of Type III, IV or V construction has a fire separation distance of less than 30 feet (9144 mm) from property lot lines, and an adjacent property has an existing structure or otherwise can be built on, the water supply shall provide either a minimum of 500 gallons per minute (1893 L/m), or the entire fire flow required for the building when constructed, whichever is greater.
|  | 3313.3.2 Fire separation of 30 feet up to 60 feet. | Where a building of Type III, IV or V construction has a fire separation distance of 30 feet (9144 mm) up to 60 feet (18 288 mm) from property lot lines, and an adjacent property has an existing structure or otherwise can be built on, the water supply shall provide a minimum of 500 gallons per minute (1893 L/m), or 50 percent of the fire flow required for the building when constructed, whichever is greater.
|  | 3313.3.3 Fire separation of 60 feet or greater. | Where a building of Type III, IV or V construction has a fire separation of 60 feet (18 288 mm) or greater from a property lot line, a water supply of 500 gallons per minute (1893 L/m) shall be provided.
|  | 3313.4 Vertical construction, Types I and II construction. | If combustible building materials are delivered to the construction site, water supply in accordance with Section 3313.2 shall be provided. Additional water supply for fire flow is not required prior to commencing vertical construction of Type I and II buildings.
|  | 3313.5 Standpipe supply. | Regardless of the presence of combustible building materials, the construction type or the fire separation distance, where a standpipe is required in accordance with Section 3313, a water supply providing a minimum flow of 500 gallons per minute (1893 L/m) shall be provided. The fire hydrant used for this water supply shall be located within 100 feet (30 480 mm) of the fire department connection supplying the standpipe.
|  | 3314.1 Fire watch during combustible construction. | A fire watch shall be provided during nonworking hours for construction that exceeds 40 feet (12 192 mm) in height above the lowest adjacent grade at any point along the building perimeter, for new multistory construction with an aggregate area exceeding 50,000 square feet (4645 m2) per story or as required by the fire code official.

## BC34
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED

## BC35
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
3501.1 General. | This chapter lists the standards that are referenced in various sections of this document. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title and the section or sections of this document that reference the standard.
3501.2 Subsequent additions, modifications or deletions. | Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to these standards in accordance with Section 28-103.19 of the Administrative Code.
3501.3 Applicability. | The application of the referenced standards shall be as specified in Section 102.4.

## BC-A
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | A101.1 Building official. | The building official shall have not fewer than 10 years’ experience or equivalent as an architect, engineer, inspector, contractor or superintendent of construction, or any combination of these, 5 years of which shall have been supervisory experience. The building official should be certified as a building official through a recognized certification program. The building official shall be appointed or hired by the applicable governing authority.
|  | A101.2 Chief inspector. | The building official can designate supervisors to administer the provisions of this code and the International Mechanical, Plumbing and Fuel Gas Codes. Each supervisor shall have not fewer than 10 years experience or equivalent as an architect, engineer, inspector, contractor or superintendent of construction, or any combination of these, 5 years of which shall have been in a supervisory capacity. They shall be certified through a recognized certification program for the appropriate trade.
|  | A101.3 Inspector and plans examiner. | The building official shall appoint or hire such number of officers, inspectors, assistants and other employees as shall be authorized by the jurisdiction. A person who has fewer than 5 years of experience as a contractor, engineer, architect, or as a superintendent, foreman or competent mechanic in charge of construction shall not be appointed or hired as inspector of construction or plans examiner. The inspector or plans examiner shall be certified through a recognized certification program for the appropriate trade.
|  | A101.4 Termination of employment. | Employees in the position of building official, chief inspector or inspector shall not be removed from office except for cause after full opportunity has been given to be heard on specific charges before such applicable governing authority.
|  | A102.1 General. | See Table A102.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.

## BC-B
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | B101.1 Scope. | A board of appeals shall be established within the jurisdiction for the purpose of hearing applications for modification of the requirements of this code pursuant to the provisions of Section 113. The board shall be established and operated in accordance with this section, and shall be authorized to hear evidence from appellants and the building official pertaining to the application and intent of this code for the purpose of issuing orders pursuant to these provisions.
|  | B101.2 Application for appeal. | Any person shall have the right to appeal a decision of the building official to the board. An application for appeal shall be based on a claim that the intent of this code or the rules legally adopted hereunder have been incorrectly interpreted, the provisions of this code do not fully apply or an equally good or better form of construction is proposed. The application shall be filed on a form obtained from the building official within 20 days after the notice was served.
|  | B101.2.1 Limitation of authority. | The board shall not have authority to waive requirements of this code or interpret the administration of this code.
|  | B101.2.2 Stays of enforcement. | Appeals of notice and orders, other than Imminent Danger notices, shall stay the enforcement of the notice and order until the appeal is heard by the board.
|  | B101.3 Membership of board. | The board shall consist of five voting members appointed by the chief appointing authority of the jurisdiction. Each member shall serve for years or until a successor has been appointed. The board members’ terms shall be staggered at intervals, so as to provide continuity. The building official shall be an ex officio member of said board but shall not vote on any matter before the board.
|  | B101.3.1 Qualifications. | The board shall consist of five individuals, who are qualified by experience and training to pass on matters pertaining to building construction and are not employees of the jurisdiction.
|  | B101.3.2 Alternate members. | The chief appointing authority is authorized to appoint two alternate members who shall be called by the board chairperson to hear appeals during the absence or disqualification of a member. Alternate members shall possess the qualifications required for board membership, and shall be appointed for the same term or until a successor has been appointed.
|  | B101.3.3 Vacancies. | Vacancies shall be filled for an unexpired term in the same manner in which original appointments are required to be made.
|  | B101.3.4 Chairperson. | The board shall annually select one of its members to serve as chairperson.
|  | B101.3.5 Secretary. | The chief appointing authority shall designate a qualified clerk to serve as secretary to the board. The secretary shall file a detailed record of all proceedings, which shall set forth the reasons for the board’s decision, the vote of each member, the absence of a member and any failure of a member to vote.
|  | B101.3.6 Conflict of interest. | A member with any personal, professional or financial interest in a matter before the board shall declare such interest and refrain from participating in discussions, deliberations and voting on such matters.
|  | B101.3.7 Compensation of members. | Compensation of members shall be determined by law.
|  | B101.3.8 Removal from the board. | A member shall be removed from the board prior to the end of their term only for cause. Any member with continued absence from regular meeting of the board may be removed at the discretion of the chief appointing authority.
|  | B101.4 Rules and procedures. | The board shall establish policies and procedures necessary to carry out its duties consistent with the provisions of this code and applicable state law. The procedures shall not require compliance with strict rules of evidence, but shall mandate that only relevant information be presented.
|  | B101.5 Notice of meeting. | The board shall meet upon notice from the chairperson, within 10 days of the filing of an appeal or at stated periodic intervals.
|  | B101.5.1 Open hearing. | All hearings before the board shall be open to the public. The appellant, the appellant’s representative, the building official and any person whose interests are affected shall be given an opportunity to be heard.
|  | B101.5.2 Quorum. | Three members of the board shall constitute a quorum.
|  | B101.5.3 Postponed hearing. | When five members are not present to hear an appeal, either the appellant or the appellant’s representative shall have the right to request a postponement of the hearing.
|  | B101.6 Legal counsel. | The jurisdiction shall furnish legal counsel to the board to provide members with general legal advice concerning matters before them for consideration. Members shall be represented by legal counsel at the jurisdiction’s expense in all matters arising from service within the scope of their duties.
|  | B101.7 Board decision. | The board shall only modify or reverse the decision of the building official by a concurring vote of three or more members.
|  | B101.7.1 Resolution. | The decision of the board shall be by resolution. Every decision shall be promptly filed in writing in the office of the building official within three days and shall be open to the public for inspection. A certified copy shall be furnished to the appellant or the appellant’s representative and to the building official.
|  | B101.7.2 Administration. | The building official shall take immediate action in accordance with the decision of the board.
|  | B101.8 Court review. | Any person, whether or not a previous party of the appeal, shall have the right to apply to the appropriate court for a writ of certiorari to correct errors of law. Application for review shall be made in the manner and time required by law following the filing of the decision in the office of the chief administrative officer.

## BC-C
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
RESERVED | RESERVED | C101.1 Scope. | The provisions of this appendix shall apply exclusively to agricultural buildings. Such buildings shall be classified as Group U and shall include the following uses:
|  | C102.1 General. | Buildings classified as Group U Agricultural shall not exceed the area or height limits specified in Table C102.1.
|  | C102.2 One-story unlimited area. | The area of a one-story Group U agricultural building shall not be limited if the building is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width.
|  | C102.3 Two-story unlimited area. | The area of a two-story Group U agricultural building shall not be limited if the building is surrounded and adjoined by public ways or yards not less than 60 feet (18 288 mm) in width and is provided with an approved automatic sprinkler system throughout in accordance with Section 903.3.1.1.
|  | C103.1 Mixed occupancies. | Mixed occupancies shall be protected in accordance with Section 508.
|  | C104.1 Exit facilities. | Exits shall be provided in accordance with Chapters 10 and 11.

## BC-D
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
D101.1 Scope. | The provisions of this appendix shall regulate the division of the city of New York into geographical territo­ries known as fire districts and control the occupancy groups and construction classes permitted in the fire districts. Wher­ever reference is made to the fire district, it shall be construed to mean the fire districts designated and referred to in this appen­dix. | D101.1 Scope. | The fire district shall include such territory or portion as outlined in an ordinance or law entitled “An Ordinance (Resolution) Creating and Establishing a Fire District.” Wherever, in such ordinance creating and establishing a fire district, reference is made to the fire district, it shall be construed to mean the fire district designated and referred to in this appendix.
|  | D101.1.1 Mapping. | The fire district complying with the provisions of Section D101.1 shall be shown on a map that shall be available to the public.
D102.1 Types of construction permitted. | Every building hereafter erected within the fire district, or located partially in the fire district pursuant to Section D104. 1, shall be either Type I, II, III or IV. | D102.1 Types of construction permitted. | Within the fire district every building hereafter erected shall be Type I, II, III or IV, except as permitted in Section D104.
|  | D101.2 Establishment of area. | For the purpose of this code, the fire district shall include that territory or area as described in Sections D101.2.1 through D101.2.3.
D102.2 Other specific requirements. |  | D102.2 Other specific requirements.
|  | D101.2.1 Adjoining blocks. | Two or more adjoining blocks, exclusive of intervening streets, where not less than 50 percent of the ground area is built upon and more than 50 percent of the built-on area is devoted to hotels and motels of Group R-1; Group B occupancies; theaters, nightclubs, restaurants of Group A-1 and A-2 occupancies; garages, express and freight depots, warehouses and storage buildings used for the storage of finished products (not located with and forming a part of a manufactured or industrial plant); or Group S occupancy. Where the average height of a building is two and one-half stories or more, a block should be considered if the ground area built upon is not less than 40 percent.
|  | D101.2.2 Buffer zone. | Where four contiguous blocks or more comprise a fire district, there shall be a buffer zone of 200 feet (60 960 mm) around the perimeter of such district. Streets, rights-of-way and other open spaces not subject to building construction can be included in the 200- foot (60 960 mm) buffer zone.
|  | D101.2.3 Developed blocks. | Where blocks adjacent to the fire district have developed to the extent that not less than 25 percent of the ground area is built upon and 40 percent or more of the built-on area is devoted to the occupancies specified in Section D101.2.1, they can be considered for inclusion in the fire district, and can form all or a portion of the 200-foot (60 960 mm) buffer zone required in Section D101.2.2.
|  | D102.2.1 Exterior walls. | Exterior walls of buildings located in the fire district shall comply with the requirements in Table 601 except as required in Section D102.2.6.
|  | D102.2.2 Group H prohibited. | Group H occupancies shall be prohibited from location within the fire district.
|  | D102.2.3 Construction type. | Every building shall be constructed as required based on the type of construction indicated in Chapter 6.
|  | D102.2.4 Roof covering. | Roof covering in the fire district shall conform to the requirements of Class A or B roof coverings as defined in Section 1505.
|  | D102.2.5 Structural fire rating. | Walls, floors, roofs and their supporting structural members shall be not less than 1-hour fire-resistance-rated construction.
|  | D102.2.6 Exterior walls. | Exterior load-bearing walls of Type II buildings shall have a fire-resistance rating of 2 hours or more where such walls are located within 30 feet (9144 mm) of a common property line or an assumed property line. Exterior nonload-bearing walls of Type II buildings located within 30 feet (9144 mm) of a common property line or an assumed property line shall have fire-resistance ratings as required by Table 601, but not less than 1 hour. Exterior walls located more than 30 feet (9144 mm) from a common property line or an assumed property line shall comply with Table 601.
|  | D102.2.7 Architectural trim. | Architectural trim on buildings located in the fire district shall be constructed of approved noncombustible materials or fire-retardant-treated wood.
|  | D102.2.8 Permanent canopies. | Permanent canopies are permitted to extend over adjacent open spaces provided that all of the following are met:
|  | D102.2.9 Roof structures. | Structures, except aerial supports 12 feet (3658 mm) high or less, flagpoles, water tanks and cooling towers, placed above the roof of any building within the fire district shall be of noncombustible material and shall be supported by construction of noncombustible material.
|  | D102.2.10 Plastic signs. | The use of plastics complying with Section 2611 for signs is permitted provided that the structure of the sign in which the plastic is mounted or installed is noncombustible.
|  | D102.2.11 Plastic veneer. | Exterior plastic veneer is not permitted in the fire district.
D103.1 Existing buildings within the fire district. | An exist­ing building shall not hereafter be increased in height or area unless it is of a type of construction permitted for new buildings within the fire district or is altered to comply with the require­ments for such type of construction. Nor shall any existing building be hereafter extended on any side, nor square footage or floors added within the existing building unless such modifi­cations are of a type of construction permitted for new build­ings within the fire district. | D103.1 Existing buildings within the fire district. | An existing building shall not be increased in height or area unless it is of a type of construction permitted for new buildings within the fire district or is altered to comply with the requirements for such type of construction. Nor shall any existing building be extended on any side, nor square footage or floors added within the existing building unless such modifications are of a type of construction permitted for new buildings within the fire district.
D103.2 Other alterations. | Nothing in Section D103.1 shall prohibit other alterations within the fire district provided there is no change of occupancy that is otherwise prohibited and pro­vided the fire hazard is not increased by such alteration. | D103.2 Other alterations. | Nothing in Section D103.1 shall prohibit other alterations within the fire district provided that such alterations do not create a change of occupancy that is otherwise prohibited or increase the fire hazard.
D103.3 Moving buildings. | Buildings shall not hereafter be moved into the fire district or to another lot in the fire district unless the building is of a type of construction permitted in the fire district. | D103.3 Moving buildings. | Buildings shall not hereafter be moved into the fire district or to another lot in the fire district unless the building is of a type of construction permitted in the fire district.
D104.1 General. | Any building located partially in the fire dis­trict, so that it is both inside and outside the district, shall be of a type of construction required for the fire district if more than 25 percent of the total floor area of the building is located inside the fire district. | D104.1 General. | Any building located partially in the fire district shall be of a type of construction required for the fire district, unless the major portion of such building lies outside of the fire district and all portions of it extend not more than 10 feet (3048 mm) inside the boundaries of the fire district.
D105.1 General. | The preceding provisions of this appendix shall not apply in the following instances: | D105.1 General. | The preceding provisions of this appendix shall not apply in the following instances:
|  | D106.1 General. | See Table D106.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.
D101.2 Establishment of fire district. | The following city areas are hereby established as being inside the fire districts:
D102.2.1 Group H-1 prohibited. | Group H-1 occupancies shall be prohibited from location within the fire district.
D102.2.2 Construction type. | Every building, room, or space hereafter altered or erected shall be constructed as required based on the type of construction indicated in Chapter 6 except as provided in Section D102.2.4.
D102.2.3 Roof covering. | Roof covering in the fire district shall conform to the requirements of Class A or B roof cov­erings as defined in Section 1505.
D102.2.4 Structural fire rating. | The fire-resistance rating of bearing walls, floors, roofs and their supporting struc­tural members shall comply with Table 601 of Chapter 6, but in no event shall such rating be less than 1 hour.
D102.2.5 R-1 and R-2 occupancies. | No building or space classified in Occupancy Group R-1 or R-2 may be located on a lot containing a building classified in construction Type IIB, VA or VB.
D106.1 Fire district maps. | Within the boroughs of Staten Island (Richmond County) and Queens, the fire districts shall comprise such areas indi­cated on the “fire district maps” as per Figures D106.1(1) and D106.1(2).

## BC-E
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
E101.1 Scope. | The provisions of this appendix shall control the supplementary requirements for the design and construction of facilities for accessibility for individuals with disabilities. | E101.1 Scope. | The provisions of this appendix shall control the supplementary requirements for the design and construction of facilities for accessibility for individuals with disabilities.
E101.2 Design. | Technical requirements for items herein shall comply with this code and ICC A117.1. | E101.2 Design. | Technical requirements for items herein shall comply with this code and ICC A117.1.
|  | E102.1 General. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein. Refer to Chapter 2 of this code for general definitions.
E103.1 Raised platforms. | In banquet rooms or spaces where a head table or speaker’s lectern is located on a raised platform, an accessible route shall be provided to the platform. | E103.1 Raised platforms. | In banquet rooms or spaces where a head table or speaker’s lectern is located on a raised platform, an accessible route shall be provided to the platform.
E104.1 General. | Transient lodging facilities shall be provided with accessible features in accordance with Sections E104.2 and E104.3. Group I-3 occupancies shall be provided with accessible features in accordance with Sections E104.2 and E104.4. | E104.1 General. | Transient lodging facilities shall be provided with accessible features in accordance with Section E104.2. Group I-3 occupancies shall be provided with accessible features in accordance with Section E104.2.
E104.2 Communication features. | Accessible communication features complying with Chapter 7 of ICC A117.1 shall be provided in accordance with Sections E104.2.1 through E104.2.4 of this code. | E104.2 Communication features. | Accessible communication features shall be provided in accordance with Sections E104.2.1 through E104.2.4.
E104.2.1 Transient lodging. | In transient lodging facilities, sleeping units with accessible communication features shall be provided in accordance with Table E104.2.1. Units required to comply with Table E104.2.1 shall be dispersed among the various classes of units. | E104.2.1 Transient lodging. | In transient lodging facilities, sleeping units with accessible communication features shall be provided in accordance with Table E104.2.1. Units required to comply with Table E104.2.1 shall be dispersed among the various classes of units.
E104.2.2 Group I-3. | In Group I-3 occupancies at least 2 percent, but no fewer than one of the total number of general holding cells and general housing cells equipped with audible emergency alarm systems and permanently installed telephones within the cell, shall comply with Section E104.2.4. | E104.2.2 Group I-3. | In Group I-3 occupancies at least 2 percent of the total number of general holding cells and general housing cells equipped with audible emergency notification systems, and not less than one cell, shall be provided with visual notification devices. Permanently installed telephones within the cell shall comply with Section E104.2.4.
E104.2.3 Dwelling units and sleeping units. | Where dwelling units and sleeping units are altered or added, the requirements of Section E104.2 shall apply only to the units being altered or added until the number of units with accessible communication features complies with the minimum number required for new construction. | E104.2.3 Dwelling units and sleeping units. | Where dwelling units and sleeping units are altered or added, the requirements of Section E104.2 shall apply only to the units being altered or added until the number of units with accessible communication features complies with the minimum number required for new construction.
E104.2.4 Notification devices. | Visual notification devices shall be provided to alert room occupants of incoming telephone calls and a door knock or bell. Notification devices shall not be connected to visual alarm signal appliances. Permanently installed telephones shall have volume controls and an electrical outlet complying with ICC A117.1, including Section 309 (Operable Parts), located within 48 inches (1219 mm) of the telephone to facilitate the use of a TTY. | E104.2.4 Notification devices. | Visual notification devices shall be provided to alert room occupants of incoming telephone calls and a door knock or bell. Notification devices shall not be connected to visual alarm signal appliances. Permanently installed telephones shall have volume controls and an electrical outlet complying with ICC A117.1 located within 48 inches (1219 mm) of the telephone to facilitate the use of a TTY.
E105.1 Portable toilets and bathing rooms. | Where multiple single-user portable toilet or bathing units are clustered at a single location, at least 5 percent, but not less than one toilet unit or bathing unit at each cluster, shall be accessible and comply with ICC A117.1, including Section 603 (Toilet and Bathing Rooms). Signs containing the dynamic accessibility symbol and complying with Section 703 (Signs) of ICC A117.1 shall identify accessible portable toilets and bathing units. Exception: Portable toilet units provided for use exclusively by construction personnel on a construction site. | E105.1 Portable toilets and bathing rooms. | Where multiple single-user portable toilet or bathing units are clustered at a single location, at least 5 percent, but not less than one toilet unit or bathing unit at each cluster, shall be accessible. Signs containing the International Symbol of Accessibility shall identify accessible portable toilets and bathing units. Exception: Portable toilet units provided for use exclusively by construction personnel on a construction site.
E105.2 Laundry equipment. | Where provided in spaces required to be accessible, washing machines and clothes dryers shall comply with this section. Where laundry equipment is provided within a dwelling or sleeping unit, not for public use or common use, such equipment shall comply with Section 1107.2.8. | E105.2 Laundry equipment. | Where provided in spaces required to be accessible, washing machines and clothes dryers shall comply with this section.
E105.2.1 Washing machines. | Where three or fewer washing machines are provided, at least one shall comply with ICC A117.1, including Section 611 (Washing Machines and Clothes Dryers), and shall be accessible. Where more than three washing machines are provided, at least two shall comply with ICC A117.1, including Section 611 and shall be accessible. | E105.2.1 Washing machines. | Where three or fewer washing machines are provided, one or more shall be accessible. Where more than three washing machines are provided, two or more shall be accessible.
E105.2.2 Clothes dryers. | Where three or fewer clothes dryers are provided, at least one shall comply with ICC A117.1, including Section 611 (Washing Machines and Clothes Dryers), and shall be accessible. Where more than three clothes dryers are provided, at least two shall comply with ICC A117.1, including Section 611, and shall be accessible. | E105.2.2 Clothes dryers. | Where three or fewer clothes dryers are provided, one or more shall be accessible. Where more than three clothes dryers are provided, two or more shall be accessible.
|  | E105.3 Gaming machines, depositories, vending machines, change machines and similar equipment. | Not fewer than one of each type of depository, vending machine, change machine and similar equipment shall be accessible. Two percent of gaming machines shall be accessible and provided with a front approach. Accessible gaming machines shall be distributed throughout the different types of gaming machines provided. Exception: Drive-up-only depositories are not required to comply with this section.
Exception: Drive-up-only depositories are not required to comply with this section.
E105.4 Mailboxes. | Where mailboxes are provided in facilities not subject to Section 1107.3.1, but required to be accessible pursuant to the Americans with Disabilities Act, at least five percent, but not less than one, of each type shall comply with ICC A117.1. | E105.4 Mailboxes. | Where mailboxes are provided in an interior location, 5 percent of the total, but not less than one, of each type shall be accessible. In residential and institutional facilities, where mailboxes are provided for each dwelling unit or sleeping unit, accessible mailboxes shall be provided for each unit required to be an Accessible unit.
E105.5 Automatic teller machines and fare machines. | Where automatic teller machines or self-service fare vending, collection or adjustment machines are provided, at least one machine of each type at each location where such machines are provided shall be accessible and comply with ICC A117.1, including Section 707 (ATMs and Fare Machines). Where bins are provided for envelopes, wastepaper or other purposes, at least one of each type shall be accessible and comply with ICC A117.1, including Section 905 (Storage Facilities). | E105.5 Automatic teller machines and fare machines. | Where automatic teller machines or self-service fare vending, collection or adjustment machines are provided, not fewer than one machine of each type at each location where such machines are provided shall be accessible. Where bins are provided for envelopes, wastepaper or other purposes, not fewer than one of each type shall be accessible.
E105.6 Two-way communication systems. | Where two-way communication systems are provided to gain admittance to a building or facility or to restricted areas within a building or facility, the system shall be accessible and comply with ICC A117.1, including Section 708 (Two-Way Communication Systems). | E105.6 Two-way communication systems. | Where two-way communication systems are provided to gain admittance to a building or facility or to restricted areas within a building or facility, the system shall be accessible.
E106.1 General. | Where coin-operated public pay telephones, coinless public pay telephones, public closed-circuit telephones, courtesy phones or other types of public telephones are provided, accessible public telephones shall be provided in accordance with Sections E106.2 through E106.5 for each type of public telephone provided. For purposes of this section, a bank of telephones shall be considered two or more adjacent telephones. | E106.1 General. | Where coin-operated public pay telephones, coinless public pay telephones, public closed-circuit telephones, courtesy phones or other types of public telephones are provided, accessible public telephones shall be provided in accordance with Sections E106.2 through E106.5 for each type of public telephone provided. For purposes of this section, a bank of telephones shall be considered to consist of two or more adjacent telephones.
E106.2 Wheelchair-accessible telephones. | Where public telephones are provided, wheelchair-accessible telephones complying with ICC A117.1, including Section 704 (Tele­phones), shall be provided in accordance with Table E106.2. Exception: Drive-up-only public telephones are not required to be accessible. | E106.2 Wheelchair-accessible telephones. | Where public telephones are provided, wheelchair-accessible telephones shall be provided in accordance with Table E106.2. Exception: Drive-up-only public telephones are not required to be accessible.
E106.3 Volume controls. | All public telephones provided shall have accessible volume control complying with Section 704.3 (Volume-Control Telephones) of ICC A117.1. | E106.3 Volume controls. | All public telephones provided shall have accessible volume control.
E106.4 TTYs. | TTYs complying with ICC A117.1, including Sections 704.4 through 704.7, shall be provided in accordance with Sections E106.4.1 through E106.4.9. | E106.4 TTYs. | TTYs shall be provided in accordance with Sections E106.4.1 through E106.4.9.
E106.4.1 Bank requirement. | Where four or more public pay telephones are provided at a bank of telephones, at least one public TTY shall be provided at that bank. Exception: TTYs are not required at banks of telephones located within 200 feet (60 960 mm) of, and on the same floor as, a bank containing a public TTY. | E106.4.1 Bank requirement. | Where four or more public pay telephones are provided at a bank of telephones, at least one public TTY shall be provided at that bank. Exception: TTYs are not required at banks of telephones located within 200 feet (60 960 mm) of, and on the same floor as, a bank containing a public TTY.
E106.4.2 Floor requirement. | Where four or more public pay telephones are provided on a floor of a privately owned building, at least one public TTY shall be provided on that floor. Where at least one public pay telephone is provided on a floor of a publicly owned building, at least one public TTY shall be provided on that floor. | E106.4.2 Floor requirement. | Where four or more public pay telephones are provided on a floor of a privately owned building, one or more public TTY shall be provided on that floor. Where one public pay telephone or more, is provided on a floor of a publicly owned building, not fewer than one public TTY shall be provided on that floor.
E106.4.3 Building requirement. | Where four or more public pay telephones are provided in a privately owned building, at least one public TTY shall be provided in the building. Where at least one public pay telephone is provided in a publicly owned building, at least one public TTY shall be provided in the building. | E106.4.3 Building requirement. | Where four or more public pay telephones are provided in a privately owned building, one or more public TTY shall be provided in the building. Where at least one public pay telephone is provided in a publicly owned building, one or more public TTY shall be provided in the building.
E106.4.4 Site requirement. | Where four or more public pay telephones are provided on a site, at least one public TTY shall be provided on the site. | E106.4.4 Site requirement. | Where four or more public pay telephones are provided on a site, one or more public TTY shall be provided on the site.
E106.4.5 Rest stops, emergency road stops and service plazas. | Where a public pay telephone is provided at a public rest stop, emergency road stop or service plaza, at least one public TTY shall be provided. | E106.4.5 Rest stops, emergency road stops and service plazas. | Where a public pay telephone is provided at a public rest stop, emergency road stop or service plaza, at least one public TTY shall be provided.
E106.4.6 Hospitals. | Where a public pay telephone is provided in or adjacent to a hospital emergency room, hospital recovery room or hospital waiting room, at least one public TTY shall be provided at each such location. | E106.4.6 Hospitals. | Where a public pay telephone is provided in or adjacent to a hospital emergency room, hospital recovery room or hospital waiting room, one or more public TTY shall be provided at each such location.
E106.4.7 Transportation facilities. | Transportation facilities shall be provided with TTYs in accordance with Section E109.2.5 in addition to the TTYs required by Sections E106.4.1 through E106.4.4. | E106.4.7 Transportation facilities. | Transportation facilities shall be provided with TTYs in accordance with Sections E109.2.5 and E110.2 in addition to the TTYs required by Sections E106.4.1 through E106.4.4.
E106.4.8 Detention and correctional facilities. | In detention and correctional facilities, where a public pay telephone is provided in a secured area used only by detainees or inmates and security personnel, then at least one TTY shall be provided in at least one secured area. | E106.4.8 Detention and correctional facilities. | In detention and correctional facilities, where a public pay telephone is provided in a secured area used only by detainees or inmates and security personnel, then not fewer than one TTY shall be provided in not fewer than one secured area.
E106.4.9 Signs. | Public TTYs shall be identified by the International Symbol of TTY complying with Section 703.6.3.2 (International Symbol of TTY) of ICC A117.1. Directional signs indicating the location of the nearest public TTY shall be provided at banks of public pay telephones not containing a public TTY. Additionally, where signs provide direction to public pay telephones, they shall also provide direction to public TTYs. Such signs shall comply with visual signage requirements in ICC A117.1, including Section 703.2 (Visual Characters), and shall include the International Symbol of TTY. | E106.4.9 Signs. | Public TTYs shall be identified by the International Symbol of TTY complying with ICC A117.1. Directional signs indicating the location of the nearest public TTY shall be provided at banks of public pay telephones not containing a public TTY. Additionally, where signs provide direction to public pay telephones, they shall provide direction to public TTYs. Such signs shall comply with visual signage requirements in ICC A117.1 and shall include the International Symbol of TTY.
E106.5 Shelves for portable TTYs. | Where a bank of telephones in the interior of a building consists of three or more public pay telephones, at least one public pay telephone at the bank shall be provided with a shelf and an electrical outlet in accordance with Section 704.6 (TTY Shelf) of ICC A117.1. Exceptions: 1. In secured areas of detention and correctional facilities, if shelves and outlets are prohibited for purposes of security or safety shelves and outlets for TTYs are not required to be provided. 2. The shelf and electrical outlet shall not be required at a bank of telephones with a TTY. | E106.5 Shelves for portable TTYs. | Where a bank of telephones in the interior of a building consists of three or more public pay telephones, not fewer than one public pay telephone at the bank shall be provided with a shelf and an electrical outlet. Exceptions: 1. In secured areas of detention and correctional facilities, if shelves and outlets are prohibited for purposes of security or safety shelves and outlets for TTYs are not required to be provided. 2. The shelf and electrical outlet shall not be required at a bank of telephones with a TTY.
E107.1 Signs. | Required accessible portable toilets and bathing facilities shall be identified by the dynamic accessibility symbol, in accordance with Figure 1111.1. | E107.1 Signs. | Required accessible portable toilets and bathing facilities shall be identified by the International Symbol of Accessibility.
E107.2 Designations. | Interior and exterior signs identifying permanent rooms and spaces shall have visual characters, raised characters and braille complying with ICC A117.1. Where pictograms are provided as designations of interior rooms and spaces, the pictograms shall have visual characters, raised characters and braille complying with Sections 703.2 through 703.5 of ICC A117.1. Exceptions: 1. Exterior signs that are not located at the door to the space they serve are not required to comply. 2. Building directories, menus, seat and row designations in assembly areas, occupant names, building addresses and company names and logos are not required to comply. 3. Signs in parking facilities are not required to comply. 4. Temporary (seven days or less) signs are not required to comply. 5. In detention and correctional facilities, signs not located in public areas are not required to comply. | E107.2 Designations. | Interior and exterior signs identifying permanent rooms and spaces shall be visual characters, raised characters and braille complying with ICC A117.1. Where pictograms are provided as designations of interior rooms and spaces, the pictograms shall have visual characters, raised characters and braille complying with ICC A117.1. Exceptions: 1. Exterior signs that are not located at the door to the space they serve are not required to comply. 2. Building directories, menus, seat and row designations in assembly areas, occupant names, building addresses and company names and logos are not required to comply. 3. Signs in parking facilities are not required to comply. 4. Temporary (seven days or less) signs are not required to comply. 5. In detention and correctional facilities, signs not located in public areas are not required to comply.
E107.3 Directional and informational signs. | Signs that provide direction to, or information about, permanent interior spaces of the site and facilities shall contain visual characters complying with Section 703.2 (Visual Characters) of ICC A117.1. Exception: Building directories, personnel names, company or occupant names and logos, menus and temporary (seven days or less) signs are not required to comply with ICC A117.1. | E107.3 Directional and informational signs. | Signs that provide direction to, or information about, permanent interior spaces of the site and facilities shall contain visual characters complying with ICC A117.1. Exception: Building directories, personnel names, company or occupant names and logos, menus and temporary (seven days or less) signs are not required to comply with ICC A117.1.
1
E107.4 Other signs. | Signage indicating special accessibility provisions shall be provided at fixed facilities and stations, signage must be provided in accordance with Sections E109.2.2 through E109.2.2.3. | E107.4 Other signs. | Signage indicating special accessibility provisions shall be provided as follows:
|  | E108.1 General. | Bus stops shall comply with Sections E108.2 through E108.5.
|  | E108.2 Bus boarding and alighting areas. | Bus boarding and alighting areas shall comply with Sections E108.2.1 through E108.2.4.
|  | E108.2.1 Surface. | Bus boarding and alighting areas shall have a firm, stable surface.
|  | E108.2.2 Dimensions. | Bus boarding and alighting areas shall have a clear length of 96 inches (2440 mm) minimum, measured perpendicular to the curb or vehicle roadway edge, and a clear width of 60 inches (1525 mm) minimum, measured parallel to the vehicle roadway.
|  | E108.2.3 Connection. | Bus boarding and alighting areas shall be connected to streets, sidewalks or pedestrian paths by an accessible route complying with Section 1104.
|  | E108.2.4 Slope. | Parallel to the roadway, the slope of the bus boarding and alighting area shall be the same as the roadway, to the maximum extent practicable. For water drainage, a maximum slope of 1:48 perpendicular to the roadway is allowed.
E109.1 General. | Fixed transportation facilities and stations shall comply with the applicable provisions of Section E109.2. | E109.1 General. | Fixed transportation facilities and stations shall comply with the applicable provisions of Section E109.2.
|  | E108.3 Bus shelters. | Where provided, new or replaced bus shelters shall provide a minimum clear floor or ground space complying with ICC A117.1, Section 305, entirely within the shelter. Such shelters shall be connected by an accessible route to the boarding area required by Section E108.2.
E109.2 New construction. | New stations in rapid rail, light rail, commuter rail, intercity rail, high speed rail and other fixed guideway systems shall comply with Sections E109.2.1 through E109.2.8. | E109.2 New construction. | New stations in rapid rail, light rail, commuter rail, intercity rail, high speed rail and other fixed guideway systems shall comply with Sections E109.2.1 through E109.2.8.
|  | E108.4 Signs. | New bus route identification signs shall have finish and contrast complying with ICC A117.1. Additionally, to the maximum extent practicable, new bus route identification signs shall provide visual characters complying with ICC A117.1. Exception: Bus schedules, timetables and maps that are posted at the bus stop or bus bay are not required to meet this requirement.
E109.2.1 Station entrances. | Where different entrances to a station serve different transportation fixed routes or groups of fixed routes, all entrance serving each group or route shall comply with Section 1104 and ICC A117.1, including Section 404 (Doors and Doorways). | E109.2.1 Station entrances. | Where different entrances to a station serve different transportation fixed routes or groups of fixed routes, at least one entrance serving each group or route shall comply with Section 1104.
E109.2.2 Signs. | Signage in fixed transportation facilities and stations shall comply with Sections E109.2.2.1 through E109.2.2.3. | E109.2.2 Signs. | Signage in fixed transportation facilities and stations shall comply with Sections E109.2.2.1 through E109.2.2.3.
|  | E108.5 Bus stop siting. | Bus stop sites shall be chosen such that, to the maximum extent practicable, the areas where lifts or ramps are to be deployed comply with Sections E108.2 and E108.3.
E109.2.2.1 Raised character and braille signs. | Where signs are provided at entrances to stations identifying the station or the entrance, or both, at least one sign at each entrance shall have raised characters and braille. A minimum of one raised character and braille sign identifying the specific station shall be provided on each platform or boarding area. Such signs shall be placed in uniform locations at entrances and on platforms or boarding areas within the transit system to the maximum extent practicable. Raised character and braille signs shall comply with Sections 703.3 (Raised Characters) and 703.4 (Braille) of ICC A117.1. Exceptions: 1. Where the station has no defined entrance but signs are provided, the raised character and braille signs shall be placed in a central location. 2. Signs are not required to be raised character and braille where audible signs are remotely transmitted to hand-held receivers, or are user or proximity actuated. | E109.2.2.1 Raised character and braille signs. | Where signs are provided at entrances to stations identifying the station or the entrance, or both, at least one sign at each entrance shall be raised characters and braille. A minimum of one raised character and braille sign identifying the specific station shall be provided on each platform or boarding area. Such signs shall be placed in uniform locations at entrances and on platforms or boarding areas within the transit system to the maximum extent practicable. Exceptions: 1. Where the station does not have a defined entrance but signs are provided, the raised characters and braille signs shall be placed in a central location. 2. Signs are not required to be raised characters and braille where audible signs are remotely transmitted to hand-held receivers, or are user or proximity actuated.
E109.2.2.2 Identification signs. | Stations covered by this section shall have identification signs containing visual characters complying with Section 703.2 (Visual Characters) of ICC A117.1. Signs shall be clearly visible and within the sightlines of a standing or sitting passenger from within the train on both sides when not obstructed by another train. | E109.2.2.2 Identification signs. | Stations covered by this section shall have identification signs containing visual characters complying with ICC A117.1. Signs shall be clearly visible and within the sightlines of a standing or sitting passenger from within the train on both sides when not obstructed by another train.
E109.2.2.3 Informational signs. | Lists of stations, routes and destinations served by the station that are located on boarding areas, platforms or mezzanines shall provide visual characters complying with Section 703.2 (Visual Characters) of ICC A117.1. Signs covered by this provision shall, to the maximum extent practicable, be placed in uniform locations within the transit system. | E109.2.2.3 Informational signs. | Lists of stations, routes and destinations served by the station that are located on boarding areas, platforms or mezzanines shall provide visual characters complying with ICC A117.1. Signs covered by this provision shall, to the maximum extent practicable, be placed in uniform locations within the transit system.
E109.2.3 Fare machines. | Self-service fare vending, collection and adjustment machines shall comply with Section 707 (ATMs and Fare Machines). Where self-service fare vending, collection or adjustment machines are provided for the use of the general public, at least one accessible machine of each type provided shall be provided at each accessible point of entry and exit. | E109.2.3 Fare machines. | Self-service fare vending, collection and adjustment machines shall comply with ICC A117.1, Section 707. Where self-service fare vending, collection or adjustment machines are provided for the use of the general public, at least one accessible machine of each type provided shall be provided at each accessible point of entry and exit.
E109.2.4 Rail-to-platform height. | Station platforms shall be positioned to coordinate with vehicles in accordance with the applicable provisions of 36 CFR, Part 1192. Low-level platforms shall be 8 inches (203 mm) minimum above top of rail. Exception: Where vehicles are boarded from sidewalks or street level, low-level platforms shall be permitted to be less than 8 inches (203 mm). | E109.2.4 Rail-to-platform height. | Station platforms shall be positioned to coordinate with vehicles in accordance with the applicable provisions of 36 CFR, Part 1192. Low-level platforms shall be 8 inches (250 mm) minimum above top of rail. Exception: Where vehicles are boarded from sidewalks or street level, low-level platforms shall be permitted to be less than 8 inches (250 mm).
E109.2.5 TTYs. | Where a public pay telephone is provided in a transit facility (as defined by the Department of Transportation), at least one public TTY complying with ICC A117.1, Sections 704.4 through 704.7, shall be provided in the station. In addition, where one or more public pay telephones serve a particular entrance to a transportation facility, at least one TTY telephone complying with ICC A117.1, Sections 704.4 through 704.7 shall be provided to serve that entrance. | E109.2.5 TTYs. | Where a public pay telephone is provided in a transit facility (as defined by the Department of Transportation), at least one public TTY complying with ICC A117.1, Section 704.4, shall be provided in the station. In addition, where one or more public pay telephones serve a particular entrance to a transportation facility, at least one TTY telephone complying with ICC A117.1, Section 704.4, shall be provided to serve that entrance.
E109.2.6 Track crossings. | Where a circulation path serving boarding platforms crosses tracks, an accessible route complying with ICC A117.1, including Section 402 (Accessible Routes) shall be provided. Exception: Openings for wheel flanges shall be permitted to be 21/2 inches (64 mm) maximum. | E109.2.6 Track crossings. | Where a circulation path serving boarding platforms crosses tracks, an accessible route shall be provided. Exception: Openings for wheel flanges shall be permitted to be 21/2 inches (64 mm) maximum.
E109.2.7 Public address systems. | Where public address systems convey audible information to the public, the same or equivalent information shall be provided in a visual format. | E109.2.7 Public address systems. | Where public address systems convey audible information to the public, the same or equivalent information shall be provided in a visual format.
E109.2.8 Clocks. | Where clocks are provided for use by the general public, the clock face shall be uncluttered so that its elements are clearly visible. Hands, numerals and digits shall contrast with the background either light-on-dark or dark-on-light. Where clocks are mounted overhead, numerals and digits shall comply with ICC A117.1, Section 703.2 (Visual Characters). | E109.2.8 Clocks. | Where clocks are provided for use by the general public, the clock face shall be uncluttered so that its elements are clearly visible. Hands, numerals and digits shall contrast with the background either light-on-dark or dark-on-light. Where clocks are mounted overhead, numerals and digits shall comply with visual character requirements.
|  | E110.1 New construction. | New construction of airports shall comply with Sections E110.2 through E110.4.
|  | E110.2 TTYs. | Where public pay telephones are provided, at least one TTY shall be provided in compliance with ICC A117.1, Section 704.4. Additionally, if four or more public pay telephones are located in a main terminal outside the security areas, a concourse within the security areas or a baggage claim area in a terminal, at least one public TTY complying with ICC A117.1, Section 704.4, shall also be provided in each such location.
|  | E110.3 Terminal information systems. | Where terminal information systems convey audible information to the public, the same or equivalent information shall be provided in a visual format.
|  | E110.4 Clocks. | Where clocks are provided for use by the general public, the clock face shall be uncluttered so that its elements are clearly visible. Hands, numerals and digits shall contrast with the background either light-on-dark or dark-on-light. Where clocks are mounted overhead, numerals and digits shall comply with visual character requirements.
E111.1 General. | This section lists the standards that are referenced in various sections of this appendix. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title and the section or sections of this document that reference the standard. | E111.1 General. | See Table E111.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix that reference the standard.
E102.1 Definitions. | The following terms are defined in Chapter 2:
E104.3 Accessible beds. | In rooms or spaces having more than 25 beds, five percent of the beds shall have a clear floor space complying with Section 305 (Clear Floor Space) of ICC A117.1.
E104.3.1 Sleeping areas. | A clear floor space complying with Section 305 (Clear Floor Space) of ICC A117.1 shall be provided on both sides of the accessible bed. The clear floor space shall be positioned for parallel approach to the side of the bed. Exception: This requirement shall not apply where a single clear floor space complying with Section 305 (Clear Floor Space) of ICC A117.1 positioned for parallel approach is provided between two beds.
E104.4 Partitions. | Solid partitions or security glazing that separates visitors from detainees in Group I-3 occupancies shall provide a method to facilitate voice communication. Such methods are permitted to include, but are not limited to, grilles, slats, talk-through baffles, intercoms or telephone handset devices. The method of communication shall be accessible to individuals who use wheelchairs and individuals who have difficulty bending or stooping. Hand-operable communication devices, if provided, shall comply with Section E106.3.
E105.3 Depositories, vending machines, change machines and similar equipment. | At least one of each type of depository, vending machine, change machine and similar equipment shall be accessible. Exception: Drive-up-only depositories are not required to comply with this section.
E111.2 Subsequent additions, modifications, or deletions. | Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to these standards in accordance with Section 28-103.19 of the Administrative Code.
E111.3 Applicability. | The application of the referenced standards shall be as specified in Section 102.4.
E111.4 Standards.

## BC-F
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
F101.1 Scope. | The provisions of this appendix provide rodent-proofing design and construction requirements for the resistance of rodent ingress and infestation. For rodent exter­mination provisions related to demolition operations, see Sec­tion 3306. The New York City Health Code, the New York City Housing Maintenance Code, and the New York City Sanitation Code may contain additional provisions, as enforced by the New York City Department of Health and Mental Hygiene, the New York City Department of Housing Preservation and Development, and the New York City Sanitation Department.
F101.2 General. | Every structure, room, or space hereafter altered or erected in which persons live, sleep or work, or in which feed, food or foodstuffs are stored, prepared, processed, served or sold, shall be constructed in accordance with the pro­visions of this section. All metal or wire protection materials specified herein shall be noncorrosive.
F101.3 Reserved.
F101.4 Reserved.
F101.5 Reserved.
F101.6 Reserved.
F102.1 Exterior walls and underground walls. | For walls or portions thereof within 2 feet (610 mm) of the outside ground level, and for walls below the outside ground level, all open­ings, including but not limited to, annular spaces around pipes, electric cables, and conduits, shall be protected by closing such openings with cement mortar, concrete masonry, metal plates or screening designed to prevent the passage of rodents. Open­ings for doors, windows and vents shall be as provided for in Sections F102.3, F102.4 and F102.5, respectively.
F102.2 Floors on grade. | Unless otherwise specified in this code, floors on grade, including but not limited to cellar floors and crawl space floors, shall be constructed of a minimum 2 inches (51 mm) thick continuous concrete slab. Gaps shall not be permitted between the slab and the abutting foundation walls or columns, except where expansion joints, thermal breaks, and control joints are located. All openings, including but not lim­ited to, annular spaces around pipes, electric cables, and con­duits in the slab shall be protected by closing such openings with cement mortar, concrete masonry, metal plates or screen­ing designed to prevent the passage of rodents.
F102.3 Exterior doors. | Where an exterior door is nonmetal or nonmetal-clad, such door shall be covered with a kick plate of a minimum thickness of 0.033 inch (0.84 mm), extending at least 8 inches (203 mm) from the bottom of the door, and covering the entire width of the door. When closed, the maximum clearance between any door, door jambs and sills shall not be greater than 3/8 inch (9.5 mm).
F102.4 Windows and other openings. | Windows and other openings shall comply with Sections F102.4.1 and F102.4.2.
F102.4.1 Openings within 2 feet of ground level. | Opera­ble windows and other openings providing required or vol­untary natural ventilation located with any portion within 2 feet (610 mm) above outside ground level immediately below such opening shall be covered for their entire height and width of the operable portion with hardware cloth of at least 0.035 inch (0.89 mm) wire or heavier. The openings in the hardware cloth shall not exceed ¼ inch (6.4 mm).
F102.4.2 Rodent-accessible openings. | Operable windows and other openings providing required or voluntary natural ventilation in the exterior located within 2 feet (610 mm) of exposed pipes, wires, conduits and other appurtenances, shall be covered with wire cloth of at least 0.035 inch (0.89 mm) wire. The openings in the hardware cloth shall not exceed ¼inch (6.4 mm).
F102.5 Exterior wall ventilation openings. | Exterior wall ventilator openings located with any portion within 2 feet (610 mm) of outside ground level shall be covered for their height and width with perforated sheet metal plates no less than 0.070 inch (1.8 mm) thick, expanded sheet metal plates not less than 0.047 inch (1.2 mm) thick, cast-iron grills or grating, extruded aluminum load-bearing vents or with hardware cloth of 0.035 inch (0.89 mm) wire or heavier. The openings therein shall not exceed ¼ inch (6.4 mm).
|  | F101.1 General. | Buildings or structures and the walls enclosing habitable or occupiable rooms and spaces in which persons live, sleep or work, or in which feed, food or foodstuffs are stored, prepared, processed, served or sold, shall be constructed in accordance with the provisions of this section.
|  | F101.2 Foundation wall ventilation openings. | Foundation wall ventilation openings shall be covered for their height and width with perforated sheet metal plates not less than 0.070 inch (1.8 mm) thick, expanded sheet metal plates not less than 0.047 inch (1.2 mm) thick, cast-iron grills or grating, extruded aluminum load-bearing vents or with hardware cloth of 0.035 inch (0.89 mm) wire or heavier. The openings therein shall not exceed 1/4 inch (6.4 mm).
|  | F101.3 Foundation and exterior wall sealing. | Annular spaces around pipes, electric cables, conduits or other openings in the walls shall be protected against the passage of rodents by closing such openings with cement mortar, concrete masonry or noncorrosive metal.
|  | F101.4 Doors. | Doors on which metal protection has been applied shall be hinged so as to be free swinging. When closed, the maximum clearance between any door, door jambs and sills shall be not greater than 3/8 inch (9.5 mm).
|  | F101.5 Windows and other openings. | Windows and other openings for the purpose of light or ventilation located in exterior walls within 2 feet (610 mm) above the existing ground level immediately below such opening shall be covered for their entire height and width, including frame, with hardware cloth of not less than 0.035-inch (0.89 mm) wire or heavier.
|  | F101.5.1 Rodent-accessible openings. | Windows and other openings for the purpose of light and ventilation in the exterior walls not covered in this chapter, accessible to rodents by way of exposed pipes, wires, conduits and other appurtenances, shall be covered with wire cloth of at least 0.035-inch (0.89 mm) wire. In lieu of wire cloth covering, said pipes, wires, conduits and other appurtenances shall be blocked from rodent usage by installing solid sheet metal guards 0.024 inch (0.61 mm) thick or heavier. Guards shall be fitted around pipes, wires, conduits or other appurtenances. In addition, they shall be fastened securely to and shall extend perpendicularly from the exterior wall for not less than 12 inches (305 mm) beyond and on either side of pipes, wires, conduits or appurtenances.
F101.6 Pier and wood construction.
|  | F101.6.1 Sill less than 12 inches above ground. | Buildings not provided with a continuous foundation shall be provided with protection against rodents at grade by providing either an apron in accordance with Section F101.6.1.1 or a floor slab in accordance with Section F101.6.1.2.
|  | F101.6.1.1 Apron. | Where an apron is provided, the apron shall be not less than 8 inches (203 mm) above, nor less than 24 inches (610 mm) below, grade. The apron shall not terminate below the lower edge of the siding material. The apron shall be constructed of an approved nondecayable, water-resistant rodentproofing material of required strength and shall be installed around the entire perimeter of the building. Where constructed of masonry or concrete materials, the apron shall be not less than 4 inches (102 mm) in thickness.
|  | F101.6.1.2 Grade floors. | Where continuous concrete-grade floor slabs are provided, open spaces shall not be left between the slab and walls, and openings in the slab shall be protected.
|  | F101.6.2 Sill at or above 12 inches above ground. | Buildings not provided with a continuous foundation and that have sills 12 inches (305 mm) or more above ground level shall be provided with protection against rodents at grade in accordance with any of the following:

## BC-G
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
G101.1 Purpose. | The purpose of this appendix is to promote the public health, safety and general welfare and to minimize public and private losses due to flood conditions in specific flood hazard areas through the establishment of comprehensive regulations for management of flood hazard areas designed to: | G101.1 Purpose. | The purpose of this appendix is to promote the public health, safety and general welfare and to minimize public and private losses due to flood conditions in specific flood hazard areas through the establishment of comprehensive regulations for management of flood hazard areas designed to:
G101.2 Objectives. | The objectives of this appendix are to: | G101.2 Objectives. | The objectives of this appendix are to protect human life, minimize the expenditure of public money for flood control projects, minimize the need for rescue and relief efforts associated with flooding, minimize prolonged business interruption, minimize damage to public facilities and utilities, help maintain a stable tax base by providing for the sound use and development of flood-prone areas, contribute to improved construction techniques in the flood plain and ensure that potential owners and occupants are notified that property is within flood hazard areas.
G101.3 Referenced standards. | Where this code makes reference to the nationally recognized standard ASCE 24, such standard shall be as modified for New York City in accordance with Section G501 of this appendix.
G101.4 Reserved.
G102.1 General. | This appendix, in conjunction with the New York City Construction Codes, provides minimum requirements for development located, in whole or in part, in special flood hazard areas and shaded X-Zones within the jurisdiction of New York City, including: | G102.1 General. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein. Refer to Chapter 2 of this code for general definitions.
G102.2 Establishment of flood hazard areas. | The following flood hazard map and supporting data are adopted as referenced standards and declared to be a part of this appendix.
G102.2.1 Preliminary flood insurance study and rate maps. | Until such time that the department by rule adopts revised FEMA FIS 360497 and FEMA FIRMs 360497 with a final effective date later than April 18, 2018, the following flood hazard maps and supporting data are also adopted as a referenced standard and declared a part of this appendix.
G102.2.2 Effect of preliminary flood insurance study and rate maps. | Notwithstanding any other provision in this appendix to the contrary:
G102.3 Letters of map change. | Map changes to FEMA FIRMs 360497 shall be administered in compliance with Sections G102.3.1 through G102.3.3.
G102.3.1 Letters of map amendment (LOMA). | Where FEMA FIRMs 360497 indicates that a structure or tax lot is within a delineated special flood hazard area, but the pre-FIRM ground elevations adjacent to the structure or throughout the tax lot are at or above the base flood elevation, the commissioner shall deem such structure or tax lot as being within the special flood hazard area and shall not approve plans except in compliance with this appendix, unless a letter of map amendment (LOMA) is issued by FEMA removing such structure or tax lot from the special flood hazard area.
G102.3.1.1 Letters of map amendment (LOMAs) during pendency of PFIRMs. | Until such time that the department by rule adopts revised FEMA FIS 360497 and FEMA FIRMs 360497 with a final effective date later than April 18, 2018, the commissioner shall not deem issuance of a LOMA by FEMA as removing such structure or tax lot from the special flood hazard area unless the elevations specified in the LOMA equal or exceed the applicable corresponding elevations on the FEMA PFIS 360497/FEMA PFIRMs 360497.
G102.3.2 Letter of map revision based on fill (LOMR-F). | Where FEMA FIRMs 360497 indicates that a structure or tax lot is within a delineated special flood hazard area, but post-FIRM compacted fill is proposed to be added adjacent to the structure or throughout the tax lot to an elevation at or above the base flood elevation, the commissioner shall deem such structure or tax lot as being within the special flood hazard area and shall not approve plans except in compliance with this appendix, unless a conditional or final letter of map revision based on fill (LOMR-F) is issued by FEMA removing such structure or tax lot from the special flood hazard area. Buildings constructed with basements below the Base Flood Elevation on filled land shall maintain a minimum setback distance of 20 feet (6096 mm), at or above the Base Flood Elevation, from the edge of the special flood hazard area to the nearest wall of the basement, regardless of the design approach used. The commissioner shall promulgate rules establishing procedures for processing letters of map revision based on fill (LOMR-F).
G102.3.2.1 Letters of map revision based on fill (LOMR-Fs) during pendency of PFIRMs. | Until such time that the department by rule adopts revised FEMA FIS 360497 and FEMA FIRMs 360497 with a final effective date later than April 18, 2018, the commissioner shall not deem issuance of a LOMR-F as removing such structure or tax lot from the special flood hazard area unless the elevations specified in the LOMR-F equal or exceed the applicable corresponding elevations on the FEMA PFIS 360497/FEMA PFIRMs 360497.
G102.3.3 Certificates of occupancy. | Certificates of occupancy shall indicate that the structure or tax lot is subject to a letter of map amendment (LOMA) or letter of map revision based on fill (LOMR-F) as per Section G106.5.
G103.1 Permit applications. | The commissioner is hereby designated as the floodplain administrator for the City of New York and shall review permit applications to determine that:
G103.2 Reserved.
G103.3 Determination of flood elevations. | Flood elevations shall be determined in accordance with Sections G103.3.1 through G103.3.2.
G103.3.1 Determination of base flood elevations. | Where the proposed development is within a special flood hazard area but the base flood elevations are not specified in the FEMA FIRMs 360497, the commissioner shall require the applicant to request base flood elevation data from the New York State Department of Environmental Conservation (DEC); and
G103.3.2 Determination of 500-year flood elevations. | Where 500-year flood elevations are not specified in the FEMA FIRMs 360497 or FEMA FIS 360497, such elevations shall be determined by a registered design professional using modeling based on generally accepted engineering methods or a review of available data from city, state and federal agencies.
G103.4 Reserved.
G103.5 Floodway encroachment. | Prior to issuing a permit for any floodway encroachment, including fill, new construction, substantial improvements and other development or land-disturbing activity, the commissioner shall require submission of a certification, prepared by a registered design professional, along with supporting technical data, demonstrating that such development will not cause any increase of the level of the base flood.
G103.5.1 Floodway revisions. | A floodway encroachment that increases the level of the base flood is authorized if the applicant has applied for a conditional Flood Insurance Rate Map (FIRM) revision and has received the approval of the Federal Emergency Management Agency (FEMA).
G103.6 Watercourse alteration. | Prior to issuing a permit for any alteration or relocation of any watercourse within a special flood hazard area, the commissioner shall require the applicant to:
G103.7 Alterations in coastal areas. | Prior to issuing a permit for any alteration of sand dunes in coastal high-hazard areas and coastal A- zones, the commissioner shall require submission of an engineering analysis, prepared by a registered design professional, demonstrating that the proposed alteration will not increase the potential for flood damage.
G103.8 Records. | The commissioner shall maintain records of the following:
G103.9 Violations. | See Chapter 2 of Title 28 of the Administrative Code.
G104.1 Required. | Any person, owner or owner’s authorized agent who intends to conduct any development, as applicable pursuant to Section G102.1, within a flood hazard area, shall first make application to the commissioner and shall obtain the required permit in accordance with Section 28-105.1 of the Administrative Code, notwithstanding any exemption pursuant to Section 28-105.4 of the Administrative Code.
G104.2 Application for permit. | The applicant shall file an application in writing on a form furnished by the commissioner. The commissioner shall not approve such application unless the applicant submits all plans, details, data and documents demonstrating that the development complies with Sections G104.2.1 through G104.2.3 and all other provisions of this appendix.
G104.2.1 Flood zone compliance plans. | The permit application shall include flood zone compliance plans. Such plans shall include plans and drawings, shall be sealed by a registered design professional and shall include a site plan and the following information and any other data as may be required by the department:
G104.2.2 Watercourse alteration. | The permit application shall include documentation required by Section G103.6 and, if applicable, a description of the extent to which any watercourse will be altered or relocated as a result of proposed development.
G104.2.3 Certifications. | The permit application shall include the applicable certifications in accordance with Sections G104.2.3.1 through G104.2.3.3.
G104.2.3.1 A-Zones. | For construction in A-Zones, the permit application shall include the following certifications, as applicable:
G104.2.3.2 Coastal high-hazard areas and coastal A-Zones. | For construction in coastal high-hazard areas and coastal A-Zones, the permit application shall include the following certifications, as applicable:
G107.1 General. | Periodic, progress and special inspections shall be performed in accordance with this section. All work applications, regardless of the scope of work, shall be subject to the progress and special inspection requirements of Sections G107.2 through G107.4. | G107.1 General. | Any subdivision proposal, including proposals for manufactured home parks and subdivisions, or other proposed new development in a flood hazard area shall be reviewed to verify all of the following:
G104.2.3.3 Floodway encroachment certification. | For any floodway encroachment, including fill, new construction, substantial improvements and other development or land-disturbing activity, the applicant shall submit a certification, along with supporting technical data, demonstrating that such development will not cause any increase of the level of the base flood in accordance with the requirements of Section G103.5.
G104.3 Validity of permit. | The issuance of a permit under this appendix shall not be construed to be a permit for, or approval of, any violation of this appendix or any other provision of this code. The issuance of a permit based on submitted documents and information shall not prevent the commissioner from requiring the correction of errors. The commissioner is authorized to prevent occupancy or use of a structure or site that is in violation of this appendix or other provisions of this code.
G104.4 Expiration. | A permit shall become invalid if the proposed development is not commenced within 180 days after its issuance, or if the work authorized is suspended or abandoned for a period of 180 days after the work commences.
G104.5 Suspension or revocation. | The commissioner is authorized to suspend or revoke a permit issued under this appendix wherever the permit is issued in error or on the basis of incorrect, inaccurate or incomplete information, or in violation of this code, in accordance with Section 28-105 of the Administrative Code.
G104.6 Reinstatement. | Permit reinstatements for a permit that has expired pursuant to Section G104.4 shall be requested in writing. The commissioner is authorized to grant such reinstatement, provided that the work shall comply with all of the requirements of this appendix, including any revised FEMA FIRMs 360497 in effect at the time the application for reinstatement is made, and provided further that the applicant shall pay all reinstatement fees as required in Article 112 of Title 28 of the Administrative Code.
G105.1 General. | The Board of Standards and Appeals shall hear and decide requests for variances from the requirements of this appendix. The Board of Standards and Appeals shall base its determination on technical justifications, and has the right to attach such conditions to variances as it deems necessary to further the purposes and objectives of this appendix.
G105.2 Records. | The Board of Standards and Appeals shall:
G105.3 Historic structures. | A variance is authorized to be issued by the Board of Standards and Appeals for the repair or rehabilitation of a historic structure upon a determination that the proposed repair or rehabilitation will not preclude the structure’s continued designation as a historic structure, and the variance is the minimum necessary to preserve the historic character and design of the structure.
G105.4 Functionally dependent facilities. | The Board of Standards and Appeals is authorized to issue a variance for the construction or substantial improvement of a functionally dependent facility provided the criteria in Sections G105.3, G105.5 and G105.7 are met and the variance is the minimum necessary to allow the construction or substantial improvement, and that all due consideration has been given to methods and materials that minimize flood damages during the base flood and create no additional threats to public safety.
G105.5 Floodway restrictions. | The Board of Standards and Appeals shall not issue a variance for any proposed development in a floodway if any increase in flood levels would result during the base flood discharge.
G105.6 Conditions. | In reviewing applications for variances, the Board of Standards and Appeals shall consider all technical evaluations, all relevant factors, all other portions of this appendix and the following:
G105.7 Conditions for issuance. | Except for historic structures as provided for in Section G105.3, the Board of Standards and Appeals is authorized to issue a variance where all of the following criteria are met:
G106.1 Applicability. | This section shall apply to post-FIRM construction and substantial improvements where the work results in the issuance of a new or amended certificate of occupancy.
G106.2 Enclosed areas subject to flooding in A-Zones. | The certificate of occupancy shall describe all enclosed areas below the design flood elevation that are subject to flooding and that meet the requirements of this appendix for wet floodproofing as wet floodproofed, subject to flooding. The certificate of occupancy shall indicate the use of wet floodproofed spaces as either parking, storage, building access or crawl spaces. The certificate of occupancy shall be issued with the following restriction: “Levels subject to flooding shall not be used for any other use except as stated on this certificate.”
G106.3 Enclosed areas subject to flooding in coastal high-hazard areas and coastal A-Zones. | The certificate of occupancy shall describe all enclosed areas below the design flood elevation that are not dry floodproofed as subject to flooding. The certificate of occupancy shall indicate the use of spaces enclosed by open lattice breakaway walls below the design flood elevation as either unconditioned parking, unconditioned storage, or unconditioned building access. The certificate of occupancy shall be issued with the following restriction: Levels subject to flooding shall not be used for any other use except as stated on this certificate.
G106.4 Dry floodproofed spaces. | The certificate of occupancy shall describe any dry floodproofed spaces as dry floodproofed. Where flood shields or other flood control devices are installed, the certificate of occupancy shall also provide notations describing these features. For evacuated buildings or evacuated portions of buildings utilizing the temporary stair or ramp provisions of Section G308.10.1, the certificate of occupancy shall note In portions of this building planned to be evacuated during flood conditions, occupancy shall be prohibited except for maintenance or emergency personnel.
G106.4.1 Restrictive declaration. | Where dry floodproofed buildings contain dwelling units, patient care areas (for flood zone purposes) or spaces intended to be used by persons for sleeping purposes, the certificate of occupancy shall also provide notations as required by Section G304.1.2, Item 2.2.
G106.5 Letters of map change. | Where applicable, the certificate of occupancy shall indicate that “the structure is exempted from the special flood hazard area pursuant to FEMA Letter of Map Amendment (LOMA) # (_______),” or that “the structure is exempted from the special flood hazard area pursuant to FEMA Letter of Map Revision Based on Fill (LOMR-F) # (_______),” or that “the structure is exempted from the special flood hazard area pursuant to FEMA Letter of Map Revision (LOMR) # (_______).”
G107.2 All work applications other than new buildings, horizontal enlargements and substantial improvements. | All work applications other than new buildings, horizontal enlargements and substantial improvements, shall be subject to the following special inspection:
G107.3 New buildings, horizontal enlargements and substantial improvements. | All applications for new buildings, horizontal enlargements or substantial improvements shall be subject to the following inspections:
G107.4 Flood shield inspection. | Where flood shields or other flood control devices are installed as part of a dry floodproofing system in buildings and structures that are nonresidential (for flood zone purposes), the special inspector or special inspection agency responsible for the flood zone compliance special inspection shall inspect the shields or devices in their stored positions or locations, witness their activation or transportation to their installed positions, and witness their deactivation or transportation back to their stored locations. The special inspector or special inspection agency shall also confirm the installation of signage required by ASCE 24, Section 6.2.3, Item 3.
G107.5 Periodic inspections of dry floodproofing systems. | Covered buildings, as described in Section 28-324 of the Administrative Code, shall be subject to periodic inspections for dry floodproofing systems in accordance with Sections G107.5.1 and G107.5.2.
G107.5.1 Annual inspection of dry floodproofing system. | An inspection of the dry floodproofing system shall be conducted annually in accordance with Section 28-324.2 of the Administrative Code.
G107.5.2 Triennial full scale deployment inspection. | A full-scale deployment inspection shall be conducted every three years in accordance with Section 28-324.3 of the Administrative Code.
G201.1 Definitions. | This section contains terms defined elsewhere in this code, and terms with definitions that are specific to this appendix.
G201.1.1 Terms defined elsewhere in this code. | The following terms are defined in Chapter 2:
G201.1.2 Definitions specific to this appendix. | The following words and terms shall, for the purposes of this appendix, have the meanings shown herein:
G301.1 All developments. | To the extent required by Section G102.1, all developments, including but not limited to utility installation, site improvements, placement of prefabricated buildings and manufactured homes, new building construction, alterations and repairs, shall be designed and constructed to resist the effects of flood hazards and flood loads in accordance with this appendix and ASCE 24.
G301.1.1 Multiple flood zones. | For a structure that is located in more than one zone (for instance both an A-Zone and an X-Zone, or both an A-Zone and a V-Zone), the provisions associated with the most restrictive zone shall apply to the entire structure.
G301.2 Design requirements and load combinations. | Any construction subject to the requirements of Section G102.1 shall be designed and constructed to resist the loads and load combinations specified in Chapter 16.
G302.1 General. | Any subdivision proposal, including proposals for manufactured home parks and subdivisions, or other proposed new development within a special flood hazard area shall be reviewed to verify all of the following:
G302.2 Subdivision requirements. | The following requirements shall apply in the case of any proposed subdivision, including proposals for manufactured home parks and subdivisions, any portion of which lies within a special flood hazard area:
G303.1 Development in floodways. | Development or land-disturbing activity shall not be authorized in the floodway unless it has been demonstrated through hydrologic and hydraulic analyses performed in accordance with standard engineering practice, and prepared by a registered design professional, that the proposed encroachment will not result in any increase in the base flood level, in accordance with Section G103.5.
G303.2 Coastal high-hazard areas and coastal A-Zones. | In coastal high-hazard areas and coastal A-Zones:
G303.3 Sewer facilities. | All new or replaced sanitary sewer facilities, private sewage treatment plants (including all pumping stations and collector systems) and on-site waste disposal systems shall be designed in accordance with Chapter 7, ASCE 24, to minimize or eliminate infiltration of floodwaters into the facilities and discharge from the facilities into floodwaters, or impairment of the facilities and systems.
G303.4 Water facilities. | All new or replacement water facilities shall be designed in accordance with the provisions of Chapter 7, ASCE 24, to minimize or eliminate infiltration of floodwaters into the systems.
G303.5 Storm drainage. | Storm drainage shall be designed to convey the flow of surface waters to minimize or eliminate damage to persons or property and shall meet the requirements of ASCE 24.
G303.6 Streets and sidewalks. | Streets and sidewalks shall be designed to minimize potential for increasing or aggravating flood levels and shall meet the requirements of Section G303.8.
G303.7 Retaining walls and driveways. | Retaining walls shall be designed in accordance with Section 1807. Retaining walls and driveways shall meet the requirements of Section G303.8.
G303.8 Grading and fill. | In flood hazard areas, grading and/or fill shall not be approved:
G304.1 A-Zone construction standards. | In addition to the requirements of ASCE 24, the following standards shall apply to post-FIRM construction, horizontal enlargements and substantial improvements located within A-Zones, other than Coastal A-Zones.
G304.1.1 Residential. | For buildings or structures that are residential (for flood zone purposes), all post-FIRM new buildings, horizontal enlargements and substantial improvements shall comply with the applicable requirements of this appendix and ASCE 24, and shall be elevated as follows:
G304.1.2 Nonresidential. | For buildings or structures that are nonresidential (for flood zone purposes), all post-FIRM new buildings, horizontal enlargements and substantial improvements shall comply with the applicable requirements of this appendix and ASCE 24, and shall comply with either of the following:
G304.2 Coastal high-hazard area construction standards. | In addition to the requirements of ASCE 24, the following standards shall apply to post-FIRM construction, horizontal enlargements and substantial improvements located within coastal high-hazard area.
G304.3 Coastal A-Zone construction standards. | In addition to the requirements of ASCE 24, all post-FIRM new buildings, horizontal enlargements and substantial improvements in a Coastal A-Zone shall comply with the coastal high-hazard area construction standards of Section G304.2.
G304.4 Construction standards for shaded X-Zones. | In shaded X-Zones, flood design class 4 buildings, as defined in ASCE 24, Table 1-1, shall comply with the requirements of this appendix and the applicable provisions of ASCE 24 for A-Zone construction.
G304.4.1 Alterations to certain flood design class 4 buildings. | Where existing emergency vehicle garages and fire, rescue, ambulance, and police stations located within shaded X-Zones are undergoing either a substantial improvement or an increase in the degree of noncompliance as such term is described in Item 10 of Section G102.1, they shall comply with this appendix to the maximum extent practicable as described in Sections G304.4.1.1 through G304.4.1.4.
G304.4.1.1 Existing emergency vehicle garages and fire, rescue, ambulance, and police stations to remain. | Where an existing emergency vehicle garage or fire, rescue, ambulance, or police station building is undergoing substantial improvement or an increase in the degree of noncompliance, such existing emergency vehicle storage area shall be permitted to be located below the design flood elevation, provided such space is wet floodproofed in accordance with ASCE 24 and an emergency action plan is filed with the department in accordance with ASCE 24, Section 6.2.3. Such emergency action plan shall include actionable directives for the relocation of such emergency vehicles in advance of a flood event.
G304.4.1.2 Equipment within existing emergency vehicle garages and fire, rescue, ambulance, and police stations. | Where an existing emergency vehicle garage or fire, rescue, ambulance, or police station building is undergoing substantial improvement or an increase in the degree of noncompliance, equipment necessary to support operations of such facilities may be located below the design flood elevation where elevation of such equipment to the design flood elevation is physically unfeasible. Such equipment shall be elevated to the maximum extent practicable.
G304.4.1.3 Conversion of space below the design flood elevation. | Conversion of existing nonoccupiable space to occupiable space without such space being in full compliance with this appendix shall be prohibited.
G304.4.1.4 Subgrade spaces to remain. | Where an existing emergency vehicle garage or fire, rescue, ambulance, or police station building is undergoing substantial improvement or an increase in the degree of noncompliance, the existing subgrade space shall be provided with a sump pump system, designed to be fully submerged and remain operational post-flood-event to remove flood waters after a storm surge has receded. Such pump system shall be designed with the pump controller located above the design flood elevation and all electrical wiring below the design flood elevation shall be listed and marked for use with a submersible pump. The pump system shall be connected to a standby power source, which shall be elevated above the design flood elevation.
G304.5 Additional construction standards with respect to connections for temporary external generators, boilers and chillers. | In addition to the other requirements of this appendix, connections for temporary external generators, boilers and chillers shall be provided in accordance with Sections G304.5.1 through G304.5.4.
G304.5.1 Group I-1 and adult homes, enriched housing, community residences and intermediate care facilities. | An occupancy that is classified as Group I-1, or that is an adult home, enriched housing, community residence or intermediate care facility and classified as Group R pursuant to an exception to Section 308.3.1 or 308.3.2, shall comply with the following requirements:
G304.5.2 Group I-2 hospitals. | An occupancy that is a Group I-2 hospital shall comply with the following requirements:
G304.5.3 Group I-2 nursing homes. | An occupancy that is a Group I-2 nursing home shall comply with Section G304.5.2.
G304.5.4 Group I-2 occupancies, other than hospitals and nursing homes. | A Group I-2 occupancy, other than a hospital or a nursing home, shall comply with Section G304.5.1.
G305.1 Elevation. | All new and replacement manufactured homes shall be prohibited in coastal high-hazard areas. Within A-Zones, all new, replaced or substantially improved manufactured homes shall be elevated such that the lowest floor of the manufactured home is elevated to or above the design flood elevation as specified in ASCE 24, Table 2-1.
G305.2 Foundations. | Within A-Zones, all new and replacement manufactured homes, including substantial improvement of existing manufactured homes, shall be placed on a permanent, reinforced foundation that is designed in accordance with ASCE 24.
G305.3 Anchoring. | Manufactured homes shall be securely anchored to an adequately anchored foundation system to resist flotation, collapse and lateral movement. Methods of anchoring are authorized to include, but are not limited to, use of over-the-top or frame ties to ground anchors. This requirement is in addition to applicable state and local anchoring requirements for resisting wind forces.
G305.4 Protection of mechanical equipment and outside appliances. | Mechanical equipment and outside appliances shall be elevated to or above the design flood elevation.
G305.5 Enclosures. | Fully enclosed areas below elevated manufactured homes shall comply with the requirements of Section G304.1.1, Item 2.
G306.1 Placement prohibited. | The placement of recreational vehicles shall not be authorized in coastal high-hazard areas or in floodways.
G306.2 Temporary placement in A-Zones. | Recreational vehicles in A-Zones shall be fully licensed and ready for highway use, and shall be placed on a site for less than 180 consecutive days.
G306.3 Permanent placement. | Recreational vehicles in A-Zones that are not fully licensed and ready for highway use, or that are to be placed on a site for 180 or more consecutive days, shall meet the requirements of Section G305 for manufactured homes.
G307.1 Underground tanks. | Underground tanks in special flood hazard areas shall be designed, constructed, installed, and anchored to prevent flotation, collapse and lateral movement resulting from hydrostatic loads, including the effects of buoyancy, during conditions of flooding to the design flood elevation, in accordance with ASCE 24.
G307.2 Above-ground tanks. | Above-ground tanks in special flood hazard areas shall be:
G307.3 Tank inlets and vents. | In special flood hazard areas, tank inlets, fill openings, outlets and vents shall be:
G307.4 Additional fuel-oil storage capacity. | Fuel-oil storage capacity in special flood hazard areas and shaded X-Zones shall comply with the following:
G307.4.1 Additional requirements. | Where fuel-oil storage capacity exceeds the quantity set forth in Section 1305.11.1.3 of the New York City Mechanical Code, the fuel-oil storage shall comply with Sections G307.4.1.1 and G307.4.1.2 in addition to Section 1305 of the New York City Mechanical Code.
G307.4.1.1 Vault. | Each fuel-oil storage tank shall be separately enclosed in a vault complying with all of the following requirements:
G307.4.1.2 Extinguishing system. | Fuel-oil storage shall be protected with an alternative automatic fire-extinguishing system complying with Section 904.
G307.5 Elevation of certain tanks and containers serving flood design class 4 buildings. | The following tanks and containers shall be located at or above the design flood elevation specified in ASCE 24, Table 7-1, when serving flood design class 4 buildings. Such tanks and containers must be designed to maintain service to such structure during flood conditions and shall comply with Section 9.7 of ASCE 24:
G308.1 Garages and accessory structures. | Garages and accessory structures shall be designed and constructed in accordance with ASCE 24, Section 9.4.
G308.2 Fences. | Fences in floodways that may block the passage of floodwaters, such as stockade fences and wire mesh fences, shall meet the requirement of Section G103.5.
G308.3 Oil derricks. | Oil derricks located in special flood hazard areas shall be designed in conformance with ASCE 24.
G308.4 Retaining walls, sidewalks and driveways. | Retaining walls, sidewalks and driveways shall meet the requirements of Sections G303.6 and G303.7.
G308.5 Swimming pools. | Swimming pools shall be designed and constructed in accordance with ASCE 24. Above-ground swimming pools, on-ground swimming pools and in-ground swimming pools that involve placement of fill in floodways shall also meet the requirements of Section G103.5.
G308.6 Decks, porches, and patios. | Decks, porches and patios shall be designed and constructed in accordance with ASCE 24.
G308.7 Nonstructural concrete slabs in coastal high-hazard areas and coastal A-Zones. | In coastal high-hazard areas and coastal A-Zones, nonstructural concrete slabs used as parking pads, enclosure floors, landings, decks, walkways, patios and similar nonstructural uses are permitted beneath or adjacent to buildings and structures provided that the concrete slabs shall be constructed in accordance with ASCE 24, Section 9.3.
G308.8 Roads and watercourse crossings in regulated floodways. | Roads and watercourse crossings that encroach into regulated floodways, including roads, bridges, culverts, low-water crossings and similar means for vehicles or pedestrians to travel from one side of a watercourse to the other, shall meet the requirement of Section G103.5.
G308.9 Temporary flood shields. | Temporary flood shields shall be permitted in accordance with Section 6.2.3 of ASCE 24. Temporary flood shields shall be located and arranged so as to allow hose lines to be attached to the inlets of fire department connections without interference in accordance with Section 6.4.5 of NFPA 14 as modified by Appendix Q. Where temporary flood shields extend beyond the property line, Section 3202 for permitted encroachments into the public right-of-way shall apply.
G308.10 Temporary stairs and ramps. | Temporary stairs and ramps shall comply with the requirements of Sections G308.10.1 and G308.10.2. Temporary stairs and ramps shall be located and arranged so as to allow hose lines to be attached to the inlets of fire department connections without interference in accordance with Section 6.4.5 of NFPA 14, as modified by Appendix Q. Where temporary stairs and ramps extend beyond the property line, Section 3202 for permitted encroachments into the public right-of-way shall apply.
G308.10.1 Evacuated buildings. | Temporary stairs and ramps shall be permitted to provide elevated ingress and egress in compliance with Item 3 of Section 6.2.2 of ASCE 24 for buildings or portions of buildings that are planned to be evacuated during design flood conditions, except for maintenance and emergency personnel, provided that such temporary stairs and ramps shall not be permitted to serve as a required means of egress for a dwelling unit or for any area described in Item 2.2.1 of Section G304.1.2 required to be located at or above the design flood elevation.
G308.10.2 Existing buildings. | Temporary stairs and ramps for an existing building or portions thereof shall be permitted to provide elevated ingress and egress in compliance with Item 3 of Section 6.2.2 of ASCE 24, including as a required means of egress for dwelling units or for areas described in Item 2.2.1 of Section G304.1.2 required to be located at or above the design flood elevation, where such temporary stairs and ramps comply with Sections 1009 and 1010.
G308.11 Alterations to pre-FIRM buildings involving flood protective works. | Where alterations to pre-FIRM buildings within the flood hazard area, other than substantial improvements or horizontal enlargements, include the installation of flood protective works, compliance with ASCE 24, Section 6.2.2 shall be required. Flood protective works shall be located and arranged so as to allow hose lines to be attached to the inlets of fire department connections without interference in accordance with Section 6.4.5 of NFPA 14, as modified by Appendix Q of this code.
G309.1 Temporary structures. | Temporary structures shall be erected for a period of less than 180 days. Temporary structures shall be anchored to prevent flotation, collapse or lateral movement resulting from hydrostatic loads, including the effects of buoyancy, during conditions of the base flood. Fully enclosed temporary structures shall have flood openings that are in accordance with ASCE 24 to allow for the automatic entry and exit of floodwaters.
G309.2 Temporary storage. | Temporary storage includes storage of goods and materials for a period of fewer than 180 days. Stored materials shall not include hazardous materials.
G309.3 Floodway encroachment. | Temporary structures and temporary storage in floodways shall meet the requirements of Section G103.5.
G310.1 Utility and miscellaneous Group U. | Section G310 shall govern utility and miscellaneous Group U, including buildings that are accessory in character and miscellaneous structures not classified in any specific occupancy in this code, including, but not limited to, agricultural buildings, aircraft hangars (accessory to a one- or two-family residence), barns, carports, fences more than 6 feet (1829 mm) high, grain silos (accessory to a residential occupancy), greenhouses, livestock shelters, private garages, retaining walls, sheds, stables and towers.
G310.2 Flood loads. | Utility and miscellaneous Group U buildings and structures, including substantial improvement of such buildings and structures, shall be anchored to prevent flotation, collapse or lateral movement resulting from flood loads, including the effects of buoyancy, during conditions of the design flood.
G310.3 Elevation. | Utility and miscellaneous Group U buildings and structures, including substantial improvement of such buildings and structures, shall be elevated such that the lowest floor, including basement, is elevated to or above the design flood elevation specified in ASCE 24, unless otherwise permitted to comply with requirements of Section 9.4 of ASCE 24.
G310.4 Enclosures below design flood elevation. | Fully enclosed areas below the design flood elevation shall be constructed in accordance with Section G304.
G310.5 Flood-damage-resistant materials. | Flood-damage-resistant materials shall be used below the design flood elevation.
G310.6 Protection of mechanical, plumbing and electrical systems. | Mechanical, plumbing and electrical systems, including plumbing fixtures, shall be elevated to or above the design flood elevation.
G311.1 Hazardous substances. | Portable containers located in the flood hazard area that store hazardous substances, as defined in Section 41-03 of Title 15 of the Rules of the City of New York, shall comply with Section 41-14 of Title 15 of the Rules of the City of New York.
G312.1 General. | Notwithstanding any other provision of the New York City Construction Codes, the provisions of this section shall apply retroactively to all buildings and structures specified herein.
G312.2 Connections for temporary external generators. | The following buildings shall be provided with connections for temporary external generators in accordance with Sections G304.5.1 through G304.5.4, as applicable, by January 1, 2033, and a report detailing compliance with such requirements shall be filed with the department in accordance with Section G312.2.2 by such date:
G312.2.1 Modification to the flood hazard area. | Where the special flood hazard area or shaded X-Zone is modified on or after the effective date of this section, any building identified in Section G312.2 and newly identified as being within such modified special flood hazard area or shaded X-Zone shall, no later than 20 years following the adoption of such modification, comply with the retroactive requirements of Section G312.2. The owner of such building shall, no later than 20 years following the adoption of such modification, file with the department a report detailing compliance with such requirements in accordance with Section G312.2.2.
G312.2.2 Report of compliance. | The owner of a building required to comply with the provisions of Section G312.2 shall file with the department, by January 1, 2033, a report prepared by a registered design professional or licensed master electrician (i) certifying that the requirements of Section G312.2 have been satisfied and detailing how such requirements were satisfied or (ii) certifying that the building met or was altered to meet the provisions of any applicable exception in Sections G304.5.1 or G304.5.2.
G312.2.3 Filing. | The department may promulgate rules establishing filing fees for the review and examination of such reports.
G312.3 Connections for temporary external boilers and chillers. | Buildings whose main use or dominant occupancy is Group I-2 hospital and that are located in a flood hazard area shall be provided with connections for temporary external boilers and chillers in accordance with Section G304.5.2 by January 1, 2033, and a report detailing compliance with such requirements shall be filed with the department in accordance with Section G312.3.2 by such date.
G312.3.1 Modification to the flood hazard area. | Where the special flood hazard area or shaded X-Zone is modified on or after the effective date of this section, any building whose main use or dominant occupancy is Group I-2 hospital and that is newly identified as being within such modified special flood hazard area or shaded X-Zone shall comply with the retroactive requirements of Section G312.3 no later than 20 years following the adoption of such modification. The owner of such building shall file with the department a report detailing compliance with such requirements in accordance with Section 312.3.2 no later than 20 years following the adoption of such modification.
G312.3.2 Report of compliance. | The owner of a building required to comply with the provisions of Section G312.3 shall file with the department, by January 1, 2033, a report prepared by a registered design professional (i) certifying that the requirements of Section G312.3 have been satisfied and detailing how such requirements were satisfied or (ii) certifying that any boiler and chiller plants that serve the spaces specified in Item 2 of Section G304.5.2 are located at or above the design flood elevation specified in Table 7-1 of ASCE 24.
G312.3.3 Filing. | The department may promulgate rules establishing filing fees for the review and examination of such reports.
G401.1 General. | This section lists the standards that are referenced in various sections of this appendix. The standards are listed herein by the promulgating agency of the standard, the standard identification, the effective date and title and the section or sections of this document that reference the standard.
G401.2 Subsequent additions, modifications or deletions. | Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to these standards in accordance with Section 28-103.19 of the Administrative Code.
G401.3 Applicability. | The application of the referenced standards shall be as specified in Section G105.1.
G501.1 Amendments to ASCE 24-14. | The following amendments are hereby made to the applicable sections of ASCE 24-14. Refer to the rules of the department for any subsequent additions, modifications or deletions that may have been made to this standard in accordance with Section 28-103.19 of the Administrative Code.
|  | G101.3 Scope. | The provisions of this appendix shall apply to all proposed development in a flood hazard area established in Section 1612 of this code, including certain building work exempt from permit under Section 105.2.
|  | G101.4 Violations. | Any violation of a provision of this appendix, or failure to comply with a permit or variance issued pursuant to this appendix or any requirement of this appendix, shall be handled in accordance with Section 114.
|  | G101.5 Designation of floodplain administrator. | The is designated as the floodplain administrator and is authorized and directed to enforce the provisions of this appendix. The floodplain administrator is authorized to delegate performance of certain duties to other employees of the jurisdiction. Such designation shall not alter any duties and powers of the building official.
|  | G103.1 General. | This appendix, in conjunction with this code, provides minimum requirements for development located in flood hazard areas, including:
|  | G103.2 Establishment of flood hazard areas. | Flood hazard areas are established in Section 1612.3 of this code, adopted by the applicable governing authority on .
|  | G104.1 Permit applications. | All applications for permits shall comply with the following:
|  | G104.2 Other permits. | It shall be the responsibility of the floodplain administrator to ensure that approval of a proposed development shall not be given until proof that necessary permits have been granted by federal or state agencies having jurisdiction over such development.
|  | G104.3 Determination of design flood elevations. | If design flood elevations are not specified, the floodplain administrator is authorized to require the applicant to meet one of the following:
|  | G104.4 Activities in riverine flood hazard areas. | In riverine flood hazard areas where design flood elevations are specified but floodways have not been designated, the floodplain administrator shall not permit any new construction, substantial improvement or other development, including fill, unless the applicant submits an engineering analysis prepared by a registered design professional, demonstrating that the cumulative effect of the proposed development, when combined with all other existing and anticipated flood hazard area encroachment, will not increase the design flood elevation more than 1 foot (305 mm) at any point within the community.
|  | G104.5 Floodway encroachment. | Prior to issuing a permit for any floodway encroachment, including fill, new construction, substantial improvements and other development or land-disturbing activity, the floodplain administrator shall require submission of a certification, prepared by a registered design professional, along with supporting technical data, demonstrating that such development will not cause any increase of the base flood level.
|  | G104.5.1 Floodway revisions. | A floodway encroachment that increases the level of the base flood is authorized if the applicant has applied for a conditional Flood Insurance Rate Map (FIRM) revision and has received the approval of the Federal Emergency Management Agency (FEMA).
|  | G104.6 Watercourse alteration. | Prior to issuing a permit for any alteration or relocation of any watercourse, the floodplain administrator shall require the applicant to provide notification of the proposal to the appropriate authorities of all adjacent government jurisdictions, as well as appropriate state agencies. A copy of the notification shall be maintained in the permit records and submitted to FEMA.
|  | G104.6.1 Engineering analysis. | The floodplain administrator shall require submission of an engineering analysis, prepared by a registered design professional, demonstrating that the flood-carrying capacity of the altered or relocated portion of the watercourse will not be decreased. Such watercourses shall be maintained in a manner that preserves the channel’s flood-carrying capacity.
|  | G104.7 Alterations in coastal areas. | Prior to issuing a permit for any alteration of sand dunes and mangrove stands in coastal high-hazard areas and coastal A zones, the floodplain administrator shall require submission of an engineering analysis, prepared by a registered design professional, demonstrating that the proposed alteration will not increase the potential for flood damage.
|  | G104.8 Records. | The floodplain administrator shall maintain a permanent record of all permits issued in flood hazard areas, including supporting certifications and documentation required by this appendix and copies of inspection reports, design certifications and documentation of elevations required in Section 1612 of this code and Section R322 of the International Residential Code.
|  | G104.9 Inspections. | Development for which a permit under this appendix is required shall be subject to inspection. The floodplain administrator or the floodplain administrator’s designee shall make, or cause to be made, inspections of all development in flood hazard areas authorized by issuance of a permit under this appendix.
|  | G104.10 Use of changed technical data. | The floodplain administrator and the applicant shall not use changed flood hazard area boundaries or base flood elevations for proposed buildings or developments unless the floodplain administrator or applicant has applied for a conditional Flood Insurance Rate Map (FIRM) revision and has received the approval of the Federal Emergency Management Agency (FEMA).
|  | G105.1 Required. | Any person, owner or owner’s authorized agent who intends to conduct any development in a flood hazard area shall first make application to the floodplain administrator and shall obtain the required permit.
|  | G105.2 Application for permit. | The applicant shall file an application in writing on a form furnished by the floodplain administrator. Such application shall:
|  | G105.3 Validity of permit. | The issuance of a permit under this appendix shall not be construed to be a permit for, or approval of, any violation of this appendix or any other ordinance of the jurisdiction. The issuance of a permit based on submitted documents and information shall not prevent the floodplain administrator from requiring the correction of errors. The floodplain administrator is authorized to prevent occupancy or use of a structure or site that is in violation of this appendix or other ordinances of this jurisdiction.
|  | G105.4 Expiration. | A permit shall become invalid if the proposed development is not commenced within 180 days after its issuance, or if the work authorized is suspended or abandoned for a period of 180 days after the work commences. Extensions shall be requested in writing and justifiable cause demonstrated. The floodplain administrator is authorized to grant, in writing, one or more extensions of time, for periods not more than 180 days each.
|  | G105.5 Suspension or revocation. | The floodplain administrator is authorized to suspend or revoke a permit issued under this appendix wherever the permit is issued in error or on the basis of incorrect, inaccurate or incomplete information, or in violation of any ordinance or code of this jurisdiction.
|  | G106.1 General. | The board of appeals established pursuant to Section 113, or other established or designed board, shall hear and decide requests for variances. The board shall base its determination on technical justifications, and has the right to attach such conditions to variances as it deems necessary to further the purposes and objectives of this appendix and Section 1612.
|  | G106.2 Records. | The floodplain administrator shall maintain a permanent record of all variance actions, including justification for their issuance.
|  | G106.3 Historic structures. | A variance is authorized to be issued for the repair or rehabilitation of a historic structure upon a determination that the proposed repair or rehabilitation will not preclude the structure’s continued designation as a historic structure, and the variance is the minimum necessary to preserve the historic character and design of the structure.
|  | G106.4 Functionally dependent facilities. | A variance is authorized to be issued for the construction or substantial improvement of a functionally dependent facility provided that the criteria in Section 1612.1 are met and the variance is the minimum necessary to allow the construction or substantial improvement, and that all due consideration has been given to methods and materials that minimize flood damages during the design flood and do not create additional threats to public safety.
|  | G106.5 Restrictions. | The board shall not issue a variance for any proposed development in a floodway if any increase in flood levels would result during the base flood discharge.
|  | G106.6 Considerations. | In reviewing applications for variances, the board shall consider all technical evaluations, all relevant factors, all other portions of this appendix and the following:
|  | G106.7 Conditions for issuance. | Variances shall only be issued by the board where all of the following criteria are met:
|  | G107.2 Subdivision requirements. | The following requirements shall apply in the case of any proposed subdivision, including proposals for manufactured home parks and subdivisions, any portion of which lies within a flood hazard area:
|  | G108.1 Development in floodways. | Development or land-disturbing activity shall not be authorized in the floodway unless it has been demonstrated through hydrologic and hydraulic analyses performed in accordance with standard engineering practice, and prepared by a registered design professional, that the proposed encroachment will not result in any increase in the base flood level.
|  | G108.2 Coastal high-hazard areas and coastal A zones. | In coastal high-hazard areas and coastal A zones:
|  | G108.3 Sewer facilities. | All new or replaced sanitary sewer facilities, private sewage treatment plants (including all pumping stations and collector systems) and on-site waste disposal systems shall be designed in accordance with Chapter 7, ASCE 24, to minimize or eliminate infiltration of floodwaters into the facilities and discharge from the facilities into floodwaters, or impairment of the facilities and systems.
|  | G108.4 Water facilities. | All new or replacement water facilities shall be designed in accordance with the provisions of Chapter 7, ASCE 24, to minimize or eliminate infiltration of floodwaters into the systems.
|  | G108.5 Storm drainage. | Storm drainage shall be designed to convey the flow of surface waters to minimize or eliminate damage to persons or property.
|  | G108.6 Streets and sidewalks. | Streets and sidewalks shall be designed to minimize potential for increasing or aggravating flood levels.
|  | G109.1 Elevation. | All new and replacement manufactured homes to be placed or substantially improved in a flood hazard area shall be elevated such that the lowest floor of the manufactured home is elevated to or above the design flood elevation.
|  | G109.2 Foundations. | All new and replacement manufactured homes, including substantial improvement of existing manufactured homes, shall be placed on a permanent, reinforced foundation that is designed in accordance with Section R322 of the International Residential Code.
|  | G109.3 Anchoring. | All new and replacement manufactured homes to be placed or substantially improved in a flood hazard area shall be installed using methods and practices that minimize flood damage. Manufactured homes shall be securely anchored to an adequately anchored foundation system to resist flotation, collapse and lateral movement. Methods of anchoring are authorized to include, but are not limited to, use of over-the-top or frame ties to ground anchors. This requirement is in addition to applicable state and local anchoring requirements for resisting wind forces.
|  | G109.4 Protection of mechanical equipment and outside appliances. | Mechanical equipment and outside appliances shall be elevated to or above the design flood elevation.
|  | G109.5 Enclosures. | Fully enclosed areas below elevated manufactured homes shall comply with the requirements of Section R322 of the International Residential Code.
|  | G110.1 Placement prohibited. | The placement of recreational vehicles shall not be authorized in coastal high-hazard areas and in floodways.
|  | G110.2 Temporary placement. | Recreational vehicles in flood hazard areas shall be fully licensed and ready for highway use, or shall be placed on a site for less than 180 consecutive days.
|  | G110.3 Permanent placement. | Recreational vehicles that are not fully licensed and ready for highway use, or that are to be placed on a site for more than 180 consecutive days, shall meet the requirements of Section G109 for manufactured homes.
|  | G111.1 Tanks. | Underground and above-ground tanks shall be designed, constructed, installed and anchored in accordance with ASCE 24.
|  | G112.1 Garages and accessory structures. | Garages and accessory structures shall be designed and constructed in accordance with ASCE 24.
|  | G112.2 Fences. | Fences in floodways that have the potential to block the passage of floodwaters, such as stockade fences and wire mesh fences, shall meet the requirement of Section G104.5.
|  | G112.3 Oil derricks. | Oil derricks located in flood hazard areas shall be designed in conformance with the flood loads in Sections 1603.1.7 and 1612.
|  | G112.4 Retaining walls, sidewalks and driveways. | Retaining walls, sidewalks and driveways shall meet the requirements of Section 1804.5.
|  | G112.5 Swimming pools. | Swimming pools shall be designed and constructed in accordance with ASCE 24. Above-ground swimming pools, on-ground swimming pools and in-ground swimming pools that involve placement of fill in floodways shall also meet the requirements of Section G104.5.
|  | G112.6 Decks, porches, and patios. | Decks, porches and patios shall be designed and constructed in accordance with ASCE 24.
|  | G112.7 Nonstructural concrete slabs in coastal high-hazard areas and coastal A zones. | In coastal high-hazard areas and coastal A zones, nonstructural concrete slabs used as parking pads, enclosure floors, landings, decks, walkways, patios and similar nonstructural uses are permitted beneath or adjacent to buildings and structures provided that the concrete slabs shall be constructed in accordance with ASCE 24.
|  | G112.8 Roads and watercourse crossings in regulated floodways. | Roads and watercourse crossings that encroach into regulated floodways, including roads, bridges, culverts, low-water crossings and similar means for vehicles or pedestrians to travel from one side of a watercourse to the other, shall meet the requirement of Section G104.5.
|  | G113.1 Temporary structures. | Temporary structures shall be erected for a period of less than 180 days. Temporary structures shall be anchored to prevent flotation, collapse or lateral movement resulting from hydrostatic loads, including the effects of buoyancy, during conditions of the design flood. Fully enclosed temporary structures shall have flood openings that are in accordance with ASCE 24 to allow for the automatic entry and exit of floodwaters.
|  | G113.2 Temporary storage. | Temporary storage includes storage of goods and materials for a period of less than 180 days. Stored materials shall not include hazardous materials.
|  | G113.3 Floodway encroachment. | Temporary structures and temporary storage in floodways shall meet the requirements of G104.5.
|  | G114.1 Utility and miscellaneous Group U. | Utility and miscellaneous Group U includes buildings that are accessory in character and miscellaneous structures not classified in any specific occupancy in this code, including, but not limited to, agricultural buildings, aircraft hangars (accessory to a one- or two-family residence), barns, carports, fences more than 6 feet (1829 mm) high, grain silos (accessory to a residential occupancy), greenhouses, livestock shelters, private garages, retaining walls, sheds, stables and towers.
|  | G114.2 Flood loads. | Utility and miscellaneous Group U buildings and structures, including substantial improvement of such buildings and structures, shall be anchored to prevent flotation, collapse or lateral movement resulting from flood loads, including the effects of buoyancy, during conditions of the design flood.
|  | G114.3 Elevation. | Utility and miscellaneous Group U buildings and structures, including substantial improvement of such buildings and structures, shall be elevated such that the lowest floor, including basement, is elevated to or above the design flood elevation in accordance with Section 1612 of this code.
|  | G114.4 Enclosures below design flood elevation. | Fully enclosed areas below the design flood elevation shall be constructed in accordance with ASCE 24.
|  | G114.5 Flood-damage-resistant materials. | Flood-damage-resistant materials shall be used below the design flood elevation.
|  | G114.6 Protection of mechanical, plumbing and electrical systems. | Mechanical, plumbing and electrical systems, including plumbing fixtures, shall be elevated to or above the design flood elevation.
|  | G115.1 General. | See Table G115.1 for standards that are referenced in various sections of this appendix. Standards are listed by the standard identification with the effective date, standard title, and the section or sections of this appendix referenced in the standard.

## BC-H
2022 NYC MC Section # | 2022 NYC MC Text | ICC MC Section # | 2021 ICC Text | 2022 NYC MC Text with 2021 ICC Text Overlay | NYC MC TABLE LINK | ICC NC TABLE LINK | 2018 Significant Changes (Yes/No) | 2021 Significant Changes (Yes/No)
H101.1 General. | An outdoor sign shall not be erected in a manner that would confuse or obstruct the view of or interfere with exit signs required by Chapter 10 of this code or with official traffic signs, signals or devices. Signs and sign support structures, together with their supports, braces, guys and anchors, shall be kept in repair and in proper state of preservation. The display surfaces of signs shall be kept neatly painted or posted at all times. No sign shall project beyond the street line except as per­mitted by Chapter 32 of this code. | H101.1 General. | A sign shall not be erected in a manner that would confuse or obstruct the view of or interfere with exit signs required by Chapter 10 or with official traffic signs, signals or devices. Signs and sign support structures, together with their supports, braces, guys and anchors, shall be kept in repair and in proper state of preservation. The display surfaces of signs shall be kept neatly painted or posted at all times.
H101.2 Signs exempt from permits. | The signs specified in Section 28-105.4.5 of the Administrative Code are exempt from the requirements to obtain a permit before erection. The changing of moveable parts of an approved sign that is designed for such changes, or the repainting or repositioning of display matter shall not be deemed an alteration requiring a separate permit. | H101.2 Signs exempt from permits. | The following signs are exempt from the requirements to obtain a permit before erection:
H102.1 Definitions. | The following terms are defined in Chapter 2:
H103.1 Location restrictions. | Signs shall not be erected, con­structed or maintained so as to obstruct any fire escape or any window or door or opening used as a means of egress or so as to prevent free passage from one part of a roof to any other part thereof. A sign shall not be attached in any form, shape or man­ner to a fire escape or exterior stair, nor be placed in such man­ner as to interfere with any opening required for natural light or natural ventilation. | H103.1 Location restrictions. | Signs shall not be erected, constructed or maintained so as to obstruct any fire escape or any window or door or opening used as a means of egress or so as to prevent free passage from one part of a roof to any other part thereof. A sign shall not be attached in any form, shape or manner to a fire escape, nor be placed in such manner as to interfere with any opening required for ventilation.
H103.2 Fire Department access. | Signs erected to cover doors or windows required by Section 501.3.2 for Fire Department access to existing buildings shall be provided with access pan­els to such openings.
H104.1 Identification. | Every outdoor advertising display sign hereafter erected, constructed or maintained, for which a per­mit is required, shall be marked and identified in accordance with Section 28-502.5 of the Administrative Code and as required elsewhere in this appendix. | H104.1 Identification. | Every outdoor advertising display sign hereafter erected, constructed or maintained, for which a permit is required, shall be plainly marked with the name of the person, firm or corporation erecting and maintaining such sign and shall have affixed on the front thereof the permit number issued for said sign or other method of identification approved by the building official.
H105.1 General requirements. | Signs shall be designed and constructed to comply with the provisions of this code for use of materials, loads and stresses. | H105.1 General requirements. | Signs shall be designed and constructed to comply with the provisions of this code for use of materials, loads and stresses.
H105.2 Permits, drawings and specifications. | Where a per­mit is required, as provided in Chapter 1, construction docu­ments shall be required. These documents shall show the dimensions, material and required details of construction, including loads, stresses and anchors. It is the responsibility of the property owner to have every sign for which a permit is required inspected at least once every calen­dar year. | H105.2 Permits, drawings and specifications. | Where a permit is required, as provided in Chapter 1, construction documents shall be required. These documents shall show the dimensions, material and required details of construction, including loads, stresses and anchors.
H105.3 Wind load. | Signs shall be designed and constructed to withstand wind pressure as provided for in Chapter 16 of this code. | H105.3 Wind load. | Signs shall be designed and constructed to withstand wind pressure as provided for in Chapter 16.
H105.4 Seismic load. | Signs shall be designed to meet seismic requirements of Chapter 16 of this code. | H105.4 Seismic load. | Signs designed to withstand wind pressures shall be considered capable of withstanding earthquake loads, except as provided for in Chapter 16.
H105.5 Working stresses. | In outdoor advertising display signs, the allowable working stresses shall conform to the requirements of Chapter 16 of this code. The working stresses of wire rope and its fastenings shall not exceed 25 percent of the ultimate strength of the rope or fasteners. | H105.5 Working stresses. | In outdoor advertising display signs, the allowable working stresses shall conform to the requirements of Chapter 16. The working stresses of wire rope and its fastenings shall not exceed 25 percent of the ultimate strength of the rope or fasteners.
H105.6 Attachment. | Signs attached to masonry, concrete or steel shall be safely and securely fastened by means of metal anchors, bolts or approved expansion screws of sufficient size and anchorage to safely support the loads applied. | H105.6 Attachment. | Signs attached to masonry, concrete or steel shall be safely and securely fastened by means of metal anchors, bolts or approved expansion screws of sufficient size and anchorage to safely support the loads applied.
H106.1 Illumination. | A sign shall not be illuminated by other than electrical means, and electrical devices and wiring shall be installed in accordance with the requirements of the New York City Electrical Code. Any open spark or flame shall not be used for display purposes unless specifically approved. | H106.1 Illumination. | A sign shall not be illuminated by other than electrical means, and electrical devices and wiring shall be installed in accordance with the requirements of NFPA 70. Any open spark or flame shall not be used for display purposes unless specifically approved.